## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 26-03-2026 | [28 empty] | Date: | 26-03-2026 | [28 empty] | Date: | 26-03-2026 | [28 empty] | Date: | 26-03-2026 | [28 empty] | Date: | 26-03-2026 | [17 empty] | Date: | 26-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [17 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 342.010 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 344 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11 | 18 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 470 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 521 | 0 | 0 | 8 | 350 | 0 | 69 | 40 | 5 | 203 | 42 | 0 | 51 | 0 | 0 | 8 | 0 | 110 | 0 | 0 | 0 | 320 | 0 | 383 | 41 | 0 | 159 | 0 | 0 | 0 | 5 | 17 | 100 | 0 | 95 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 5199 | 886 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 504 | 0 | 0 | 0 | 967.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 414 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 125 | 220 | 0 | 0 | 960 | 0 | 4936.72 | 10135.72 | 86.13
01:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 345 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11 | 18 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 470 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 520 | 0 | 0 | 8 | 340 | 0 | 99 | 40 | 5 | 200 | 42 | 0 | 51 | 0 | 0 | 8 | 0 | 106 | 0 | 0 | 0 | 320 | 0 | 386 | 41 | 0 | 158 | 0 | 0 | 0 | 5 | 17 | 100 | 0 | 95 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 5202 | 886 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 826.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 406 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 125 | 220 | 0 | 0 | 900 | 0 | 4631.06 | 9833.06 | 86.13
02:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 339 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11 | 18 | 0 | 425 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 470 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 433 | 0 | 0 | 8 | 315 | 0 | 147 | 40 | 5 | 200 | 42 | 0 | 103 | 0 | 0 | 8 | 0 | 106 | 0 | 0 | 0 | 320 | 0 | 386 | 41 | 0 | 140 | 0 | 0 | 0 | 5 | 17 | 100 | 0 | 95 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 5175 | 871 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 827.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 378 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 125 | 220 | 0 | 0 | 800 | 0 | 4377.64 | 9552.64 | 86.12
03:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 339 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11 | 18 | 0 | 420 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 350 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 422 | 0 | 0 | 8 | 305 | 0 | 154 | 5 | 5 | 196 | 42 | 0 | 103 | 0 | 0 | 8 | 0 | 104 | 0 | 0 | 0 | 315 | 0 | 386 | 41 | 0 | 140 | 0 | 0 | 0 | 5 | 17 | 100 | 0 | 95 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 4984 | 871 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 829.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 360 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 125 | 220 | 0 | 0 | 680 | 0 | 4229.8 | 9213.8 | 86.12
04:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 330 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 11 | 18 | 0 | 430 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 424 | 0 | 0 | 0 | 320 | 0 | 206 | 0 | 0 | 194 | 0 | 0 | 103 | 0 | 0 | 19 | 0 | 100 | 0 | 0 | 0 | 315 | 0 | 351 | 41 | 0 | 140 | 0 | 0 | 0 | 0 | 17 | 100 | 0 | 95 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 4917 | 871 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 829.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 388 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 125 | 220 | 0 | 0 | 520 | 0 | 4092.94 | 9009.94 | 86.11
05:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 319 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 11 | 18 | 0 | 345 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 424 | 0 | 0 | 0 | 320 | 0 | 335 | 0 | 0 | 194 | 0 | 0 | 103 | 0 | 0 | 19 | 0 | 98 | 0 | 0 | 0 | 320 | 0 | 330 | 41 | 0 | 142 | 0 | 0 | 0 | 0 | 17 | 100 | 0 | 95 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 4824 | 872 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 831.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 386 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 50 | 220 | 0 | 0 | 500 | 0 | 3975.05 | 8799.05 | 86.11
06:00 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 316 | 0 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 11 | 18 | 0 | 320 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0.01 | 40 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 250 | 0 | 345 | 0 | 0 | 184 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 94 | 0 | 0 | 0 | 310 | 0 | 330 | 41 | 0 | 139 | 0 | 0 | 0 | 0 | 17 | 100 | 0 | 95 | 0 | 0 | 0 | 111 | 0 | 0 | 0 | 4584.01 | 871 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 829.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 359 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 50 | 180 | 0 | 0 | 500 | 0 | 3859.26 | 8443.27 | 86.1
07:00 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 327 | 0 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 4 | 0 | 11 | 18 | 0 | 340 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0.57 | 40 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 309 | 3 | 0 | 0 | 319 | 0 | 345 | 0 | 0 | 192 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 98 | 0 | 11 | 0 | 320 | 0 | 343 | 41 | 0 | 146 | 2 | 0 | 0 | 0 | 17 | 101 | 0 | 95 | 0 | 0 | 0 | 163 | 0.3 | 7.21 | 0 | 4745.08 | 882 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 385 | 0 | 0 | 0 | 832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.08 | 11 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 167 | 0 | 414 | 0 | 0.6 | 0 | 50 | 0 | 3 | 0 | 0 | 0 | 0 | 0.2 | 21 | 0.07 | 0 | 140 | 65 | 180 | 0 | 0 | 500 | 0 | 4031.95 | 8777.03 | 86.1
08:00 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 347 | 0 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 12 | 0 | 12.5 | 18 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.55 | 40 | 0 | 22 | 300 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 380 | 5 | 0 | 0 | 314 | 0 | 305 | 19 | 0 | 187 | 0 | 0 | 70 | 0 | 0 | 14 | 0 | 102 | 0 | 30 | 0 | 325 | 0 | 330 | 41 | 0 | 159 | 5 | 0 | 0 | 5 | 17 | 101 | 0 | 0 | 0 | 10 | 8 | 160 | 0.9 | 19.89 | 0 | 4794.84 | 886 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 385 | 0 | 0 | 0 | 827.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.31 | 40 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 181 | 0 | 402 | 0 | 2.15 | 0 | 50 | 0 | 11 | 0 | 0 | 0 | 0 | 2.7 | 70 | 0.13 | 0 | 140 | 65 | 180 | 0 | 0 | 500 | 0 | 4199.97 | 8994.81 | 86.09
09:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 338 | 0 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 20 | 0 | 12.5 | 18 | 0 | 320 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2.44 | 40 | 0 | 22 | 300 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 300 | 13 | 0 | 0 | 308 | 0 | 300 | 51 | 0 | 188 | 0 | 0 | 70 | 0 | 0 | 14 | 0 | 100 | 0 | 48 | 0 | 315 | 0 | 324 | 42 | 0 | 155 | 8 | 0 | 0 | 5 | 20 | 101 | 0 | 0 | 0 | 16 | 8 | 159 | 1.5 | 34.48 | 0 | 4759.92 | 886 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 374 | 0 | 0 | 0 | 830.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.84 | 67 | 0 | 0 | 41.8 | 0 | 0 | 0 | 0 | 194 | 0 | 410 | 0 | 3.71 | 0 | 51 | 0 | 21 | 0 | 0 | 0 | 0 | 3.9 | 130 | 0.31 | 0 | 140 | 65 | 180 | 0 | 0 | 500 | 0 | 4335.3 | 9095.22 | 86.09
10:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 327 | 0 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 28 | 0 | 12.5 | 14 | 0 | 320 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 3.22 | 40 | 0 | 21 | 300 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 309 | 16 | 0 | 0 | 305 | 0 | 305 | 51 | 0 | 193 | 0 | 0 | 70 | 0 | 0 | 14 | 0 | 112 | 0 | 61 | 0 | 310 | 0 | 330 | 41 | 0 | 151 | 10 | 8 | 0 | 5 | 20 | 100 | 0 | 0 | 0 | 16 | 8 | 159 | 1.9 | 44.86 | 0 | 4807.48 | 889 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 370 | 0 | 0 | 0 | 832.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.57 | 90 | 0 | 0 | 53.75 | 0 | 0 | 0 | 0 | 193 | 0 | 358 | 0 | 4.7 | 0 | 52 | 0 | 29 | 0 | 0 | 0 | 0 | 5.7 | 167 | 0.54 | 0 | 140 | 65 | 180 | 0 | 0 | 500 | 0 | 4433.3 | 9240.78 | 86.08
11:00 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 346 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 31 | 0 | 12.5 | 14 | 0 | 370 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 3.64 | 40 | 0 | 21 | 300 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 309 | 17 | 0 | 0 | 333 | 0 | 320 | 51 | 0 | 209 | 0 | 0 | 70 | 0 | 0 | 14 | 0 | 122 | 0 | 71 | 0 | 320 | 0 | 360 | 42 | 0 | 157 | 12 | 17 | 0 | 5 | 20 | 100 | 0 | 0 | 0 | 16 | 8 | 157 | 2.2 | 49.3 | 0 | 5050.64 | 888 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 375 | 0 | 0 | 0 | 839.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.54 | 102 | 0 | 0 | 60.77 | 0 | 0 | 0 | 0 | 203 | 0 | 408 | 0 | 5.43 | 0 | 53 | 0 | 33 | 0 | 0 | 0 | 0 | 6.8 | 195 | 0.66 | 0 | 140 | 65 | 180 | 0 | 0 | 500 | 0 | 4594.44 | 9645.08 | 86.08
12:00 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 357 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 32 | 0 | 15.5 | 14 | 0 | 440 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 3.72 | 76 | 0 | 21 | 300 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 425 | 19 | 0 | 18 | 365 | 0 | 340 | 51 | 0 | 211 | 37 | 0 | 72 | 0 | 0 | 11 | 0 | 126 | 0 | 74 | 0 | 320 | 0 | 400 | 42 | 0 | 157 | 12 | 17 | 0 | 5 | 30 | 100 | 0 | 0 | 0 | 16 | 8 | 152 | 2.3 | 50.82 | 0 | 5493.34 | 888 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 380 | 0 | 0 | 0 | 848.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.27 | 115 | 0 | 0 | 63.76 | 0 | 0 | 0 | 0 | 200 | 0 | 414 | 0 | 5.69 | 0 | 53 | 0 | 34 | 0 | 0 | 0 | 0 | 7.2 | 201 | 0.65 | 0 | 200 | 65 | 220 | 0 | 0 | 550 | 0 | 4788.98 | 10282.32 | 86.07
13:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 365 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 31 | 0 | 15 | 14 | 0 | 440 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 3.57 | 80 | 0 | 21 | 360 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 557 | 18 | 0 | 53 | 370 | 0 | 335 | 51 | 0 | 211 | 42 | 0 | 95 | 0 | 0 | 17 | 0 | 130 | 0 | 70 | 0 | 325 | 0 | 400 | 42 | 0 | 154 | 12 | 17 | 0 | 5 | 30 | 100 | 0 | 0 | 0 | 26 | 24 | 152 | 2.2 | 49.16 | 0 | 5796.93 | 889 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 502 | 0 | 0 | 0 | 977.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.48 | 104 | 0 | 0 | 38.91 | 0 | 0 | 0 | 0 | 202 | 0 | 408 | 0 | 4.22 | 0 | 53 | 0 | 37 | 0 | 0 | 0 | 0 | 7.1 | 201 | 0.61 | 0 | 258 | 65 | 220 | 0 | 0 | 762 | 0 | 5262.84 | 11059.77 | 86.07
14:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 359 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 5 | 0 | 15 | 14 | 0 | 470 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 3.18 | 70 | 0 | 21 | 470 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 552 | 17 | 0 | 8 | 326 | 0 | 335 | 51 | 0 | 192 | 5 | 0 | 96 | 0 | 0 | 19 | 0 | 138 | 0 | 62 | 0 | 325 | 0 | 359 | 42 | 0 | 153 | 11 | 17 | 0 | 5 | 30 | 100 | 0 | 0 | 0 | 35 | 24 | 151 | 2 | 44.52 | 0 | 5647.7 | 888 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 543 | 0 | 0 | 0 | 1055.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.89 | 95 | 0 | 0 | 56.83 | 0 | 0 | 0 | 0 | 201 | 0 | 409 | 0 | 4.95 | 0 | 53 | 0 | 30 | 0 | 0 | 0 | 0 | 6.4 | 182 | 0.55 | 0 | 307 | 60 | 220 | 0 | 0 | 972 | 0 | 5603.07 | 11250.77 | 86.06
15:00 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 314 | 0 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 11 | 0 | 21 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.48 | 80 | 0 | 21 | 470 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 560 | 13 | 0 | 0 | 330 | 0 | 295 | 51 | 0 | 197 | 5 | 0 | 94 | 0 | 0 | 19 | 0 | 142 | 0 | 49 | 0 | 315 | 0 | 344 | 42 | 0 | 153 | 8 | 17 | 0 | 5 | 30 | 100 | 0 | 0 | 0 | 35 | 24 | 99 | 1.5 | 35.82 | 0 | 5459.8 | 888 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 534 | 0 | 0 | 0 | 1063.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.39 | 23 | 0 | 0 | 42.47 | 0 | 0 | 0 | 0 | 194 | 0 | 406 | 0 | 3.79 | 0 | 55 | 0 | 25 | 0 | 0 | 0 | 0 | 3 | 143 | 0.42 | 0 | 284 | 60 | 220 | 0 | 0 | 1080 | 0 | 5511.56 | 10971.36 | 86.05
16:00 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 306 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 13 | 0 | 21 | 14 | 0 | 460 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1.34 | 80 | 0 | 15 | 470 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 560 | 9 | 0 | 0 | 335 | 0 | 305 | 51 | 0 | 199 | 5 | 0 | 96 | 0 | 0 | 19 | 0 | 138 | 0 | 31 | 0 | 310 | 0 | 344 | 42 | 0 | 144 | 5 | 17 | 0 | 50 | 30 | 100 | 0 | 0 | 0 | 45 | 45 | 112 | 0.9 | 23.11 | 0 | 5516.35 | 888 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 444 | 0 | 0 | 0 | 967.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.64 | 39 | 0 | 0 | 24.85 | 0 | 0 | 0 | 0 | 182 | 0 | 378 | 0 | 2.28 | 0 | 55 | 0 | 15 | 0 | 0 | 0 | 0 | 1.9 | 91 | 0.25 | 0 | 267 | 60 | 220 | 0 | 0 | 1000 | 0 | 5071.4 | 10587.75 | 86.05
17:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 309 | 0 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 4 | 0 | 17 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49 | 80 | 0 | 17 | 470 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 560 | 3 | 0 | 0 | 360 | 0 | 295 | 51 | 0 | 192 | 5 | 0 | 96 | 0 | 0 | 19 | 0 | 132 | 0 | 11 | 0 | 310 | 0 | 326 | 42 | 20 | 137 | 2 | 17 | 0 | 52 | 30 | 100 | 0 | 0 | 0 | 45 | 45 | 110 | 0.3 | 9.06 | 0 | 5439.85 | 888 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 445 | 0 | 0 | 0 | 961.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.48 | 12 | 0 | 0 | 9.48 | 0 | 0 | 0 | 0 | 174 | 0 | 358 | 0 | 0.82 | 0 | 54 | 0 | 6 | 0 | 0 | 0 | 0 | 1.3 | 36 | 0.1 | 0 | 265 | 60 | 220 | 0 | 0 | 1000 | 0 | 4894.84 | 10334.69 | 86.04
18:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 332 | 0 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 17 | 17 | 14 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 21 | 470 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 575 | 0 | 0 | 0 | 330 | 0 | 320 | 51 | 0 | 200 | 5 | 0 | 97 | 0 | 0 | 19 | 0 | 122 | 0 | 1 | 0 | 305 | 0 | 361 | 42 | 20 | 137 | 0 | 17 | 0 | 52 | 30 | 101 | 0 | 0 | 0 | 45 | 45 | 152 | 0 | 0.39 | 0 | 5589.39 | 888 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 495 | 0 | 0 | 0 | 1072.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 398 | 0 | 0.05 | 0 | 54 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 3 | 0 | 0 | 275 | 60 | 220 | 0 | 0 | 1000 | 0 | 5019.4 | 10608.79 | 86.04
19:00 | 0 | 0 | 2 | 192 | 0 | 0 | 0 | 0 | 343 | 0 | 315 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 225 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 35 | 17 | 14 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 21 | 470 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 612 | 0 | 6 | 0 | 290 | 0 | 305 | 51 | 0 | 192 | 5 | 1 | 100 | 0 | 0 | 20 | 0 | 134 | 0 | 0 | 0 | 325 | 0 | 354 | 42 | 30 | 155 | 0 | 24 | 0 | 80 | 30 | 99 | 0 | 0 | 0 | 51 | 51 | 155 | 0 | 0 | 0 | 5966 | 888 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 591 | 0 | 0 | 0 | 1398.45 | 0 | 0 | 0 | 30 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 414 | 0 | 0 | 0 | 55 | 50 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 60 | 220 | 0 | 0 | 1100 | 0 | 5753.45 | 11719.45 | 86.03
19:30 | 0 | 0 | 25 | 192 | 0 | 0 | 0 | 0 | 329 | 0 | 293 | 31.5 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 225 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 52 | 17 | 14 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 21 | 470 | 0 | 0 | 5 | 0 | 0 | 221 | 0 | 0 | 0 | 612 | 0 | 50 | 0 | 295 | 0 | 290 | 51 | 0 | 183 | 5 | 34 | 100 | 0 | 0 | 20 | 0 | 134 | 0 | 0 | 0 | 310 | 0 | 330 | 42 | 30 | 154 | 0 | 24 | 0 | 80 | 30 | 101 | 0 | 0 | 0 | 96 | 74 | 158 | 0 | 0 | 0 | 6090.5 | 883 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 0 | 0 | 0 | 1446.81 | 0 | 0 | 0 | 70 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 414 | 0 | 0 | 0 | 55 | 93 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 60 | 220 | 0 | 0 | 1190 | 0 | 6051.81 | 12142.31
20:00 | 0 | 0 | 33 | 192 | 0 | 0 | 0 | 0 | 341 | 0 | 295 | 30.2 | 0 | 0 | 0 | 15 | 0 | 0 | 53 | 0 | 225 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 52 | 17 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 21 | 470 | 0 | 0 | 13 | 0 | 0 | 221 | 0 | 0 | 0 | 612 | 0 | 50 | 0 | 320 | 0 | 300 | 51 | 0 | 186 | 5 | 29 | 100 | 0 | 0 | 20 | 0 | 138 | 0 | 0 | 0 | 310 | 0 | 340 | 42 | 30 | 154 | 0 | 24 | 0 | 80 | 30 | 100 | 0 | 0 | 0 | 98 | 74 | 159 | 0 | 0 | 0 | 6107.2 | 884 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 0 | 0 | 0 | 1454.81 | 0 | 0 | 0 | 70 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 362 | 0 | 0 | 0 | 54 | 93 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 60 | 220 | 0 | 0 | 1215 | 0 | 6013.81 | 12121.01 | 86.02
21:00 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 332 | 0 | 284 | 30.1 | 0 | 0 | 0 | 15 | 0 | 0 | 47 | 0 | 225 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 52 | 17 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 21 | 470 | 0 | 0 | 25 | 0 | 0 | 222 | 0 | 0 | 0 | 612 | 0 | 50 | 0 | 350 | 0 | 305 | 51 | 0 | 182 | 5 | 34 | 100 | 0 | 0 | 20 | 0 | 136 | 0 | 0 | 0 | 310 | 0 | 337 | 41 | 30 | 152 | 0 | 24 | 0 | 80 | 30 | 100 | 0 | 0 | 0 | 98 | 78 | 159 | 0 | 0 | 0 | 6107.1 | 884 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 1458.14 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 352 | 0 | 0 | 0 | 54 | 95 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 60 | 220 | 0 | 0 | 1244 | 0 | 5970.14 | 12077.24 | 86.01
22:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 331 | 0 | 289 | 30.5 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 225 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 35 | 17 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 22 | 470 | 0 | 0 | 25 | 0 | 0 | 222 | 0 | 0 | 0 | 612 | 0 | 50 | 0 | 350 | 0 | 295 | 51 | 0 | 184 | 5 | 32 | 100 | 0 | 0 | 20 | 0 | 140 | 0 | 0 | 0 | 310 | 0 | 320 | 41 | 30 | 151 | 0 | 24 | 0 | 80 | 30 | 100 | 0 | 0 | 0 | 45 | 45 | 159 | 0 | 0 | 0 | 5988.5 | 885 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 0 | 0 | 0 | 1457.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 352 | 0 | 0 | 0 | 54 | 95 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 60 | 220 | 0 | 0 | 1244 | 0 | 5893.74 | 11882.24 | 86
23:00 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 327 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 13 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 23 | 470 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 350 | 0 | 300 | 51 | 0 | 196 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 140 | 0 | 0 | 0 | 305 | 0 | 329 | 41 | 30 | 151 | 0 | 22 | 0 | 80 | 30 | 100 | 0 | 0 | 0 | 24 | 8 | 160 | 0 | 0 | 0 | 5697 | 884 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 0 | 0 | 0 | 1472.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 399 | 0 | 0 | 0 | 54 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 65 | 220 | 0 | 0 | 1244 | 0 | 5783.91 | 11480.91 | 85.99
Total KWH | 0 | 0 | 48480 | 4557764 | 0 | 0 | 0 | 0 | 8146800 | 0 | 7027010 | 106200 | 0 | 0 | 0 | 24087 | 0 | 0 | 185760 | 0 | 4494300 | 0 | 0 | 0 | 0 | 7034239 | 0 | 0 | 207010 | 184800 | 345600 | 404280 | 0 | 10081818.18 | 0 | 0 | 0 | 0 | 98880 | 104210 | 0 | 0 | 0 | 0 | 25797 | 1434600 | 0 | 375840 | 9650909.09 | 0 | 0 | 85440 | 0 | 0 | 4941447 | 0 | 0 | 0 | 11574544 | 134595 | 200727 | 117091 | 7878000 | 0 | 6708000 | 1016849 | 21120 | 4823000 | 283320 | 115200 | 2053995 | 0 | 0 | 402100 | 0 | 2850240 | 0 | 520845 | 0 | 7680000 | 0 | 8582000 | 986000 | 199200 | 3586745 | 86208 | 231024 | 0 | 660480 | 585792 | 2388000 | 0 | 691120 | 0 | 688800 | 540000 | 3442560 | 15550 | 370880 | 0 | 128999256.27 | 21373090 | 9262656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 637920 | 11003634 | 0 | 0 | 0 | 24499137 | 0 | 0 | 96000 | 124608 | 172704 | 0 | 0 | 0 | 0 | 396784 | 736260 | 0 | 0 | 429744 | 0 | 0 | 0 | 0 | 4673282 | 0 | 9363927 | 0 | 37920 | 0 | 1244509 | 343631 | 241633 | 207244 | 0 | 0 | 0 | 48539.16 | 1433520 | 4338 | 0 | 5433000 | 1777000 | 5306790 | 0 | 0 | 20740363.64 | 0 | 119588233.8 | 248587490.07

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 27-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-03-2026 | during | 27-03-2026 | during | 27-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 191 | 192 | 190 | 190 | 190 | 190 | GBC 1 and 3 under maintenance
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 357 | 329 | 412 | 412 | 370 | 370 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 170 | 225 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 270 | 330 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 31.5 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 15.5 | 17 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 22 | 22 | 22.5 | 22.5 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 52 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 440 | 530 | 584 | 584 | 526 | 526 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 320 | 293 | 718 | 718 | 330 | 330 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 52 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1809.5 | 2090.5 | 5876.22 | 5845.22 | 3123.02 | 3092.02
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 5 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 76 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 221 | 220 | 225 | 220 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 64 | 56 | 64 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 68 | 68 | 68 | 68 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 21 | 21 | 40 | 40 | 40 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.72 | 0 | 3.85 | 0 | 3.85 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 425 | 612 | 1224 | 1224 | 612 | 612 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 8 | 0 | 7 | 0 | 7 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 300 | 470 | 1045 | 1045 | 300 | 471 | Plant availability less
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1066.72 | 1409 | 3994.71 | 3977.86 | 2113.35 | 2267.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 211 | 183 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 340 | 290 | 342.01 | 342.01 | 306 | 306 | Able to ON FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 365 | 295 | 393 | 393 | 351 | 351 | FGMO
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 37 | 5 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 55 | 55 | 20 | 20 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 18 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 50 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 16 | 16 | 16 | 16 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 72 | 100 | 163 | 163 | 100 | 100 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 126 | 134 | 84 | 78 | 142 | 142 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 34 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 74 | 0 | 74 | 0 | 74 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2876.261 | 1305 | 1162 | 2404.36 | 2324.36 | 2120.2 | 2046.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-03-2026 | during | 27-03-2026 | during | 27-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 152 | 158 | 157.5 | 157.5 | 10 | 10 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.3 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 74 | 60 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 16 | 96 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.82 | 0 | 45.12 | 0 | 45.12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 229.12 | 328 | 411.12 | 429 | 216.12 | 252
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 41 | 41 | 41 | 41 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 30 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 154 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 100 | 101 | 100 | 100 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 0 | 0 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 80 | 83 | 83 | 80 | 80 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 100 | 100 | plant availability zero
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 24 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 400 | 330 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1083 | 1101 | 1168 | 1168 | 1054 | 1054
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 888 | 883 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 390 | 390 | 410 | 410 | 400 | 400 | -
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 95 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 380 | 607 | 0 | 0 | 617 | 617 | plant availability zero
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1753 | 1880 | 2368 | 2278 | 2214.1 | 2124.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 65 | 60 | 65 | 65 | 65 | 65 | GT-1 & ST under maint
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 550 | 1190 | 1244 | 1244 | 1184 | 1184 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 75 | 75 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 307 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.65 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1035.65 | 1777 | 2097 | 2096 | 1868 | 1867
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 58.27 | 0 | 64 | 0 | 64 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 200 | 197 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 22 | 22 | 21 | 21 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 50 | 50 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.69 | 0 | 6 | 0 | 6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 848.41 | 1446.81 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 63.76 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 115 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1705.13 | 2197.81 | 3156.87 | 2925.87 | 2618.49 | 2387.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 53 | 55 | 53 | 53 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 49 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.2 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 93 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 201 | 0 | 189.67 | 0 | 189.67 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 295.2 | 197 | 525.87 | 301 | 507.87 | 283
System Total |  |  |  |  | 28823.2 | 29275.503 | 10282.32 | 12142.31 | 22002.15 | 21345.31 | 15835.15 | 15373.31
Forecast Scenario (27-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 10700 |  | 0 |  | 10700
|  |  |  | 1:00 | 10250 |  | 0 |  | 10250
|  |  |  | 2:00 | 10040 |  | 0 |  | 10040
|  |  |  | 3:00 | 9550 |  | 0 |  | 9550
|  |  |  | 4:00 | 9330 |  | 0 |  | 9330
|  |  |  | 5:00 | 9090 |  | 0 |  | 9090
|  |  |  | 6:00 | 8620 |  | 0 |  | 8620
|  |  |  | 7:00 | 8330 |  | 0 |  | 8330
|  |  |  | 8:00 | 8190 |  | 0 |  | 8190
|  |  |  | 9:00 | 8250 |  | 0 |  | 8250
|  |  |  | 10:00 | 8460 |  | 0 |  | 8460
|  |  |  | 11:00 | 8910 |  | 0 |  | 8910
|  |  |  | 12:00 | 9860 |  | 0 |  | 9860
|  |  |  | 13:00 | 10940 |  | 0 |  | 10940
|  |  |  | 14:00 | 9770 |  | 0 |  | 9770
|  |  |  | 15:00 | 9450 |  | 0 |  | 9450
|  |  |  | 16:00 | 9160 |  | 0 |  | 9160
|  |  |  | 17:00 | 8910 |  | 0 |  | 8910
|  |  |  | 18:00 | 9260 |  | 0 |  | 9260
|  |  |  | 18:30 | 9800 |  | 0 |  | 9800
|  |  |  | 19:00 | 10460 |  | 0 |  | 10460
|  |  |  | 19:30 | 10950 |  | 0 |  | 10950
|  |  |  | 20:00 | 11150 |  | 0 |  | 11150
|  |  |  | 21:00 | 11230 |  | 0 |  | 11230
|  |  |  | 22:00 | 11040 |  | 0 |  | 11040
|  |  |  | 23:00 | 10380 |  | 0 |  | 10380
Probable Maximum Temperature: |  |  | 35.00°C
Probable Maximum Demand at Day Peak: |  |  | 9860.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11230.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11230.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 231.33 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:17 hrs on 27-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 26-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10282.32 | MW | 12:00 Hr. | Energy Generated |  |  | 248.5875 |  | MKWHr.
| Day Peak Demand |  |  | 10282.32 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 12142.31 | MW | 19:30 Hr. | Energy Demand |  |  | 248.5875 |  | MKWHr.
| Evening Peak Demand |  |  | 12142.31 | MW | 19:30 Hr. | Maximum Temperature |  |  | 31.9 |  | °C
| Minimum Generation of the Day |  |  | 8443.27 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 937.82 |  | MMCFD
| Maximum Generation of the Day |  |  | 12142.31 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.0995 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 42.0918 | 0 | 0.54933 | 0 | 0 | 0.20701 | 0 | 0 | 42.8481 | Gas | 130.2251 | Gas | 457097848.3306
| Chattogram Zone |  |  | 5.3173 | 21.2255 | 0.18965 | 0 | 1.4346 | 0.16039 | 0 | 0.09888 | 28.4263 | Coal | 59.647 | Coal | 399410122.9589
| Cumilla Zone |  |  | 23.3035 | 0 | 0.31593 | 0 | 0 | 0.52085 | 2.8502 | 0 | 26.9905 | HFO | 3.1319 | HFO | 51285778.86
| Mymensingh Zone |  |  | 3.4426 | 0 | 1.2288 | 0 | 0 | 0.38643 | 0 | 0 | 5.0578 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.5904 | 0 | 0 | 0 | 0 | 0.086208 | 0 | 0 | 25.6766 | Hydro | 1.4346 | Hydro | 143460
| Khulna Zone |  |  | 9.2627 | 11.0036 | 0 | 0 | 0 | 0.63792 | 21.3731 | 0 | 42.2773 | Solar | 5.3275 | Solar | 85746316.462
| Barishal Zone |  |  | 7.0838 | 26.1734 | 0 | 0 | 0 | 0.004338 | 0 | 0 | 33.2615 | Import | 48.7225 | Import | 272521840.63
| Rajshahi Zone |  |  | 14.1332 | 0 | 0.29731 | 0 | 0 | 1.6007 | 24.4991 | 0 | 40.5304 | Wind | 0.09888 | Wind | 1454524.8
| Rangpur Zone |  |  | 0 | 1.2445 | 0.55088 | 0 | 0 | 1.7237 | 0 | 0 | 3.5191
| Total |  |  | 130.2251 | 59.647 | 3.1319 | 0 | 1.4346 | 5.3275 | 48.7225 | 0.09888 | 248.5875
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 457097848.3306 |  | Hydro | 143460
|  |  |  | Coal | 399410122.9589 |  | Solar | 85746316.462
|  |  |  | HFO | 51285778.86 |  | Import | 272521840.63
|  |  |  | HSD | 0 |  | Wind | 1454524.8
[5 empty] | Total: | 126,76,59,892 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.3731 | Peak Hr Flow | 883.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 7475945.45 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.4991 | Peak Hr Flow | 1446.81 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1683 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.8502 | Peak Hr Flow | 134.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1698 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.7225 | Peak Hr Flow | 2463.81 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3386
|  |  |  | Chattogram |  | 0 |  | 1381
|  |  |  | Cumilla |  | 0 |  | 1271
|  |  |  | Mymensingh |  | 0 |  | 1071
|  |  |  | Sylhet |  | 0 |  | 514
|  |  |  | Khulna |  | 0 |  | 1605
|  |  |  | Barishal |  | 0 |  | 403
|  |  |  | Rajshahi |  | 0 |  | 1371
|  |  |  | Rangpur |  | 0 |  | 819
|  |  |  | Total |  | 0 |  | 11821
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:07 | Daudkandi 132/33kV S/S Transformer-3 LT is restored.
| 12:00 |  | Day peak Generation : 10277 MW
| 14:23 | 15:02 | Chowmuhani-Feni 132 kV Ckt-1 Tripped from Feni 132/33kV end showing 21-Ph-C, 79-A/R Fail,
51x3 51G-Inst-C relays.
| 19:36 | 20:26 | Thakurgaon 132/33kV S/S T-3(432T) LT Forced S/D Due to LT side R-Phase bushing red hot
| 19:36 | 20:26 | Thakurgaon 132/33kV S/S T-3(432T) HT Forced S/D Due to LT side R-Phase bushing red hot
| 22:24 |  | Khulshi-Sholoshohor ckt-2 CB opened from Khulshi end as per instruction from NLDC
| 02:50 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- STG
| 03:14 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- GT
| 06:00 |  | Minimum generation 9064 MW
| 06:56 |  | Jashore 132/33kV S/S Cap. Bank-1 Tripped showing 132kv capacitor bank relays.
| 06:56 |  | Jashore 132/33kV S/S Cap. Bank-2 Tripped showing 132kv capacitor bank relays.
| 07:17 | 07:48 | Siddhirganj 132/33kV S/S T-1 HT Scheduled S/D Due to Maintenance work (painting)
| 07:17 | 07:49 | Siddhirganj 132/33kV S/S T-1 LT Scheduled S/D Due to Maintenance work
| 07:59 |  | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 26-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 192 | 4557764 | GBC 1 and 3 under maintenance
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | On test
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 329 | 8146800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4494300 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7034239 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 31.5 | 106200 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 345600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 404280 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 48480 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 24087 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 0 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 52 | 185760 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 207010 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 530 | 10081818.18 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 293 | 7027010 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 52 | 184800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2090.5 | 42848148.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 134595 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 5 | 85440 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1434600 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 4941447 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 104210 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 21 | 375840 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 25797 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 11574544 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 98880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 470 | 9650909.09 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 1409 | 28426262.09
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 183 | 4823000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 290 | 6708000 | Able to ON FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 295 | 7878000 | FGMO
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 5 | 283320 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 21120 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 117091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1016849 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 200727 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2053995 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 134 | 2850240 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 402100 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 34 | 115200 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 520845 | -
Cumilla Area Total |  |  |  |  | 2876.261 | 1162 | 26990487
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 158 | 3442560 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15550 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 74 | 540000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 96 | 688800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 370880 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 328 | 5057790
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 86208 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 986000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 199200 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3586745 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 101 | 2388000 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 585792 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 660480 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 691120 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 231024 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7680000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 330 | 8582000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1101 | 25676569
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 883 | 21373090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 390 | 9262656 | -
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 637920 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 607 | 11003634 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1880 | 42277300
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 60 | 1777000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1190 | 20740363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5306790 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5433000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4338 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1777 | 33261491.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 396784 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 96000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 197 | 4673282 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9363927 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 172704 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 70 | 124608 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 37920 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1446.81 | 24499137 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 429744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 736260 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2197.81 | 40530366
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 55 | 1244509 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 207244 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 48539.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 93 | 343631 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 241633 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1433520 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 197 | 3519076.16
Eastern Grid Total |  |  |  |  | 17423.308 | 6090.5 | 128999256.27
Western Grid Total |  |  |  |  | 11852.195 | 6051.81 | 119588233.8
National Grid Total |  |  |  |  | 29275.503 | 12142.31 | 248587490.07
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 26-03-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7623.12 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4197.4 | MW
i) Dhaka area |  |  | 3385.72 |  | MW | i) Khulna area |  |  |  | 1604.7 | MW
ii) Chattogram area |  |  | 1381.4 |  | MW | ii) Barishal area |  |  |  | 402.7 | MW
iii) Cumilla area |  |  | 1271 |  | MW | iii) Rajshahi area |  |  |  | 1371 | MW
iv) Mymensingh area |  |  | 1071 |  | MW | iv) Rangpur area |  |  |  | 819 | MW
v) Sylhet area |  |  | 514 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11820.52 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 58 | 15:00 | 133 | Natore | 145 | 19:30
2 | AKSML | 17.7 | 02:00 | 68 | Hathazari | 75 | 19:30 | 134 | Nawabganj | 49.6 | 14:00
3 | Aftabnagar | 26 | 19:00 | 69 | Hatirjheel | 20 | 14:00 | 135 | Netrakona | 112 | 19:30
4 | Agargaon | 74 | 14:00 | 70 | Ishurdi | 61 | 19:30 | 136 | New | 36 | 19:30
5 | Agrabad | 48 | 20:00 | 71 | Jaldhaka | 65 | 19:00 | 137 | Niamatpur | 90 | 19:00
6 | Amnura | 39 | 19:00 | 72 | Jamalpur | 119 | 19:00 | 138 | Noapara | 39 | 19:00
7 | Ashuganj | 62 | 13:00 | 73 | Jashore | 140 | 20:00 | 139 | PHP | 8 | 10:00
8 | BSRM | 191 | 18:30 | 74 | Jhenaidah | 99 | 19:00 | 140 | Pabna | 80 | 19:30
9 | Bagerhat | 77 | 13:00 | 75 | Joydebpur | 80 | 19:30 | 141 | Palashbari | 110 | 13:00
10 | Bajitpur | 83 | 18:30 | 76 | Joypurhat | 58 | 19:00 | 142 | Panchagarh | 50 | 19:00
11 | Bakerganj | 10 | 22:00 | 77 | Juldah | 19 | 23:00 | 143 | Patiya | 10 | 18:30
12 | Bakulia | 68 | 22:00 | 78 | KSRM | 8 | 00:00 | 144 | Patuakhali | 61.7 | 22:00
13 | Banani | 13.2 | 18:30 | 79 | Kabirpur | 129 | 22:00 | 145 | Payra | 30 | 19:00
14 | Bangabhaban | 4 | 18:00 | 80 | Kachua | 84 | 20:00 | 146 | Postogola | 31 | 13:00
15 | Barapukuria | 53 | 13:00 | 81 | Kaliganj | 30 | 19:00 | 147 | Pubail | 19 | 14:00
16 | Barguna | 20 | 21:00 | 82 | Kallyanpur | 75 | 21:00 | 148 | Purbachal | 21 | 14:00
17 | Barishal | 85 | 13:00 | 83 | Kalurghat | 24 | 21:00 | 149 | Purbasadipur | 101 | 19:30
18 | Barishal-230 | 92 | 18:30 | 84 | Kamrangirchar | 37 | 13:00 | 150 | Rahanpur | 30 | 20:00
19 | Baroaulia | 52 | 00:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 1 | 02:00
20 | Baroirhat | 57 | 18:00 | 86 | Kasba | 34 | 19:00 | 152 | Rajbari | 68 | 19:00
21 | Bashundhara | 113 | 21:00 | 87 | Kazla | 76 | 15:00 | 153 | Rajendrapur | 89 | 18:30
22 | BashundharaCement | 6 | 00:00 | 88 | Keranigonj | 50 | 21:00 | 154 | Rajshahi | 104 | 19:30
23 | Beanibazar | 58 | 18:30 | 89 | Khagrachori | 30 | 18:30 | 155 | Rajshahi-230 | 68 | 19:30
24 | Benapole | 71 | 13:00 | 90 | Khulna | 54 | 13:00 | 156 | Ramganj | 100 | 18:30
25 | Bhaluka | 114 | 18:30 | 91 | Khulshi | 158 | 23:00 | 157 | Rampur | 36 | 23:00
26 | Bhandaria | 53 | 21:00 | 92 | Kishoreganj | 111 | 19:00 | 158 | Rangamati | 19 | 18:30
27 | Bhangura | 40 | 14:00 | 93 | Kodda | 156 | 21:00 | 159 | Rangpur | 117 | 19:30
28 | Bheramara(GK) | 60 | 19:00 | 94 | Kulaura | 36 | 18:30 | 160 | Ruppur | 3.2 | 10:00
29 | Bhulta | 128 | 20:00 | 95 | Kurigram | 60 | 18:00 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 72 | 19:00 | 96 | Kushtia | 120 | 19:30 | 162 | Saidpur | 73 | 19:30
31 | Bogura | 139 | 19:30 | 97 | Laksam | 30 | 21:00 | 163 | Satkhira | 133 | 20:00
32 | Borhanuddin | 89 | 18:30 | 98 | Lakshmipur | 27 | 18:30 | 164 | Satmasjid | 68 | 14:00
33 | Brahmanbaria | 120 | 20:00 | 99 | Lalbag | 20 | 12:00 | 165 | Savar | 102 | 19:00
34 | Cantonment | 110 | 19:30 | 100 | Lalmonirhat | 55 | 19:30 | 166 | SevenRings | 5.42 | 14:00
35 | Chandina | 16 | 18:30 | 101 | MI_Cement | 11.3 | 01:00 | 167 | ShahCement | 36 | 01:00
36 | Chandpur | 56 | 19:30 | 102 | Madanganj | 34 | 21:00 | 168 | Shahjadpur | 66 | 19:30
37 | Chandraghona | 36 | 18:30 | 103 | Madaripur | 94 | 13:00 | 169 | Shahjibazar | 111 | 19:00
38 | Chapai | 70 | 19:30 | 104 | Madartek | 54 | 22:00 | 170 | Shahmirpur | 56 | 00:00
39 | Charsaidpur | 29 | 19:00 | 105 | Madunaghat | 50 | 18:30 | 171 | Shariatpur | 74 | 14:00
40 | Chauddagram | 73 | 19:00 | 106 | Magura | 63 | 19:00 | 172 | Sherpur | 140 | 19:00
41 | Chhatak | 33 | 19:00 | 107 | Mahasthangarh | 68 | 19:30 | 173 | Shikalbaha | 24 | 00:00
42 | Chowmuhani | 142 | 19:30 | 108 | Maijdee | 44 | 22:00 | 174 | Shitalakhya | 50.6 | 14:00
43 | Chuadanga | 113 | 19:30 | 109 | Manikganj | 116 | 21:00 | 175 | Sholosohor | 35 | 22:00
44 | Coxsbazar | 147 | 19:00 | 110 | Maniknagar | 46 | 23:00 | 176 | Shyampur | 94 | 12:00
45 | Cumilla(N) | 112 | 19:30 | 111 | Matarbari | 52 | 22:00 | 177 | Siddhirganj | 71 | 21:00
46 | Cumilla(S) | 141 | 15:00 | 112 | Matuail | 30 | 22:00 | 178 | Sirajganj | 98 | 19:30
47 | Daganbhuiyan | 30 | 19:00 | 113 | Metrorail_Motijheel | 19 | 18:30 | 179 | Sonargaon | 74 | 22:00
48 | Daudkandi | 118 | 21:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreemongol | 67 | 18:30
49 | DhakaUniversity | 24 | 13:00 | 115 | Millgate | 40 | 21:00 | 181 | Sreepur | 85 | 18:30
50 | Dhamrai | 78 | 18:30 | 116 | Mirpur | 91 | 13:00 | 182 | Srinagar | 41.9 | 14:00
51 | Dhanmondi | 54.6 | 14:00 | 117 | Mirsorai | 7 | 00:00 | 183 | Sunamganj | 50 | 20:00
52 | Dohazari | 109 | 19:30 | 118 | Mirzapur | 51 | 19:30 | 184 | Sylhet | 51 | 15:00
53 | Faridpur | 126 | 19:30 | 119 | Mithapukur | 58 | 19:00 | 185 | Sylhet-132 | 89 | 19:00
54 | Fatullah | 51 | 13:00 | 120 | Modern | N/A | N/A | 186 | TK | 22 | 18:30
55 | Fenchuganj | 31 | 18:30 | 121 | Mogbazar | 33 | 20:00 | 187 | Tangail | 170 | 19:00
56 | Feni | 88 | 19:30 | 122 | Mongla | 46 | 05:00 | 188 | Taraganj | 18 | 19:00
57 | GPH | 74 | 02:00 | 123 | Motijheel | 24 | 18:30 | 189 | Tasnim | 14 | 01:00
58 | Ghatail | 90 | 18:30 | 124 | Muktagacha | 37 | 19:00 | 190 | Thakurgaon | 87 | 19:30
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 95 | 19:30 | 191 | Tongi | 66 | 21:00
60 | Ghorashal-230 | 73 | 22:00 | 126 | Muradnagar | 38 | 18:30 | 192 | Ullahpara | 37 | 19:00
61 | Goalpara | 33 | 00:00 | 127 | Mymensingh | 163 | 19:30 | 193 | Ullon | 38 | 13:00
62 | Gollamari | 84 | 13:00 | 128 | Nabinagar | 6 | 12:00 | 194 | Uttara | 59 | 19:00
63 | Gopalganj | 105.4 | 19:00 | 129 | Naogaon | 117 | 19:30 | 195 | UttaraNew | 21 | 13:00
64 | Gulshan | 62 | 13:00 | 130 | Narail | 61 | 19:00 | 196 | Zigatola | 66 | 14:00
65 | Halishahar | 56.5 | 19:30 | 131 | Narinda | 31 | 20:00
66 | HaripurSBU | 88 | 23:00 | 132 | Narshingdi | 127 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 26-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 10135.72 | 0 |  | 10135.72
1:00 | 9833.06 | 0 |  | 9833.06
2:00 | 9552.64 | 0 |  | 9552.64
3:00 | 9213.8 | 0 |  | 9213.8
4:00 | 9009.94 | 0 |  | 9009.94
5:00 | 8799.05 | 0 |  | 8799.05
6:00 | 8443.27 | 0 |  | 8443.27
7:00 | 8777.03 | 0 |  | 8777.03
8:00 | 8994.81 | 0 |  | 8994.81
9:00 | 9095.22 | 0 |  | 9095.22
10:00 | 9240.78 | 0 |  | 9240.78
11:00 | 9645.08 | 0 |  | 9645.08
12:00 | 10282.32 | 0 |  | 10282.32
13:00 | 11059.77 | 0 |  | 11059.77
14:00 | 11250.77 | 0 |  | 11250.77
15:00 | 10971.36 | 0 |  | 10971.36
16:00 | 10587.75 | 0 |  | 10587.75
17:00 | 10334.69 | 0 |  | 10334.69
18:00 | 10608.79 | 0 |  | 10608.79
19:00 | 11719.45 | 0 |  | 11719.45
19:30 | 12142.31 | 0 |  | 12142.31
20:00 | 12121.01 | 0 |  | 12121.01
21:00 | 12077.24 | 0 |  | 12077.24
22:00 | 11882.24 | 0 |  | 11882.24
23:00 | 11480.91 | 0 |  | 11480.91
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 26-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5199 | 4936.72 | 10135.72 | DAILY GENERATION CURVE
00:30 | 5200.5 | 4783.89 | 9984.39
01:00 | 5202 | 4631.06 | 9833.06 | 26-03-2026
01:30 | 5188.5 | 4504.35 | 9692.85
02:00 | 5175 | 4377.64 | 9552.64
02:30 | 5079.5 | 4303.72 | 9383.22
03:00 | 4984 | 4229.8 | 9213.8
03:30 | 4950.5 | 4161.37 | 9111.87
04:00 | 4917 | 4092.94 | 9009.94
04:30 | 4870.5 | 4033.995 | 8904.495
05:00 | 4824 | 3975.05 | 8799.05
05:30 | 4704.005 | 3917.155 | 8621.16
06:00 | 4584.01 | 3859.26 | 8443.27
06:30 | 4664.545 | 3945.605 | 8610.15
07:00 | 4745.08 | 4031.95 | 8777.03
07:30 | 4769.96 | 4115.96 | 8885.92
08:00 | 4794.84 | 4199.97 | 8994.81
08:30 | 4777.38 | 4267.635 | 9045.015
09:00 | 4759.92 | 4335.3 | 9095.22
09:30 | 4783.7 | 4384.3 | 9168
10:00 | 4807.48 | 4433.3 | 9240.78
10:30 | 4929.06 | 4513.87 | 9442.93
11:00 | 5050.64 | 4594.44 | 9645.08
11:30 | 5271.99 | 4691.71 | 9963.7
12:00 | 5493.34 | 4788.98 | 10282.32
12:30 | 5645.135 | 5025.91 | 10671.045
13:00 | 5796.93 | 5262.84 | 11059.77
13:30 | 5722.315 | 5432.955 | 11155.27
14:00 | 5647.7 | 5603.07 | 11250.77
14:30 | 5553.75 | 5557.315 | 11111.065
15:00 | 5459.8 | 5511.56 | 10971.36
15:30 | 5488.075 | 5291.48 | 10779.555
16:00 | 5516.35 | 5071.4 | 10587.75
16:30 | 5478.1 | 4983.12 | 10461.22
17:00 | 5439.85 | 4894.84 | 10334.69
17:30 | 5514.62 | 4957.12 | 10471.74
18:00 | 5589.39 | 5019.4 | 10608.79
18:30 | 5777.695 | 5386.425 | 11164.12
19:00 | 5966 | 5753.45 | 11719.45
19:30 | 6090.5 | 6051.81 | 12142.31
20:00 | 6107.2 | 6013.81 | 12121.01
20:30 | 6107.15 | 5991.975 | 12099.125 |  | Executive Engineer
21:00 | 6107.1 | 5970.14 | 12077.24 |  | Network Operation Division
21:30 | 6047.8 | 5931.94 | 11979.74
22:00 | 5988.5 | 5893.74 | 11882.24
22:30 | 5842.75 | 5838.825 | 11681.575
23:00 | 5697 | 5783.91 | 11480.91

## En-Curve
QF-LDC-12
Date | 26-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3689 | 1716 | 886 | 0 | 110 | 967.72 | 40 | 2727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3695.5 | 1709.5 | 886 | 0 | 108 | 896.89 | 40 | 2648.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26-03-2026
01:00 | 3702 | 1703 | 886 | 0 | 106 | 826.06 | 40 | 2570 | 0 | 0 | 0 | 0 | 0 | 0 | 0
01:30 | 3706 | 1696.5 | 878.5 | 0 | 106 | 826.85 | 40 | 2438 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Energy Generated | 248.5875 |  | MKWHr
02:00 | 3710 | 1690 | 871 | 0 | 106 | 827.64 | 40 | 2306 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3694.5 | 1663 | 871 | 0 | 105 | 828.72 | 40 | 2176.5 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0 | Total Energy Requirement | 248.5875 |  | MKWHr
03:00 | 3679 | 1636 | 871 | 0 | 104 | 829.8 | 40 | 2047 | 0 | 0 | 0 | 0 | 0 | 7 | 0
03:30 | 3651 | 1639.5 | 871 | 0 | 102 | 829.87 | 40 | 1971 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0
04:00 | 3623 | 1643 | 871 | 0 | 100 | 829.94 | 40 | 1895 | 0 | 0 | 0 | 0 | 0 | 8 | 0
04:30 | 3588 | 1576.5 | 871.5 | 0 | 99 | 830.495 | 40 | 1886 | 0 | 0 | 0 | 0 | 0 | 13 | 0
05:00 | 3553 | 1510 | 872 | 0 | 98 | 831.05 | 40 | 1877 | 0 | 0 | 0 | 0 | 0 | 18 | 0
05:30 | 3472.5 | 1462.5 | 871.5 | 0 | 96 | 830.155 | 40 | 1833 | 0.005 | 0 | 0 | 0 | 0 | 15.5 | 0
06:00 | 3392 | 1415 | 871 | 0 | 94 | 829.26 | 40 | 1789 | 0.01 | 0 | 0 | 0 | 0 | 13 | 0
06:30 | 3536 | 1440.5 | 876.5 | 0 | 96 | 830.63 | 40 | 1736.5 | 43.02 | 0 | 0 | 0 | 0 | 11 | 0
07:00 | 3680 | 1466 | 882 | 0 | 98 | 832 | 40 | 1684 | 86.03 | 0 | 0 | 0 | 0 | 9 | 0
07:30 | 3639 | 1485.75 | 884 | 0 | 100 | 829.84 | 40 | 1719.5 | 174.33 | 0 | 9 | 0 | 0 | 4.5 | 0
08:00 | 3598 | 1505.5 | 886 | 0 | 102 | 827.68 | 40 | 1755 | 262.63 | 0 | 18 | 0 | 0 | 0 | 0
08:30 | 3587 | 1510.5 | 886 | 0 | 101 | 829.21 | 40 | 1710 | 359.805 | 0 | 21 | 0 | 0 | 0.5 | 0
09:00 | 3576 | 1515.5 | 886 | 0 | 100 | 830.74 | 40 | 1665 | 456.98 | 0 | 24 | 0 | 0 | 1 | 0
09:30 | 3547.5 | 1509.5 | 887.5 | 0 | 106 | 831.39 | 40 | 1668 | 551.11 | 0 | 24 | 0 | 0 | 3 | 0
10:00 | 3519 | 1503.5 | 889 | 0 | 112 | 832.04 | 40 | 1671 | 645.24 | 0 | 24 | 0 | 0 | 5 | 0
10:30 | 3611.5 | 1555.5 | 888.5 | 0 | 117 | 835.64 | 40 | 1674 | 691.29 | 0 | 24 | 0 | 0 | 5.5 | 0
11:00 | 3704 | 1607.5 | 888 | 0 | 122 | 839.24 | 40 | 1677 | 737.34 | 0 | 24 | 0 | 0 | 6 | 0
11:30 | 3777 | 1693.5 | 888 | 0 | 124 | 843.825 | 58 | 1792.5 | 755.875 | 0 | 24 | 0 | 0 | 7 | 0
12:00 | 3850 | 1779.5 | 888 | 0 | 126 | 848.41 | 76 | 1908 | 774.41 | 0 | 24 | 0 | 0 | 8 | 0
12:30 | 3865 | 1801.75 | 888.5 | 0 | 128 | 912.965 | 78 | 2200 | 749.83 | 0 | 37 | 0 | 0 | 10 | 0
13:00 | 3880 | 1824 | 889 | 0 | 130 | 977.52 | 80 | 2492 | 725.25 | 0 | 50 | 0 | 0 | 12 | 0
13:30 | 3788 | 1807.5 | 888.5 | 0 | 134 | 1016.485 | 75 | 2694.5 | 689.785 | 0 | 54.5 | 0 | 0 | 7 | 0
14:00 | 3696 | 1791 | 888 | 0 | 138 | 1055.45 | 70 | 2897 | 654.32 | 0 | 59 | 0 | 0 | 2 | 0
14:30 | 3616.5 | 1772 | 888 | 0 | 140 | 1059.47 | 75 | 2940 | 560.095 | 0 | 59 | 0 | 0 | 1 | 0
15:00 | 3537 | 1753 | 888 | 0 | 142 | 1063.49 | 80 | 2983 | 465.87 | 0 | 59 | 0 | 0 | 0 | 0
15:30 | 3525.5 | 1773.5 | 888 | 0 | 140 | 1015.485 | 80 | 2889.5 | 391.57 | 0 | 74.5 | 0 | 0 | 1.5 | 0
16:00 | 3514 | 1794 | 888 | 0 | 138 | 967.48 | 80 | 2796 | 317.27 | 0 | 90 | 0 | 0 | 3 | 0
16:30 | 3508 | 1780 | 888 | 0 | 135 | 964.57 | 80 | 2795 | 219.15 | 0 | 90 | 0 | 0 | 1.5 | 0
17:00 | 3502 | 1766 | 888 | 0 | 132 | 961.66 | 80 | 2794 | 121.03 | 0 | 90 | 0 | 0 | 0 | 0
17:30 | 3574.5 | 1791.5 | 888 | 0 | 127 | 1016.865 | 80 | 2831.5 | 63.875 | 8.5 | 90 | 0 | 0 | 0 | 0
18:00 | 3647 | 1817 | 888 | 0 | 122 | 1072.07 | 80 | 2869 | 6.72 | 17 | 90 | 0 | 0 | 0 | 0
18:30 | 3698.5 | 1907 | 888 | 0 | 128 | 1235.26 | 80 | 3002 | 3.36 | 27 | 195 | 0 | 0 | 0 | 0
19:00 | 3750 | 1997 | 888 | 0 | 134 | 1398.45 | 80 | 3135 | 0 | 37 | 300 | 0 | 0 | 0 | 0
19:30 | 3697 | 1959 | 883 | 0 | 134 | 1446.81 | 80 | 3241 | 0 | 77 | 624.5 | 0 | 0 | 0 | 0
20:00 | 3696 | 1881 | 884 | 0 | 138 | 1454.81 | 80 | 3265 | 0 | 85 | 635.2 | 0 | 0 | 2 | 0
20:30 | 3694 | 1874.5 | 884 | 0 | 137 | 1456.475 | 80 | 3282 | 0 | 77 | 613.15 | 0 | 0 | 1 | 0
21:00 | 3692 | 1868 | 884 | 0 | 136 | 1458.14 | 80 | 3299 | 0 | 69 | 591.1 | 0 | 0 | 0 | 0
21:30 | 3679 | 1870.5 | 884.5 | 0 | 138 | 1457.94 | 80 | 3296.5 | 0 | 69 | 504.3 | 0 | 0 | 0 | 0
22:00 | 3666 | 1873 | 885 | 0 | 140 | 1457.74 | 80 | 3294 | 0 | 69 | 417.5 | 0 | 0 | 0 | 0
22:30 | 3700 | 1870.5 | 884.5 | 0 | 140 | 1465.325 | 80 | 3252.5 | 0 | 51.5 | 237.25 | 0 | 0 | 0 | 0
23:00 | 3734 | 1868 | 884 | 0 | 140 | 1472.91 | 80 | 3211 | 0 | 34 | 57 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 26-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 415 | 06:00 | 401 | 14:00 | Madunaghat | 406 | 07:00 | 395 | 20:00
Amtali | 421 | 06:00 | 410 | 21:00 | Meghnaghat | 416 | 05:00 | 405 | 15:00
Ashuganj | 415 | 6:00 | 402 | 14:00 | Payra | 422 | 06:00 | 412 | 21:00
Bhulta | 410 | 06:00 | 397 | 14:00 | Rahanpur | 415 | 05:00 | 397 | 23:00
Bibiana | 416 | 05:00 | 407 | 15:00 | Rampal | 410 | 05:00 | 393 | 19:30
BIPTC | 398 | 03:00 | 389 | 12:00
Bogura | 411 | 06:00 | 388 | 23:00
Gopalganj | 416 | 06:00 | 401 | 19:30
Kaliakoir | 411 | 05:00 | 395 | 13:00
Korerhat | 415 | 08:00 | 401 | 19:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 237 | 06:00 | 228 | 13:00 | Jhenaidah | 234 | 06:00 | 217 | 13:00
AKSML | 237 | 08:00 | 227 | 19:00 | Kachua | 236 | 08:00 | 225 | 19:00
Aminbazar | 237 | 05:00 | 229 | 13:00 | Kaliakoir | 239 | 05:00 | 230 | 14:00
Ashuganj | 238 | 06:00 | 229 | 14:00 | Keranigonj | 235 | 03:00 | 227 | 14:00
Ashuganj-400 | 238 | 06:00 | 229 | 14:00 | Khulna(S) | 236 | 06:00 | 221 | 21:00
Baghabari | 238 | 05:00 | 226 | 23:00 | Korerhat | 236 | 04:00 | 227 | 19:30
Barapukuria | 229 | 04:00 | 214 | 13:00 | Madunaghat | 235 | 07:00 | 228 | 18:30
Barapukuria-230 | 229 | 04:00 | 214 | 13:00 | Madunaghat-400 | 235 | 06:00 | 228 | 20:00
Barishal | 234 | 06:00 | 225 | 22:00 | Maniknagar | 237 | 08:00 | 229 | 13:00
Bheramara | 235 | 04:00 | 222 | 13:00 | Meghnaghat | 243 | 04:00 | 234 | 19:30
Bhulta | 238 | 05:00 | 230 | 14:00 | Meghnaghat-400 | 237 | 06:00 | 229 | 19:00
Bibiana | 243 | 08:00 | 233 | 14:00 | Mirsorai | 241 | 09:00 | 233 | 19:00
BIPTC | 237 | 03:00 | 222 | 13:00 | Purbasadipur | 228 | 05:00 | 213 | 13:00
Bogura | 237 | 06:00 | 224 | 23:00 | Rajshahi | 234 | 04:00 | 219 | 13:00
Bogura-400 | 236 | 05:00 | 224 | 18:30 | Rampal | 235 | 05:00 | 221 | 14:00
Borhanuddin | 236 | 09:00 | 229 | 22:00 | Rampur | N/A | N/A | N/A | N/A
BSRM | 236 | 08:00 | 226 | 19:00 | Rampura | 237 | 06:00 | 229 | 23:00
Chowmuhani | 236 | 8:00 | 227 | 15:00 | Shikalbaha | 233 | 07:00 | 226 | 19:30
Cumilla(N) | 236 | 06:00 | 227 | 21:00 | Shyampur | 236 | 06:00 | 228 | 14:00
Faridpur | 234 | 06:00 | 223 | 14:00 | Siddhirganj | 238 | 03:00 | 232 | 13:00
Fenchuganj | 242 | 06:00 | 234 | 14:00 | Sirajgonj | 242 | 06:00 | 233 | 23:00
Feni | 236 | 06:00 | 227 | 19:30 | Sreepur | 234 | 08:00 | 220 | 17:00
Ghorashal | 240 | 01:00 | 232 | 22:00 | Tongi | 240 | 07:00 | 230 | 18:30
Ghorashal-230 | 236 | 04:00 | 228 | 15:00
Gopalganj | 232 | 05:00 | 222 | 19:00
GPH | 237 | 08:00 | 227 | 19:00
Haripur | 238 | 06:00 | 230 | 15:00
Hasnabad | 238 | 13:00 | 228 | 14:00
Hathazari | 231 | 05:00 | 226 | 00:00
Ishurdi | 238 | 04:00 | 225 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 05:00 | 130 | 14:00 | Madunaghat | 136 | 07:00 | 131 | 18:30
Agargaon | 135 | 02:00 | 130 | 13:00 | Magura | 136 | 06:00 | 121 | 13:00
Agrabad | 135 | 07:00 | 129 | 19:00 | Mahasthangarh | 134 | 04:00 | 125 | 13:00
AKS | 132 | 02:00 | 130 | 00:00 | Maijdee | 131 | 06:00 | 125 | 15:00
Aminbazar | 137 | 03:00 | 132 | 13:00 | Manikganj | 135 | 04:00 | 125 | 19:30
Amnura | 136 | 04:00 | 127 | 13:00 | Maniknagar | 133 | 01:00 | 129 | 13:00
Ashuganj | 143 | 08:00 | 136 | 14:00 | Matarbari | 121 | 18:30 | 104 | 19:30
Ashuganj-230 | 143 | 08:00 | 136 | 14:00 | Matuail | 137 | 06:00 | 132 | 14:00
Bagerhat | 130 | 05:00 | 118 | 19:30 | Metrorail_Motijheel | 133 | 01:00 | 129 | 13:00
Bajitpur | 136 | 05:00 | 128 | 14:00 | Metrorail_Uttara | 137 | 06:00 | 131 | 13:00
Bakerganj | 136 | 06:00 | 130 | 19:00 | Millgate | 137 | 03:00 | 130 | 14:00
Bakulia | 134 | 05:00 | 129 | 19:00 | Mirpur | 137 | 06:00 | 131 | 14:00
Banani | 137 | 02:00 | 130 | 14:00 | Mirzapur | 133 | 05:00 | 124 | 15:00
Bangabhaban | 135 | 04:00 | 129 | 13:00 | Mithapukur | 135 | 16:00 | 121 | 13:00
Barapukuria | 130 | 04:00 | 120 | 13:00 | MI_Cement | 137 | 05:00 | 131 | 13:00
Barguna | 136 | 06:00 | 130 | 14:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 136 | 06:00 | 130 | 14:00 | Mogbazar | 135 | 01:00 | 130 | 13:00
Barishal-230 | 136 | 05:00 | 130 | 14:00 | Mongla | 131 | 09:00 | 119 | 19:30
Baroaulia | 135 | 05:00 | 130 | 19:00 | Motijheel | 135 | 04:00 | 129 | 13:00
Baroirhat | 134 | 04:00 | 130 | 13:00 | Muktagacha | 133 | 21:00 | 118 | 15:00
Bashundhara | 138 | 08:00 | 130 | 13:00 | Munshiganj | 136 | 05:00 | 131 | 14:00
BashundharaCement | 135 | 01:00 | 132 | 13:00 | Muradnagar | 136 | 08:00 | 127 | 19:30
Beanibazar | 132 | 09:00 | 125 | 14:00 | Mymensingh | 134 | 21:00 | 117 | 15:00
Benapole | 131 | 05:00 | 112 | 14:00 | Nabinagar | 135 | 05:00 | 129 | 14:00
Bhaluka | 137 | 09:00 | 127 | 14:00 | Naogaon | 139 | 04:00 | 123 | 14:00
Bhandaria | 132 | 04:00 | 124 | 21:00 | Narail | 137 | 06:00 | 119 | 19:30
Bhangura | 139 | 13:00 | 127 | 14:00 | Narinda | 133 | 01:00 | 129 | 13:00
Bheramara | 136 | 02:00 | 131 | 13:00 | Narshingdi | 135 | 04:00 | 128 | 19:30
Bheramara(GK) | 136 | 03:00 | 131 | 13:00 | Natore | 134 | 05:00 | 126 | 13:00
Bhulta | 132 | 07:00 | 127 | 23:00 | Nawabganj | 134 | 05:00 | 128 | 14:00
Bog-Sherpur | 136 | 05:00 | 128 | 13:00 | Netrakona | 133 | 03:00 | 121 | 13:00
Bogura | 136 | 03:00 | 128 | 13:00 | New | 138 | 05:00 | 130 | 23:00
Bogura-230 | 137 | 06:00 | 129 | 13:00 | Niamatpur | 138 | 04:00 | 131 | 19:30
Brahmanbaria | 138 | 08:00 | 130 | 14:00 | Noapara | 134 | 05:00 | 122 | 19:30
Cantonment | 135 | 03:00 | 129 | 14:00 | Pabna | 135 | 03:00 | 129 | 19:30
Chandina | 137 | 06:00 | 131 | 15:00 | Palashbari | 130 | 04:00 | 118 | 13:00
Chandpur | 133 | 08:00 | 127 | 15:00 | Panchagarh | 137 | 21:00 | 127 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 137 | 07:00 | 131 | 18:30 | Patiya | 133 | 07:00 | 126 | 19:00
Chapai | 137 | 04:00 | 130 | 22:00 | Patuakhali | 135 | 07:00 | 130 | 14:00
Charsaidpur | 136 | 03:00 | 131 | 14:00 | Payra | 138 | 06:00 | 133 | 23:00
Chauddagram | 134 | 06:00 | 120 | 17:00 | PHP | 134 | 06:00 | 128 | 19:30
Chhatak | 131 | 06:00 | 122 | 14:00 | Postogola | 138 | 06:00 | 132 | 13:00
Chowmuhani | 131 | 05:00 | 126 | 13:00 | Pubail | 142 | 06:00 | 135 | 23:00
Chuadanga | 131 | 03:00 | 116 | 19:30 | Purbachal | 137 | 04:00 | 130 | 14:00
Coxsbazar | 118 | 07:00 | 103 | 19:00 | Purbasadipur | 132 | 05:00 | 122 | 13:00
Cumilla(N) | 137 | 05:00 | 131 | 18:30 | Rahanpur | 139 | 04:00 | 132 | 23:00
Cumilla(S) | 136 | 04:00 | 121 | 14:00 | Rahanpur-400 | 139 | 04:00 | 133 | 19:30
Daganbhuiyan | 133 | 06:00 | 127 | 14:00 | Rahim | 137 | 04:00 | 132 | 14:00
Daudkandi | 135 | 05:00 | 125 | 19:00 | Rajbari | 134 | 05:00 | 126 | 23:00
DhakaUniversity | 135 | 05:00 | 130 | 13:00 | Rajendrapur | 139 | 06:00 | 131 | 14:00
Dhamrai | 135 | 04:00 | 129 | 15:00 | Rajshahi | 134 | 03:00 | 125 | 13:00
Dhanmondi | 138 | 06:00 | 133 | 15:00 | Rajshahi-230 | 135 | 04:00 | 126 | 13:00
Dohazari | 129 | 06:00 | 120 | 19:30 | Ramganj | 130 | 06:00 | 124 | 13:00
Faridpur | 135 | 05:00 | 129 | 14:00 | Rampur | 135 | 09:00 | 130 | 14:00
Fatullah | 138 | 06:00 | 131 | 14:00 | Rampura | 134 | 03:00 | 130 | 13:00
Fenchuganj | 137 | 08:00 | 133 | 15:00 | Rangamati | 135 | 06:00 | 130 | 19:00
Feni | 132 | 05:00 | 127 | 14:00 | Rangpur | 131 | 05:00 | 120 | 13:00
Feni-230 | 133 | 06:00 | 127 | 19:30 | Ruppur | 137 | 03:00 | 130 | 19:00
Ghatail | 130 | 05:00 | 119 | 15:00 | Saidpur | 130 | 05:00 | 120 | 13:00
Ghorashal | 143 | 01:00 | 135 | 15:00 | Satkhira | 131 | 04:00 | 118 | 19:30
Goalpara | 135 | 06:00 | 124 | 19:30 | Satmasjid | 135 | 05:00 | 130 | 14:00
Gollamari | 136 | 06:00 | 126 | 19:30 | Savar | 136 | 05:00 | 131 | 13:00
Gopalganj | 136 | 06:00 | 127 | 19:30 | SevenRings | 143 | 06:00 | 137 | 14:00
Gopalganj-400 | 138 | 05:00 | 132 | 14:00 | ShahCement | 136 | 03:00 | 131 | 14:00
Gulshan | 134 | 05:00 | 129 | 14:00 | Shahjadpur | 140 | 02:00 | 133 | 19:30
Halishahar | 136 | 08:00 | 129 | 19:00 | Shahjibazar | 136 | 08:00 | 128 | 14:00
Haripur | 137 | 05:00 | 132 | 23:00 | Shahmirpur | 135 | 07:00 | 129 | 19:00
HaripurSBU | 137 | 06:00 | 132 | 15:00 | Shariatpur | 137 | 07:00 | 128 | 14:00
Hasnabad | 138 | 07:00 | 133 | 13:00 | Sherpur | 132 | 21:00 | 106 | 15:00
Hathazari | 136 | 04:00 | 132 | 14:00 | Shikalbaha | 125 | 08:00 | 119 | 19:00
Hatirjheel | 135 | 06:00 | 130 | 13:00 | Shikalbaha-230 | 136 | 07:00 | 130 | 19:30
Ishurdi | 138 | 03:00 | 132 | 19:30 | Shitalakhya | 137 | 05:00 | 131 | 13:00
Jaldhaka | 130 | 05:00 | 119 | 13:00 | Sholosohor | 136 | 06:00 | 130 | 19:30
Jamalpur | 135 | 21:00 | 111 | 15:00 | Shyampur | 136 | 02:00 | 132 | 14:00
Jashore | 133 | 05:00 | 116 | 13:00 | Shyampur-230 | 137 | 05:00 | 132 | 13:00
Jhenaidah | 135 | 04:00 | 122 | 13:00 | Siddhirganj | 137 | 02:00 | 132 | 13:00
Jhenaidah-230 | 138 | 11:00 | 123 | 13:00 | Sirajganj | 134 | 04:00 | 127 | 22:00
Joydebpur | 140 | 05:00 | 132 | 15:00 | Sonargaon | 136 | 02:00 | 132 | 13:00
Joypurhat | 131 | 04:00 | 121 | 13:00 | Sreemongol | 136 | 09:00 | 127 | 15:00
Juldah | 135 | 09:00 | 130 | 20:00 | Sreepur | 140 | 06:00 | 133 | 15:00
Kabirpur | 136 | 06:00 | 125 | 18:00 | Srinagar | 134 | 04:00 | 128 | 13:00
Kachua | 134 | 03:00 | 127 | 19:00 | SSM | 140 | 04:00 | 132 | 18:00
Kaliakoir | 137 | 03:00 | 131 | 13:00 | Sunamganj | 129 | 06:00 | 120 | 14:00
Kaliganj | 135 | 05:00 | 121 | 13:00 | Sylhet | 132 | 06:00 | 125 | 15:00
Kallyanpur | 137 | 04:00 | 132 | 13:00 | Sylhet-132 | 132 | 05:00 | 126 | 13:00
Kalurghat | 136 | 07:00 | 131 | 18:30 | Tangail | 129 | 04:00 | 120 | 15:00
Kamrangirchar | 136 | 06:00 | 128 | 13:00 | Taraganj | 129 | 06:00 | 120 | 13:00
Kaptai | 138 | 8:00 | 134 | 1:00 | Tasnim | 136 | 05:00 | 132 | 15:00
Kasba | 136 | 06:00 | 127 | 19:30 | Thakurgaon | 135 | 21:00 | 125 | 13:00
Kazla | 133 | 04:00 | 129 | 14:00 | TK | 137 | 08:00 | 131 | 19:00
Keranigonj | 135 | 06:00 | 129 | 13:00 | Tongi | 140 | 07:00 | 132 | 21:00
Khagrachori | 135 | 06:00 | 129 | 19:00 | Ullahpara | 136 | 04:00 | 128 | 19:00
Khulna | 135 | 06:00 | 124 | 19:30 | Ullon | 137 | 09:00 | 129 | 14:00
Khulna(S) | 136 | 06:00 | 125 | 21:00 | Uttara | 137 | 05:00 | 131 | 13:00
Khulshi | 135 | 08:00 | 128 | 19:00 | UttaraNew | 137 | 05:00 | 131 | 13:00
Kishoreganj | 136 | 06:00 | 127 | 14:00 | Zigatola | 134 | 05:00 | 128 | 14:00
Kodda | 138 | 07:00 | 127 | 14:00
Korerhat | 136 | 04:00 | 131 | 19:30
KSRM | 136 | 07:00 | 130 | 19:00
Kulaura | 136 | 07:00 | 131 | 13:00
Kurigram | 129 | 04:00 | 114 | 13:00
Kushtia | 135 | 06:00 | 127 | 19:30
Laksam | 133 | 03:00 | 127 | 15:00
Lakshmipur | 132 | 06:00 | 125 | 15:00
Lalbag | 135 | 05:00 | 129 | 13:00
Lalmonirhat | 130 | 05:00 | 118 | 14:00
Madanganj | 135 | 01:00 | 132 | 13:00
Madaripur | 137 | 06:00 | 130 | 14:00
Madartek | 134 | 05:00 | 129 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division