## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 28-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-03-2026 | during | 28-03-2026 | during | 28-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 192 | 192 | 190 | 190 | 190 | 190 | GBC 1 and 3 under maintenance
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 357 | 332 | 412 | 412 | 390 | 390 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 450 | 450 | 226 | 226 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 150 | 150 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 10 | 31.5 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 22 | 12 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 8 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 15 | 145 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 8 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 34 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 15 | 93 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 0 | 0 | 31 | 0 | 31 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 495 | 530 | 584 | 584 | 526 | 526 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 272 | 342 | 718 | 718 | 350 | 350 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 35 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1650 | 2066.5 | 5876.22 | 5845.22 | 3203.52 | 3172.52
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 26 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 221 | 220 | 225 | 220 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 2 | 51 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 64 | 56 | 64 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 68 | 68 | 68 | 68 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 19 | 20 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.56 | 0 | 3.72 | 0 | 3.72 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 1 | 28 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 100 | 100 | 100 | 100 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 15 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 520 | 1087 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 0 | 15 | 0 | 15 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 470 | 470 | 1045 | 1045 | 471 | 471 | FL-U2
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1328.56 | 2110 | 3967.58 | 3962.86 | 2944.22 | 2939.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 0 | 135 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 315 | 290 | 342.01 | 342.01 | 306 | 306 | Able to ON FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 390 | 215 | 393 | 393 | 216 | 216 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 41 | 36 | 41.65 | 41.65 | 41.65 | 41.65 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 48 | 5 | 55 | 55 | 55 | 55 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 35 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 2 | 30 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 16 | 16 | 16 | 16 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 97 | 163 | 163 | 103 | 103 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 9 | 92 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 140 | 140 | 84 | 78 | 84 | 78 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 1 | 60 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 70 | 0 | 74 | 0 | 74 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2876.261 | 1218 | 1171 | 2404.36 | 2324.36 | 1827.85 | 1747.85
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-03-2026 | during | 28-03-2026 | during | 28-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 152 | 160 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 35 | 55 | 60 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 98 | 70 | 115 | 70 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.96 | 0 | 45.12 | 0 | 45.12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 34 | 34 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 302.96 | 313 | 411.02 | 429 | 380.52 | 398.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 41 | 41 | 41 | 41 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 20 | 0 | 0 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 149 | 150 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 99 | 100 | 100 | 100 | 100 | 100 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 79 | 81 | 81 | 80 | 80 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | plant availability zero
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 23 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 401 | 391 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1153 | 1144 | 1186 | 1186 | 1084 | 1084
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 889 | 888 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 380 | 375 | 410 | 410 | 370 | 370 | -
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 97 | 0 | 65 | 0 | 65 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 438 | 603 | 1234.2 | 1234.2 | 617 | 617 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1804 | 1866 | 3577.2 | 3512.2 | 2159.1 | 2094.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 65 | 65 | 65 | 65 | 65 | 65 | GT-1 & ST under maint
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 992 | 1244 | 1244 | 1244 | 1184 | 1184 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 75 | 75 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 190 | 307 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.65 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1427.65 | 1836 | 2097 | 2096 | 1868 | 1867
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 60.07 | 0 | 59 | 0 | 59 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 175 | 187 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 402 | 354 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 22 | 22 | 21 | 21 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 50 | 50 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.24 | 0 | 6 | 0 | 6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1181 | 1424 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 42.2 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 113 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1977.51 | 2050 | 3151.87 | 2925.87 | 2613.49 | 2387.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 54 | 54 | 55 | 55 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 49 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.7 | 0 | 6.2 | 0 | 6.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 101 | 0 | 157.44 | 0 | 157.44 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 193.7 | 173 | 496.64 | 303 | 476.64 | 283
System Total |  |  |  |  | 28823.2 | 29275.503 | 11055.38 | 12729.5 | 23167.89 | 22584.51 | 16557.34 | 15973.96
Forecast Scenario (28-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11700 |  | 0 |  | 11700
|  |  |  | 1:00 | 11320 |  | 0 |  | 11320
|  |  |  | 2:00 | 10990 |  | 0 |  | 10990
|  |  |  | 3:00 | 10640 |  | 0 |  | 10640
|  |  |  | 4:00 | 10340 |  | 0 |  | 10340
|  |  |  | 5:00 | 9920 |  | 0 |  | 9920
|  |  |  | 6:00 | 9460 |  | 0 |  | 9460
|  |  |  | 7:00 | 9700 |  | 0 |  | 9700
|  |  |  | 8:00 | 9700 |  | 0 |  | 9700
|  |  |  | 9:00 | 10390 |  | 0 |  | 10390
|  |  |  | 10:00 | 10620 |  | 0 |  | 10620
|  |  |  | 11:00 | 11220 |  | 0 |  | 11220
|  |  |  | 12:00 | 11600 |  | 0 |  | 11600
|  |  |  | 13:00 | 11750 |  | 0 |  | 11750
|  |  |  | 14:00 | 12030 |  | 0 |  | 12030
|  |  |  | 15:00 | 12030 |  | 0 |  | 12030
|  |  |  | 16:00 | 12020 |  | 0 |  | 12020
|  |  |  | 17:00 | 11910 |  | 0 |  | 11910
|  |  |  | 18:00 | 11860 |  | 0 |  | 11860
|  |  |  | 18:30 | 12500 |  | 0 |  | 12500
|  |  |  | 19:00 | 12914.12 |  | 0 |  | 12914.12
|  |  |  | 19:30 | 12924.12 |  | 0 |  | 12924.12
|  |  |  | 20:00 | 12933.12 |  | 0 |  | 12933.12
|  |  |  | 21:00 | 12982.39 |  | 0 |  | 12982.39
|  |  |  | 22:00 | 12982.39 |  | 0 |  | 12982.39
|  |  |  | 23:00 | 12993.39 |  | 0 |  | 12993.39
Probable Maximum Temperature: |  |  | 31.90°C
Probable Maximum Demand at Day Peak: |  |  | 11600.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12982.39 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12982.39 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 274.00541 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:04 hrs on 28-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 27-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 11055.38 | MW | 12:00 Hr. | Energy Generated |  |  | 263.1343 |  | MKWHr.
| Day Peak Demand |  |  | 11055.38 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 12729.5 | MW | 19:30 Hr. | Energy Demand |  |  | 263.1343 |  | MKWHr.
| Evening Peak Demand |  |  | 12729.5 | MW | 19:30 Hr. | Maximum Temperature |  |  | 31.9 |  | °C
| Minimum Generation of the Day |  |  | 9064.07 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 883.11 |  | MMCFD
| Maximum Generation of the Day |  |  | 12729.5 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.3202 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.5715 | 0 | 1.9177 | 0 | 0 | 0.19639 | 0 | 0 | 41.6857 | Gas | 128.0061 | Gas | 454243346.6853
| Chattogram Zone |  |  | 5.7756 | 26.5309 | 1.524 | 0 | 1.9219 | 0.14952 | 0 | 0.0384 | 35.9403 | Coal | 69.7561 | Coal | 466517185.0286
| Cumilla Zone |  |  | 22.498 | 0 | 0.93505 | 0 | 0 | 0.50955 | 3.1402 | 0 | 27.0827 | HFO | 6.7803 | HFO | 111131387.48
| Mymensingh Zone |  |  | 3.7085 | 0 | 1.6848 | 0 | 0 | 0.32057 | 0 | 0 | 5.7138 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.5635 | 0 | 0 | 0 | 0 | 0.072845 | 0 | 0 | 26.6363 | Hydro | 1.9219 | Hydro | 192192
| Khulna Zone |  |  | 9.1005 | 11.5273 | 0 | 0 | 0 | 0.6948 | 21.4982 | 0 | 42.8208 | Solar | 4.5858 | Solar | 72135756.6
| Barishal Zone |  |  | 6.8611 | 30.4233 | 0 | 0 | 0 | 0.004317 | 0 | 0 | 37.2887 | Import | 52.0457 | Import | 295138139.71
| Rajshahi Zone |  |  | 13.9275 | 0 | 0.098688 | 0 | 0 | 1.5816 | 27.4073 | 0 | 43.0151 | Wind | 0.0384 | Wind | 564864
| Rangpur Zone |  |  | 0 | 1.2746 | 0.62001 | 0 | 0 | 1.0562 | 0 | 0 | 2.9508
| Total |  |  | 128.0061 | 69.7561 | 6.7803 | 0 | 1.9219 | 4.5858 | 52.0457 | 0.0384 | 263.1343
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 454243346.6853 |  | Hydro | 192192
|  |  |  | Coal | 466517185.0286 |  | Solar | 72135756.6
|  |  |  | HFO | 111131387.48 |  | Import | 295138139.71
|  |  |  | HSD | 0 |  | Wind | 564864
[5 empty] | Total: | 139,99,22,871 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.4982 | Peak Hr Flow | 888.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 28650400 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.4073 | Peak Hr Flow | 1424.00 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1320 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.1402 | Peak Hr Flow | 140.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2048 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.0457 | Peak Hr Flow | 2452.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3729
|  |  |  | Chattogram |  | 0 |  | 1384
|  |  |  | Cumilla |  | 0 |  | 1326
|  |  |  | Mymensingh |  | 0 |  | 948
|  |  |  | Sylhet |  | 0 |  | 503
|  |  |  | Khulna |  | 0 |  | 1708
|  |  |  | Barishal |  | 0 |  | 435
|  |  |  | Rajshahi |  | 0 |  | 1426
|  |  |  | Rangpur |  | 0 |  | 803
|  |  |  | Total |  | 0 |  | 12262
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:11 |  | Khulna (C) S/S Tr-3 405T LT Scheduled S/D Due to oil centrifuzing.
| 08:12 |  | Khulna (C) S/S Tr-3 405T HT Scheduled S/D Due to oil centrifuzing.
| 09:30 | 18:24 | Siddhirganj 230/132kV S/S 335MW EGCB 1 Scheduled S/D Due to Emergency maintenance work
| 09:39 |  | Ghorasal- Ishwardi 230 kV Ckt-2 Project Work S/D from Ishurdi 230/132kV end Due to
reconductoring work by kEC
| 10:06 |  | Naogaon 132/33kV S/S T-3 LT Project Work S/D Due to Project work
| 10:07 |  | Naogaon 132/33kV S/S T-3 HT Project Work S/D Due to Project work
| 10:38 | 14:32 | Ghorasal-Joydeb-B 132kV Ckt-1 Scheduled S/D from Joydebpur 132/33kV end Due to S/D From
pubail end.
| 12:00 |  | Day peak generation 11052 MW
|  | 12:17 | Jashore 132/33kV S/S Cap. Bank-2 is restored.
|  | 12:17 | Jashore 132/33kV S/S Cap. Bank-1 is restored.
| 13:05 | 13:32 | Chowmuhani-Feni 132 kV Ckt-1 Tripped from Feni 132/33kV end showing Quadramho-21, OC _51G
relays Due to Distance trip, O/C
| 13:40 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- GT
| 14:45 | 17:25 | Rangpur 132/33kV S/S T-2 (404T) HT Forced S/D Due to 33Kv Bus -3 red hot | [7 empty] | 45.0MW load
interrup.
| 14:45 | 17:25 | Rangpur 132/33kV S/S T-2 (404T) LT Forced S/D Due to 33Kv bus- 3 Y -Phase red hot | [7 empty] | 45.0MW load
interrup.
| 15:03 | 16:03 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Scheduled S/D Due to chandanaish 33kv | [7 empty] | 61.0MW load
|  |  | Feeder redhot maintenance. | [7 empty] | interrup.
| 15:04 | 16:02 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Scheduled S/D Due to Chadanaish 33kv | [7 empty] | 61.0MW load
|  |  | feeder redhot maintenance | [7 empty] | interrup.
| 15:17 | 17:32 | BIPTC S/S 20DF32 Tripped showing 87 relays Due to Capacitor unbalance Y-phase stage-3
operated
| 16:16 |  | Bashkhali U-1 synch
| 17:09 | 17:32 | BIPTC S/S 20DF32 Forced S/D Due to Tripped
| 18:45 | 02:11 | Rampal 400/230kV S/S Gopalganj Line-1 Reactor Forced S/D Due to Khulna ALDC Demand
| 18:45 | 02:13 | Rampal 400/230kV S/S Gopalganj Line-2 Reactor Forced S/D Due to Khulna ALDC Demand
| 19:22 | 02:57 | Rampal 400/230kV S/S Bus Reactor Forced S/D Due to Khulna ALDC Demand
| 19:30 |  | Evening Peak Generation: 12729 MW.
| 20:17 | 22:42 | Kabirpur 132/33kV S/S XFR, T-2 LT Forced S/D Due to RedHot Maintenance of TR-02 ,Y phase | [7 empty] | 40.0MW load
|  |  | 33kV incoming Bus DS . | [7 empty] | interrup.
| 20:17 | 22:41 | Kabirpur 132/33kV S/S XFR, T-2 HT Forced S/D Due to RedHot Maintenance of TR-02 Y phase | [7 empty] | 40.0MW load
|  |  | 33kV incoming Bus DS. | [7 empty] | interrup.
| 01:57 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- ST
| 02:24 | 06:42 | Goalpara 132/33kV S/S Goalpara-NWPGCL Tripped showing earth fault / over current Relay
P127 relays Due to earth fault
| 02:25 | 03:08 | Khulna(C )-Noapara 132kV Ckt-1 Tripped from Noapara 132/33kV end showing Distance Relay
-QUABRAMHO SHPM101 relays Due to Distance Relay Trip and from
Khulna (C) end showing Zone-1, blue phase relays Due to unknown
| 02:44 | 03:03 | Faridpur 132/33kV S/S Transformer-2 LT Tripped showing 132kV O/C relays Due to 33kV CB | [7 empty] | 45.0MW load
|  |  | trip | [7 empty] | interrup.
| 02:44 | 03:03 | Faridpur 132/33kV S/S Transformer-1 LT Tripped showing 132kV o/c relays Due to 33kV CB | [7 empty] | 45.0MW load
|  |  | trip | [7 empty] | interrup.
|  | 03:29 | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) is restored.
| 04:58 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 Forced S/D Due to Due to reduce
system voltage. NLDC Instruction.
| 04:58 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Forced S/D Due to Due to reduce
system voltage. NLDC Instruction.
| 06:00 |  | Minimum generation 7732 MW
| 06:48 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 27-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 192 | 4531127 | GBC 1 and 3 under maintenance
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 332 | 8092800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5103500 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 178354 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 297000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 2650438 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 31.5 | 134640 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 217576 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 12 | 372000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 379440 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 114720 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 237611 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 8 | 16992 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 271680 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 93 | 423360 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 196395 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 530 | 11755909.09 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 342 | 6389310 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 35 | 322800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2066.5 | 41685652.09
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 125280 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 26 | 266400 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1921920 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 5242782 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 252581 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 356232 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 73920 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 532800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24242 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 28 | 180654 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 330240 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 15 | 63982 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1087 | 16079999 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 38400 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 470 | 10450909.09 | Plant availability less
Chattogram Area Total |  |  |  |  | 4898.863 | 2110 | 35940341.09
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 135 | 1652000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 290 | 7496000 | Able to ON FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 215 | 7585000 | FGMO
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 36 | 853272 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 702240 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 284364 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1249096 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 30 | 217454 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 97 | 2191223 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 92 | 408480 | -
| Import (Tripura) |  | Import | 0 | 160 | 140 | 3140160 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 484780 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 60 | 309120 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 509555 | -
Cumilla Area Total |  |  |  |  | 2876.261 | 1171 | 27082744
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 160 | 3708480 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 55 | 566400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 98 | 1118400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 307970 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 313 | 5713850
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 72845 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 952000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 91560 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 150 | 3594273 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 100 | 2342700 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 711840 | Gas Restrction
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1850880 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | plant availability zero
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 23 | 472224 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7638000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 391 | 8910000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1144 | 26636322
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 888 | 21498181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 375 | 9100512 | -
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 694800 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 603 | 11527270 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1866 | 42820763
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 65 | 1528000 | GT-1 & ST under maint
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 24663272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5333090 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5760000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4317 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1836 | 37288679.73
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 403784 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Machine Problem
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 187 | 4628800 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 354 | 9298691 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 56160 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 42528 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 35520 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1424 | 27407334 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 379504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 762820 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2050 | 43015141
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 54 | 1274618 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 280656 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 43636.8 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 339355 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 190315 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 822240 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 173 | 2950820.8
Eastern Grid Total |  |  |  |  | 17423.308 | 6804.5 | 137058909.18
Western Grid Total |  |  |  |  | 11852.195 | 5925 | 126075404.53
National Grid Total |  |  |  |  | 29275.503 | 12729.5 | 263134313.71
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 27-03-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7890.08 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4372.2 | MW
i) Dhaka area |  |  | 3729.38 |  | MW | i) Khulna area |  |  |  | 1708 | MW
ii) Chattogram area |  |  | 1383.7 |  | MW | ii) Barishal area |  |  |  | 435 | MW
iii) Cumilla area |  |  | 1326 |  | MW | iii) Rajshahi area |  |  |  | 1426.2 | MW
iv) Mymensingh area |  |  | 948 |  | MW | iv) Rangpur area |  |  |  | 803 | MW
v) Sylhet area |  |  | 503 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12262.28 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 59 | 19:30 | 133 | Natore | 153 | 19:30
2 | AKSML | 18.5 | 17:00 | 68 | Hathazari | 75 | 18:30 | 134 | Nawabganj | 53.6 | 21:00
3 | Aftabnagar | 28 | 19:00 | 69 | Hatirjheel | 22 | 18:00 | 135 | Netrakona | 115 | 19:00
4 | Agargaon | 82 | 19:30 | 70 | Ishurdi | 66 | 19:00 | 136 | New | 40 | 19:00
5 | Agrabad | 50 | 22:00 | 71 | Jaldhaka | 64 | 18:30 | 137 | Niamatpur | 96 | 19:00
6 | Amnura | 41 | 19:30 | 72 | Jamalpur | 122 | 14:00 | 138 | Noapara | 41.5 | 22:00
7 | Ashuganj | 68 | 23:00 | 73 | Jashore | 145 | 19:30 | 139 | PHP | 12 | 11:00
8 | BSRM | 199 | 09:00 | 74 | Jhenaidah | 105 | 18:30 | 140 | Pabna | 82 | 19:00
9 | Bagerhat | 80 | 21:00 | 75 | Joydebpur | 92 | 19:30 | 141 | Palashbari | 108 | 19:00
10 | Bajitpur | 73 | 14:00 | 76 | Joypurhat | 64 | 20:00 | 142 | Panchagarh | 43 | 19:00
11 | Bakerganj | 10.5 | 22:00 | 77 | Juldah | 17.5 | 00:00 | 143 | Patiya | 9 | 00:00
12 | Bakulia | 70 | 22:00 | 78 | KSRM | 12 | 06:00 | 144 | Patuakhali | 65.5 | 22:00
13 | Banani | 15 | 19:00 | 79 | Kabirpur | 168 | 19:00 | 145 | Payra | 32 | 23:00
14 | Bangabhaban | 4 | 17:00 | 80 | Kachua | 87 | 20:00 | 146 | Postogola | 35 | 23:00
15 | Barapukuria | 57 | 19:00 | 81 | Kaliganj | 30 | 19:00 | 147 | Pubail | 20 | 12:00
16 | Barguna | 20 | 21:00 | 82 | Kallyanpur | 84 | 13:00 | 148 | Purbachal | 23 | 18:30
17 | Barishal | 88 | 22:00 | 83 | Kalurghat | 26 | 21:00 | 149 | Purbasadipur | 103 | 13:00
18 | Barishal-230 | 98 | 23:00 | 84 | Kamrangirchar | 39 | 13:00 | 150 | Rahanpur | 34 | 21:00
19 | Baroaulia | 54 | 19:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 1 | 00:00
20 | Baroirhat | 60 | 19:00 | 86 | Kasba | 34 | 19:00 | 152 | Rajbari | 72 | 19:00
21 | Bashundhara | 134 | 19:00 | 87 | Kazla | 80 | 14:00 | 153 | Rajendrapur | 103 | 18:30
22 | BashundharaCement | 1 | 00:00 | 88 | Keranigonj | 52 | 13:00 | 154 | Rajshahi | 112 | 21:00
23 | Beanibazar | 60 | 18:30 | 89 | Khagrachori | 32 | 18:30 | 155 | Rajshahi-230 | 74 | 21:00
24 | Benapole | 68 | 19:30 | 90 | Khulna | 58 | 22:00 | 156 | Ramganj | 100 | 19:30
25 | Bhaluka | 104 | 00:00 | 91 | Khulshi | 158 | 22:00 | 157 | Rampur | 36 | 20:00
26 | Bhandaria | 55 | 23:00 | 92 | Kishoreganj | 106 | 14:00 | 158 | Rangamati | 17 | 19:00
27 | Bhangura | 42 | 13:00 | 93 | Kodda | 191 | 20:00 | 159 | Rangpur | 124 | 18:30
28 | Bheramara(GK) | 62 | 19:00 | 94 | Kulaura | 37 | 18:30 | 160 | Ruppur | 3.6 | 11:00
29 | Bhulta | 141 | 00:00 | 95 | Kurigram | 60 | 07:00 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 76 | 19:30 | 96 | Kushtia | 130 | 19:00 | 162 | Saidpur | 89 | 13:00
31 | Bogura | 142 | 19:30 | 97 | Laksam | 30 | 19:30 | 163 | Satkhira | 138 | 19:30
32 | Borhanuddin | 92 | 22:00 | 98 | Lakshmipur | 26 | 20:00 | 164 | Satmasjid | 72 | 13:00
33 | Brahmanbaria | 126 | 19:00 | 99 | Lalbag | 25 | 13:00 | 165 | Savar | 116 | 23:00
34 | Cantonment | 124 | 20:00 | 100 | Lalmonirhat | 52 | 19:00 | 166 | SevenRings | 4.72 | 16:00
35 | Chandina | 16 | 19:00 | 101 | MI_Cement | 18.2 | 15:00 | 167 | ShahCement | 34 | 10:00
36 | Chandpur | 68 | 20:00 | 102 | Madanganj | 35 | 18:30 | 168 | Shahjadpur | 70 | 19:00
37 | Chandraghona | 37 | 19:00 | 103 | Madaripur | 103 | 20:00 | 169 | Shahjibazar | 102 | 18:30
38 | Chapai | 71 | 20:00 | 104 | Madartek | 58 | 13:00 | 170 | Shahmirpur | 53 | 23:00
39 | Charsaidpur | 39 | 20:00 | 105 | Madunaghat | 49 | 19:00 | 171 | Shariatpur | 80 | 21:00
40 | Chauddagram | 73 | 18:30 | 106 | Magura | 70 | 19:00 | 172 | Sherpur | 130 | 18:30
41 | Chhatak | 35 | 21:00 | 107 | Mahasthangarh | 71 | 19:30 | 173 | Shikalbaha | 23 | 20:00
42 | Chowmuhani | 136 | 18:00 | 108 | Maijdee | 45 | 21:00 | 174 | Shitalakhya | 46.4 | 13:00
43 | Chuadanga | 113 | 19:00 | 109 | Manikganj | 128 | 19:00 | 175 | Sholosohor | 35 | 22:00
44 | Coxsbazar | 145 | 18:30 | 110 | Maniknagar | 52 | 13:00 | 176 | Shyampur | 113 | 11:00
45 | Cumilla(N) | 123 | 18:30 | 111 | Matarbari | 53 | 19:30 | 177 | Siddhirganj | 78 | 21:00
46 | Cumilla(S) | 152 | 21:00 | 112 | Matuail | 34 | 22:00 | 178 | Sirajganj | 98 | 19:30
47 | Daganbhuiyan | 32 | 19:00 | 113 | Metrorail_Motijheel | 24 | 16:00 | 179 | Sonargaon | 80 | 20:00
48 | Daudkandi | 137 | 19:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreemongol | 71 | 19:00
49 | DhakaUniversity | 26 | 13:00 | 115 | Millgate | 48 | 22:00 | 181 | Sreepur | 90 | 18:30
50 | Dhamrai | 86 | 22:00 | 116 | Mirpur | 103 | 19:30 | 182 | Srinagar | 43.6 | 22:00
51 | Dhanmondi | 74 | 18:30 | 117 | Mirsorai | 19 | 23:00 | 183 | Sunamganj | 47 | 19:30
52 | Dohazari | 110 | 20:00 | 118 | Mirzapur | 48 | 19:30 | 184 | Sylhet | 48 | 18:30
53 | Faridpur | 140 | 20:00 | 119 | Mithapukur | 56 | 08:00 | 185 | Sylhet-132 | 87 | 21:00
54 | Fatullah | 55 | 23:00 | 120 | Modern | N/A | N/A | 186 | TK | 21 | 00:00
55 | Fenchuganj | 32 | 18:30 | 121 | Mogbazar | 36 | 19:00 | 187 | Tangail | 174 | 19:30
56 | Feni | 91 | 20:00 | 122 | Mongla | 36 | 00:00 | 188 | Taraganj | 17 | 18:30
57 | GPH | 75 | 07:00 | 123 | Motijheel | 27 | 18:30 | 189 | Tasnim | 21 | 18:30
58 | Ghatail | 92 | 18:30 | 124 | Muktagacha | 39 | 13:00 | 190 | Thakurgaon | 86 | 19:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 99 | 21:00 | 191 | Tongi | 100 | 21:00
60 | Ghorashal-230 | 86 | 21:00 | 126 | Muradnagar | 37 | 19:00 | 192 | Ullahpara | 38 | 19:30
61 | Goalpara | 33 | 13:00 | 127 | Mymensingh | 164 | 13:00 | 193 | Ullon | 43 | 19:30
62 | Gollamari | 86 | 13:00 | 128 | Nabinagar | 7 | 18:30 | 194 | Uttara | 68 | 20:00
63 | Gopalganj | 109 | 19:30 | 129 | Naogaon | 116 | 19:00 | 195 | UttaraNew | 24 | 13:00
64 | Gulshan | 74 | 19:00 | 130 | Narail | 62.5 | 19:00 | 196 | Zigatola | 72 | 13:00
65 | Halishahar | 59.5 | 21:00 | 131 | Narinda | 35 | 13:00
66 | HaripurSBU | 92 | 23:00 | 132 | Narshingdi | 131 | 22:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 27-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 11178.84 | 0 |  | 11178.84
1:00 | 10929.82 | 0 |  | 10929.82
2:00 | 10393.66 | 0 |  | 10393.66
3:00 | 9939.07 | 0 |  | 9939.07
4:00 | 9555.07 | 0 |  | 9555.07
5:00 | 9145.9 | 0 |  | 9145.9
6:00 | 9064.07 | 0 |  | 9064.07
7:00 | 9387.8 | 0 |  | 9387.8
8:00 | 9810.42 | 0 |  | 9810.42
9:00 | 9873.14 | 0 |  | 9873.14
10:00 | 9981.58 | 0 |  | 9981.58
11:00 | 10260.62 | 0 |  | 10260.62
12:00 | 11055.38 | 0 |  | 11055.38
13:00 | 11976.51 | 0 |  | 11976.51
14:00 | 11482.74 | 0 |  | 11482.74
15:00 | 11287.4 | 0 |  | 11287.4
16:00 | 10884.42 | 0 |  | 10884.42
17:00 | 10541.98 | 0 |  | 10541.98
18:00 | 10767.5 | 0 |  | 10767.5
19:00 | 12542.2 | 0 |  | 12542.2
19:30 | 12729.5 | 0 |  | 12729.5
20:00 | 12597.5 | 0 |  | 12597.5
21:00 | 12671.3 | 0 |  | 12671.3
22:00 | 12478.1 | 0 |  | 12478.1
23:00 | 12206 | 0 |  | 12206
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 27-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5614 | 5564.84 | 11178.84 | DAILY GENERATION CURVE
00:30 | 5616 | 5438.33 | 11054.33
01:00 | 5618 | 5311.82 | 10929.82 | 27-03-2026
01:30 | 5548 | 5113.74 | 10661.74
02:00 | 5478 | 4915.66 | 10393.66
02:30 | 5389.5 | 4776.865 | 10166.365
03:00 | 5301 | 4638.07 | 9939.07
03:30 | 5308 | 4439.07 | 9747.07
04:00 | 5315 | 4240.07 | 9555.07
04:30 | 5185.5 | 4164.985 | 9350.485
05:00 | 5056 | 4089.9 | 9145.9
05:30 | 5016.5 | 4088.485 | 9104.985
06:00 | 4977 | 4087.07 | 9064.07
06:30 | 5074.075 | 4151.86 | 9225.935
07:00 | 5171.15 | 4216.65 | 9387.8
07:30 | 5281.485 | 4317.625 | 9599.11
08:00 | 5391.82 | 4418.6 | 9810.42
08:30 | 5327.32 | 4514.46 | 9841.78
09:00 | 5262.82 | 4610.32 | 9873.14
09:30 | 5285.46 | 4641.9 | 9927.36
10:00 | 5308.1 | 4673.48 | 9981.58
10:30 | 5312.61 | 4808.49 | 10121.1
11:00 | 5317.12 | 4943.5 | 10260.62
11:30 | 5484.82 | 5173.18 | 10658
12:00 | 5652.52 | 5402.86 | 11055.38
12:30 | 5736.935 | 5779.01 | 11515.945
13:00 | 5821.35 | 6155.16 | 11976.51
13:30 | 5767.525 | 5962.1 | 11729.625
14:00 | 5713.7 | 5769.04 | 11482.74
14:30 | 5652.44 | 5732.63 | 11385.07
15:00 | 5591.18 | 5696.22 | 11287.4
15:30 | 5405.155 | 5680.755 | 11085.91
16:00 | 5219.13 | 5665.29 | 10884.42
16:30 | 5255.645 | 5457.555 | 10713.2
17:00 | 5292.16 | 5249.82 | 10541.98
17:30 | 5400.33 | 5254.41 | 10654.74
18:00 | 5508.5 | 5259 | 10767.5
18:30 | 6075.35 | 5579.5 | 11654.85
19:00 | 6642.2 | 5900 | 12542.2
19:30 | 6804.5 | 5925 | 12729.5
20:00 | 6671.5 | 5926 | 12597.5
20:30 | 6723.4 | 5911 | 12634.4 |  | Executive Engineer
21:00 | 6775.3 | 5896 | 12671.3 |  | Network Operation Division
21:30 | 6713.2 | 5861.5 | 12574.7
22:00 | 6651.1 | 5827 | 12478.1
22:30 | 6515.05 | 5827 | 12342.05
23:00 | 6379 | 5827 | 12206

## En-Curve
QF-LDC-12
Date | 27-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3680 | 1879 | 884 | 0 | 128 | 1395.84 | 80 | 3098 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3681 | 1876 | 884 | 0 | 126 | 1331.83 | 80 | 3032.5 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 27-03-2026
01:00 | 3682 | 1873 | 884 | 0 | 124 | 1267.82 | 80 | 2967 | 0 | 52 | 0 | 0 | 0 | 0 | 0
01:30 | 3682 | 1855 | 886 | 0 | 124 | 1194.24 | 80 | 2806 | 0 | 34.5 | 0 | 0 | 0 | 0 | 0 | Energy Generated | 263.1343 |  | MKWHr
02:00 | 3682 | 1837 | 888 | 0 | 124 | 1120.66 | 80 | 2645 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3644.5 | 1844 | 888.5 | 0 | 120 | 1066.365 | 80 | 2513.5 | 0 | 8.5 | 0 | 0 | 0 | 1 | 0 | Total Energy Requirement | 263.1343 |  | MKWHr
03:00 | 3607 | 1851 | 889 | 0 | 116 | 1012.07 | 80 | 2382 | 0 | 0 | 0 | 0 | 0 | 2 | 0
03:30 | 3610.5 | 1856.5 | 889 | 0 | 116 | 917.07 | 80 | 2277 | 0 | 0 | 0 | 0 | 0 | 1 | 0
04:00 | 3614 | 1862 | 889 | 0 | 116 | 822.07 | 80 | 2172 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 3500 | 1845.5 | 889 | 0 | 119 | 822.485 | 80 | 2094.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 3386 | 1829 | 889 | 0 | 122 | 822.9 | 80 | 2017 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 3402.5 | 1768 | 889 | 0 | 117 | 824.485 | 80 | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:00 | 3419 | 1707 | 889 | 0 | 112 | 826.07 | 80 | 2031 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 3449 | 1781.5 | 888.5 | 0 | 113 | 830.49 | 80 | 2045 | 38.445 | 0 | 0 | 0 | 0 | 0 | 0
07:00 | 3479 | 1856 | 888 | 0 | 114 | 834.91 | 80 | 2059 | 76.89 | 0 | 0 | 0 | 0 | 0 | 0
07:30 | 3540.5 | 1900.5 | 888.5 | 0 | 115 | 831.26 | 80 | 2050.5 | 163.35 | 0 | 29.5 | 0 | 0 | 0 | 0
08:00 | 3602 | 1945 | 889 | 0 | 116 | 827.61 | 80 | 2042 | 249.81 | 0 | 59 | 0 | 0 | 0 | 0
08:30 | 3489 | 1963 | 889 | 0 | 116 | 825.805 | 80 | 2078 | 326.475 | 0 | 74.5 | 0 | 0 | 0 | 0
09:00 | 3376 | 1981 | 889 | 0 | 116 | 824 | 80 | 2114 | 403.14 | 0 | 90 | 0 | 0 | 0 | 0
09:30 | 3362 | 1987.5 | 889 | 0 | 118 | 826 | 80 | 2134.5 | 453.86 | 0 | 76.5 | 0 | 0 | 0 | 0
10:00 | 3348 | 1994 | 889 | 0 | 120 | 828 | 80 | 2155 | 504.58 | 0 | 63 | 0 | 0 | 0 | 0
10:30 | 3330.5 | 1977.5 | 889.5 | 0 | 123 | 889 | 80 | 2169 | 588.6 | 11 | 63 | 0 | 0 | 0 | 0
11:00 | 3313 | 1961 | 890 | 0 | 126 | 950 | 80 | 2183 | 672.62 | 22 | 63 | 0 | 0 | 0 | 0
11:30 | 3331.5 | 1956.5 | 889.5 | 0 | 133 | 1065.5 | 80 | 2423.5 | 640 | 27.5 | 110.5 | 0 | 0 | 0.5 | 0
12:00 | 3350 | 1952 | 889 | 0 | 140 | 1181 | 80 | 2664 | 607.38 | 33 | 158 | 0 | 0 | 1 | 0
12:30 | 3274 | 1991.5 | 889 | 0 | 141 | 1289.5 | 80 | 2910.5 | 651.545 | 51.5 | 233.4 | 0 | 0 | 4 | 0
13:00 | 3198 | 2031 | 889 | 0 | 142 | 1398 | 80 | 3157 | 695.71 | 70 | 308.8 | 0 | 0 | 7 | 0
13:30 | 3229 | 2026.5 | 889 | 0 | 142 | 1312.5 | 80 | 3112 | 628.725 | 82 | 220.4 | 0 | 0 | 7.5 | 0
14:00 | 3260 | 2022 | 889 | 0 | 142 | 1227 | 80 | 3067 | 561.74 | 94 | 132 | 0 | 0 | 8 | 0
14:30 | 3238 | 2009.25 | 889 | 0 | 142 | 1228 | 80 | 3079.5 | 484.82 | 94 | 132.5 | 0 | 0 | 8 | 0
15:00 | 3216 | 1996.5 | 889 | 0 | 142 | 1229 | 80 | 3092 | 407.9 | 94 | 133 | 0 | 0 | 8 | 0
15:30 | 3201 | 1844 | 888.5 | 0 | 138 | 1239.5 | 80 | 3119.5 | 350.41 | 85.5 | 133.5 | 0 | 0 | 6 | 0
16:00 | 3186 | 1691.5 | 888 | 0 | 134 | 1250 | 80 | 3147 | 292.92 | 77 | 134 | 0 | 0 | 4 | 0
16:30 | 3177.5 | 1677.5 | 888 | 0 | 127 | 1201 | 80 | 3143 | 202.7 | 77 | 134 | 0 | 0 | 5.5 | 0
17:00 | 3169 | 1663.5 | 888 | 0 | 120 | 1152 | 80 | 3139 | 112.48 | 77 | 134 | 0 | 0 | 7 | 0
17:30 | 3136.5 | 1715 | 888.5 | 0 | 126 | 1203.5 | 80 | 3144 | 57.74 | 93 | 207 | 0 | 0 | 3.5 | 0
18:00 | 3104 | 1766.5 | 889 | 0 | 132 | 1255 | 80 | 3149 | 3 | 109 | 280 | 0 | 0 | 0 | 0
18:30 | 3227 | 1894.25 | 888.5 | 0 | 136 | 1355 | 80 | 3395 | 1.5 | 109.5 | 568.1 | 0 | 0 | 0 | 0
19:00 | 3350 | 2022 | 888 | 0 | 140 | 1455 | 80 | 3641 | 0 | 110 | 856.2 | 0 | 0 | 0 | 0
19:30 | 3241 | 2001 | 888 | 0 | 140 | 1424 | 80 | 3765 | 0 | 127 | 1063.5 | 0 | 0 | 0 | 0
20:00 | 3330 | 2009 | 889 | 0 | 138 | 1473 | 80 | 3784 | 0 | 67 | 827.5 | 0 | 0 | 0 | 0
20:30 | 3320.5 | 2014.5 | 889 | 0 | 144 | 1462.5 | 80 | 3833.5 | 0 | 67 | 823.4 | 0 | 0 | 0 | 0
21:00 | 3311 | 2020 | 889 | 0 | 150 | 1452 | 80 | 3883 | 0 | 67 | 819.3 | 0 | 0 | 0 | 0
21:30 | 3329 | 2018 | 888.5 | 0 | 148 | 1447.5 | 80 | 3890 | 0 | 58.5 | 715.2 | 0 | 0 | 0 | 0
22:00 | 3347 | 2016 | 888 | 0 | 146 | 1443 | 80 | 3897 | 0 | 50 | 611.1 | 0 | 0 | 0 | 0
22:30 | 3323 | 2016.5 | 888 | 0 | 148 | 1450 | 80 | 3895 | 0 | 50 | 491.55 | 0 | 0 | 0 | 0
23:00 | 3299 | 2017 | 888 | 0 | 150 | 1457 | 80 | 3893 | 0 | 50 | 372 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 27-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 414 | 05:00 | 393 | 13:00 | Madunaghat | 404 | 07:00 | 396 | 13:00
Amtali | 421 | 06:00 | 408 | 13:00 | Meghnaghat | 416 | 05:00 | 399 | 13:00
Ashuganj | 416 | 05:00 | 398 | 13:00 | Payra | 421 | 05:00 | 410 | 13:00
Bhulta | 410 | 05:00 | 387 | 13:00 | Rahanpur | 414 | 05:00 | 399 | 00:00
Bibiana | 417 | 04:00 | 405 | 23:00 | Rampal | 411 | 04:00 | 394 | 15:00
BIPTC | 397 | 04:00 | 388 | 15:00
Bogura | 410 | 05:00 | 389 | 00:00
Gopalganj | 416 | 05:00 | 398 | 13:00
Kaliakoir | 411 | 05:00 | 384 | 13:00
Korerhat | 412 | 05:00 | 399 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 238 | 05:00 | 223 | 13:00 | Jhenaidah | 233 | 05:00 | 216 | 18:30
AKSML | 235 | 05:00 | 227.5 | 18:30 | Kachua | 234 | 07:00 | 223 | 23:00
Aminbazar | 237 | 05:00 | 223 | 13:00 | Kaliakoir | 240 | 05:00 | 225 | 13:00
Ashuganj | 237 | 06:00 | 225 | 13:00 | Keranigonj | 236 | 05:00 | 222 | 13:00
Ashuganj-400 | 237 | 06:00 | 225 | 13:00 | Khulna(S) | 236 | 05:00 | 221 | 13:00
Baghabari | 237 | 05:00 | 227 | 19:00 | Korerhat | 234 | 06:00 | 226 | 13:00
Barapukuria | 228 | 03:00 | 214 | 13:00 | Madunaghat | 234 | 05:00 | 228 | 13:00
Barapukuria-230 | 228 | 03:00 | 214 | 13:00 | Madunaghat-400 | 234 | 06:00 | 229 | 13:00
Barishal | 232 | 05:00 | 223 | 13:00 | Maniknagar | 236 | 03:00 | 223 | 13:00
Bheramara | 235 | 05:00 | 221 | 12:00 | Meghnaghat | 243 | 04:00 | 227 | 14:00
Bhulta | 237 | 05:00 | 224 | 13:00 | Meghnaghat-400 | 236 | 05:00 | 224 | 13:00
Bibiana | 243 | 05:00 | 232 | 18:30 | Mirsorai | 239 | 05:00 | 232 | 13:00
BIPTC | 238 | 05:00 | 221 | 18:30 | Purbasadipur | 227 | 04:00 | 213 | 13:00
Bogura | 236 | 05:00 | 224 | 13:00 | Rajshahi | 234 | 05:00 | 219 | 12:00
Bogura-400 | 235 | 04:00 | 224 | 00:00 | Rampal | 235 | 04:00 | 220 | 19:00
Borhanuddin | 234 | 07:00 | 228 | 13:00 | Rampur | N/A | N/A | N/A | N/A
BSRM | 234 | 05:00 | 225 | 13:00 | Rampura | 236 | 05:00 | 224 | 13:00
Chowmuhani | 230 | 10:00 | 224 | 13:00 | Shikalbaha | 232 | 08:00 | 226 | 12:00
Cumilla(N) | 234 | 06:00 | 224 | 13:00 | Shyampur | 236 | 05:00 | 223 | 13:00
Faridpur | 232 | 05:00 | 220 | 13:00 | Siddhirganj | 237 | 06:00 | 22 | 18:00
Fenchuganj | 243 | 09:00 | 235 | 18:30 | Sirajgonj | 241 | 04:00 | 232 | 13:00
Feni | 235 | 05:00 | 226 | 13:00 | Sreepur | 235 | 05:00 | 221 | 13:00
Ghorashal | 242 | 05:00 | 230 | 11:00 | Tongi | 239 | 04:00 | 225 | 23:00
Ghorashal-230 | 237 | 06:00 | 223 | 23:00
Gopalganj | 231 | 05:00 | 222 | 18:30
GPH | 234 | 05:00 | 227 | 13:00
Haripur | 237 | 05:00 | 224 | 13:00
Hasnabad | 235 | 05:00 | 224 | 12:00
Hathazari | 233 | 07:00 | 226 | 13:00
Ishurdi | 238 | 05:00 | 224 | 18:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 04:00 | 126 | 13:00 | Madunaghat | 136 | 05:00 | 131 | 13:00
Agargaon | 136 | 05:00 | 126 | 13:00 | Magura | 133 | 06:00 | 118 | 18:30
Agrabad | 134 | 07:00 | 129 | 12:00 | Mahasthangarh | 134 | 04:00 | 125 | 13:00
AKS | 130 | 00:00 | 128 | 12:00 | Maijdee | 130 | 06:00 | 124 | 13:00
Aminbazar | 138 | 06:00 | 129 | 00:00 | Manikganj | 132 | 06:00 | 120 | 21:00
Amnura | 136 | 04:00 | 127 | 12:00 | Maniknagar | 133 | 04:00 | 125 | 13:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 116 | 09:00 | 108 | 18:30
Ashuganj-230 | 143 | 03:00 | 135 | 13:00 | Matuail | 136 | 02:00 | 129.5 | 13:00
Bagerhat | 131 | 06:00 | 116 | 18:30 | Metrorail_Motijheel | 133 | 05:00 | 125 | 13:00
Bajitpur | 137 | 05:00 | 125 | 13:00 | Metrorail_Uttara | 139 | 08:00 | 128 | 13:00
Bakerganj | 135 | 06:00 | 129 | 13:00 | Millgate | 137 | 04:00 | 126 | 13:00
Bakulia | 135 | 07:00 | 129 | 13:00 | Mirpur | 137 | 04:00 | 128 | 12:00
Banani | 135 | 07:00 | 126 | 23:00 | Mirzapur | 136 | 04:00 | 122 | 13:00
Bangabhaban | 133 | 04:00 | 125 | 12:00 | Mithapukur | 131 | 04:00 | 121 | 13:00
Barapukuria | 130 | 03:00 | 121 | 13:00 | MI_Cement | 136.3 | 06:00 | 127 | 13:00
Barguna | 135 | 04:00 | 129 | 13:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 135 | 05:00 | 128 | 13:00 | Mogbazar | 134 | 05:00 | 128 | 12:00
Barishal-230 | 135 | 04:00 | 129 | 13:00 | Mongla | 131 | 04:00 | 119 | 18:30
Baroaulia | 133 | 03:00 | 130 | 12:00 | Motijheel | 133 | 03:00 | 125 | 12:00
Baroirhat | 134 | 05:00 | 129 | 13:00 | Muktagacha | 133 | 09:00 | 121 | 13:00
Bashundhara | 136 | 04:00 | 126 | 13:00 | Munshiganj | 134 | 06:00 | 127 | 13:00
BashundharaCement | 133 | 00:00 | 129 | 14:00 | Muradnagar | 133 | 05:00 | 124 | 23:00
Beanibazar | 134 | 08:00 | 124 | 18:30 | Mymensingh | 134 | 09:00 | 119 | 13:00
Benapole | 131 | 05:00 | 112 | 12:00 | Nabinagar | 138 | 05:00 | 126 | 13:00
Bhaluka | 137 | 06:00 | 126 | 13:00 | Naogaon | 138 | 04:00 | 122 | 13:00
Bhandaria | 130 | 05:00 | 123 | 22:00 | Narail | 134 | 05:00 | 117 | 19:00
Bhangura | 135 | 05:00 | 127 | 13:00 | Narinda | 133 | 04:00 | 125 | 13:00
Bheramara | 136 | 04:00 | 130 | 18:30 | Narshingdi | 133 | 06:00 | 125 | 12:00
Bheramara(GK) | 136 | 04:00 | 131 | 18:30 | Natore | 134 | 05:00 | 127 | 13:00
Bhulta | 132 | 05:00 | 125 | 00:00 | Nawabganj | 134 | 05:00 | 125 | 13:00
Bog-Sherpur | 136 | 05:00 | 128 | 00:00 | Netrakona | 133 | 18:00 | 119 | 13:00
Bogura | 133 | 05:00 | 129 | 00:00 | New | 137 | 06:00 | 127 | 12:00
Bogura-230 | 136 | 04:00 | 128 | 13:00 | Niamatpur | 137 | 03:00 | 131 | 00:00
Brahmanbaria | 138 | 05:00 | 129 | 13:00 | Noapara | 132 | 06:00 | 121 | 18:30
Cantonment | 135 | 05:00 | 126 | 13:00 | Pabna | 136 | 05:00 | 129 | 18:30
Chandina | 135 | 05:00 | 128 | 23:00 | Palashbari | 130 | 05:00 | 119 | 13:00
Chandpur | 131 | 19:00 | 126 | 14:00 | Panchagarh | 138 | 05:00 | 126 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 136 | 06:00 | 131 | 12:00 | Patiya | 131 | 05:00 | 126 | 13:00
Chapai | 136 | 05:00 | 130 | 19:30 | Patuakhali | 135 | 05:00 | 130 | 12:00
Charsaidpur | 134 | 06:00 | 128 | 13:00 | Payra | 137 | 04:00 | 134 | 00:00
Chauddagram | 133 | 06:00 | 126 | 13:00 | PHP | 133 | 06:00 | 128 | 13:00
Chhatak | 132 | 05:00 | 122 | 21:00 | Postogola | 137 | 05:00 | 129 | 13:00
Chowmuhani | 129 | 05:00 | 124 | 14:00 | Pubail | 139 | 07:00 | 133 | 12:00
Chuadanga | 131 | 06:00 | 116 | 23:00 | Purbachal | 137 | 04:00 | 126 | 12:00
Coxsbazar | 121 | 15:00 | 108 | 18:30 | Purbasadipur | 132 | 06:00 | 122 | 13:00
Cumilla(N) | 136 | 06:00 | 128 | 13:00 | Rahanpur | 138 | 03:00 | 133 | 00:00
Cumilla(S) | 135 | 06:00 | 120 | 12:00 | Rahanpur-400 | 139 | 05:00 | 133 | 00:00
Daganbhuiyan | 132 | 10:00 | 126 | 13:00 | Rahim | 136 | 03:00 | 130 | 14:00
Daudkandi | 132 | 05:00 | 121 | 22:00 | Rajbari | 133 | 05:00 | 125 | 13:00
DhakaUniversity | 134 | 06:00 | 126 | 13:00 | Rajendrapur | 139 | 06:00 | 128 | 13:00
Dhamrai | 138 | 05:00 | 127 | 12:00 | Rajshahi | 155 | 19:00 | 125 | 12:00
Dhanmondi | 137 | 06:00 | 130 | 13:00 | Rajshahi-230 | 134 | 04:00 | 126 | 12:00
Dohazari | 128 | 15:00 | 121 | 18:30 | Ramganj | 129 | 06:00 | 122 | 23:00
Faridpur | 134 | 05:00 | 128 | 13:00 | Rampur | 133 | 05:00 | 128 | 12:00
Fatullah | 137 | 05:00 | 128 | 13:00 | Rampura | 134 | 05:00 | 126 | 13:00
Fenchuganj | 138 | 09:00 | 132 | 18:30 | Rangamati | 135 | 05:00 | 130 | 13:00
Feni | 130 | 05:00 | 125 | 15:00 | Rangpur | 130 | 04:00 | 122 | 08:00
Feni-230 | 132 | 05:00 | 126 | 18:30 | Ruppur | 137 | 06:00 | 131 | 18:30
Ghatail | 133 | 04:00 | 117 | 13:00 | Saidpur | 130 | 03:00 | 119 | 13:00
Ghorashal | 142 | 04:00 | 135 | 11:00 | Satkhira | 131 | 06:00 | 116 | 19:00
Goalpara | 135 | 05:00 | 123 | 18:30 | Satmasjid | 135 | 05:00 | 126 | 13:00
Gollamari | 136 | 05:00 | 125 | 18:30 | Savar | 137 | 05:00 | 129 | 12:00
Gopalganj | 135 | 05:00 | 126 | 13:00 | SevenRings | 144 | 05:00 | 135 | 21:00
Gopalganj-400 | 138 | 05:00 | -138 | 05:00 | ShahCement | 134 | 07:00 | 128 | 13:00
Gulshan | 133 | 04:00 | 125 | 13:00 | Shahjadpur | 140 | 04:00 | 132 | 18:30
Halishahar | 134 | 05:00 | 129 | 13:00 | Shahjibazar | 138 | 04:00 | 130 | 19:00
Haripur | 136 | 05:00 | 129 | 13:00 | Shahmirpur | 134 | 05:00 | 129 | 12:00
HaripurSBU | 136 | 05:00 | 129 | 13:00 | Shariatpur | 136 | 06:00 | 127 | 13:00
Hasnabad | 138 | 05:00 | 130 | 14:00 | Sherpur | 130 | 20:00 | 113 | 07:00
Hathazari | 136 | 07:00 | 132 | 12:00 | Shikalbaha | 123 | 06:00 | 118 | 13:00
Hatirjheel | 134 | 05:00 | 126 | 13:00 | Shikalbaha-230 | 135 | 07:00 | 130 | 12:00
Ishurdi | 138 | 04:00 | 131 | 18:30 | Shitalakhya | 136.3 | 06:00 | 127 | 13:00
Jaldhaka | 129 | 06:00 | 118 | 13:00 | Sholosohor | 135 | 05:00 | 131 | 13:00
Jamalpur | 134 | 19:30 | 113 | 07:00 | Shyampur | 135 | 06:00 | 132 | 15:00
Jashore | 133 | 06:00 | 115 | 12:00 | Shyampur-230 | 137 | 05:00 | 128 | 13:00
Jhenaidah | 134 | 05:00 | 122 | 12:00 | Siddhirganj | 136 | 03:00 | 129 | 13:00
Jhenaidah-230 | 135 | 05:00 | 122 | 13:00 | Sirajganj | 135 | 04:00 | 126 | 18:30
Joydebpur | 139 | 05:00 | 131 | 13:00 | Sonargaon | 135 | 00:00 | 127 | 13:00
Joypurhat | 131 | 05:00 | 119 | 13:00 | Sreemongol | 137 | 07:00 | 129 | 19:00
Juldah | 133 | 03:00 | 130 | 12:00 | Sreepur | 141 | 05:00 | 131 | 13:00
Kabirpur | 137 | 04:00 | 125 | 21:00 | Srinagar | 135 | 05:00 | 125 | 13:00
Kachua | 132 | 05:00 | 126 | 23:00 | SSM | 139 | 06:00 | 133 | 09:00
Kaliakoir | 138 | 04:00 | 127 | 13:00 | Sunamganj | 130 | 06:00 | 120 | 18:30
Kaliganj | 134 | 05:00 | 120 | 12:00 | Sylhet | 134 | 07:00 | 125 | 19:00
Kallyanpur | 138 | 05:00 | 129 | 12:00 | Sylhet-132 | 134 | 06:00 | 126 | 13:00
Kalurghat | 135 | 05:00 | 131 | 13:00 | Tangail | 132 | 04:00 | 120 | 13:00
Kamrangirchar | 137 | 05:00 | 125 | 13:00 | Taraganj | 131 | 04:00 | 122 | 12:00
Kaptai | N/A | N/A | N/A | N/A | Tasnim | 135 | 05:00 | 128 | 14:00
Kasba | 133 | 06:00 | 124 | 13:00 | Thakurgaon | 135 | 04:00 | 123 | 13:00
Kazla | 133 | 06:00 | 125 | 13:00 | TK | 136 | 06:00 | 131 | 12:00
Keranigonj | 135 | 05:00 | 126 | 13:00 | Tongi | 138 | 04:00 | 128 | 21:00
Khagrachori | 134 | 05:00 | 128 | 18:30 | Ullahpara | 135 | 02:00 | 128 | 18:30
Khulna | 133 | 09:00 | 123 | 18:30 | Ullon | 134 | 05:00 | 126 | 13:00
Khulna(S) | 136 | 05:00 | 124 | 19:00 | Uttara | 138 | 05:00 | 128 | 12:00
Khulshi | 132 | 04:00 | 128 | 12:00 | UttaraNew | 137 | 04:00 | 128 | 12:00
Kishoreganj | 137 | 05:00 | 123 | 13:00 | Zigatola | 135 | 06:00 | 125 | 13:00
Kodda | 140 | 05:00 | 124 | 11:00
Korerhat | 135 | 06:00 | 131 | 00:00
KSRM | 135 | 01:00 | 130 | 23:00
Kulaura | 137 | 04:00 | 131 | 13:00
Kurigram | 129 | 05:00 | 117 | 07:00
Kushtia | 134 | 04:00 | 127 | 18:30
Laksam | 131 | 05:00 | 126 | 13:00
Lakshmipur | 130 | 06:00 | 125 | 13:00
Lalbag | 134 | 04:00 | 127 | 12:00
Lalmonirhat | 128 | 05:00 | 119 | 13:00
Madanganj | 133 | 00:00 | 129 | 14:00
Madaripur | 135 | 06:00 | 130 | 13:00
Madartek | 134 | 05:00 | 126 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 27-03-2026 | [28 empty] | Date: | 27-03-2026 | [28 empty] | Date: | 27-03-2026 | [28 empty] | Date: | 27-03-2026 | [28 empty] | Date: | 27-03-2026 | [17 empty] | Date: | 27-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [17 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 342.010 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 329 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 17 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 23 | 470 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 335 | 0 | 295 | 51 | 0 | 196 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 128 | 0 | 0 | 0 | 315 | 0 | 324 | 41 | 0 | 151 | 0 | 22 | 0 | 80 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 5614 | 884 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 537 | 0 | 0 | 0 | 1395.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 398 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 65 | 220 | 0 | 0 | 1182 | 0 | 5564.84 | 11178.84 | 85.98
01:00 | 0 | 0 | 18 | 192 | 0 | 0 | 0 | 0 | 326 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 17 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 23 | 470 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 575 | 0 | 0 | 0 | 335 | 0 | 300 | 51 | 0 | 194 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 124 | 0 | 0 | 0 | 310 | 0 | 324 | 41 | 0 | 151 | 0 | 22 | 0 | 80 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 5618 | 884 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418 | 0 | 0 | 0 | 1267.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 398 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 65 | 220 | 0 | 0 | 1175 | 0 | 5311.82 | 10929.82 | 85.97
02:00 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 320 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 17 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 23 | 470 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 350 | 0 | 300 | 51 | 0 | 192 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 124 | 0 | 0 | 0 | 310 | 0 | 324 | 41 | 0 | 150 | 0 | 22 | 0 | 80 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 5478 | 888 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 0 | 1120.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 396 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 65 | 220 | 0 | 0 | 1050 | 0 | 4915.66 | 10393.66 | 85.96
03:00 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 330 | 0 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 17 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 23 | 470 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 416 | 0 | 0 | 0 | 355 | 0 | 300 | 51 | 11 | 65 | 30 | 0 | 100 | 0 | 0 | 20 | 0 | 116 | 0 | 0 | 0 | 310 | 0 | 324 | 41 | 0 | 151 | 0 | 17 | 0 | 80 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 5301 | 889 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 1012.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 399 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 65 | 220 | 0 | 0 | 900 | 0 | 4638.07 | 9939.07 | 85.95
04:00 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 329 | 0 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 17 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 23 | 470 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 393 | 0 | 320 | 51 | 42 | 0 | 40 | 0 | 101 | 0 | 0 | 20 | 0 | 116 | 0 | 0 | 0 | 315 | 0 | 330 | 41 | 0 | 151 | 0 | 17 | 0 | 80 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 5315 | 889 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 822.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 398 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 65 | 218 | 0 | 0 | 700 | 0 | 4240.07 | 9555.07 | 85.94
05:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 306 | 0 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 23 | 360 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 415 | 0 | 0 | 0 | 393 | 0 | 320 | 51 | 48 | 0 | 43 | 0 | 50 | 0 | 0 | 20 | 0 | 122 | 0 | 0 | 0 | 310 | 0 | 305 | 41 | 0 | 137 | 0 | 17 | 0 | 80 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 5056 | 889 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 822.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 351 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 65 | 215 | 0 | 0 | 650 | 0 | 4089.9 | 9145.9 | 85.93
06:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 312 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 23 | 360 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 425 | 0 | 0 | 0 | 393 | 0 | 325 | 51 | 48 | 0 | 43 | 0 | 50 | 0 | 0 | 20 | 0 | 112 | 0 | 0 | 0 | 315 | 0 | 335 | 41 | 0 | 136 | 0 | 17 | 0 | 0 | 30 | 100 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 4977 | 889 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 826.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 354 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 65 | 213 | 0 | 0 | 650 | 0 | 4087.07 | 9064.07 | 85.92
07:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 316 | 0 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 3 | 0 | 20 | 14 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23 | 80 | 0 | 23 | 360 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 430 | 1 | 0 | 0 | 393 | 0 | 340 | 51 | 47 | 0 | 42 | 0 | 50 | 0 | 0 | 20 | 0 | 114 | 0 | 11 | 0 | 315 | 0 | 331 | 41 | 0 | 139 | 0 | 17 | 0 | 75 | 30 | 101 | 0 | 0 | 0 | 0 | 0 | 160 | 0.2 | 5.72 | 0 | 5171.15 | 888 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 393 | 0 | 0 | 0 | 834.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.74 | 11 | 0 | 0 | 5.84 | 0 | 0 | 0 | 0 | 161 | 0 | 389 | 0 | 0.51 | 0 | 54 | 0 | 2 | 0 | 0 | 0 | 0 | 0.6 | 21 | 0.05 | 0 | 172 | 65 | 211 | 0 | 0 | 650 | 0 | 4216.65 | 9387.8 | 85.91
08:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 338 | 0 | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 12 | 0 | 25 | 14 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86 | 80 | 0 | 21 | 360 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 427 | 4 | 0 | 28 | 393 | 0 | 335 | 51 | 48 | 0 | 42 | 0 | 100 | 0 | 0 | 20 | 0 | 116 | 0 | 29 | 0 | 315 | 0 | 360 | 41 | 0 | 155 | 3 | 17 | 0 | 75 | 30 | 100 | 0 | 0 | 0 | 24 | 35 | 159 | 0.8 | 15.16 | 0 | 5391.82 | 889 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 380 | 0 | 0 | 0 | 827.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.66 | 38 | 0 | 0 | 20.3 | 0 | 0 | 0 | 0 | 186 | 0 | 414 | 0 | 1.81 | 0 | 54 | 0 | 5 | 0 | 0 | 0 | 0 | 2 | 62 | 0.22 | 0 | 171 | 65 | 215 | 0 | 0 | 650 | 0 | 4418.6 | 9810.42 | 85.9
09:00 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 341 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 22 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.47 | 80 | 0 | 21 | 360 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 429 | 13 | 0 | 35 | 393 | 0 | 345 | 51 | 48 | 0 | 40 | 0 | 98 | 0 | 0 | 20 | 0 | 116 | 0 | 48 | 0 | 310 | 0 | 360 | 41 | 0 | 158 | 7 | 17 | 0 | 80 | 30 | 100 | 0 | 0 | 0 | 55 | 35 | 157 | 1.3 | 23.05 | 0 | 5262.82 | 889 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 384 | 0 | 0 | 0 | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.22 | 67 | 0 | 0 | 38.38 | 0 | 0 | 0 | 0 | 196 | 0 | 414 | 0 | 3.36 | 0 | 54 | 0 | 19 | 0 | 0 | 0 | 0 | 3 | 72 | 0.36 | 0 | 172 | 65 | 220 | 0 | 0 | 715 | 0 | 4610.32 | 9873.14 | 85.89
10:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 345 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 22 | 14 | 0 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.15 | 80 | 0 | 21 | 360 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 432 | 17 | 0 | 35 | 393 | 0 | 315 | 51 | 46 | 0 | 40 | 0 | 98 | 0 | 0 | 20 | 0 | 120 | 0 | 60 | 0 | 320 | 0 | 400 | 41 | 0 | 148 | 9 | 17 | 0 | 80 | 30 | 100 | 0 | 0 | 0 | 55 | 8 | 155 | 1.7 | 34.25 | 0 | 5308.1 | 889 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 388 | 0 | 0 | 0 | 828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.79 | 91 | 0 | 0 | 51.26 | 0 | 0 | 0 | 0 | 186 | 0 | 397 | 0 | 4.54 | 0 | 54 | 0 | 12 | 0 | 0 | 0 | 0 | 3.3 | 60 | 0.59 | 0 | 171 | 65 | 220 | 0 | 0 | 750 | 0 | 4673.48 | 9981.58 | 85.88
11:00 | 0 | 6 | 16 | 192 | 0 | 0 | 0 | 0 | 347 | 0 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 22 | 14 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.54 | 80 | 0 | 21 | 360 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 430 | 18 | 0 | 35 | 393 | 0 | 315 | 51 | 47 | 0 | 40 | 0 | 96 | 0 | 0 | 20 | 0 | 126 | 0 | 68 | 0 | 320 | 0 | 394 | 41 | 0 | 147 | 10 | 17 | 0 | 80 | 30 | 99 | 0 | 0 | 0 | 55 | 8 | 155 | 1.9 | 45.68 | 0 | 5317.12 | 890 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 382 | 0 | 0 | 0 | 950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.7 | 107 | 0 | 0 | 59.26 | 0 | 0 | 0 | 0 | 169 | 0 | 384 | 0 | 3.72 | 0 | 54 | 0 | 28 | 0 | 0 | 0 | 0 | 6.2 | 142 | 0.62 | 0 | 172 | 65 | 220 | 0 | 0 | 785 | 0 | 4943.5 | 10260.62 | 85.88
12:00 | 0 | 17 | 16 | 192 | 0 | 0 | 0 | 0 | 357 | 0 | 272 | 10 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 0 | 495 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3.56 | 80 | 1 | 19 | 470 | 0 | 0 | 0 | 0 | 2 | 214 | 0 | 0 | 0 | 520 | 18 | 2 | 35 | 390 | 0 | 315 | 51 | 48 | 0 | 41 | 1 | 96 | 9 | 0 | 20 | 0 | 140 | 0 | 70 | 0 | 325 | 0 | 401 | 41 | 0 | 149 | 11 | 17 | 0 | 80 | 30 | 99 | 0 | 0 | 0 | 68 | 35 | 152 | 1 | 46.96 | 0 | 5652.52 | 889 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 438 | 0 | 0 | 0 | 1181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.07 | 113 | 0 | 0 | 42.2 | 0 | 0 | 0 | 0 | 175 | 0 | 402 | 0 | 4.24 | 0 | 54 | 0 | 32 | 0 | 0 | 0 | 0 | 6.7 | 101 | 0.65 | 0 | 190 | 65 | 180 | 0 | 0 | 992 | 0 | 5402.86 | 11055.38 | 85.88
13:00 | 0 | 17 | 18 | 192 | 0 | 0 | 0 | 0 | 338 | 0 | 286 | 15.8 | 0 | 0 | 0 | 30 | 7 | 7 | 49 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 35 | 22 | 14 | 0 | 530 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 2 | 3.47 | 80 | 16 | 20 | 470 | 0 | 0 | 10 | 0 | 17 | 214 | 0 | 0 | 0 | 580 | 17 | 12 | 35 | 350 | 0 | 295 | 51 | 48 | 0 | 41 | 23 | 80 | 17 | 0 | 20 | 0 | 142 | 0 | 67 | 0 | 315 | 0 | 344 | 41 | 0 | 149 | 11 | 17 | 0 | 79 | 30 | 100 | 0 | 0 | 0 | 68 | 35 | 152 | 2.1 | 44.98 | 0 | 5821.35 | 889 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 602 | 0 | 0 | 0 | 1398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.32 | 108 | 0 | 0 | 61.33 | 0 | 0 | 0 | 0 | 192 | 0 | 396 | 0 | 5.39 | 0 | 54 | 0 | 29 | 0 | 0 | 0 | 0 | 6.5 | 155 | 0.62 | 0 | 301 | 60 | 220 | 0 | 0 | 1150 | 0 | 6155.16 | 11976.51 | 85.87
14:00 | 0 | 34 | 8 | 192 | 0 | 0 | 0 | 0 | 317 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 52 | 22 | 14 | 0 | 540 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 12 | 3.07 | 80 | 0 | 20 | 470 | 0 | 0 | 18 | 0 | 0 | 214 | 0 | 0 | 0 | 582 | 17 | 0 | 35 | 340 | 0 | 305 | 51 | 46 | 101 | 41 | 0 | 50 | 0 | 0 | 20 | 0 | 142 | 0 | 61 | 0 | 320 | 0 | 360 | 41 | 0 | 153 | 9 | 17 | 0 | 76 | 30 | 100 | 0 | 0 | 0 | 67 | 35 | 152 | 1 | 40.63 | 0 | 5713.7 | 889 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 603 | 0 | 0 | 0 | 1227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.29 | 92 | 0 | 0 | 35.78 | 0 | 0 | 0 | 0 | 169 | 0 | 405 | 0 | 4.82 | 0 | 55 | 0 | 18 | 0 | 0 | 0 | 0 | 5.6 | 107 | 0.55 | 0 | 307 | 60 | 220 | 0 | 0 | 1050 | 0 | 5769.04 | 11482.74 | 85.87
15:00 | 0 | 34 | 8 | 192 | 0 | 0 | 0 | 0 | 320 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 52 | 13.5 | 14 | 0 | 530 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 12 | 2.21 | 80 | 0 | 20 | 470 | 0 | 0 | 19 | 0 | 0 | 215 | 0 | 0 | 0 | 580 | 13 | 0 | 8 | 215 | 0 | 300 | 51 | 33 | 110 | 38 | 0 | 94 | 0 | 0 | 20 | 0 | 142 | 0 | 48 | 0 | 320 | 0 | 381 | 41 | 0 | 153 | 7 | 17 | 0 | 76 | 30 | 100 | 0 | 0 | 0 | 67 | 35 | 152 | 1.4 | 25.07 | 0 | 5591.18 | 889 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 591 | 0 | 0 | 0 | 1229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.45 | 52 | 0 | 0 | 43.11 | 0 | 0 | 0 | 0 | 185 | 0 | 400 | 0 | 3.58 | 0 | 54 | 0 | 17 | 0 | 0 | 0 | 0 | 4.6 | 57 | 0.48 | 0 | 307 | 60 | 220 | 0 | 0 | 1090 | 0 | 5696.22 | 11287.4 | 85.86
16:00 | 0 | 34 | 8 | 190 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 35 | 13.5 | 14 | 0 | 530 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 12 | 1.3 | 80 | 0 | 20 | 470 | 0 | 0 | 19 | 0 | 0 | 215 | 0 | 0 | 0 | 580 | 8 | 0 | 8 | 215 | 0 | 305 | 51 | 30 | 110 | 39 | 0 | 94 | 0 | 0 | 20 | 0 | 134 | 0 | 31 | 0 | 310 | 0 | 395 | 41 | 0 | 152 | 1 | 21 | 0 | 77 | 30 | 101 | 0 | 0 | 0 | 68 | 35 | 152 | 0.6 | 18.73 | 0 | 5219.13 | 888 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 546 | 0 | 0 | 0 | 1250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.44 | 43 | 0 | 0 | 24.59 | 0 | 0 | 0 | 0 | 189 | 0 | 367 | 0 | 2.18 | 0 | 54 | 0 | 10 | 0 | 0 | 0 | 0 | 2.8 | 67 | 0.28 | 0 | 307 | 60 | 220 | 0 | 0 | 1190 | 0 | 5665.29 | 10884.42 | 85.85
17:00 | 0 | 34 | 8 | 191 | 0 | 0 | 0 | 0 | 304 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 35 | 13.5 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 12 | 0.49 | 80 | 0 | 20 | 470 | 0 | 0 | 19 | 0 | 0 | 216 | 0 | 0 | 0 | 753 | 2 | 0 | 8 | 215 | 0 | 310 | 51 | 30 | 116 | 35 | 0 | 94 | 0 | 0 | 20 | 0 | 120 | 0 | 11 | 0 | 310 | 0 | 376 | 42 | 0 | 148 | 1 | 21 | 0 | 78 | 30 | 99 | 0 | 0 | 0 | 68 | 35 | 153 | 0.3 | 7.87 | 0 | 5292.16 | 888 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 501 | 0 | 0 | 0 | 1152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.84 | 16 | 0 | 0 | 8.86 | 0 | 0 | 0 | 0 | 185 | 0 | 373 | 0 | 0.82 | 0 | 54 | 0 | 5 | 0 | 0 | 0 | 0 | 1.2 | 26 | 0.1 | 0 | 231 | 60 | 220 | 0 | 0 | 1130 | 0 | 5249.82 | 10541.98 | 85.84
18:00 | 0 | 34 | 8 | 192 | 0 | 0 | 0 | 0 | 300 | 0 | 150 | 10 | 0 | 2 | 0 | 30 | 4 | 4 | 66 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 13.5 | 14 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 8 | 12 | 0 | 80 | 0 | 20 | 470 | 0 | 0 | 19 | 0 | 0 | 216 | 0 | 0 | 0 | 760 | 0 | 4 | 8 | 215 | 0 | 290 | 51 | 30 | 101 | 35 | 1 | 96 | 10 | 0 | 20 | 0 | 132 | 0 | 1 | 0 | 315 | 0 | 365 | 42 | 0 | 141 | 0 | 21 | 0 | 78 | 30 | 100 | 0 | 0 | 0 | 65 | 35 | 158 | 0 | 0 | 0 | 5508.5 | 889 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 490 | 0 | 0 | 0 | 1255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0.08 | 0 | 0 | 0 | 0 | 177 | 0 | 357 | 0 | 0.01 | 0 | 53 | 0 | 0 | 10 | 0 | 0 | 0 | 0.2 | 0 | 0.01 | 0 | 266 | 60 | 220 | 0 | 0 | 1110 | 0 | 5259 | 10767.5 | 85.83
19:00 | 0 | 34 | 8 | 192 | 0 | 0 | 0 | 0 | 412 | 0 | 332 | 30.2 | 0 | 8 | 0 | 145 | 21 | 24 | 106 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 12 | 14 | 0 | 530 | 5 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 12 | 50 | 0 | 80 | 2 | 20 | 470 | 0 | 0 | 24 | 0 | 4 | 221 | 0 | 0 | 0 | 1030 | 0 | 30 | 0 | 215 | 0 | 305 | 51 | 24 | 120 | 36 | 43 | 97 | 60 | 0 | 20 | 0 | 140 | 0 | 0 | 0 | 320 | 0 | 373 | 42 | 0 | 152 | 0 | 23 | 0 | 79 | 30 | 100 | 0 | 0 | 0 | 88 | 55 | 160 | 0 | 0 | 0 | 6642.2 | 888 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 570 | 0 | 0 | 0 | 1455 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 410 | 0 | 0 | 0 | 54 | 70 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 65 | 220 | 0 | 0 | 1210 | 0 | 5900 | 12542.2 | 85.82
19:30 | 0 | 34 | 8 | 192 | 0 | 0 | 0 | 0 | 332 | 0 | 342 | 31.5 | 0 | 8 | 0 | 145 | 30 | 35 | 93 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 12 | 14 | 0 | 530 | 15 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 50 | 0 | 80 | 28 | 20 | 470 | 0 | 0 | 26 | 0 | 51 | 221 | 0 | 0 | 0 | 1087 | 0 | 30 | 0 | 215 | 0 | 290 | 51 | 5 | 135 | 36 | 60 | 97 | 92 | 0 | 20 | 0 | 140 | 0 | 0 | 0 | 310 | 0 | 391 | 41 | 20 | 150 | 0 | 23 | 0 | 79 | 30 | 100 | 0 | 0 | 0 | 98 | 55 | 160 | 0 | 0 | 0 | 6804.5 | 888 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 603 | 0 | 0 | 0 | 1424 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 354 | 0 | 0 | 0 | 54 | 70 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 65 | 220 | 0 | 0 | 1244 | 0 | 5925 | 12729.5
20:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 363 | 0 | 346 | 30.5 | 0 | 0 | 0 | 0 | 30 | 35 | 99 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 12 | 18 | 0 | 530 | 13 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 50 | 0 | 80 | 30 | 20 | 470 | 0 | 0 | 26 | 0 | 45 | 221 | 0 | 0 | 0 | 1106 | 0 | 30 | 0 | 215 | 0 | 305 | 51 | 5 | 136 | 36 | 61 | 98 | 94 | 0 | 20 | 0 | 138 | 0 | 0 | 0 | 310 | 0 | 395 | 42 | 20 | 152 | 0 | 23 | 0 | 77 | 30 | 100 | 0 | 0 | 0 | 98 | 55 | 160 | 0 | 0 | 0 | 6671.5 | 889 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 603 | 0 | 0 | 0 | 1473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 386 | 0 | 0 | 0 | 54 | 70 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 65 | 220 | 0 | 0 | 1244 | 0 | 5926 | 12597.5 | 85.81
21:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 341 | 0 | 346 | 32.3 | 0 | 0 | 0 | 0 | 30 | 35 | 72 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 12 | 18 | 0 | 530 | 16 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 50 | 0 | 80 | 32 | 20 | 470 | 0 | 0 | 26 | 0 | 50 | 221 | 0 | 0 | 0 | 1212 | 0 | 30 | 0 | 215 | 0 | 300 | 51 | 5 | 141 | 42 | 64 | 98 | 98 | 0 | 20 | 0 | 150 | 0 | 0 | 0 | 315 | 0 | 394 | 42 | 20 | 155 | 0 | 23 | 0 | 80 | 30 | 100 | 0 | 0 | 0 | 98 | 55 | 160 | 0 | 0 | 0 | 6775.3 | 889 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 596 | 0 | 0 | 0 | 1452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 374 | 0 | 0 | 0 | 54 | 70 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 65 | 220 | 0 | 0 | 1244 | 0 | 5896 | 12671.3 | 85.8
22:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 336 | 0 | 346 | 16.1 | 0 | 0 | 0 | 0 | 30 | 35 | 35 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 12 | 21 | 0 | 530 | 13 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 50 | 0 | 80 | 31 | 20 | 470 | 0 | 0 | 26 | 0 | 48 | 222 | 0 | 0 | 0 | 1224 | 0 | 30 | 0 | 215 | 0 | 290 | 51 | 5 | 142 | 42 | 61 | 99 | 51 | 0 | 20 | 0 | 146 | 0 | 0 | 0 | 310 | 0 | 374 | 42 | 20 | 153 | 0 | 23 | 0 | 80 | 30 | 99 | 0 | 0 | 0 | 65 | 24 | 159 | 0 | 0 | 0 | 6651.1 | 888 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 598 | 0 | 0 | 0 | 1443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 355 | 0 | 0 | 0 | 54 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 65 | 220 | 0 | 0 | 1244 | 0 | 5827 | 12478.1 | 85.79
23:00 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 327 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 15 | 35 | 33 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 12 | 21 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 24 | 0 | 80 | 30 | 23 | 470 | 0 | 0 | 26 | 0 | 17 | 222 | 0 | 0 | 0 | 1224 | 0 | 25 | 0 | 250 | 0 | 305 | 51 | 5 | 28 | 42 | 0 | 100 | 17 | 0 | 20 | 0 | 150 | 0 | 0 | 0 | 310 | 0 | 389 | 42 | 20 | 151 | 0 | 23 | 0 | 80 | 30 | 103 | 0 | 0 | 0 | 45 | 24 | 159 | 0 | 0 | 0 | 6379 | 888 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 594 | 0 | 0 | 0 | 1457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 369 | 0 | 0 | 0 | 54 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 65 | 220 | 0 | 0 | 1244 | 0 | 5827 | 12206 | 85.78
Total KWH | 0 | 271680 | 114720 | 4531127 | 0 | 0 | 0 | 0 | 8092800 | 0 | 6389310 | 134640 | 0 | 16992 | 0 | 237611 | 178354 | 217576 | 423360 | 0 | 5103500 | 0 | 0 | 0 | 0 | 2650438 | 297000 | 0 | 196395 | 322800 | 372000 | 379440 | 0 | 11755909.09 | 63982 | 0 | 0 | 0 | 38400 | 356232 | 0 | 0 | 73920 | 330240 | 24242 | 1921920 | 180654 | 532800 | 10450909.09 | 0 | 0 | 266400 | 0 | 252581 | 5242782 | 0 | 0 | 0 | 16079999 | 125280 | 217454 | 284364 | 7585000 | 0 | 7496000 | 1249096 | 702240 | 1652000 | 853272 | 309120 | 2191223 | 408480 | 0 | 484780 | 0 | 3140160 | 0 | 509555 | 0 | 7638000 | 0 | 8910000 | 952000 | 91560 | 3594273 | 72845 | 472224 | 0 | 1850880 | 711840 | 2342700 | 0 | 0 | 0 | 1118400 | 566400 | 3708480 | 12600 | 307970 | 0 | 137058909.18 | 21498181 | 9100512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 694800 | 11527270 | 0 | 0 | 0 | 27407334 | 0 | 0 | 0 | 42528 | 56160 | 0 | 0 | 0 | 0 | 403784 | 762820 | 0 | 0 | 379504 | 0 | 0 | 0 | 0 | 4628800 | 0 | 9298691 | 0 | 35520 | 0 | 1274618 | 339355 | 190315 | 280656 | 0 | 0 | 0 | 43636.8 | 822240 | 4317 | 0 | 5760000 | 1528000 | 5333090 | 0 | 0 | 24663272.73 | 0 | 126075404.53 | 263134313.71