## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-01-05 | Saturday
|  | Date (day): | 2019-01-05 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10412 | MW |  |  | (b) At Evening Peak Hour : |  | 12335 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-01-04 | 2019-01-05 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit #1 Under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | On test.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 320 | 350 | 350 | 350
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 35 | 40 | 40 | 38 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 22 | 52 | 100 | 100
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 380 | 348 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 320 | 365 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 350 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 |  |  | Reserve
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 120 | 130 | 150 | 200 |  |  | FGMO
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 120 | 180 | 200 | 200
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
21 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102
22 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 6 | 47 | 47
23 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 54 | 54
24 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
25 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
26 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 36 | 36 |  | 19 | Engine problem
27 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 8 | 8 | 47 |  | 61 | Engine problem
28 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 43 | 57 | 58 | 58 |  | 22 | Engine problem
29 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
30 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 25 | 43 | 43 |  | 9 | Engine problem
32 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
33 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 0 | 300
34 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 130 | 130 |  | 19 | Engine problem
| Dhaka area Total |  |  |  |  | 6034 | 5798 | 1796 | 2080 | 3832 | 4421 | 298 | 530
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 150 | 150 | 150 | 30 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 44 | 42 | 67 | 67 |  | 163 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 120 | 120 | 120 |  |  | FGMO
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 18 | 50 | 50 | 50
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 70
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 5 | 17 | 0 | 68
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 90 | 90 |  | 10 | Engine problem
50 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 40 | 92 | 100 | 100
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 14 | 40 | 25 | 30
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 90 | 100 |  | 8 | Engine problem
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 313 | 608 | 809 | 942 | 210 | 446
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 100 | 100 | 100 | 29 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 100 | 100 | 100 | 34 |  | Gas shortage
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 206 | 186 | 210 | 210 |  |  | FGMO
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 260 | 260 |  | 100 | ST Under maint.
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 294 | 261 | 360 | 360 |  |  | FGMO
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 40 | 40 | 40 |  | 5 | Engine problem
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 30 | 55
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas Shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 6 | 42 | 51 | 51
62 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
63 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 5 | 85 | 85 | 85
64 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 40
65 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100 |  | 63 | FGMO & STG under maint.
66 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 180 | 180
67 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
68 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 0 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 78 | 108 | 84 | 109
69 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 24 | 0 | 33
70 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
71 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 20 | 22 | 22
72 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 911 | 1114 | 1859 | 2193 | 433 | 168
73 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 141 | 159 | 160 | 160 | 42 |  | Gas shortage
74 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
75 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 81 | 80 | 80 |  | 15 | Engine problem.
76 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 1.7 | 0 | 2 | 0
77 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 7 | 7 | 100 | 200
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 171.7 | 269 | 364 | 462 | 42 | 15
78 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 20 | 56 | 56 | 56
79 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 63 | 63 | 63
80 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 163 | 163 | 163
81 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 218 | 204 | 230 | 230 |  |  | FGMO
82 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 53 | 51 | 51
83 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 47 | 21 | 21 |  | 23 | Engine problem
84 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 3 | 11 | 11 | 11
85 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 51 | 53 | 66 | 66 |  |  | FGMO
86 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 89 | 86 | 86
87 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 1 | 48 | 50 | 50
88 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 80 | 100 | 78 | 140
89 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 20 | 20 | 20
90 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 2 | 25 | 50 | 50
91 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 25 | 0 | 25
92 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 330 | 329 | 341 | 341 |  |  | FGMO
| Bibiyana-3 285MW |  | Gas | PDB | 285 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
93 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 9 | 0 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 860 | 1295 | 1286 | 1383 | 0 | 23
94 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 328 | 656 | 366 | 663
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
95 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 24 | 115 | 115
96 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 40
97 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
98 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 2 | 50 | 0 | 80
99 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 270 | 320 | 410 | 410
100 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
102 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105
| Khulna Area Total |  |  |  |  | 2223 | 2209 | 600 | 1195 | 1136 | 1599 | 0 | 0
103 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
104 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
105 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 11 | 26 | 25 | 25 |  | 8 | Engine problem
106 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 199 | 194 | 194 | 194
107 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 221 | 317 | 424 | 454 | 0 | 8
108 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage.
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 80 | 80 | 80 | 80 |  | 20
109 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 17 | 0 | 50
110 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
111 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
112 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
113 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
114 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
115 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 175 | 0 | 0 | 0 |  |  | Gas shortage.
116 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 141 | 141 | 0 | 58 | 150 | 150 |  |  | Gas shortage.
117 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 0 | 0 | 0 | 0 | 282 |  | Gas shortage.
118 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 0 | 35
119 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 6 | 22 | 22 | 22
120 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 11 | 7 | 10 |  | 0
121 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
122 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 43 | 52
123 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 60 | 90 | 100
| Rajshahi Area Total |  |  |  |  | 1556 | 1546 | 266 | 392 | 553 | 700 | 563 | 20
124 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
125 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 148 | 149 | 149 | 149 | 125 |  | Coal shortage
126 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 17
127 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15
| Rangpur Area Total |  |  |  |  | 564 | 484 | 148 | 166 | 149 | 181 | 125 | 170
| Total |  |  |  |  | 17685 | 17142 | 5286.7 | 7436 | 10412 | 12335 | 1671 | 1380
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 4897.8048 | 6889 | 9646.0823 | 11427.6244
A. |  | 2019-01-04 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 7436 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 4711 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 7436 | MW
3 | Day peak Generation : |  |  | 5286.7 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 6889 | MW
4 | Evening peak Generation : |  |  | 7436 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 134.5469 | MKWHr | By Solar | 0.13914 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 113.4488 | MKWHr |  | By Oil: | 4.4363 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.6582 | MKWHr |  | By Hydro: | 1.0122 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1671 | MW | Dhaka | 2311 | 2311 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1380 | MW | Chittagong | 676 | 676 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3051 | MW | Khulna | 933 | 933 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 961.47 | MMCFD |  |  | Rajshahi | 778 | 778 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 83200021.724 | ii) Oil : | Taka | 31862456.35 | Comilla | 626 | 626 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14120652 | Total | Taka | 129183130.074 | Mymensingh | 546 | 546 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 4.7485 | MKWHr. | Sylhet | 300 | 300 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -620 | MW at | 19:30 | hrs | Barisal | 194 | 194 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -630 | MW at | 18:30 | hrs | Rangpur | 525 | 525 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 24.8° C |  |  | Total | 6889 | 6889 |  | 0
B. |  | 2019-01-05 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 24.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12335 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6300 | MW
4 | Reserve(Generation end) |  |  |  | 4235 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 146.5613 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4473 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 9.8938 | MKWHr. | ii) HVDC Flow at Peak Time |  | 656 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9584 | MKWHr. | iii) Maximum HVDC Flow : |  | 656 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.25 |  | (b) Today: | 98.21 |  | (c) Rule Curve: |  | 102.24
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-01-04
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 0 | 300 | 104 | 0 | 347 | 325 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 120 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 0 | 0 | 42 | 0 | 0 | 150 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 0 | 100 | 100 | 0 | 261 | 185 | 8 | 96 | 40 | 5 | 5 | 45 | 50 | 0 | 0 | 19 | 0 | 8 | 15 | 82 | 144 | 0 | 0 | 0 | 56 | 63 | 5 | 5 | 130 | 220 | 40 | 5 | 49 | 78 | 0 | 50 | 0 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 280 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 20 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 3 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 163 | 0 | 51 | 0 | 0 | 0 | 0 | 0 |  | 4302 | 1251 | 5553 | 3507 | 280 | 1481 | 12 | 149 | 42 | 0 | 82 | 0 | 0 | 98.26
2:00 | 35 | 0 | 0 | 0 | 300 | 12 | 0 | 348 | 298 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 0 | 0 | 42 | 0 | 0 | 150 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 0 | 80 | 80 | 0 | 261 | 186 | 8 | 100 | 37 | 5 | 5 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 15 | 80 | 144 | 0 | 0 | 0 | 56 | 63 | 5 | 5 | 100 | 230 | 40 | 5 | 1 | 77 | 0 | 2 | 0 | 290 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 281 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 19 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 170 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3875 | 1218 | 5093 | 3381 | 281 | 1150 | 10 | 149 | 42 | 0 | 80 | 0 | 0 | 98.26
3:00 | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 350 | 297 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 0 | 0 | 42 | 0 | 0 | 150 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 80 | 80 | 0 | 276 | 194 | 8 | 100 | 3 | 5 | 5 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 15 | 76 | 146 | 0 | 0 | 0 | 30 | 30 | 5 | 5 | 100 | 230 | 40 | 5 | 1 | 78 | 0 | 2 | 0 | 310 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 281 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 19 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 3 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 167 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3743 | 1208 | 4951 | 3293 | 281 | 1096 | 14 | 149 | 42 | 0 | 76 | 0 | 0 | 98.26
4:00 | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 345 | 297 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 42 | 0 | 0 | 150 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 80 | 80 | 0 | 261 | 160 | 8 | 100 | 3 | 5 | 5 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 15 | 76 | 151 | 0 | 0 | 0 | 30 | 30 | 5 | 5 | 100 | 221 | 40 | 5 | 1 | 79 | 0 | 2 | 0 | 305 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 281 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 17 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 3 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 148 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3672 | 1158 | 4830 | 3180 | 281 | 1089 | 13 | 149 | 42 | 0 | 76 | 0 | 0 | 98.25
5:00 | 35 | 0 | 0 | 0 | 280 | 0 | 0 | 345 | 265 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 33 | 33 | 0 | 0 | 42 | 0 | 0 | 150 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 80 | 80 | 0 | 264 | 164 | 8 | 100 | 3 | 5 | 5 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 15 | 72 | 154 | 0 | 0 | 0 | 30 | 30 | 5 | 5 | 100 | 219 | 40 | 5 | 1 | 78 | 0 | 2 | 0 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 281 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 17 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 142 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3594 | 1117 | 4711 | 3127 | 281 | 1032 | 8 | 149 | 42 | 0 | 72 | 0 | 0 | 98.25
6:00 | 35 | 0 | 0 | 0 | 330 | 0 | 0 | 355 | 266 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 120 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 33 | 33 | 0 | 0 | 43 | 0 | 0 | 150 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 80 | 80 | 0 | 279 | 171 | 8 | 100 | 3 | 5 | 5 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 15 | 70 | 155 | 0 | 0 | 0 | 30 | 30 | 5 | 5 | 130 | 216 | 40 | 5 | 1 | 78 | 0 | 2 | 0 | 310 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 280 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 18 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 148 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3744 | 1122 | 4866 | 3243 | 280 | 1074 | 7 | 149 | 43 | 0 | 70 | 0 | 0 | 98.25
7:00 | 35 | 0 | 0 | 0 | 280 | 64 | 0 | 340 | 246 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 120 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 33 | 33 | 0 | 0 | 43 | 0 | 0 | 150 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 0 | 80 | 80 | 0 | 260 | 184 | 8 | 96 | 25 | 5 | 5 | 6 | 5 | 0 | 0 | 19 | 0 | 0 | 15 | 68 | 155 | 0 | 22 | 0 | 20 | 30 | 5 | 5 | 100 | 205 | 40 | 5 | 1 | 78 | 0 | 2 | 0 | 284 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0.66 | 0 | 0 | 0 | 0 |  | 279 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 16 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 159 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3705.66 | 1114 | 4819.66 | 3192 | 279 | 1081 | 7 | 149 | 43 | 0 | 68 | 0.66 | 0 | 98.24
8:00 | 35 | 0 | 0 | 0 | 250 | 62 | 0 | 280 | 246 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 33 | 33 | 0 | 0 | 43 | 0 | 0 | 150 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 0 | 80 | 80 | 0 | 294 | 201 | 8 | 100 | 40 | 5 | 5 | 6 | 5 | 0 | 0 | 19 | 0 | 0 | 15 | 68 | 154 | 0 | 22 | 0.3 | 20 | 30 | 5 | 5 | 100 | 221 | 40 | 5 | 1 | 76 | 0 | 2 | 0 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7.3 | 4 | 0 | 0 | 0 |  | 328 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207 | 17 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 163 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3782.6 | 1183 | 4965.6 | 3262 | 328 | 1097 | 11 | 149 | 43 | 0 | 68 | 7.6 | 0 | 98.24
9:00 | 35 | 0 | 0 | 0 | 320 | 62 | 0 | 300 | 244 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 33 | 33 | 0 | 0 | 44 | 0 | 0 | 150 | 0 | 0 | 0 | 130 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 0 | 80 | 80 | 0 | 261 | 185 | 8 | 100 | 40 | 5 | 5 | 6 | 5 | 0 | 0 | 19 | 0 | 0 | 15 | 72 | 149 | 0 | 22 | 0.9 | 20 | 40 | 5 | 5 | 100 | 215 | 69 | 5 | 1 | 80 | 0 | 2 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 13.4 | 10 | 0 | 0 | 0 |  | 328 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 17 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 164 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3905.3 | 1183 | 5088.3 | 3324 | 328 | 1126 | 31 | 149 | 44 | 0 | 72 | 14.3 | 0 | 98.24
10:00 | 35 | 0 | 0 | 0 | 280 | 22 | 0 | 345 | 244 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 33 | 33 | 0 | 0 | 44 | 0 | 0 | 150 | 0 | 0 | 0 | 130 | 0 | 0 | 16 | 0 | 4 | 0 | 0 | 0 | 22 | 14 | 0 | 80 | 80 | 0 | 268 | 188 | 8 | 100 | 40 | 5 | 5 | 6 | 5 | 0 | 0 | 19 | 0 | 0 | 15 | 74 | 147 | 0 | 0 | 1.4 | 20 | 40 | 5 | 5 | 100 | 207 | 55 | 5 | 1 | 80 | 0 | 2 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 17.8 | 10 | 0 | 0 | 0 |  | 328 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 10 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 153 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3839.2 | 1150 | 4989.2 | 3267 | 328 | 1071 | 33 | 149 | 44 | 4 | 74 | 19.2 | 0 | 98.24
11:00 | 35 | 0 | 0 | 0 | 280 | 23 | 0 | 350 | 245 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 33 | 33 | 0 | 0 | 44 | 0 | 0 | 150 | 0 | 0 | 0 | 130 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 22 | 7 | 0 | 80 | 80 | 0 | 283 | 202 | 8 | 100 | 10 | 5 | 5 | 6 | 5 | 0 | 0 | 19 | 0 | 0 | 15 | 74 | 144 | 0 | 22 | 1.6 | 20 | 40 | 5 | 5 | 100 | 221 | 40 | 5 | 1 | 80 | 0 | 2 | 0 | 310 | 0 | 3 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 20 | 10 | 0 | 0 | 0 |  | 328 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 166 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3849.6 | 1175 | 5024.6 | 3306 | 328 | 1069 | 33 | 149 | 44 | 0 | 74 | 21.6 | 0 | 98.23
12:00 | 35 | 0 | 0 | 0 | 320 | 22 | 0 | 380 | 320 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 33 | 33 | 0 | 0 | 44 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 0 | 22 | 14 | 0 | 80 | 80 | 0 | 294 | 206 | 8 | 100 | 10 | 5 | 5 | 6 | 5 | 0 | 0 | 19 | 0 | 0 | 15 | 78 | 141 | 0 | 22 | 1.7 | 20 | 40 | 5 | 5 | 100 | 218 | 51 | 5 | 1 | 80 | 0 | 2 | 0 | 330 | 0 | 3 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 20 | 40 | 0 | 0 | 0 |  | 328 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 199 | 11 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 175 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 4051.7 | 1235 | 5286.7 | 3364 | 328 | 1231 | 65 | 148 | 44 | 7 | 78 | 21.7 | 0 | 98.23
13:00 | 35 | 0 | 0 | 0 | 320 | 22 | 0 | 365 | 362 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 13 | 33 | 33 | 0 | 0 | 44 | 0 | 0 | 150 | 0 | 0 | 0 | 130 | 0 | 0 | 39 | 0 | 2 | 0 | 0 | 0 | 22 | 14 | 0 | 80 | 80 | 0 | 261 | 185 | 8 | 100 | 10 | 5 | 5 | 6 | 5 | 0 | 0 | 19 | 0 | 0 | 15 | 84 | 143 | 0 | 22 | 1.6 | 20 | 52 | 5 | 5 | 100 | 201 | 49 | 5 | 1 | 80 | 0 | 2 | 0 | 330 | 0 | 2 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 19.2 | 10 | 0 | 0 | 0 |  | 328 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 199 | 12 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 166 | 0 | 12 | 0 | 0 | 0 | 0 | 0 |  | 4178.8 | 1321 | 5499.8 | 3495 | 328 | 1305 | 68 | 149 | 44 | 6 | 84 | 20.8 | 0 | 98.23
14:00 | 35 | 0 | 0 | 0 | 250 | 23 | 0 | 350 | 240 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 120 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 25 | 13 | 33 | 33 | 0 | 0 | 43 | 0 | 0 | 150 | 0 | 0 | 0 | 80 | 0 | 0 | 8 | 0 | 7 | 0 | 0 | 0 | 22 | 14 | 0 | 80 | 80 | 0 | 261 | 185 | 8 | 100 | 10 | 5 | 5 | 6 | 5 | 0 | 0 | 19 | 0 | 0 | 15 | 78 | 143 | 0 | 22 | 1.1 | 20 | 52 | 5 | 5 | 100 | 203 | 40 | 5 | 1 | 80 | 0 | 2 | 0 | 290 | 0 | 2 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 16 | 10 | 0 | 0 | 0 |  | 328 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 198 | 12 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 151 | 0 | 12 | 0 | 0 | 0 | 0 | 0 |  | 3723.1 | 1165 | 4888.1 | 3145 | 328 | 1044 | 73 | 149 | 43 | 11 | 78 | 17.1 | 0 | 98.22
15:00 | 35 | 0 | 0 | 0 | 200 | 22 | 0 | 354 | 240 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 11 | 33 | 33 | 0 | 0 | 42 | 0 | 0 | 150 | 0 | 0 | 0 | 80 | 0 | 0 | 8 | 0 | 7 | 0 | 0 | 0 | 22 | 15 | 0 | 80 | 80 | 0 | 279 | 196 | 8 | 100 | 10 | 5 | 5 | 6 | 5 | 0 | 0 | 19 | 0 | 0 | 15 | 74 | 154 | 0 | 22 | 0.9 | 20 | 63 | 5 | 5 | 100 | 201 | 40 | 5 | 1 | 80 | 0 | 2 | 0 | 320 | 0 | 2 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 11.3 | 10 | 0 | 0 | 0 |  | 328 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 198 | 11 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 134 | 0 | 12 | 0 | 0 | 0 | 0 | 0 |  | 3708.2 | 1149 | 4857.2 | 3141 | 328 | 1073 | 25 | 149 | 42 | 13 | 74 | 12.2 | 0 | 98.22
16:00 | 35 | 0 | 0 | 0 | 200 | 11 | 0 | 300 | 240 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 11 | 33 | 33 | 0 | 0 | 42 | 0 | 0 | 150 | 0 | 0 | 0 | 80 | 0 | 0 | 8 | 0 | 10 | 0 | 0 | 0 | 22 | 15 | 0 | 80 | 80 | 0 | 279 | 195 | 8 | 100 | 10 | 5 | 5 | 6 | 5 | 0 | 0 | 19 | 0 | 0 | 15 | 74 | 154 | 0 | 22 | 0.4 | 20 | 63 | 7 | 5 | 100 | 225 | 51 | 5 | 1 | 78 | 0 | 2 | 0 | 295 | 0 | 2 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 6.2 | 10 | 0 | 0 | 0 |  | 328 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 179 | 11 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 119 | 0 | 12 | 0 | 4 | 0 | 0 | 0 |  | 3649.6 | 1103 | 4752.6 | 3069 | 328 | 1039 | 25 | 149 | 42 | 20 | 74 | 6.6 | 0 | 98.22
17:00 | 35 | 0 | 0 | 0 | 200 | 12 | 0 | 300 | 240 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 120 | 0 | 123 | 0 | 0 | 7 | 0 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 25 | 14 | 33 | 33 | 2 | 0 | 42 | 0 | 0 | 150 | 8 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 5 | 10 | 10 | 2 | 22 | 24 | 0 | 80 | 80 | 0 | 253 | 186 | 8 | 100 | 10 | 5 | 5 | 6 | 5 | 0 | 1 | 19 | 11 | 5 | 15 | 82 | 156 | 30 | 22 | 0 | 30 | 63 | 5 | 5 | 100 | 203 | 52 | 5 | 1 | 98 | 0 | 3 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 0.6 | 10 | 6 | 5 | 0 |  | 401 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 0 | 25 | 8 | 181 | 11 | 0 | 0 | 80 | 0 | 0 | 0 | 9 | 12 | 0 | 0 | 8 | 0 | 22 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 68 | 0 | 11 | 0 | 13 | 0 | 0 | 17 |  | 3854.6 | 1281 | 5135.6 | 3105 | 401 | 1138 | 179 | 149 | 42 | 39 | 82 | 0.6 | 0 | 98.22
18:00 | 35 | 0 | 0 | 0 | 300 | 52 | 35 | 320 | 320 | 0 | 0 | 350 | 0 | 0 | 7 | 13 | 120 | 0 | 125 | 0 | 0 | 7 | 0 | 0 | 46 | 0 | 29 | 54 | 18 | 0 | 19 | 25 | 14 | 33 | 33 | 32 | 0 | 42 | 0 | 0 | 150 | 25 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 48 | 10 | 13 | 29 | 22 | 40 | 0 | 100 | 100 | 0 | 261 | 186 | 8 | 100 | 40 | 5 | 5 | 20 | 40 | 0 | 8 | 19 | 11 | 8 | 15 | 104 | 157 | 81 | 22 | 0 | 56 | 63 | 28 | 22 | 100 | 202 | 53 | 40 | 47 | 98 | 19 | 25 | 7 | 295 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 14 | 0 | 80 | 32 | 14 | 0 |  | 656 | 0 | 320 | 0 | 20 | 0 | 0 | 0 | 0 | 56 | 35 | 201 | 24 | 16 | 0 | 80 | 0 | 17 | 0 | 51 | 50 | 0 | 0 | 52 | 38 | 22 | 5 | 11 | 0 | 0 | 149 | 17 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 17 | 0 | 0 | 105 |  | 5014 | 1957 | 6971 | 3491 | 656 | 1505 | 797 | 149 | 42 | 227 | 104 | 0 | 0 | 98.22
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 0 | 0 | 350 | 52 | 35 | 348 | 360 | 0 | 0 | 350 | 0 | 0 | 10 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 46 | 54 | 0 | 0 | 19 | 25 | 26 | 33 | 33 | 25 | 0 | 42 | 0 | 0 | 150 | 25 | 0 | 0 | 120 | 0 | 0 | 38 | 0 | 15 | 10 | 7 | 50 | 22 | 40 | 0 | 100 | 100 | 0 | 261 | 184 | 8 | 100 | 40 | 5 | 5 | 42 | 85 | 0 | 0 | 19 | 11 | 10 | 20 | 108 | 158 | 81 | 22 | 0 | 56 | 63 | 53 | 47 | 163 | 206 | 51 | 89 | 48 | 98 | 20 | 25 | 9 | 295 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 92 | 0 | 0 | 0 |  | 656 | 0 | 320 | 0 | 22 | 0 | 0 | 0 | 0 | 50 | 40 | 201 | 26 | 0 | 0 | 80 | 0 | 17 | 0 | 60 | 50 | 0 | 0 | 52 | 31 | 22 | 11 | 11 | 0 | 0 | 149 | 17 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 48 | 0 | 0 | 105 |  | 5329 | 2065 | 7394 | 3636 | 656 | 1867 | 746 | 149 | 42 | 190 | 108 | 0 | 0 | 98.22
19:30 | 35 | 0 | 0 | 0 | 350 | 52 | 35 | 348 | 365 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 180 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 54 | 0 | 0 | 19 | 25 | 32 | 33 | 33 | 25 | 0 | 42 | 0 | 0 | 150 | 25 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 17 | 0 | 0 | 50 | 22 | 40 | 0 | 100 | 100 | 0 | 261 | 186 | 8 | 100 | 40 | 5 | 5 | 42 | 85 | 0 | 0 | 19 | 11 | 24 | 20 | 108 | 159 | 81 | 22 | 0 | 56 | 63 | 53 | 47 | 163 | 204 | 53 | 89 | 48 | 100 | 20 | 25 | 9 | 329 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 92 | 0 | 0 | 0 |  | 656 | 0 | 320 | 0 | 24 | 0 | 0 | 0 | 0 | 50 | 40 | 194 | 26 | 0 | 0 | 80 | 0 | 17 | 0 | 60 | 50 | 0 | 0 | 52 | 31 | 22 | 11 | 11 | 0 | 0 | 149 | 17 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 58 | 0 | 0 | 105 |  | 5366 | 2070 | 7436 | 3714 | 656 | 1906 | 669 | 149 | 42 | 192 | 108 | 0 | 0 | 0
20:00 | 35 | 0 | 0 | 0 | 350 | 52 | 35 | 348 | 368 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 180 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 6 | 18 | 0 | 0 | 19 | 25 | 32 | 33 | 33 | 8 | 0 | 42 | 0 | 0 | 150 | 25 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 17 | 0 | 0 | 50 | 22 | 42 | 0 | 100 | 100 | 0 | 261 | 184 | 8 | 95 | 40 | 5 | 5 | 42 | 85 | 0 | 0 | 19 | 11 | 25 | 20 | 110 | 159 | 50 | 22 | 0 | 53 | 63 | 53 | 47 | 163 | 200 | 49 | 89 | 48 | 98 | 20 | 25 | 9 | 305 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 92 | 0 | 0 | 0 |  | 656 | 0 | 320 | 0 | 23 | 0 | 0 | 0 | 0 | 50 | 40 | 196 | 25 | 0 | 0 | 80 | 0 | 17 | 0 | 60 | 50 | 0 | 0 | 52 | 31 | 22 | 11 | 11 | 0 | 0 | 149 | 17 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 59 | 0 | 0 | 105 |  | 5240 | 2071 | 7311 | 3698 | 656 | 1886 | 578 | 149 | 42 | 192 | 110 | 0 | 0 | 98.21
21:00 | 35 | 0 | 0 | 0 | 350 | 52 | 35 | 347 | 366 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 180 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 19 | 25 | 32 | 33 | 33 | 0 | 0 | 42 | 0 | 0 | 150 | 25 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 17 | 0 | 0 | 18 | 22 | 40 | 0 | 100 | 100 | 0 | 261 | 184 | 8 | 100 | 40 | 5 | 5 | 42 | 85 | 0 | 0 | 19 | 11 | 0 | 22 | 102 | 159 | 24 | 22 | 0 | 53 | 62 | 53 | 47 | 163 | 201 | 53 | 89 | 49 | 98 | 0 | 25 | 0 | 305 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 92 | 0 | 0 | 0 |  | 656 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 40 | 200 | 25 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 52 | 0 | 22 | 11 | 11 | 0 | 0 | 149 | 0 | 15 | 0 | 0 | 0 | 0 | 97 | 0 | 143 | 0 | 0 | 53 |  | 5086 | 1954 | 7040 | 3726 | 656 | 1874 | 429 | 149 | 42 | 62 | 102 | 0 | 0 | 98.21
22:00 | 35 | 0 | 0 | 0 | 350 | 52 | 35 | 346 | 337 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 150 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 19 | 25 | 26 | 33 | 33 | 0 | 0 | 42 | 0 | 0 | 150 | 0 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 100 | 100 | 0 | 261 | 184 | 8 | 96 | 40 | 5 | 5 | 5 | 85 | 0 | 0 | 19 | 11 | 0 | 22 | 96 | 160 | 0 | 22 | 0 | 56 | 62 | 53 | 47 | 100 | 198 | 42 | 5 | 49 | 80 | 0 | 25 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 0 | 0 | 0 |  | 656 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 187 | 23 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 11 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 147 | 0 | 0 | 0 |  | 4599 | 1795 | 6394 | 3638 | 656 | 1636 | 177 | 149 | 42 | 0 | 96 | 0 | 0 | 98.21
23:00 | 35 | 0 | 0 | 0 | 350 | 12 | 0 | 346 | 334 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 150 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 26 | 33 | 33 | 0 | 0 | 43 | 0 | 0 | 150 | 0 | 0 | 0 | 120 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 100 | 100 | 0 | 261 | 184 | 8 | 100 | 40 | 5 | 5 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 21 | 86 | 161 | 0 | 0 | 0 | 56 | 62 | 5 | 5 | 100 | 202 | 40 | 5 | 5 | 78 | 0 | 7 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 652 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 200 | 21 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 22 | 11 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 147 | 0 | 0 | 0 |  | 4173 | 1667 | 5840 | 3580 | 652 | 1279 | 51 | 149 | 43 | 0 | 86 | 0 | 0 | 98.21
24:00 | 35 | 0 | 0 | 0 | 350 | 12 | 0 | 346 | 336 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 120 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 33 | 33 | 0 | 0 | 43 | 0 | 0 | 150 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 100 | 100 | 0 | 268 | 191 | 8 | 101 | 40 | 5 | 5 | 5 | 6 | 0 | 0 | 0 | 0 | 0 | 22 | 76 | 159 | 0 | 0 | 0 | 56 | 52 | 5 | 5 | 100 | 199 | 40 | 5 | 5 | 78 | 0 | 7 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 434 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 20 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 |  | 4094 | 1340 | 5434 | 3508 | 434 | 1217 | 7 | 149 | 43 | 0 | 76 | 0 | 0 | 98.21
KWH | 740000 | 0 | 0 | 0 | 6799590 | 828000 | 225792 | 8377340 | 7037000 | 0 | 0 | 7887525 | 0 | 0 | 22896 | 25816 | 3251783 | 0 | 2585000 | 0 | 0 | 15696 | 0 | 0 | 78720 | 0 | 178320 | 169560 | 34807 | 0 | 99612 | 600000 | 562860 | 793900 | 821241 | 99204 | 0 | 1012189 | 0 | 0 | 3700000 | 102240 | 0 | 0 | 2381260 | 0 | 0 | 347040 | 0 | 155223 | 22560 | 28800 | 158400 | 451536 | 585600 | 0 | 2097740 | 2073726 | 0 | 6492000 | 4534000 | 200727 | 2328970 | 541080 | 152640 | 120000 | 400137 | 550920 | 0 | 14362 | 331380 | 57060 | 66400 | 408070 | 1958400 | 3557280 | 296640 | 331776 | 9950 | 838000 | 1181109 | 379800 | 305000 | 3085240 | 4624000 | 1116000 | 486720 | 341280 | 2018900 | 69000 | 213460 | 28260 | 7748950 | 97440 | 167424 | 0 | 0 | 0 | 0 | 218400 | 0 | 40320 | 129195 | 488460 | 60000 | 35127 | 0 |  | 9893818 | 0 | 6914016 | 0 | 91200 | 0 | 0 | 0 | 0 | 217088 | 226875 | 4814889 | 401800 | 24960 | 0 | 1878000 | 0 | 47307 | 0 | 169316 | 220180 | 0 | 0 | 289440 | 99336 | 289680 | 96984 | 157372 | 0 | 0 | 3658200 | 50000 | 13000 | 0 | 0 | 2722018 | 0 | 726240 | 0 | 775296 | 0 | 0 | 395040 |  | 100374853 | 34172055 | 134546908 | 81357068 | 9893818 | 32091755 | 3685063 | 3658200 | 1012189 | 751270 | 1958400 | 139145 | 0
Fuel Cost | 636400 | 0 | 0 | 0 | 4351737.6 | 670680 | 212244.48 | 5110177.4 | 4292570 | 0 | 0 | 5284641.75 | 0 | 0 | 152945.28 | 157735.76 | 2113658.95 | 0 | 2869350 | 0 | 0 | 103436.64 | 0 | 0 | 471532.8 | 0 | 1189394.4 | 1208962.8 | 217543.75 | 0 | 74709 | 450000 | 0 | 0 | 0 | 938469.84 | 0 | 0 | 0 | 0 | 4070000 | 968212.8 | 0 | 0 | 2738449 | 0 | 0 | 3050481.6 | 0 | 1510319.79 | 139646.4 | 186048 | 1035936 | 383805.6 | 0 | 0 | 1908943.4 | 1887090.66 | 0 | 4479480 | 3173800 | 138501.63 | 2235811.2 | 362523.6 | 131270.4 | 110400 | 328112.34 | 523374 | 0 | 106566.04 | 255162.6 | 42795 | 51128 | 306052.5 | 13395456 | 2667960 | 2726121.6 | 255467.52 | 0 | 871520 | 1228353.36 | 364608 | 274500 | 2406487.2 | 3236800 | 1272240 | 520790.4 | 375408 | 2301546 | 88320 | 198517.8 | 26281.8 | 4959328 | 73080 | 127242.24 | 0 | 0 | 0 | 0 | 1561560 | 0 | 0 | 0 | 0 | 560400 | 328086.18 | 0 |  | 50458471.8 | 0 | 4632390.72 | 0 | 756048 | 0 | 0 | 0 | 0 | 2557296.64 | 1787775 | 3322273.41 | 397782 | 184704 | 0 | 1971900 | 0 | 541665.15 | 0 | 1517071.36 | 1904557 | 0 | 0 | 2871244.8 | 1169184.72 | 318648 | 91164.96 | 119130.604 | 0 | 0 | 14120652 | 1611500 | 348010 | 0 | 0 | 1905412.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100450175.11 | 92586882.764 | 193037057.874 | 61574710.964 | 50458471.8 | 21625310.76 | 22607408.69 | 14120652 | 0 | 9255047.66 | 13395456 | 0 | 0
Yesterday Day Peak | 35 | 0 | 0 | 0 | 320 | 22 | 0 | 380 | 320 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 120 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 33 | 33 | 0 | 0 | 44 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 0 | 22 | 14 | 0 | 80 | 80 | 0 | 294 | 206 | 8 | 100 | 10 | 5 | 5 | 6 | 5 | 0 | 0 | 19 | 0 | 0 | 15 | 78 | 141 | 0 | 22 | 1.7 | 20 | 40 | 5 | 5 | 100 | 218 | 51 | 5 | 1 | 80 | 0 | 2 | 0 | 330 | 0 | 3 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 20 | 40 | 0 | 0 | 0 |  | 328 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 199 | 11 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 175 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 5286.7 | DayPeak
Yesterday Evening Peak | 35 | 0 | 0 | 0 | 350 | 52 | 35 | 348 | 365 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 180 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 54 | 0 | 0 | 19 | 25 | 32 | 33 | 33 | 25 | 0 | 42 | 0 | 0 | 150 | 25 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 17 | 0 | 0 | 50 | 22 | 40 | 0 | 100 | 100 | 0 | 261 | 186 | 8 | 100 | 40 | 5 | 5 | 42 | 85 | 0 | 0 | 19 | 11 | 24 | 20 | 108 | 159 | 81 | 22 | 0 | 56 | 63 | 53 | 47 | 163 | 204 | 53 | 89 | 48 | 100 | 20 | 25 | 9 | 329 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 92 | 0 | 0 | 0 |  | 656 | 0 | 320 | 0 | 24 | 0 | 0 | 0 | 0 | 50 | 40 | 194 | 26 | 0 | 0 | 80 | 0 | 17 | 0 | 60 | 50 | 0 | 0 | 52 | 31 | 22 | 11 | 11 | 0 | 0 | 149 | 17 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 58 | 0 | 0 | 105 |  | 7436 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 0 | 350 | 100 | 40 | 412 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 200 | 0 | 200 | 100 | 100 | 102 | 149 | 100 | 47 | 0 | 47 | 54 | 55 | 36 | 22 | 25 | 33 | 33 | 33 | 43 | 0 | 37 | 30 | 0 | 150 | 25 | 0 | 0 | 120 | 0 | 0 | 50 | 70 | 68 | 90 | 100 | 50 | 22 | 30 | 0 | 100 | 100 | 260 | 360 | 210 | 8 | 100 | 40 | 55 | 5 | 51 | 85 | 40 | 52 | 22 | 11 | 33 | 22 | 109 | 160 | 80 | 22 | 0 | 56 | 63 | 51 | 21 | 163 | 230 | 66 | 86 | 50 | 140 | 20 | 50 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 130 | 0 | 100 | 180 | 150 | 0 |  | 663 | 46 | 410 | 0 | 115 | 0 | 0 | 0 | 40 | 80 | 40 | 194 | 25 | 110 | 30 | 80 | 0 | 50 | 40 | 100 | 50 | 50 | 50 | 52 | 35 | 22 | 10 | 11 | 0 | 0 | 149 | 17 | 15 | 0 | 0 | 0 | 0 | 95 | 100 | 150 | 0 | 0 | 105
Forecast for Day | 35 | 0 | 0 | 0 | 350 | 100 | 40 | 412 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 200 | 0 | 150 | 100 | 100 | 102 | 149 | 100 | 8 | 0 | 47 | 54 | 55 | 36 | 22 | 25 | 33 | 33 | 33 | 43 | 0 | 37 | 30 | 0 | 150 | 25 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 90 | 90 | 50 | 22 | 25 | 0 | 100 | 100 | 260 | 360 | 210 | 8 | 100 | 40 | 30 | 5 | 51 | 85 | 0 | 52 | 22 | 0 | 0 | 22 | 84 | 160 | 80 | 22 | 2 | 56 | 63 | 51 | 21 | 163 | 230 | 66 | 86 | 50 | 78 | 20 | 50 | 0 | 341 | 0 | 11 | 0 | 0 | 300 | 0 | 100 | 0 | 130 | 20 | 100 | 180 | 150 | 0 |  | 366 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 194 | 25 | 110 | 0 | 80 | 0 | 0 | 0 | 90 | 50 | 50 | 50 | 43 | 0 | 22 | 7 | 11 | 0 | 0 | 149 |  | 0 | 0 | 0 | 0 | 0 | 95 | 100 | 150 | 0 | 0 | 105
Generation at 08:00(Today) | 35 | 0 | 0 | 0 | 380 | 6 | 0 | 374 | 337 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 200 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 33 | 33 | 0 | 0 | 43 | 0 | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 14 | 0 | 100 | 100 | 0 | 353 | 209 | 8 | 50 | 30 | 5 | 5 | 5 | 2 | 0 | 0 | 19 | 8 | 0 | 10 | 70 | 161 | 0 | 22 | 0.4 | 56 | 62 | 5 | 21 | 163 | 226 | 70 | 5 | 46 | 80 | 0 | 25 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 263 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 207 | 18 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 100 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 4711 | 5:00
| Highest Generation |  | 7436 | 19:30
| Day Peak Generation |  | 5286.7 | 12:00
| Evening Peak Generation |  | 7436 | 19:30
| HVDC Max Flow |  | 656 | 18:00
| HVDC EvPeak Flow |  | 656 | 19:30
| Load factor L.F |  | 75.39%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-01-05
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2019-01-04 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 5286.7 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 4473 | MW
Evening Peak Generation : |  | 7436 | MW Hour : | 19:30 | Available Max Generation : |  | 12335 | MW
E.P. Demand (at gen end) : |  | 7436 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 8100 | MW
Maximum Generation : |  | 7436 | MW Hour : | 19:30 | Reserve(Generation end) |  | 4235 | MW
Total Gen. (MKWH) : |  | 134.5469 | System Load Factor : | 75.39% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -630 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-01-05
Actual : | 98.21 | Ft.(MSL) , | Rule curve : | 102.24 | Ft.( MSL )
Gas Consumed : | Total = | 961.47 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 83200021.724
|  | Coal : | 14120652 | Oil : | 31862456.35 | Total : | 129183130.074
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2811.9333 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 947.9768 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 847.8882 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 765.6175 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 692.1648 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 558.5317 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 322.902 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 144.0874 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 430.7167 |  |  | 0 | 0%
Total | 0 |  | 7521.8185 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 8) Raozan # 01
| Nil |  |  | 2) Khulna ST 110 MW |  | 9) Sirajganj Unit-1,2,4
|  |  |  | 3) Ghorasal Unit-1,5 |  | 10) Ashuganj #3
4) Tongi GT
5) Haripur GT-1,2
6) Siddhirganj ST 210 MW
7) Bhagabari 71 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Siddhirganj 132/33 kV T1 transformer was under shut down from 09:22 to 14:04 for A/M.
b) Maniknagar-Narinda 132 kV Ckt-2 was under shut from 09:04 to 16:57 for A/M.
c) Sikalbaha 132/33 kV T1 transformer was under shut down from 09:30 to 10:50 for Red Hot at 33 kV |  |  |  | About 18 MW Power interruption occurred under Sikalbaha S/S areas
CT, B-phase . |  |  |  | from 06:33(04/01/2019) to till now.
d) Halisahar 132/33 kV T2 transformer was under shut down from 09:30 to 17:06 for C/M.
e) Ramganj 132/33 kV T2 transformer was under shut down from 08:12 to 13:20 for D/W.
f) Khulna(c) 132/33 kV T1 transformer was under shut down from 08:46 to 18:11 for C/M.
g) Sikalbaha 150 MW was tripped at 11:14 due to IGI fault and synchronized at 12:26.
h) After maintenance Nator 132/33 kV T3(35/50) MVA transformer was synchronized at 15:48.
i) Ramganj 132/33 kV T1 transformer was under shut down from 14:10 to 17:25 for D/W.
j) Madunaghat-Sikalbaha 132 kV CKt-1 was tripped at 16:24 and switched on at 16:39 showing Dist. B-phase
E/F at Modunaghat end and Dist. Z-1,B-phase at Sikalbaha end.
k) Sirajganj unit-3 GT& ST were synchronized at 15:34 & 17:28 respectively.
l) Sirajganj unit-2 was shut down at 17:36 for unit-3 synchronizing.
m) Sirajganj unit-3 ST was force shut down at 19:35.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-01-04 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 35 | 740000 | #2 under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | On test
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 350 | 6799590
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 35 | 225792 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 52 | 828000 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 348 | 8377340 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 0 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 365 | 7037000
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 350 | 7887525 | Frequency control
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 0 | 22896 | Reserve
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 25816 | Reserve
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 99612
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 130 | 2585000 | FGMO
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 180 | 3251783 | Frequency control
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 0 | 15696 | Reserve
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 6 | 178320 | Low demand
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 169560
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 0 | 34807 | Reserve
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 8 | 78720 | Low demand
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1162860 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 793900
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 821241
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 25 | 99204 | Engine problem
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 0 | 40320 | Reserve
| Dhaka area Total |  |  |  | 5798 | 2080 | 41274982
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 150 | 3700000
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 102240
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 129195
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 50 | 158400
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 42 | 1012189 | Low water lavel
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 120 | 2381260 | FGMO
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 50 | 347040
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 17 | 155223
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 22560 | Reserve
| Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 92 | 488460 | Engine problem
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 451536
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 40 | 585600
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 0 | 28800 | Reserve
| Chattogram area Total |  |  |  | 1681 | 608 | 9562503
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2097740 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2073726 | Gas shortage
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 186 | 4534000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Reserve
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 261 | 6492000 | FGMO
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 40 | 541080 | Engine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 5 | 152640 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 42 | 400137 | Engine problem
| Midland 150MW |  | IPP | 23*7.015 | 150 | 0 | 35127 | Reserve
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 550920
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2328970 | ST Under maint.
| Chandpur Desh 200MW |  | IPP | 0 | 200 | 0 | 60000 | Reserve
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 331380
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 57060
** | Tripura |  | Imported power | 0 | 160 | 108 | 1958400
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 24 | 66400 | Engine problem
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 14362 | Reserve
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 408070
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1114 | 22422739
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 159 | 3557280 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 331776
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 81 | 296640 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 9950
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 7 | 218400 | Low demand
| Mymensingh Area Total |  |  |  | 522 | 269 | 4414046
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 56 | 838000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 63 | 1181109
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 3085240
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 204 | 4624000 | FGMO
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 379800
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 47 | 305000
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 167424
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 53 | 1116000 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 89 | 486720
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 48 | 341280
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 100 | 2018900 | Frequency control
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 20 | 69000
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 25 | 213460 | Engine problem
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 25 | 97440
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 329 | 7748950 | FGMO
| Bibiyana-3 285MW |  | PDB | 285 MW | 0 | 0 | 0 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 9 | 28260
| Sylhet Area Total |  |  |  | 1549 | 1295 | 22700583
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 656 | 9893818
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 24 | 91200 | Low demand
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 50 | 217088 | Low demand
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 320 | 6914016 | Frequency control
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 226875
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 395040
| Khulna Area Total |  |  |  | 2209 | 1195 | 17738037
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 0 | 24960 | Reserve
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 26 | 401800 | Engine problem
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 194 | 4814889 | FGMO
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 726240
| Barisal Area Total |  |  |  | 462 | 317 | 5967889
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 80 | 1878000 | Gas shortage
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 17 | 47307 | Low demand
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 220180
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 2722018 | Gas shortage
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 141 | 58 | 775296 | Gas shortage
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 0 | 0 | Gas shortage
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 31 | 99336
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 289680
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 11 | 96984 | Engine problem
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 157372
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 52 | 289440 | Engine problem
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 60 | 169316
| Rajshahi Area Total |  |  |  | 1546 | 392 | 6744929
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 149 | 3658200
122 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 50000
123 | Saidpur GT |  | PDB | 1*20 | 20 | 0 | 13000 | Reserve
| Rangpur Area Total |  |  |  | 484 | 166 | 3721200
| Total |  |  |  | 17142 | 7436 | 134546908
| Eastern Grid Total |  |  |  | 12441 | 5366 | 100374853
| Western Grid Total |  |  |  | 4701 | 2070 | 34172055
| National Grid Total |  |  |  | 17142 | 7436 | 134546908
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-01-04 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 4459 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2430 | MW
i) Dhaka area |  |  | 2311 | MW | i) Khulna area |  |  | 933 | MW
ii) Chittagong area |  |  | 676 | MW | ii) Rajshahi area |  |  | 778 | MW
iii) Comilla area |  |  | 626 | MW | iii) Barisal area |  |  | 194 | MW
iv) Mymensingh area |  |  | 546 | MW | iv) Rangpur area |  |  | 525 | MW
v) Sylhet area |  |  | 300 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 6889 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 68 | 1930 | Netrokona | 64 | 1900 | Goalpara | 21 | 1830
Munsiganj | 70 | 1930 | Jamalpur | 80 | 1830 | Central s/s | 54 | 1900
Sonargaon | 35 | 100 | Sherpur | 68 | 1900 | Noapara | 66 | 1830
Shyampur | 122 | 200 | Srimongal | 22 | 1830 | Jessore | 102 | 1830
Bhulta | 134 | 2200 | Shahjibazar | 57 | 1830 | Jhenida | 73 | 1830
Madanganj | 146 | 2100 | Fenchuganj | 26 | 1800 | Bottail | 78 | 1830
Shitalakhya | 161 | 1100 | Kulawara | 27 | 1900 | G.K Project | 33 | 1830
Rahim steel | 3 | 900 | Sylhet | 78 | 1800 | Faridpur | 122 | 1930
Matuail | 58 | 900 | Chatak | 20 | 1830 | Madaripur | 90 | 2000
Ghorasal | 56 | 1900 | Sunamganj | 24 | 1800 | Gopalganj | 60 | 1830
Narsingdi | 90 | 1900 | Biani Bazar | 27 | 1830 | Bagerhat | 63 | 1830
Haripur (SBU) | 64 | 100 | Comilla (S) | 110 | 2000 | Mongla | 20 | 100
Ullon | 51 | 1800 | Comilla(N) | 66 | 1900 | Satkhira | 66 | 1900
Hasnabad | 110 | 1900 | Chandpur | 72 | 1900 | Gallamari | 36 | 1300
Magbazar | 73 | 1200 | Feni | 81 | 1900 | Magura | 36 | 1800
Maniknagar | 52 | 1800 | Chowmuhani | 118 | 1930 | Chuadanga | 56 | 1800
Bangabhaban | 8 | 1300 | Ashuganj | 35 | 2000 | Barisal | 78 | 2000
Narinda | 46 | 1800 | Daudkandi | 66 | 2000 | Patuakhali | 61 | 1930
Dhanmondi | 57 | 1830 | B.Baria | 86 | 1900 | Bhandaria | 36 | 1930
Lalbag | 50 | 1200 | Ramganj | 26 | 1800 | Ishurdi | 39 | 1830
Madartek | 30 | 1800 | Madunaghat | 39 | 1800 | Ruppur Paromanobik | 1 | 100
Mirpur | 72 | 1800 | Hathazari | 60 | 1900 | Natore | 83 | 1830
Kalyanpur | 54 | 1200 | Khulshi | 142 | 1500 | Bogra | 157 | 1900
Gulshan | 62 | 1300 | Halishahar | 74 | 1830 | Noagaon | 84 | 1930
Uttara | 32 | 1300 | Baraulia | 112 | 500 | Rajshahi | 83 | 1900
Uttara(New) | 3 | 700 | Sikalbaha | 27 | 1800 | C.Nawabganj | 58 | 1830
Kamrangirchar | 41 | 1300 | Dohazari | 62 | 1830 | Amnura | 24 | 1900
Savar | 74 | 1830 | Cox'sbazar | 60 | 1930 | Pabna | 68 | 1830
Bhasantec | 72 | 1830 | Chandraghona | 18 | 1800 | Shahjadpur | 59 | 1900
Agargaon | 31 | 1800 | Kaptai | 3 | 1800 | Serajganj | 53 | 1830
Satmosjid | 52 | 1800 | A. Khaer Stl. | 16 | 800 | Niyamatpur | 64 | 1830
Tongi | 89 | 1100 | Bakulia | 56 | 1900 | Joypurhat | 38 | 1830
Kabirpur | 90 | 1800 | Julda | 19 | 100 | Rangpur | 88 | 1830
Basundhara | 62 | 1830 | TK chemical | 5 | 1400 | Lalmonirhat | 69 | 1800
Manikganj | 56 | 1900 | Modern Steel | 10 | 200 | Saidpur | 92 | 1830
Joydevpur | 148 | 1900 | Shahmirpur | 16 | 100 | Purbasadipur | 79 | 1900
New Tongi | 63 | 1000 | Khagrachhari | 15 | 1800 | Thakurgaon | 60 | 1930
Korda | 145 | 1830 | Matarbari | 19 | 1830 | Palashbari | 75 | 1900
Dhamrai | 26 | 1930 | Baroiar Hat | 18 | 1800 | Barapukuria | 43 | 1800
Tangail | 118 | 1800 | Rangamati | 8 | 1800 | Panchagar | 33 | 2000
Mymensing | 165 | 1830 | Abul Khair 230 | 174 | 1100
Kishorganj | 68 | 2000 | BSRM | 91 | 200
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-01-04
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 412 | 22:00 | 403 | 2:00 | Kaliakoir | 402 | 4:00 | 395 | 19:00
Bheramara | 405 | 24:00 | 394 | 10:00 | Bhulta | 405 | 4:00 | 398 | 12:00
Ashuganj(N) | 404 | 7:00 | 397 | 12:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 240 | 1:00 | 240 | 1:00 | Hathazari | 227 | 18:30 | 220 | 2:00
Ishurdi | 240 | 4:00 | 234 | 19:00 | Megnaghat | 238 | 17:00 | 230 | 8:00
Ashuganj | 244 | 6:00 | 237 | 21:00 | Fenchuganj | 244 | 15:00 | 240 | 2:00
Serajganj | 235 | 1:00 | 226 | 19:00 | Siddhirganj | 235 | 7:00 | 232 | 5:00
Baghabari | 232 | 3:00 | 225 | 19:00 | Maniknagar | 233 | 1:00 | 231 | 15:00
Barapukuria | 238 | 7:00 | 226 | 18:30 | Old Airport | 237 | 7:00 | 232 | 12:00
Bogra | 234 | 7:00 | 222 | 19:00 | Barisal | 235 | 1:00 | 227 | 21:00
Khulna South | 241 | 15:00 | 225 | 13:00 | AKSML | 227 | 18:30 | 217 | 12:00
Rampura | 231 | 2:00 | 229 | 12:00 | BSRM | 229 | 18:30 | 221 | 12:00
Haripur | 233 | 3:00 | 231 | 10:00 | Bibiyana | 243 | 17:00 | 240 | 4:00
Hasnabad | 235 | 1:00 | 232 | 13:00 | Bhulta | 235 | 7:00 | 231 | 11:00
Aminbazar | 238 | 4:00 | 233 | 12:00 | Ashuganj (S) | 241 | 2:00 | 238 | 12:00
Tongi | 233 | 23:00 | 226 | 11:00 | Kaliakoir | 240 | 4:00 | 235 | 11:00
Comilla (N) | 241 | 7:00 | 237 | 1:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 137 | 100 | 136 | 900 | Ramganj | 135 | 1830 | 134 | 700
Munsiganj | 140 | 1800 | 135 | 1100 | Madanhat | 135 | 1930 | 129 | 500
Megnaghat | 138 | 300 | 136 | 1200 | Hathazari | 135 | 1830 | 130 | 300
Shyampur | 134 | 1300 | 131 | 400 | Khulshi | 132 | 1800 | 126 | 1200
Bhulta | 139 | 1300 | 135 | 100 | Halishahar | 136 | 1830 | 129 | 1200
Madanganj | 140 | 1700 | 136 | 100 | Baraulia | 133 | 1900 | 128 | 1200
Shitalakhya | 142 | 500 | 137 | 1200 | Sikalbaha | 133 | 1800 | 126 | 1200
Rahim steal | 138 | 300 | 136 | 1000 | Dohazari | 134 | 1830 | 126 | 1200
Matuail | 137 | 600 | 135 | 100 | Cox'sbazar | 129 | 1900 | 123 | 1200
Ghorasal | 142 | 1300 | 140 | 100 | Chandraghona | 135 | 1830 | 129 | 1200
Narsinghdi | 140 | 2200 | 137 | 100 | Kaptai | 135 | 1800 | 130 | 300
Haripur (SBU) | 138 | 1400 | 136 | 100 | A. Khaer Stl. | 136 | 1930 | 128 | 300
Ullon | 134 | 600 | 131 | 1300 | Bakulia | 132 | 1830 | 126 | 1200
Hasnabad | 140 | 600 | 138 | 1300 | Julda | 135 | 1830 | 125 | 1100
Magbazar | 135 | 600 | 132 | 1300 | TK Chemical | 137 | 1830 | 130 | 1200
Maniknagar | 137 | 700 | 135 | 1300 | Modern Steel | 133 | 1800 | 126 | 500
Bangabhaban | 138 | 600 | 135 | 1200 | Shahmirpur | 134 | 1830 | 124 | 1100
Narinda | 134 | 600 | 131 | 1200 | Khagrachhari | 134 | 1830 | 128 | 1200
Dhanmondi | 134 | 600 | 131 | 1300 | Matarbari | 130 | 1800 | 126 | 100
Lalbag | 138 | 600 | 135 | 1200 | Baroiar Hat | 135 | 800 | 134 | 300
Madartek | 134 | 600 | 131 | 1200 | Rangamati | 135 | 1830 | 129 | 300
Mirpur | 136 | 500 | 133 | 1200 | Goalpara | 138 | 1400 | 129 | 700
Kalyanpur | 139 | 400 | 136 | 1100 | Central s/s | 138 | 1700 | 129 | 1300
Gulshan | 133 | 100 | 130 | 1200 | Noapara | 137 | 1700 | 128 | 700
Uttara | 137 | 100 | 133 | 1200 | Jessore | 132 | 1400 | 124 | 700
Uttara(New) | 135 | 100 | 132 | 1200 | Jhenida | 136 | 1700 | 122 | 1300
Kamrangirchar | 138 | 400 | 135 | 1200 | Bottail | 140 | 600 | 135 | 1800
Savar | 135 | 100 | 132 | 1200 | G.K.Project | 143 | 1700 | 139 | 1930
Bhasantec | 138 | 400 | 134 | 1200 | Faridpur | 137 | 200 | 130 | 1930
Agargaon | 138 | 500 | 133 | 1200 | Madaripur | 136 | 1600 | 130 | 1100
Satmosjid | 138 | 500 | 134 | 1200 | Gopalganj | 139 | 1700 | 137 | 300
Tongi | 138 | 2300 | 135 | 1000 | Bagerhat | 139 | 1700 | 130 | 800
Kabirpur | 137 | 500 | 134 | 1930 | Mongla | 136 | 1700 | 128 | 800
Basundhara | 130 | 200 | 126 | 1200 | Satkhira | 137 | 1500 | 128 | 800
Manikganj | 142 | 600 | 139 | 2100 | Gallamari | 140 | 1700 | 129 | 1300
Joydevpur | 142 | 1800 | 138 | 1600 | Magura | 136 | 300 | 127 | 1800
New Tongi | 139 | 500 | 135 | 1100 | Chuadanga | 136 | 100 | 124 | 1830
Kodda | 140 | 500 | 136 | 900 | Barisal | 139 | 600 | 133 | 1300
Dhamrai | 137 | 2400 | 135 | 2100 | Patuakhali | 138 | 700 | 130 | 1900
Tangail | 140 | 500 | 135 | 1500 | Bhandaria | 138 | 1700 | 130 | 1200
Mymensing | 139 | 700 | 132 | 2100 | Ishurdi | 140 | 1500 | 135 | 1400
Kishorganj | 137 | 400 | 135 | 700 | Ruppur Paromanobik | 141 | 500 | 138 | 1800
Netrokona | 138 | 500 | 132 | 2100 | Natore | 139 | 400 | 133 | 1300
Jamalpur | 136 | 400 | 127 | 2100 | Bogra | 139 | 600 | 131 | 1830
Sherpur | 135 | 700 | 127 | 2100 | Noagaon | 136 | 700 | 128 | 1930
Srimongal | 142 | 2200 | 139 | 1800 | Rajshahi | 136 | 500 | 130 | 900
Shahjibazar | 141 | 100 | 139 | 1200 | C.Nawabganj | 131 | 1900 | 125 | 1100
Fenchuganj | 140 | 1830 | 137 | 200 | Amnura | 135 | 1700 | 126 | 1200
Khulawara | 139 | 100 | 138 | 700 | Pabna | 137 | 500 | 132 | 1900
Sylhet | 138 | 100 | 136 | 1200 | Shahjadpur | 144 | 400 | 140 | 1800
Chatak | 138 | 100 | 136 | 1200 | Serajganj | 139 | 400 | 134 | 1800
Sunamganj | 138 | 2200 | 135 | 1300 | Niyamatpur | 136 | 1400 | 124 | 1900
Biani Bazar | 139 | 100 | 137 | 700 | Joypurhat | 138 | 700 | 129 | 800
Cumilla(s) | 132 | 700 | 130 | 1000 | Rangpur | 135 | 700 | 120 | 1900
Cumilla(n) | 142 | 900 | 140 | 2000 | Lalmonirhat | 134 | 700 | 112 | 1900
Chandpur | 141 | 700 | 139 | 1900 | Saidpur | 134 | 1700 | 122 | 1830
Feni | 136 | 1900 | 133 | 1200 | Purbasadipur | 130 | 400 | 114 | 1800
Chowmuhani | 135 | 900 | 130 | 1930 | Thakurgaon | 128 | 1700 | 100 | 1900
Ashuganj | 142 | 800 | 141 | 2000 | Palashbari | 135 | 700 | 122 | 1830
Daudkandi | 139 | 800 | 136 | 1200 | Barapukuria | 138 | 700 | 126 | 1830
B.Baria | 141 | 500 | 139 | 900 | Panchagar | 127 | 1700 | 98 | 1900

## L-Curve
Date | 2019-01-04
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 450 | 4094 | 1340 | 5434 |  |  |  | QF-LDC-12
0:30 | 445 | 4198 | 1295.5 | 5493.5 | Date: | 2019-01-04
1:00 | 440 | 4302 | 1251 | 5553
1:30 | 420 | 4088.5 | 1234.5 | 5323
2:00 | 400 | 3875 | 1218 | 5093
2:30 | 380 | 3809 | 1213 | 5022 | [5 empty] | Gen. at Eve. Peak | 7436 | 7436 MW (19:30 )
3:00 | 360 | 3743 | 1208 | 4951 | [6 empty] | 19:30
3:30 | 380 | 3707.5 | 1183 | 4890.5 | [5 empty] | Gen. at Day Peak | 5286.7 | 5286.7 MW (12:00 )
4:00 | 400 | 3672 | 1158 | 4830 | [6 empty] | 12:00
4:30 | 400 | 3633 | 1137.5 | 4770.5 | [5 empty] | Highest Generation | 7436
5:00 | 400 | 3594 | 1117 | 4711 | [6 empty] | 19:30
5:30 | 420 | 3669 | 1119.5 | 4788.5
6:00 | 440 | 3744 | 1122 | 4866
6:30 | 480 | 3724.83 | 1118 | 4842.83
7:00 | 520 | 3705.66 | 1114 | 4819.66
7:30 | 460 | 3744.13 | 1148.5 | 4892.63
8:00 | 400 | 3782.6 | 1183 | 4965.6
8:30 | 405 | 3843.95 | 1183 | 5026.95
9:00 | 410 | 3905.3 | 1183 | 5088.3
9:30 | 365 | 3872.25 | 1166.5 | 5038.75
10:00 | 320 | 3839.2 | 1150 | 4989.2
10:30 | 290 | 3844.4 | 1162.5 | 5006.9
11:00 | 260 | 3849.6 | 1175 | 5024.6
11:30 | 280 | 3950.65 | 1205 | 5155.65
12:00 | 300 | 4051.7 | 1235 | 5286.7
12:30 | 320 | 4115.25 | 1278 | 5393.25
13:00 | 340 | 4178.8 | 1321 | 5499.8
13:30 | 275 | 3950.95 | 1243 | 5193.95
14:00 | 210 | 3723.1 | 1165 | 4888.1
14:30 | 185 | 3715.65 | 1157 | 4872.65
15:00 | 160 | 3708.2 | 1149 | 4857.2
15:30 | 190 | 3678.9 | 1126 | 4804.9
16:00 | 220 | 3649.6 | 1103 | 4752.6
16:30 | 225 | 3752.1 | 1192 | 4944.1
17:00 | 230 | 3854.6 | 1281 | 5135.6
17:30 | 410 | 4434.3 | 1619 | 6053.3
18:00 | 590 | 5014 | 1957 | 6971
18:30 | 605 | 5171.5 | 2011 | 7182.5
19:00 | 620 | 5329 | 2065 | 7394
19:30 | 620 | 5366 | 2070 | 7436
20:00 | 550 | 5240 | 2071 | 7311 |  |  |  | Executive Engineer
20:30 | 525 | 5163 | 2012.5 | 7175.5 |  |  |  | Network Operation Division
21:00 | 500 | 5086 | 1954 | 7040
21:30 | 440 | 4842.5 | 1874.5 | 6717
22:00 | 380 | 4599 | 1795 | 6394 |  |  |  |  | Page 6 of 7
22:30 | 320 | 4386 | 1731 | 6117
23:00 | 260 | 4173 | 1667 | 5840
23:30 | 355 | 4133.5 | 1503.5 | 5637
24:00 | 450 | 4094 | 1340 | 5434
7436 MW (19:30 )
5286.7 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-01-04 |  | Energy | 134546908
[10 empty] | 2019-01-04 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3508 | 434 | 1217 | 7 | 149 | 43 | 0 | 0 | 76
0:30 | 3507.5 | 357 | 1349 | 9.5 | 149 | 42.5 | 0 | 0 | 79 | Date: | 2019-01-04
1:00 | 3507 | 280 | 1481 | 12 | 149 | 42 | 0 | 0 | 82
1:30 | 3444 | 280.5 | 1315.5 | 11 | 149 | 42 | 0 | 0 | 81 | [7 empty] | Total Energy | 134.5469 | Total Energy Gen 134.547 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 134.547 MKWHr
2:00 | 3381 | 281 | 1150 | 10 | 149 | 42 | 0 | 0 | 80 | [7 empty] | Energy not Served | 0
2:30 | 3337 | 281 | 1123 | 12 | 149 | 42 | 0 | 0 | 78 | [7 empty] | Energy Requirement | 134.5469
3:00 | 3293 | 281 | 1096 | 14 | 149 | 42 | 0 | 0 | 76
3:30 | 3236.5 | 281 | 1092.5 | 13.5 | 149 | 42 | 0 | 0 | 76 | [6 empty] | Shortage
4:00 | 3180 | 281 | 1089 | 13 | 149 | 42 | 0 | 0 | 76
4:30 | 3153.5 | 281 | 1060.5 | 10.5 | 149 | 42 | 0 | 0 | 74
5:00 | 3127 | 281 | 1032 | 8 | 149 | 42 | 0 | 0 | 72
5:30 | 3185 | 280.5 | 1053 | 7.5 | 149 | 42.5 | 0 | 0 | 71
6:00 | 3243 | 280 | 1074 | 7 | 149 | 43 | 0 | 0 | 70
6:30 | 3217.5 | 279.5 | 1077.5 | 7 | 149 | 43 | 0 | 0 | 69 |  |  |  |  | Coal
7:00 | 3192 | 279 | 1081 | 7 | 149 | 43 | 0 | 0 | 68
7:30 | 3227 | 303.5 | 1089 | 9 | 149 | 43 | 0 | 0 | 68 |  |  |  | Oil |  |  |  | ,
8:00 | 3262 | 328 | 1097 | 11 | 149 | 43 | 0 | 0 | 68
8:30 | 3293 | 328 | 1111.5 | 21 | 149 | 43.5 | 0 | 0 | 70
9:00 | 3324 | 328 | 1126 | 31 | 149 | 44 | 0 | 0 | 72
9:30 | 3295.5 | 328 | 1098.5 | 32 | 149 | 44 | 2 | 0 | 73
10:00 | 3267 | 328 | 1071 | 33 | 149 | 44 | 4 | 0 | 74
10:30 | 3286.5 | 328 | 1070 | 33 | 149 | 44 | 2 | 0 | 74
11:00 | 3306 | 328 | 1069 | 33 | 149 | 44 | 0 | 0 | 74
11:30 | 3335 | 328 | 1150 | 49 | 148.5 | 44 | 3.5 | 0 | 76
12:00 | 3364 | 328 | 1231 | 65 | 148 | 44 | 7 | 0 | 78
12:30 | 3429.5 | 328 | 1268 | 66.5 | 148.5 | 44 | 6.5 | 0 | 81
13:00 | 3495 | 328 | 1305 | 68 | 149 | 44 | 6 | 0 | 84
13:30 | 3495 | 328 | 1305 | 68 | 149 | 44 | 6 | 0 | 84
14:00 | 3495 | 328 | 1305 | 68 | 149 | 44 | 6 | 0 | 84
14:30 | 3318 | 328 | 1189 | 46.5 | 149 | 43 | 9.5 | 0 | 79
15:00 | 3141 | 328 | 1073 | 25 | 149 | 42 | 13 | 0 | 74
15:30 | 3105 | 328 | 1056 | 25 | 149 | 42 | 16.5 | 0 | 74
16:00 | 3069 | 328 | 1039 | 25 | 149 | 42 | 20 | 0 | 74
16:30 | 3087 | 364.5 | 1088.5 | 102 | 149 | 42 | 29.5 | 0 | 78
17:00 | 3105 | 401 | 1138 | 179 | 149 | 42 | 39 | 0 | 82
17:30 | 3298 | 528.5 | 1321.5 | 488 | 149 | 42 | 133 | 0 | 93
18:00 | 3491 | 656 | 1505 | 797 | 149 | 42 | 227 | 0 | 104
18:30 | 3563.5 | 656 | 1686 | 771.5 | 149 | 42 | 208.5 | 0 | 106
19:00 | 3636 | 656 | 1867 | 746 | 149 | 42 | 190 | 0 | 108
19:30 | 3714 | 656 | 1906 | 669 | 149 | 42 | 192 | 0 | 108
20:00 | 3698 | 656 | 1886 | 578 | 149 | 42 | 192 | 0 | 110
20:30 | 3712 | 656 | 1880 | 503.5 | 149 | 42 | 127 | 0 | 106
21:00 | 3726 | 656 | 1874 | 429 | 149 | 42 | 62 | 0 | 102
21:30 | 3682 | 656 | 1755 | 303 | 149 | 42 | 31 | 0 | 99
22:00 | 3638 | 656 | 1636 | 177 | 149 | 42 | 0 | 0 | 96
22:30 | 3609 | 654 | 1457.5 | 114 | 149 | 42.5 | 0 | 0 | 91
23:00 | 3580 | 652 | 1279 | 51 | 149 | 43 | 0 | 0 | 86
23:30 | 3544 | 543 | 1248 | 29 | 149 | 43 | 0 | 0 | 81 | Max Temp. in Dhaka |  | 24.8° C
24:00 | 3508 | 434 | 1217 | 7 | 149 | 43 | 0 | 0 | 76
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 134.547 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 134.547 MKWHr
Note on W13: Author:

## Generation
2019-01-04
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 44 | 43 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 1012189
2 | Kaptai Unit-4 & 5
3 | Chattogram ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3700000
5 | Raozan 25 MW (RPCL) | [16 empty] | 8 | 25 |  | 25 | 25 | 25 | 25 | 0 | 0 | 0 | 102240
| Teknaf Solartech 20MW | [6 empty] | 0.66 | 7.3 | 13.4 | 17.8 | 20 | 20 | 19.2 | 16 | 11.3 | 6.2 | 0.6 | 0 | [8 empty] | 129195
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 120 | 85 | 87 | 80 | 80 | 85 | 85 | 133 | 130 | 130 | 130 | 0 | 130 | 80 | 80 | 80 | 80 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2381260
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | [9 empty] | 4 | 0 | 5 | 2 | 7 | 7 | 10 | 5 | 48 |  | 15 | 17 | 17 | 17 | 0 |  |  | 155223
12 | Hathazari peaking
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 122 | 80 | 80 | 80 | 80 | 105 | 70 | 80 | 80 | 80 | 80 | 120 | 120 | 68 | 80 | 80 | 123 | 125 |  | 130 | 130 | 130 | 130 | 120 | 130 | 105 | 2585000
17 | Siddhirganj CCPP-335 MW | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 130 | 180 | 180 | 180 | 150 | 150 | 120 | 3251783
18 | Summit Gazipur -2
19 | Ashuganj 195MW Modular | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal ST: Unit-1,2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 740000
21 | Ghorasal GT: Unit-3
22 | Ghorasal GT: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 300 | 300 | 300 | 300 | 280 | 330 | 280 | 250 | 320 | 280 | 280 | 320 | 320 | 250 | 200 | 200 | 200 | 300 |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 6799590
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2097740
30 | Ashuganj ST: Unit- 5 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2073726
32 | Ashuganj Engines TSK | 40 | 37 | 3 | 3 | 3 | 3 | 25 | 40 | 40 | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 541080
33 | Ashuganj CCPP 225 MW | 185 | 186 | 194 | 160 | 164 | 171 | 184 | 201 | 185 | 188 | 202 | 206 | 185 | 185 | 196 | 195 | 186 | 186 |  | 184 | 186 | 184 | 184 | 184 | 184 | 191 | 4534000
34 | Ashuganj CCPP(South) | 261 | 261 | 276 | 261 | 264 | 279 | 260 | 294 | 261 | 268 | 283 | 294 | 261 | 261 | 279 | 279 | 253 | 261 |  | 261 | 261 | 261 | 261 | 261 | 261 | 268 | 6492000
Ashuganj CCPP(North)
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 152640
36 | Chandpur CCPP | 96 | 100 | 100 | 100 | 100 | 100 | 96 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 95 | 100 | 96 | 100 | 101 | 2328970
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 347 | 348 | 350 | 345 | 345 | 355 | 340 | 280 | 300 | 345 | 350 | 380 | 365 | 350 | 354 | 300 | 300 | 320 |  | 348 | 348 | 348 | 347 | 346 | 346 | 346 | 8377340
40 | Meghnaghat CCPP 450MW | 300 | 350 | 300 | 300 | 280 | 280 | 300 | 300 | 310 | 310 | 310 | 370 | 400 | 300 | 300 | 300 | 350 | 350 |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 7887525
41 | Haripur Power CCPP 360MW | 325 | 298 | 297 | 297 | 265 | 266 | 246 | 246 | 244 | 244 | 245 | 320 | 362 | 240 | 240 | 240 | 240 | 320 |  | 360 | 365 | 368 | 366 | 337 | 334 | 336 | 7037000
42 | Mymensingh RPCL 210MW | 144 | 144 | 146 | 151 | 154 | 155 | 155 | 154 | 149 | 147 | 144 | 141 | 143 | 143 | 154 | 154 | 156 | 157 |  | 158 | 159 | 159 | 159 | 160 | 161 | 159 | 3557280
43 | Haripur NEPC 110MW
44 | Fenchugonj CCPP-1 | 56 | 56 | 30 | 30 | 30 | 30 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 30 | 56 |  | 56 | 56 | 53 | 53 | 56 | 56 | 56 | 838000
45 | Fenchugonj CCPP-2 | 63 | 63 | 30 | 30 | 30 | 30 | 30 | 30 | 40 | 40 | 40 | 40 | 52 | 52 | 63 | 63 | 63 | 63 |  | 63 | 63 | 63 | 62 | 62 | 62 | 52 | 1181109
46 | Shajibazar 330 MW | 220 | 230 | 230 | 221 | 219 | 216 | 205 | 221 | 215 | 207 | 221 | 218 | 201 | 203 | 201 | 225 | 203 | 202 |  | 206 | 204 | 200 | 201 | 198 | 202 | 199 | 4624000
47 | Shahjibazar GT: Unit- 8, 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 69 | 55 | 40 | 51 | 49 | 40 | 40 | 51 | 52 | 53 |  | 51 | 53 | 49 | 53 | 42 | 40 | 40 | 1116000
48 | Shahjibazar 86MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 40 |  | 89 | 89 | 89 | 89 | 5 | 5 | 5 | 486720
49 | Shahjibazar (EPL) 50MW | 49 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 47 |  | 48 | 48 | 48 | 49 | 49 | 5 | 5 | 341280
50 | Sylhet GT 150 MW | 78 | 77 | 78 | 79 | 78 | 78 | 78 | 76 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 78 | 98 | 98 |  | 98 | 100 | 98 | 98 | 80 | 78 | 78 | 2018900
51 | Sylhet GT 20 MW | [17 empty] | 19 |  | 20 | 20 | 20 | 0 |  |  |  | 69000
52 | Sylhet (EPL) 50MW | 50 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 25 |  | 25 | 25 | 25 | 25 | 25 | 7 | 7 | 213460
53 | Sylhet (Desh) 10MW | [17 empty] | 7 |  | 9 | 9 | 9 | 0 |  |  |  | 28260
54 | Hobiganj 11MW | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 3 | 3 | 2 | 2 | 2 | 2 | 0 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 167424
55 | Fenchugonj (Barakatullah) 51MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 5 | 28 |  | 53 | 53 | 53 | 53 | 53 | 5 | 5 | 379800
56 | Shahjahanulla 25 MW | [17 empty] | 25 |  | 25 | 25 | 25 | 0 | 0 |  |  | 97440
57 | Summit Bibiana- 2 | 300 | 290 | 310 | 305 | 300 | 310 | 284 | 300 | 320 | 310 | 310 | 330 | 330 | 290 | 320 | 295 | 315 | 295 |  | 295 | 329 | 305 | 305 | 280 | 280 | 290 | 7748950
58 | Southern 55MW
59 | Sikalbaha (Energis) | [8 empty] | 14 | 16 | 16 | 18 | 39 | 8 | 8 | 8 | 0 | 0 |  | 38 | 50 | 50 | 50 | 50 | 8 | 0 | 347040
60 | Barabkunda (Regent) | 22 | 22 | 0 |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 451536
61 | Narshingdi (Doreen) | [16 empty] | 0 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 99612
62 | Tangail (Doreen) 22MW | [6 empty] | 22 | 22 | 22 | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 0 | 0 | 331776
63 | Tripura | 82 | 80 | 76 | 76 | 72 | 70 | 68 | 68 | 72 | 74 | 74 | 78 | 84 | 78 | 74 | 74 | 82 | 104 |  | 108 | 108 | 110 | 102 | 96 | 86 | 76 | 1958400
64 | Malancha, Ctg. EPZ (United) | 10 | 8 | 8 | 8 | 8 | 8 | 10 | 11 | 12 | 14 | 7 | 14 | 14 | 14 | 15 | 15 | 24 | 40 |  | 40 | 40 | 42 | 40 | 42 | 42 | 42 | 585600
65 | Feni (Doreen) 22MW | 19 | 0 |  |  |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 331380
66 | Feni, Mohipal (Doreen) | [15 empty] | 0 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 0 | 0 | 57060
67 | Jangalia (Summit) 33MW | 8 | 0 | [13 empty] | 0 | 5 | 8 |  | 10 | 24 | 25 | 0 | 0 |  |  | 66400
68 | Summit Cumilla 25MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 20 | 20 | 20 | 22 | 22 | 21 | 22 | 408070
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 18 | 18 | 13 | 13 | 11 | 11 | 14 | 14 |  | 26 | 32 | 32 | 32 | 26 | 26 | 26 | 562860
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 793900
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 821241
73 | Ghorashal (Regent) | 104 | 12 | 0 |  |  |  | 64 | 62 | 62 | 22 | 23 | 22 | 22 | 23 | 22 | 11 | 12 | 52 |  | 52 | 52 | 52 | 52 | 52 | 12 | 12 | 828000
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla)
78 | Gazipur (RPCL) | [16 empty] | 2 | 32 |  | 25 | 25 | 8 | 0 | 0 |  |  | 99204
79 | Kodda 149MW
80 | Jamalpur 95MW | [16 empty] | 30 | 81 |  | 81 | 81 | 50 | 24 | 0 |  |  | 296640
81 | Lakdhanvi 52 MW | [16 empty] | 1 | 8 |  | 0 | [6 empty] | 14362
82 | Madanganj 102MW | [17 empty] | 7 |  | 10 | 0 | [5 empty] | 22896
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW | 50 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 40 |  | 85 | 85 | 85 | 85 | 85 | 6 | 6 | 550920
85 | Keraniganj (Powerpac) 100MW
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL)
88 | Ghorashal 78MW (MAX) | [17 empty] | 35 |  | 35 | 35 | 35 | 35 | 35 | 0 | 0 | 225792
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | [16 empty] | 10 | 10 |  | 10 | 0 | [5 empty] | 22560
92 | Fenchuganj (EPL) 44MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 22 |  | 47 | 47 | 47 | 47 | 47 | 5 | 5 | 305000
93 | Ashuganj (Midland) 51MW | 45 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 20 |  | 42 | 42 | 42 | 42 | 5 | 5 | 5 | 400137
94 | Gagnagar (Orion) | [16 empty] | 7 | 7 |  | 0 | [6 empty] | 15696
95 | Patenga 50MW | [16 empty] | 2 | 29 |  | 50 | 50 | 50 | 18 | 0 |  |  | 158400
96 | Chattogram ECPV 108 MW | [16 empty] | 10 | 13 |  | 7 | 0 | 0 |  |  |  |  | 28800
97 | Katpotti 51 MW | [12 empty] | 12 | 48 | 0 |  |  | 29 |  | 46 | 6 | 6 | 0 |  |  |  | 178320
98 | Bosila 108MW | [15 empty] | 0 | 8 | 46 |  | 32 | 8 | 2 | 0 | 0 |  |  | 78720
99 | Madanganj-55 MW | [17 empty] | 13 |  | 0 | [6 empty] | 25816
100 | Northern 55 MW | [16 empty] | 11 | 18 |  | 0 | 0 | 0 |  |  |  |  | 34807
101 | Kushiara 163 MW CCPP GT | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 163 | 163 | 163 | 163 | 100 | 100 | 100 | 3085240
102 | Sarishabari (Solar) | [7 empty] | 0.3 | 0.9 | 1.4 | 1.6 | 1.7 | 1.6 | 1.1 | 0.9 | 0.4 | 0 | 0 | [8 empty] | 9950
103 | Banco Energy 54MW | [16 empty] | 0 | 54 |  | 54 | 54 | 18 | 18 | 18 | 0 | 0 | 169560
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 218400
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | [16 empty] | 1 | 14 |  | 0 | 0 | 0 |  |  |  |  | 40320
115 | Juldah 100 MW Unit-3 | [7 empty] | 4 | 10 | 10 | 10 | 40 | 10 | 10 | 10 | 10 | 10 | 80 |  | 92 | 92 | 92 | 92 | 10 | 0 |  | 488460
116 | Chandpur Desh 200MW | [15 empty] | 0 | 6 | 32 |  | 0 | 0 | 0 |  |  |  |  | 60000
117 | Midland 150MW | [15 empty] | 0 | 5 | 14 |  | 0 | 0 | 0 |  |  |  |  | 35127
118 | Bibiyana-3 285MW
120 | Eastern Zone Total | 4302 | 3875 | 3743 | 3672 | 3594 | 3744 | 3705.66 | 3782.6 | 3905.3 | 3839.2 | 3849.6 | 4051.7 | 4178.8 | 3723.1 | 3708.2 | 3649.6 | 3854.6 | 5014 |  | 5329 | 5366 | 5240 | 5086 | 4599 | 4173 | 4094 | 100374853
121
122 | o
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | [16 empty] | 16 | 20 |  | 22 | 24 | 23 | 0 |  |  |  | 91200
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking
Khulna CCPP 225MW
129 | Labon Chora 105 MW | [16 empty] | 17 | 105 |  | 105 | 105 | 105 | 53 | 0 |  |  | 395040
130
131
132
133
| Summit Barisal 110 MW | [16 empty] | 0 | 16 |  | 0 | [6 empty] | 24960
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 51 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 11 | 15 |  | 97 | 97 | 97 | 97 | 97 | 51 | 0 | 726240
| Bhola CCPP 194MW | 184 | 206 | 206 | 208 | 208 | 208 | 192 | 207 | 206 | 191 | 200 | 199 | 199 | 198 | 198 | 179 | 181 | 201 |  | 201 | 194 | 196 | 200 | 187 | 200 | 203 | 4814889
140 | Bhola (Venture) 33MW | 20 | 19 | 19 | 17 | 17 | 18 | 16 | 17 | 17 | 10 | 10 | 11 | 12 | 12 | 11 | 11 | 11 | 24 |  | 26 | 26 | 25 | 25 | 23 | 21 | 20 | 401800
141 | Bangla Trak Noapara
142 | Noapara (KZA) 40MW | [16 empty] | 8 | 35 |  | 40 | 40 | 40 | 40 | 40 | 24 | 0 | 226875
143 | Gopalganj Peaking | [11 empty] | 2 | 4 | 4 | 6 | 10 | 25 | 56 |  | 50 | 50 | 50 | 30 | 0 |  |  | 217088
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 280 | 281 | 281 | 281 | 281 | 280 | 279 | 328 | 328 | 328 | 328 | 328 | 328 | 328 | 328 | 328 | 401 | 656 |  | 656 | 656 | 656 | 656 | 656 | 652 | 434 | 9893818
147 | Bheramara 360 MW | 300 | 280 | 280 | 250 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 270 | 360 | 220 | 220 | 200 | 240 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 6914016
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 148 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3658200
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 50 | 50 | 1878000
| Baghabari Peaking 50MW | [17 empty] | 17 |  | 17 | 17 | 17 | 0 | 0 |  |  | 47307
157 | Sirajgonj Unit-1 225MW (Gas)
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 163 | 170 | 167 | 148 | 142 | 148 | 159 | 163 | 164 | 153 | 166 | 175 | 166 | 151 | 134 | 119 | 68 | 0 |  | 0 | [6 empty] | 2722018
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | [15 empty] | 4 | 13 | 17 |  | 48 | 58 | 59 | 143 | 147 | 147 | 148 | 775296
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking
162 | Bogra (GBB) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 6 | 6 | 6 | 6 | 6 | 6 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 5 | 289680
163 | Bogra (EPL) | 11 | 11 | 0 | [13 empty] | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 6 | 96984
164 | Ullapara (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 5 | 157372
165 | Amnura 50MW | [16 empty] | 12 | 50 |  | 50 | 50 | 50 | 50 | 0 | 0 | 0 | 220180
166 | Katakhali (Northern)
167 | Katakhali Peaking
168 | Santahar Peaking | [17 empty] | 38 |  | 31 | 31 | 31 | 0 | 0 |  |  | 99336
169 | Rajlanka 52 MW | 5 | 3 | 7 | 6 | 1 | 0 | [10 empty] | 8 | 52 |  | 52 | 52 | 52 | 52 | 52 | 12 | 0 | 289440
170 | Chapainawabganj-100 MW | [16 empty] | 9 | 51 |  | 60 | 60 | 60 | 0 | 0 |  |  | 169316
171
172
173 | Rangpur GT | [16 empty] | 0 | 17 |  | 17 | 17 | 17 | 0 | 0 |  |  | 50000
175 | Saidpur GT | [22 empty] | 15 | 0 | 0 | 0 | 13000
176
177
178
178 | Western Zone Total | 1251 | 1218 | 1208 | 1158 | 1117 | 1122 | 1114 | 1183 | 1183 | 1150 | 1175 | 1235 | 1321 | 1165 | 1149 | 1103 | 1281 | 1957 | 0 | 2065 | 2070 | 2071 | 1954 | 1795 | 1667 | 1340 | 34172055