## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 31-03-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 30-03-2026 | during | 31-03-2026 | during | 31-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 70 | 180 | 180 | 115 | 115 | ST shut down
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 408 | 412 | 412 | 412 | 392 | 392 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 450 | 450 | 225 | 225 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 16 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 20 | 17 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 15 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 14 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 0 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 24 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 125 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 88 | 96 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 34 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 16 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 75 | 162 | 162 | 145.8 | 145.8 | FGMO
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 24 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 560 | 420 | 584 | 584 | 584 | 584 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage (BPDB)
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 70 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1528 | 1702 | 5865.22 | 5835.22 | 2675.35 | 2645.35
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 39 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 221 | 220 | 225 | 220 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 7 | 64 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 8 | 56 | 64 | 56 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 51 | 51 | 51 | 51 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 46 | 100 | 100 | 100 | 100 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 5 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.87 | 0 | 1.75 | 0 | 1.75 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 30 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 42 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 60 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 27 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 15 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1190 | 1160 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 5 | 6 | 5 | 4 | 5 | 4 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 950 | 950 | 950 | 950 | 950 | 950 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2490.87 | 2804 | 3842.61 | 3854.86 | 3406.25 | 3418.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 210 | 208 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 235 | 252 | 240 | 240 | 240 | 240 | ST shut down
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 0 | 51 | 342.01 | 342.01 | 340 | 340 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 38 | 41 | 41.65 | 41.65 | 41.65 | 41.65 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 5 | 5 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 127 | 16 | 195 | 195 | 9 | 9 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 5 | 100 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 16 | 24 | 24 | 24 | 24 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 97 | 163 | 163 | 104 | 104 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 3 | 100 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 184 | 180 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 18 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 4 | 17 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 58 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2872.921 | 1036 | 1186 | 2628.36 | 2572.36 | 1884.85 | 1834.85
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 30-03-2026 | during | 31-03-2026 | during | 31-03-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 33 | 35 | 157.5 | 157.5 | 100 | 100 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.4 | 0 | 1.4 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 77 | 60 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 78 | 70 | 80 | 70 | 80 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 16.37 | 0 | 45.12 | 0 | 45.12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 22 | 22 | 12 | 12 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 177.37 | 213 | 410.52 | 394 | 305.52 | 289
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 41 | 41 | 41 | 41 | 41 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 158 | 139 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 110 | 105 | 105 | 105 | 105 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 11 | 83 | 83 | 83 | 83 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 99 | 98 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 21 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 396 | 359 | 385 | 385 | 372 | 372 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1131 | 1109 | 1273 | 1273 | 1207 | 1207
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 908 | 888 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 30 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 21 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 303 | 268 | 410 | 410 | 370 | 370 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 47 | 0 | 94 | 0 | 94 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1235 | 1224 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2493 | 2431 | 3606.2 | 3512.2 | 2805.3 | 2711.3
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 127 | 100 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1205 | 1225 | 1244 | 1244 | 1184 | 1184 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 75 | 75 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 282 | 275 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.3 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1834.3 | 1890 | 2162 | 2161 | 2007 | 2006
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 31.39 | 0 | 52 | 0 | 52 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 21 | 40 | 40 | 0 | 0 | Under Maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 205 | 180 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 406 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 15 | 22 | 22 | 22 | 22 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 12 | 80 | 80 | 80 | 80 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2 | 0 | 6 | 0 | 6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 770 | 769 | 748 | 748 | 748 | 748 | Unit-2 under maintenance
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 23.47 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 78 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1523.86 | 1508 | 2518.99 | 2299.99 | 1949.61 | 1730.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 55 | 52 | 55 | 55 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.1 | 0 | 5.2 | 0 | 5.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 18 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 145 | 0 | 155 | 0 | 155 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 221.1 | 192 | 493.2 | 303 | 473.2 | 283
System Total |  |  |  |  | 28823.2 | 29272.163 | 12435.5 | 13035 | 22800.1 | 22205.63 | 16714.08 | 16125.61
Forecast Scenario (31-03-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12060 |  | 0 |  | 12060
|  |  |  | 1:00 | 11720 |  | 0 |  | 11720
|  |  |  | 2:00 | 11290 |  | 0 |  | 11290
|  |  |  | 3:00 | 11010 |  | 0 |  | 11010
|  |  |  | 4:00 | 10830 |  | 0 |  | 10830
|  |  |  | 5:00 | 10600 |  | 0 |  | 10600
|  |  |  | 6:00 | 10650 |  | 0 |  | 10650
|  |  |  | 7:00 | 11290 |  | 0 |  | 11290
|  |  |  | 8:00 | 11710 |  | 0 |  | 11710
|  |  |  | 9:00 | 12010 |  | 0 |  | 12010
|  |  |  | 10:00 | 12350 |  | 0 |  | 12350
|  |  |  | 11:00 | 12870 |  | 0 |  | 12870
|  |  |  | 12:00 | 13000 |  | 0 |  | 13000
|  |  |  | 13:00 | 13720 |  | 0 |  | 13720
|  |  |  | 14:00 | 13570 |  | 0 |  | 13570
|  |  |  | 15:00 | 13560 |  | 0 |  | 13560
|  |  |  | 16:00 | 13300 |  | 0 |  | 13300
|  |  |  | 17:00 | 13090 |  | 0 |  | 13090
|  |  |  | 18:00 | 13000 |  | 0 |  | 13000
|  |  |  | 18:30 | 13100 |  | 0 |  | 13100
|  |  |  | 19:00 | 13260 |  | 0 |  | 13260
|  |  |  | 19:30 | 13430 |  | 0 |  | 13430
|  |  |  | 20:00 | 13530 |  | 0 |  | 13530
|  |  |  | 21:00 | 13670 |  | 0 |  | 13670
|  |  |  | 22:00 | 13030 |  | 0 |  | 13030
|  |  |  | 23:00 | 12800 |  | 0 |  | 12800
Probable Maximum Temperature: |  |  | 32.20°C
Probable Maximum Demand at Day Peak: |  |  | 13000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 13670.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13670.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 294.44705 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:15 hrs on 31-03-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 30-03-2026 | [28 empty] | Date: | 30-03-2026 | [28 empty] | Date: | 30-03-2026 | [28 empty] | Date: | 30-03-2026 | [28 empty] | Date: | 30-03-2026 | [17 empty] | Date: | 30-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [17 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 410 | 0 | 0 | 0 | 0 | 1 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 24 | 950 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1055 | 0 | 0 | 0 | 0 | 252 | 220 | 51 | 0 | 200 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 158 | 0 | 0 | 0 | 300 | 0 | 391 | 41 | 0 | 153 | 0 | 17 | 0 | 5 | 30 | 108 | 0 | 100 | 0 | 59 | 16 | 67 | 0 | 0 | 0 | 5935 | 902 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1046 | 0 | 0 | 0 | 1022.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 414 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 130 | 220 | 0 | 0 | 1244 | 0 | 5831.82 | 11766.82 | 85.14
01:00 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 21 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 24 | 950 | 0 | 0 | 21 | 0 | 0 | 222 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 0 | 255 | 220 | 51 | 0 | 195 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 148 | 0 | 0 | 0 | 290 | 0 | 390 | 41 | 0 | 151 | 0 | 17 | 0 | 5 | 30 | 110 | 0 | 100 | 0 | 45 | 16 | 68 | 0 | 0 | 0 | 5850 | 900 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 884 | 0 | 0 | 0 | 1017.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 414 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 130 | 220 | 0 | 0 | 1200 | 0 | 5572.5 | 11422.5 | 85.13
02:00 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 21 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 25 | 950 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | 257 | 220 | 51 | 0 | 194 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 144 | 0 | 0 | 0 | 290 | 0 | 380 | 41 | 0 | 150 | 0 | 17 | 0 | 5 | 30 | 111 | 0 | 100 | 0 | 35 | 16 | 69 | 0 | 0 | 0 | 5787 | 900 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 812 | 0 | 0 | 0 | 992.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 357 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 130 | 220 | 0 | 0 | 1060 | 0 | 5209.17 | 10996.17 | 85.12
03:00 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 21 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 25 | 950 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | 253 | 220 | 51 | 0 | 198 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 136 | 0 | 0 | 0 | 295 | 0 | 391 | 41 | 0 | 157 | 0 | 17 | 0 | 5 | 30 | 110 | 0 | 100 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 5752 | 900 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 784 | 0 | 0 | 0 | 762.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 375 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 130 | 220 | 0 | 0 | 1050 | 0 | 4958.14 | 10710.14 | 85.11
04:00 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 21 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 25 | 950 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 990 | 0 | 0 | 0 | 0 | 254 | 220 | 51 | 0 | 186 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 132 | 0 | 0 | 0 | 295 | 0 | 365 | 41 | 0 | 153 | 0 | 17 | 0 | 5 | 30 | 108 | 0 | 100 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 5680 | 900 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 761.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 355 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 130 | 220 | 0 | 0 | 1000 | 0 | 4851.06 | 10531.06 | 85.1
05:00 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 21 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 26 | 850 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 905 | 0 | 0 | 0 | 0 | 248 | 220 | 51 | 0 | 185 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 132 | 0 | 0 | 0 | 290 | 0 | 388 | 41 | 0 | 150 | 0 | 17 | 0 | 5 | 30 | 111 | 0 | 100 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 5491 | 900 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 685.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 376 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 130 | 220 | 0 | 0 | 1000 | 0 | 4812.89 | 10303.89 | 85.09
06:00 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 21 | 0 | 430 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0.01 | 80 | 0 | 26 | 850 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 900 | 0 | 0 | 0 | 0 | 249 | 220 | 51 | 0 | 168 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 130 | 0 | 0 | 0 | 290 | 0 | 413 | 41 | 0 | 158 | 0 | 17 | 0 | 5 | 30 | 112 | 0 | 100 | 0 | 2 | 2 | 71 | 0 | 0 | 0 | 5508.01 | 900 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 771 | 0 | 0 | 0 | 691.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 390 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 130 | 220 | 0 | 0 | 1000 | 0 | 4843.64 | 10351.65 | 85.08
07:00 | 0 | 2 | 8 | 187 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 20 | 22 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32 | 80 | 0 | 25 | 950 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 900 | 2 | 0 | 0 | 0 | 253 | 355 | 51 | 0 | 154 | 0 | 0 | 99 | 0 | 0 | 20 | 0 | 130 | 0 | 11 | 0 | 295 | 0 | 390 | 41 | 0 | 159 | 1 | 17 | 0 | 5 | 30 | 109 | 0 | 100 | 0 | 66 | 38 | 69 | 0 | 2.58 | 0 | 5839.9 | 900 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 761 | 0 | 0 | 0 | 745.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.76 | 8 | 0 | 0 | 4.64 | 0 | 0 | 0 | 0 | 193 | 0 | 414 | 0 | 0.53 | 0 | 55 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 22 | 0.07 | 0 | 274 | 130 | 220 | 0 | 0 | 1082 | 0 | 5155.91 | 10995.81 | 85.07
08:00 | 0 | 17 | 16 | 187 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 17 | 22 | 22 | 0 | 410 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 8 | 950 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1000 | 9 | 0 | 8 | 0 | 250 | 205 | 51 | 0 | 153 | 10 | 0 | 99 | 0 | 0 | 20 | 0 | 138 | 0 | 12 | 0 | 290 | 0 | 392 | 41 | 0 | 151 | 2 | 17 | 0 | 5 | 30 | 92 | 0 | 100 | 0 | 66 | 56 | 69 | 0.3 | 16.59 | 0 | 5908.89 | 903 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 892 | 0 | 0 | 0 | 765.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.81 | 20 | 0 | 0 | 13.34 | 0 | 0 | 0 | 0 | 188 | 0 | 414 | 0 | 1.18 | 0 | 55 | 0 | 11 | 0 | 0 | 0 | 0 | 0.4 | 50 | 0.18 | 0 | 275 | 130 | 220 | 0 | 0 | 1190 | 0 | 5501.49 | 11410.38 | 85.06
09:00 | 0 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17 | 20 | 22 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.48 | 80 | 0 | 4 | 950 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1170 | 14 | 0 | 10 | 0 | 244 | 0 | 51 | 0 | 201 | 38 | 0 | 98 | 0 | 0 | 20 | 0 | 144 | 0 | 16 | 0 | 295 | 0 | 414 | 41 | 0 | 158 | 6 | 17 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 68 | 56 | 62 | 0.9 | 30.72 | 0 | 5842.1 | 905 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 1103 | 0 | 0 | 0 | 765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.79 | 51 | 0 | 0 | 24.43 | 0 | 0 | 0 | 0 | 196 | 0 | 414 | 0 | 2.83 | 0 | 55 | 0 | 18 | 0 | 0 | 0 | 0 | 0.7 | 113 | 0.38 | 0 | 281 | 130 | 220 | 0 | 0 | 1190 | 0 | 5872.13 | 11714.23 | 85.05
10:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 17 | 0 | 22 | 0 | 495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 80 | 0 | 3 | 950 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1165 | 17 | 0 | 80 | 0 | 240 | 0 | 51 | 1 | 207 | 39 | 0 | 98 | 0 | 0 | 18 | 0 | 150 | 0 | 60 | 0 | 305 | 0 | 410 | 41 | 0 | 159 | 2 | 8 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 68 | 58 | 61 | 1 | 41.4 | 0 | 6085.4 | 909 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 1104 | 0 | 0 | 0 | 767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.19 | 85 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 201 | 0 | 414 | 0 | 3.64 | 0 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0.5 | 106 | 0.54 | 0 | 276 | 130 | 220 | 0 | 0 | 1195 | 0 | 5905.87 | 11991.27 | 85.04
11:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 17 | 20 | 22 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.45 | 80 | 0 | 2 | 950 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1150 | 18 | 0 | 125 | 0 | 240 | 0 | 51 | 5 | 196 | 36 | 0 | 98 | 0 | 0 | 20 | 0 | 176 | 0 | 67 | 0 | 305 | 0 | 396 | 41 | 0 | 158 | 4 | 17 | 0 | 80 | 30 | 0 | 0 | 99 | 0 | 68 | 58 | 59 | 1.9 | 32.7 | 0 | 6185.05 | 909 | 301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 1227 | 0 | 0 | 0 | 766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 85 | 0 | 0 | 47.88 | 0 | 0 | 0 | 0 | 201 | 0 | 405 | 0 | 2.93 | 0 | 55 | 0 | 15 | 0 | 0 | 0 | 0 | 2.1 | 181 | 0.47 | 0 | 274 | 130 | 220 | 0 | 0 | 1190 | 0 | 6155.38 | 12340.43 | 85.03
12:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 20 | 17 | 88 | 0 | 0 | 16 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 17 | 20 | 21 | 0 | 560 | 0 | 0 | 0 | 0 | 5 | 17 | 0 | 0 | 0 | 0 | 3.87 | 80 | 0 | 3 | 950 | 0 | 0 | 0 | 0 | 7 | 217 | 0 | 0 | 0 | 1190 | 18 | 5 | 127 | 0 | 235 | 0 | 51 | 5 | 210 | 38 | 4 | 96 | 3 | 0 | 20 | 0 | 184 | 0 | 58 | 0 | 305 | 0 | 396 | 42 | 0 | 158 | 4 | 17 | 0 | 80 | 30 | 0 | 0 | 99 | 0 | 68 | 58 | 33 | 2 | 16.37 | 0 | 6363.24 | 908 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 1235 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.39 | 78 | 0 | 0 | 23.47 | 0 | 0 | 0 | 0 | 205 | 0 | 414 | 0 | 2 | 0 | 55 | 0 | 18 | 0 | 0 | 0 | 0 | 3.1 | 145 | 0.3 | 0 | 282 | 127 | 220 | 0 | 0 | 1205 | 0 | 6072.26 | 12435.5 | 85.02
13:00 | 0 | 34 | 24 | 20 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 34 | 17 | 88 | 0 | 95 | 42 | 17 | 112 | 6 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 17 | 20 | 21 | 0 | 530 | 0 | 0 | 0 | 0 | 4 | 17 | 0 | 0 | 0 | 0 | 3.68 | 80 | 15 | 8 | 950 | 0 | 0 | 21 | 0 | 36 | 219 | 0 | 0 | 0 | 1110 | 18 | 65 | 135 | 0 | 240 | 77 | 51 | 8 | 185 | 38 | 58 | 94 | 72 | 0 | 20 | 0 | 180 | 0 | 67 | 0 | 300 | 0 | 336 | 42 | 0 | 155 | 4 | 17 | 0 | 80 | 30 | 0 | 0 | 99 | 0 | 68 | 58 | 33 | 0.7 | 42.02 | 0 | 6778.4 | 916 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.1 | 1202 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 40.95 | 101 | 0 | 0 | 58.47 | 0 | 0 | 0 | 0 | 203 | 0 | 414 | 0 | 2.65 | 0 | 55 | 50 | 27 | 49 | 0 | 0 | 0 | 3.2 | 122 | 0.54 | 0 | 265 | 127 | 220 | 0 | 0 | 1244 | 0 | 6260.91 | 13039.31 | 85.01
14:00 | 0 | 34 | 24 | 20 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 33 | 17 | 88 | 0 | 130 | 55 | 35 | 114 | 13 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 17 | 25 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 0 | 0 | 0 | 2.17 | 80 | 14 | 6 | 950 | 0 | 0 | 24 | 0 | 50 | 218 | 0 | 0 | 0 | 1155 | 16 | 80 | 55 | 0 | 200 | 191 | 51 | 17 | 156 | 36 | 68 | 94 | 94 | 0 | 20 | 0 | 182 | 0 | 57 | 0 | 300 | 0 | 348 | 42 | 0 | 135 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 98 | 0 | 68 | 58 | 33 | 1.7 | 33.81 | 0 | 6803.68 | 916 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.71 | 1206 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 36.94 | 88 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 192 | 0 | 358 | 0 | 4.99 | 0 | 55 | 50 | 19 | 51 | 0 | 0 | 0 | 4 | 75 | 0.54 | 0 | 274 | 127 | 220 | 0 | 0 | 1244 | 0 | 6133.18 | 12936.86 | 85
15:00 | 0 | 34 | 24 | 40 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 32.3 | 17 | 88 | 0 | 130 | 55 | 35 | 120 | 13 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 17 | 25 | 21 | 0 | 420 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 8 | 0 | 1.75 | 80 | 16 | 2 | 950 | 0 | 0 | 27 | 0 | 34 | 218 | 0 | 0 | 0 | 1150 | 12 | 80 | 23 | 0 | 202 | 220 | 51 | 5 | 140 | 33 | 69 | 94 | 99 | 0 | 20 | 0 | 174 | 0 | 45 | 0 | 305 | 0 | 348 | 42 | 0 | 149 | 1 | 20 | 0 | 80 | 30 | 0 | 0 | 98 | 0 | 68 | 57 | 34 | 0.7 | 5.85 | 0 | 6722.6 | 916 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.69 | 1218 | 0 | 0 | 0 | 748 | 0 | 0 | 0 | 20 | 50 | 0 | 0 | 0 | 0 | 35.71 | 71 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 195 | 0 | 394 | 0 | 3.48 | 0 | 54 | 50 | 9 | 49 | 0 | 0 | 0 | 1.1 | 103 | 0.41 | 0 | 275 | 127 | 220 | 0 | 0 | 1244 | 0 | 6175.39 | 12897.99 | 84.99
16:00 | 0 | 34 | 33 | 80 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 35 | 17 | 88 | 0 | 95 | 55 | 35 | 88 | 13 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 35 | 25 | 21 | 0 | 420 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 16 | 25 | 1.42 | 80 | 15 | 0 | 950 | 0 | 0 | 31 | 0 | 32 | 220 | 0 | 0 | 0 | 1162 | 7 | 80 | 16 | 0 | 240 | 84 | 51 | 5 | 147 | 41 | 68 | 94 | 85 | 0 | 20 | 0 | 178 | 0 | 27 | 0 | 300 | 0 | 362 | 42 | 0 | 153 | 1 | 20 | 0 | 80 | 30 | 0 | 0 | 98 | 0 | 68 | 57 | 34 | 0.5 | 17.93 | 0 | 6665.85 | 916 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.16 | 1234.2 | 0 | 0 | 0 | 748 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 23.69 | 29 | 0 | 0 | 5.94 | 0 | 0 | 0 | 0 | 185 | 0 | 410 | 0 | 0.42 | 0 | 54 | 50 | 10 | 44 | 0 | 0 | 0 | 1.2 | 44 | 0.19 | 0 | 277 | 127 | 220 | 0 | 0 | 1225 | 0 | 5997.8 | 12663.65 | 84.98
17:00 | 0 | 50 | 33 | 80 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 35 | 17 | 88 | 15 | 95 | 55 | 35 | 84 | 14 | 225 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 5 | 35 | 25 | 21 | 0 | 420 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 24 | 36 | 0.52 | 80 | 16 | 9 | 950 | 0 | 0 | 33 | 0 | 33 | 221 | 0 | 0 | 0 | 1150 | 2 | 80 | 16 | 0 | 245 | 77 | 51 | 5 | 181 | 39 | 69 | 96 | 84 | 0 | 20 | 0 | 168 | 0 | 10 | 0 | 300 | 0 | 360 | 42 | 0 | 154 | 0 | 21 | 0 | 82 | 30 | 30 | 0 | 98 | 0 | 68 | 57 | 34 | 0.3 | 6.59 | 0 | 6739.41 | 915 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.79 | 1222 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 9.78 | 21 | 0 | 0 | 15.54 | 0 | 0 | 0 | 0 | 185 | 0 | 403 | 0 | 1.17 | 0 | 53 | 35 | 5 | 34 | 0 | 0 | 0 | 1.2 | 11 | 0.1 | 10 | 275 | 127 | 220 | 0 | 0 | 1225 | 2 | 5887.58 | 12626.99 | 84.97
18:00 | 0 | 50 | 33 | 80 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 35 | 20 | 93 | 15 | 110 | 55 | 34 | 83 | 15 | 225 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 60 | 24 | 21 | 0 | 420 | 10 | 15 | 0 | 0 | 5 | 51 | 0 | 0 | 24 | 46 | 0 | 80 | 15 | 10 | 950 | 14 | 0 | 38 | 0 | 31 | 221 | 0 | 0 | 0 | 1163 | 0 | 90 | 16 | 0 | 249 | 22 | 51 | 5 | 199 | 36 | 64 | 97 | 82 | 0 | 20 | 0 | 170 | 1 | 0 | 3 | 300 | 0 | 355 | 41 | 0 | 139 | 0 | 21 | 0 | 41 | 30 | 40 | 0 | 98 | 3 | 78 | 76 | 34 | 0 | 0 | 0 | 6836 | 888 | 276 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37 | 1138 | 0 | 0 | 0 | 744 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0.04 | 0 | 10 | 0 | 0.17 | 0 | 0 | 0 | 0 | 183 | 0 | 402 | 0 | 0.01 | 0 | 52 | 55 | 0 | 55 | 0 | 0 | 0 | 0.2 | 2 | 0 | 16 | 273 | 127 | 180 | 0 | 0 | 1225 | 27 | 5724.79 | 12560.79 | 84.96
19:00 | 0 | 34 | 24 | 60 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17 | 0 | 103 | 15 | 160 | 55 | 17 | 82 | 15 | 225 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 435 | 27 | 30 | 0 | 0 | 4 | 51 | 2 | 0 | 44 | 60 | 0 | 80 | 42 | 12 | 950 | 16 | 0 | 36 | 0 | 63 | 221 | 0 | 0 | 0 | 1160 | 0 | 120 | 16 | 0 | 246 | 22 | 51 | 5 | 180 | 41 | 67 | 97 | 94 | 0 | 18 | 17 | 180 | 8 | 0 | 16 | 290 | 0 | 353 | 41 | 0 | 137 | 0 | 21 | 0 | 11 | 30 | 110 | 0 | 98 | 17 | 78 | 77 | 35 | 0 | 0 | 5 | 7020 | 888 | 268 | 0 | 25 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1140 | 0 | 0 | 0 | 750 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 410 | 0 | 0 | 0 | 52 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 247 | 127 | 180 | 0 | 0 | 1225 | 54 | 5832 | 12852 | 84.95
19:30 | 0 | 34 | 24 | 70 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17 | 0 | 96 | 15 | 125 | 55 | 17 | 75 | 16 | 225 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 70 | 14 | 0 | 0 | 420 | 27 | 30 | 0 | 0 | 6 | 51 | 8 | 0 | 46 | 60 | 0 | 80 | 42 | 5 | 950 | 15 | 0 | 39 | 0 | 64 | 221 | 0 | 0 | 0 | 1160 | 0 | 100 | 16 | 0 | 252 | 51 | 51 | 5 | 208 | 41 | 17 | 97 | 100 | 9 | 18 | 17 | 180 | 8 | 0 | 16 | 300 | 0 | 359 | 41 | 0 | 139 | 0 | 21 | 0 | 11 | 30 | 110 | 0 | 98 | 17 | 78 | 77 | 35 | 0 | 0 | 6 | 7014 | 888 | 268 | 0 | 30 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 769 | 0 | 21 | 0 | 35 | 50 | 0 | 12 | 20 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 406 | 0 | 0 | 0 | 52 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 275 | 100 | 220 | 0 | 0 | 1225 | 54 | 6021 | 13035
20:00 | 0 | 34 | 24 | 70 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17 | 1 | 93 | 15 | 95 | 55 | 17 | 64 | 16 | 225 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 70 | 25 | 21 | 0 | 435 | 28 | 30 | 0 | 0 | 5 | 51 | 8 | 0 | 24 | 36 | 0 | 80 | 48 | 12 | 950 | 16 | 0 | 39 | 0 | 65 | 220 | 0 | 0 | 0 | 1167 | 0 | 100 | 16 | 0 | 249 | 66 | 51 | 5 | 201 | 40 | 23 | 98 | 68 | 5 | 18 | 17 | 136 | 11 | 0 | 0 | 300 | 0 | 396 | 41 | 0 | 149 | 0 | 21 | 0 | 11 | 30 | 110 | 0 | 98 | 17 | 78 | 77 | 35 | 0 | 0 | 6 | 6958 | 862 | 268 | 0 | 27 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 749 | 0 | 44 | 0 | 35 | 35 | 0 | 25 | 24 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 410 | 0 | 0 | 0 | 51 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 294 | 127 | 220 | 0 | 0 | 1225 | 54 | 6065.2 | 13023.2 | 84.93
21:00 | 0 | 34 | 24 | 80 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 35 | 87 | 15 | 95 | 55 | 17 | 17 | 16 | 225 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 52 | 25 | 21 | 0 | 450 | 33 | 30 | 0 | 0 | 11 | 51 | 8 | 0 | 24 | 36 | 0 | 80 | 51 | 14 | 950 | 16 | 0 | 39 | 0 | 67 | 221 | 0 | 0 | 0 | 1165 | 0 | 70 | 16 | 0 | 250 | 69 | 51 | 5 | 199 | 42 | 17 | 98 | 68 | 9 | 18 | 17 | 146 | 25 | 0 | 0 | 290 | 0 | 397 | 41 | 0 | 160 | 0 | 13 | 0 | 5 | 30 | 110 | 0 | 98 | 17 | 78 | 77 | 35 | 0 | 0 | 6 | 6930 | 862 | 264 | 0 | 27 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 8 | 0 | 0 | 750 | 0 | 44 | 0 | 35 | 35 | 0 | 26 | 23 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 412 | 0 | 0 | 0 | 52 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 130 | 220 | 0 | 0 | 1225 | 54 | 6101.2 | 13031.2 | 84.91
22:00 | 0 | 34 | 24 | 80 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 35 | 77 | 15 | 95 | 55 | 17 | 17 | 0 | 225 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 52 | 17 | 21 | 0 | 400 | 31 | 30 | 0 | 0 | 3 | 34 | 8 | 0 | 0 | 36 | 0 | 80 | 50 | 13 | 950 | 0 | 0 | 39 | 0 | 66 | 223 | 0 | 0 | 0 | 1161 | 0 | 70 | 8 | 0 | 252 | 75 | 51 | 5 | 200 | 42 | 17 | 99 | 68 | 9 | 20 | 17 | 160 | 25 | 0 | 0 | 295 | 0 | 382 | 42 | 0 | 160 | 0 | 17 | 0 | 5 | 30 | 110 | 0 | 98 | 17 | 78 | 77 | 35 | 0 | 0 | 6 | 6787 | 862 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 12 | 0 | 0 | 752 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 0 | 0 | 0 | 52 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 130 | 220 | 0 | 0 | 1225 | 54 | 5949.2 | 12736.2 | 84.89
23:00 | 0 | 34 | 24 | 115 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 35 | 70 | 15 | 95 | 55 | 17 | 17 | 0 | 225 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 52 | 23 | 22 | 0 | 400 | 30 | 30 | 0 | 0 | 0 | 25 | 7 | 0 | 0 | 36 | 0 | 80 | 49 | 13 | 950 | 0 | 0 | 39 | 0 | 62 | 222 | 0 | 0 | 0 | 1155 | 0 | 70 | 8 | 0 | 252 | 130 | 51 | 5 | 211 | 42 | 17 | 98 | 66 | 9 | 20 | 17 | 166 | 25 | 0 | 0 | 295 | 0 | 364 | 41 | 0 | 146 | 0 | 17 | 0 | 5 | 30 | 110 | 0 | 98 | 17 | 78 | 77 | 35 | 0 | 0 | 6 | 6832 | 862 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1216 | 16 | 0 | 0 | 755 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 409 | 0 | 0 | 0 | 54 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 130 | 220 | 0 | 0 | 1225 | 54 | 5928 | 12760 | 84.87
Total KWH | 0 | 612480 | 427680 | 2298236 | 0 | 0 | 0 | 0 | 9914400 | 0 | 0 | 259200 | 287280 | 1512432 | 112320 | 1322291 | 683248 | 293712 | 809280 | 130560 | 4947000 | 0 | 0 | 0 | 142835 | 0 | 0 | 0 | 172863 | 595200 | 468600 | 489960 | 0 | 10566363.64 | 188182 | 210764 | 0 | 0 | 68640 | 525117 | 74857 | 0 | 170880 | 355200 | 20023 | 1924080 | 391418 | 352800 | 22698181.82 | 55200 | 0 | 414720 | 0 | 644000 | 5184455 | 0 | 0 | 0 | 26274543 | 128520 | 1063854 | 202545 | 0 | 6033100 | 3188000 | 1249768 | 94560 | 4620000 | 614088 | 571200 | 2342836 | 1005600 | 42840 | 479920 | 110580 | 3717120 | 123960 | 438255 | 23200 | 7180000 | 0 | 9318000 | 982000 | 0 | 3645081.82 | 32192 | 406392 | 0 | 846720 | 713856 | 1552600 | 0 | 2381400 | 110520 | 1374000 | 1190400 | 1139520 | 10700 | 247660 | 36240 | 152816229.28 | 21397818 | 7310016 | 0 | 74880 | 76800 | 0 | 0 | 0 | 0 | 0 | 0 | 532800 | 25629090 | 47620 | 0 | 0 | 18818182 | 0 | 82874 | 0 | 363936 | 538944 | 0 | 47424 | 46397 | 0 | 345504 | 641520 | 80881 | 0 | 325504 | 0 | 0 | 0 | 0 | 4718182 | 0 | 9683418 | 0 | 27300 | 0 | 1304727 | 716346 | 148318 | 678009 | 0 | 0 | 0 | 16834.08 | 846720 | 3462 | 126336 | 6262000 | 3073000 | 5412560 | 0 | 0 | 28564363.64 | 325200 | 138266965.72 | 291083195

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 30-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12435.5 | MW | 12:00 Hr. | Energy Generated |  |  | 291.0832 |  | MKWHr.
| Day Peak Demand |  |  | 12701.5 | MW | 12:00 Hr. | Energy Unserverd |  |  | 3.331 |  | MKWHr.
| Evening Peak Generation |  |  | 13035 | MW | 19:30 Hr. | Energy Demand |  |  | 294.4142 |  | MKWHr.
| Evening Peak Demand |  |  | 13370.2 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33.5 |  | °C
| Minimum Generation of the Day |  |  | 10303.89 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 846.99 |  | MMCFD
| Maximum Generation of the Day |  |  | 13039.31 | MW | 13:00 Hr. | Production Cost per KWHr |  |  | 6.0463 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 28.6846 | 0 | 7.1885 | 0 | 0 | 0.17286 | 0 | 0 | 36.0459 | Gas | 111.4094 | Gas | 387655918.5032
| Chattogram Zone |  |  | 5.5373 | 48.9727 | 3.0303 | 0 | 1.9241 | 0.14854 | 0 | 0.06864 | 59.6816 | Coal | 110.7329 | Coal | 746259045.2358
| Cumilla Zone |  |  | 18.8248 | 0 | 2.9412 | 0 | 0 | 0.43826 | 3.7171 | 0 | 25.9214 | HFO | 19.0769 | HFO | 320024668.6
| Mymensingh Zone |  |  | 1.1395 | 0 | 2.7112 | 0 | 0 | 0.25836 | 0 | 0 | 4.109 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.026 | 0 | 0 | 0 | 0 | 0.032192 | 0 | 0 | 27.0582 | Hydro | 1.9241 | Hydro | 192408
| Khulna Zone |  |  | 7.31 | 25.6291 | 0.1993 | 0 | 0 | 0.5328 | 21.3978 | 0 | 55.069 | Solar | 3.9382 | Solar | 62213154.366
| Barishal Zone |  |  | 8.4856 | 34.8264 | 0.45154 | 0 | 0 | 0.003462 | 0 | 0 | 43.7669 | Import | 43.9331 | Import | 242621425.68
| Rajshahi Zone |  |  | 14.4016 | 0 | 1.1605 | 0 | 0 | 1.3398 | 18.8182 | 0 | 35.7201 | Wind | 0.06864 | Wind | 1009694.4
| Rangpur Zone |  |  | 0 | 1.3047 | 1.3944 | 0 | 0 | 1.0119 | 0 | 0 | 3.711
| Total |  |  | 111.4094 | 110.7329 | 19.0769 | 0 | 1.9241 | 3.9382 | 43.9331 | 0.06864 | 291.0832
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 387655918.5032 |  | Hydro | 192408
|  |  |  | Coal | 746259045.2358 |  | Solar | 62213154.366
|  |  |  | HFO | 320024668.6 |  | Import | 242621425.68
|  |  |  | HSD | 0 |  | Wind | 1009694.4
[5 empty] | Total: | 175,99,76,314 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.3978 | Peak Hr Flow | 888.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 43659454.54 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 18.8182 | Peak Hr Flow | 769.00 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1706 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.7171 | Peak Hr Flow | 180.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2566 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 43.9331 | Peak Hr Flow | 1837.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 20 |  | 4447
|  |  |  | Chattogram |  | 0 |  | 1457
|  |  |  | Cumilla |  | 0 |  | 1322
|  |  |  | Mymensingh |  | 20 |  | 1013
|  |  |  | Sylhet |  | 0 |  | 408
|  |  |  | Khulna |  | 30 |  | 1745
|  |  |  | Barishal |  | 15 |  | 432
|  |  |  | Rajshahi |  | 0 |  | 1198
|  |  |  | Rangpur |  | 15 |  | 739
|  |  |  | Total |  | 100 |  | 12761
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:32 | 09:58 | Nawabganj 132/33kV S/S TR-2 LT Forced S/D Due to 33 kV incomer-02 shutdown for redhot
maintenance.
| 08:33 | 09:55 | Nawabganj 132/33kV S/S TR-2 HT Forced S/D Due to 33 kV incomer-02 shutdown for redhot
maintenance.
|  | 08:38 | Purbasadipur 230/132/33kV S/S TR-4 (H02R22) HT is restored.
|  | 08:40 | Purbasadipur 230/132/33kV S/S TR-4 (H02R22) LT is restored.
|  | 09:03 | Thakurgaon 132/33kV S/S T-2(412T) HT is restored.
|  | 09:04 | Thakurgaon 132/33kV S/S T-2(412T) LT is restored.
| 09:05 |  | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to Shutdown
by ALDC and from Bhandaria 132/33kV end Due to Barishal-Bhandaria line maintenance work
| 09:08 |  | Ashuganj 450 MW CCPP(South) Shutdown with remarks:- Plant
|  | 09:23 | Saidpur 132/33kV S/S 33 kV Bus is restored.
| 09:49 | 17:47 | KSRM 132/33kV S/S Transformer-01 HT Scheduled S/D Due to Shutdown Grid Transformer 01
(35/50 MVA) for secondary CT (33kv side) maintenance
| 11:25 | 13:53 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Scheduled S/D
| 11:25 | 13:50 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT Scheduled S/D
| 12:00 |  | Day Peak Generation: 12433 MW
| 12:20 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 14:32 | 14:37 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing OC/EF Protection Relay relays Due to
Chunarughat Feeder Tripped of PBS
| 16:03 | 17:01 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to PBS DS Redhot maintenance | [7 empty] | 23.0MW load
interrup.
| 16:03 | 17:24 | Bogura 400/230kV S/S ATR-01 HT Scheduled S/D Due to Oil leakage maintenance.
| 16:04 | 17:00 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to PBS DS Redhot maintenance | [7 empty] | 23.0MW load
interrup.
| 16:35 | 18:35 | Mirsorai 230/33kV S/S TR-1, 718T HT Project Work S/D Due to testing for SPMD
| 19:31 | 19:50 | Kasba 132/33kV S/S Muradnagar-Kasba Ckt-2 Tripped showing distantce relays Due to fault
| 19:48 | 22:09 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Shutdown Taken By PBS for Bus
Coupler Maintenance
| 19:49 | 22:08 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Shutdown Taken By Pbs for Bus
Coupler Maintenance
| 21:45 | 21:56 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing Lockout relays Due to Chunarughat
feeder Trip Under PBS.
| 21:45 | 21:54 | Shahjibazar 132/33kV S/S TR-02 HT Tripped showing Lockout Relay , 132 KV OC/EF Relay.
relays Due to Chunarughat feeder Trip Under PBS.
| 22:16 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- ST
| 05:22 |  | BIPTC S/S 20DF22 Tripped showing Pole discrepancy relays.
| 05:22 |  | BIPTC S/S 20DF11 Tripped showing Differential relays.
| 06:00 |  | Minimum generation: 10570 MW
| 06:46 |  | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 LT Scheduled S/D Due to
Maintenance
| 07:01 |  | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 HT Scheduled S/D Due to
Maintenance
| 07:22 |  | Haripur-Meghnaghat 230kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to Ordered
by NLDC
| 07:48 |  | Haripur-Meghnaghat 230kV Ckt-1 Scheduled S/D from Meghnaghat 230/132kV end Due to red
hot mainteance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 30-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 70 | 2298236 | GBC-3 Under maintenance.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 412 | 9914400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4947000 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 683248 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 259200 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 15 | 112320 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 293712 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 142835 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 14 | 468600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 0 | 489960 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 427680 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 125 | 1322291 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 96 | 1512432 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 612480 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 130560 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 75 | 809280 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 172863 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 287280 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 420 | 10566363.64 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 70 | 595200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1702 | 36045940.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 128520 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 39 | 414720 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1924080 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 5184455 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 64 | 644000 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 8 | 74857 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 525117 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 46 | 170880 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 5 | 352800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20023 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 210764 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 42 | 391418 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 60 | 355200 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 27 | 188182 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 15 | 55200 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 26274543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 6 | 68640 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 950 | 22698181.82 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 2804 | 59681580.82
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 208 | 4620000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 252 | 6033100 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 51 | 3188000 | Able to ON FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 41 | 614088 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 94560 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 16 | 202545 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1249768 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 100 | 1063854 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 16 | 23200 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 97 | 2342836 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 1005600 | -
| Import (Tripura) |  | Import | 0 | 160 | 180 | 3717120 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 123960 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 18 | 479920 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 110580 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 42840 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 17 | 571200 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 438255 | -
Cumilla Area Total |  |  |  |  | 2872.921 | 1186 | 25921426
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 35 | 1139520 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 77 | 1190400 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1374000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 247660 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 36240 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 110520 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 213 | 4109040
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 32192 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 982000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 139 | 3645081.82 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 110 | 1552600 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 713856 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 11 | 846720 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 98 | 2381400 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 21 | 406392 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7180000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 359 | 9318000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1109 | 27058241.82
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 888 | 21397818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 30 | 74880 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 21 | 76800 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 268 | 7310016 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 47620 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 532800 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1224 | 25629090 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2431 | 55069024
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 126336 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 100 | 3073000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1225 | 28564363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5412560 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 325200 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 275 | 6262000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3462 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1890 | 43766921.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 345504 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Machine Problem
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 21 | 82874 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 46397 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 180 | 4718182 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 406 | 9683418 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 15 | 80881 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 12 | 47424 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 538944 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 363936 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 27300 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 769 | 18818182 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 325504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 641520 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1508 | 35720066
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 52 | 1304727 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 678009 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 16834.08 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 716346 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 148318 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 846720 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 192 | 3710954.08
Eastern Grid Total |  |  |  |  | 17419.968 | 7014 | 152816229.28
Western Grid Total |  |  |  |  | 11852.195 | 6021 | 138266965.72
National Grid Total |  |  |  |  | 29272.163 | 13035 | 291083195
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 30-03-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8606.99 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4054.1 | MW
i) Dhaka area |  |  | 4426.99 |  | MW | i) Khulna area |  |  |  | 1715 | MW
ii) Chattogram area |  |  | 1457 |  | MW | ii) Barishal area |  |  |  | 416.9 | MW
iii) Cumilla area |  |  | 1322 |  | MW | iii) Rajshahi area |  |  |  | 1198.2 | MW
iv) Mymensingh area |  |  | 993 |  | MW | iv) Rangpur area |  |  |  | 724 | MW
v) Sylhet area |  |  | 408 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12661.09 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 71 | 17:00 | 133 | Natore | 139 | 19:30
2 | AKSML | 11 | 18:00 | 68 | Hathazari | 79 | 19:30 | 134 | Nawabganj | 58 | 22:00
3 | Aftabnagar | 36 | 18:30 | 69 | Hatirjheel | 43 | 13:00 | 135 | Netrakona | 109 | 19:00
4 | Agargaon | 119 | 15:00 | 70 | Ishurdi | 70 | 15:00 | 136 | New | 72 | 15:00
5 | Agrabad | 68 | 12:00 | 71 | Jaldhaka | 60 | 08:00 | 137 | Niamatpur | 61 | 18:30
6 | Amnura | 32 | 14:00 | 72 | Jamalpur | 120 | 08:00 | 138 | Noapara | 45.5 | 18:30
7 | Ashuganj | 72 | 23:00 | 73 | Jashore | 150 | 19:30 | 139 | PHP | 8 | 15:00
8 | BSRM | 197 | 09:00 | 74 | Jhenaidah | 107 | 18:30 | 140 | Pabna | 87 | 19:30
9 | Bagerhat | 84 | 19:30 | 75 | Joydebpur | 139 | 18:00 | 141 | Palashbari | 94 | 19:00
10 | Bajitpur | 73 | 15:00 | 76 | Joypurhat | 51 | 08:00 | 142 | Panchagarh | 42 | 18:30
11 | Bakerganj | 10.4 | 22:00 | 77 | Juldah | 17 | 12:00 | 143 | Patiya | 10 | 18:30
12 | Bakulia | 88 | 18:30 | 78 | KSRM | 12 | 09:00 | 144 | Patuakhali | 59.3 | 23:00
13 | Banani | 28 | 13:00 | 79 | Kabirpur | 220 | 18:30 | 145 | Payra | 30 | 00:00
14 | Bangabhaban | 18 | 10:00 | 80 | Kachua | 99 | 19:30 | 146 | Postogola | 45 | 13:00
15 | Barapukuria | 52 | 19:00 | 81 | Kaliganj | 29 | 18:30 | 147 | Pubail | 26 | 15:00
16 | Barguna | 18 | 00:00 | 82 | Kallyanpur | 90 | 12:00 | 148 | Purbachal | 30 | 13:00
17 | Barishal | 99 | 13:00 | 83 | Kalurghat | 40 | 15:00 | 149 | Purbasadipur | 92 | 14:00
18 | Barishal-230 | 100 | 18:30 | 84 | Kamrangirchar | 74 | 13:00 | 150 | Rahanpur | 27 | 20:00
19 | Baroaulia | 65 | 18:30 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 23 | 18:00
20 | Baroirhat | 61 | 20:00 | 86 | Kasba | 36 | 19:30 | 152 | Rajbari | 82 | 19:00
21 | Bashundhara | 171 | 13:00 | 87 | Kazla | 106 | 13:00 | 153 | Rajendrapur | 120 | 18:30
22 | BashundharaCement | 8 | 21:00 | 88 | Keranigonj | 71 | 19:00 | 154 | Rajshahi | 95 | 21:00
23 | Beanibazar | 54 | 20:00 | 89 | Khagrachori | 34 | 18:30 | 155 | Rajshahi-230 | 90 | 13:00
24 | Benapole | 64 | 22:00 | 90 | Khulna | 62 | 13:00 | 156 | Ramganj | 114 | 18:30
25 | Bhaluka | 148 | 16:00 | 91 | Khulshi | 189 | 13:00 | 157 | Rampur | 39 | 21:00
26 | Bhandaria | 52 | 18:30 | 92 | Kishoreganj | 107 | 13:00 | 158 | Rangamati | 20 | 18:30
27 | Bhangura | 40 | 14:00 | 93 | Kodda | 305 | 09:00 | 159 | Rangpur | 112 | 18:30
28 | Bheramara(GK) | 56 | 18:00 | 94 | Kulaura | 32 | 14:00 | 160 | Ruppur | 4 | 10:00
29 | Bhulta | 188 | 08:00 | 95 | Kurigram | 50 | 18:30 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 74 | 12:00 | 96 | Kushtia | 136 | 18:30 | 162 | Saidpur | 86 | 11:00
31 | Bogura | 145 | 19:00 | 97 | Laksam | 21 | 21:00 | 163 | Satkhira | 137 | 21:00
32 | Borhanuddin | 90 | 00:00 | 98 | Lakshmipur | 40 | 19:00 | 164 | Satmasjid | 93 | 14:00
33 | Brahmanbaria | 116 | 21:00 | 99 | Lalbag | 58 | 13:00 | 165 | Savar | 190 | 10:00
34 | Cantonment | 158 | 12:00 | 100 | Lalmonirhat | 46 | 18:30 | 166 | SevenRings | 6.3 | 16:00
35 | Chandina | 20 | 19:00 | 101 | MI_Cement | 16.2 | 02:00 | 167 | ShahCement | 35 | 23:00
36 | Chandpur | 84 | 20:00 | 102 | Madanganj | 44 | 19:30 | 168 | Shahjadpur | 59 | 15:00
37 | Chandraghona | 36 | 19:30 | 103 | Madaripur | 108 | 22:00 | 169 | Shahjibazar | 93 | 00:00
38 | Chapai | 63 | 12:00 | 104 | Madartek | 67 | 21:00 | 170 | Shahmirpur | 58 | 00:00
39 | Charsaidpur | 43 | 04:00 | 105 | Madunaghat | 55 | 18:30 | 171 | Shariatpur | 87 | 19:00
40 | Chauddagram | 81 | 18:30 | 106 | Magura | 70 | 19:00 | 172 | Sherpur | 118 | 18:00
41 | Chhatak | 31 | 19:00 | 107 | Mahasthangarh | 63 | 19:00 | 173 | Shikalbaha | 28 | 00:00
42 | Chowmuhani | 149 | 19:30 | 108 | Maijdee | 50 | 20:00 | 174 | Shitalakhya | 77.8 | 15:00
43 | Chuadanga | 119 | 18:30 | 109 | Manikganj | 114 | 20:00 | 175 | Sholosohor | 45 | 18:30
44 | Coxsbazar | 145 | 19:00 | 110 | Maniknagar | 71 | 13:00 | 176 | Shyampur | 124 | 01:00
45 | Cumilla(N) | 122 | 18:30 | 111 | Matarbari | 56 | 20:00 | 177 | Siddhirganj | 116 | 13:00
46 | Cumilla(S) | 185 | 18:30 | 112 | Matuail | 58 | 23:00 | 178 | Sirajganj | 98 | 19:00
47 | Daganbhuiyan | 35 | 22:00 | 113 | Metrorail_Motijheel | 21 | 14:00 | 179 | Sonargaon | 146 | 18:30
48 | Daudkandi | 154 | 18:30 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreemongol | 53 | 14:00
49 | DhakaUniversity | 68 | 13:00 | 115 | Millgate | 91 | 12:00 | 181 | Sreepur | 102 | 20:00
50 | Dhamrai | 138 | 09:00 | 116 | Mirpur | 134.5 | 15:00 | 182 | Srinagar | 48.8 | 21:00
51 | Dhanmondi | 114 | 13:00 | 117 | Mirsorai | 34 | 02:00 | 183 | Sunamganj | 48 | 18:30
52 | Dohazari | 109 | 19:00 | 118 | Mirzapur | 54 | 13:00 | 184 | Sylhet | 52 | 18:30
53 | Faridpur | 156 | 21:00 | 119 | Mithapukur | 48 | 18:30 | 185 | Sylhet-132 | 91 | 20:00
54 | Fatullah | 93 | 16:00 | 120 | Modern | N/A | N/A | 186 | TK | 25.5 | 23:00
55 | Fenchuganj | 34 | 19:00 | 121 | Mogbazar | 65.3 | 10:00 | 187 | Tangail | 172 | 14:00
56 | Feni | 102 | 18:30 | 122 | Mongla | 48 | 18:30 | 188 | Taraganj | 18 | 18:30
57 | GPH | 2 | 00:00 | 123 | Motijheel | 44 | 13:00 | 189 | Tasnim | 32 | 16:00
58 | Ghatail | 92 | 19:00 | 124 | Muktagacha | 40 | 18:30 | 190 | Thakurgaon | 80 | 19:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 121 | 18:30 | 191 | Tongi | 128 | 15:00
60 | Ghorashal-230 | 102 | 18:00 | 126 | Muradnagar | 50 | 19:00 | 192 | Ullahpara | 38 | 12:00
61 | Goalpara | 39 | 18:30 | 127 | Mymensingh | 191 | 18:30 | 193 | Ullon | 57 | 14:00
62 | Gollamari | 96 | 18:30 | 128 | Nabinagar | 16 | 20:00 | 194 | Uttara | 83 | 13:00
63 | Gopalganj | 105 | 19:00 | 129 | Naogaon | 108 | 19:00 | 195 | UttaraNew | 28 | 13:00
64 | Gulshan | 122 | 13:00 | 130 | Narail | 63 | 19:00 | 196 | Zigatola | 85 | 14:00
65 | Halishahar | 100 | 16:00 | 131 | Narinda | 61 | 13:00
66 | HaripurSBU | 113 | 09:00 | 132 | Narshingdi | 140 | 18:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 30-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 11766.82 | 0 |  | 11766.82
1:00 | 11422.5 | 0 |  | 11422.5
2:00 | 10996.17 | 0 |  | 10996.17
3:00 | 10710.14 | 0 |  | 10710.14
4:00 | 10531.06 | 0 |  | 10531.06
5:00 | 10303.89 | 0 |  | 10303.89
6:00 | 10351.65 | 0 |  | 10351.65
7:00 | 10995.81 | 0 |  | 10995.81
8:00 | 11410.38 | 0 |  | 11410.38
9:00 | 11714.23 | 0 |  | 11714.23
10:00 | 11991.27 | 58 |  | 12052.27
11:00 | 12340.43 | 223 |  | 12573.43
12:00 | 12435.5 | 255 |  | 12701.5
13:00 | 13039.31 | 368 |  | 13424.31
14:00 | 12936.86 | 323 |  | 13274.4
15:00 | 12897.99 | 350 |  | 13263.99
16:00 | 12663.65 | 326 |  | 13004.65
17:00 | 12626.99 | 159 |  | 12792.99
18:00 | 12560.79 | 134 |  | 12700.79
19:00 | 12852 | 108 |  | 12965
19:30 | 13035 | 100 |  | 13139
20:00 | 13023.2 | 202 |  | 13234.2
21:00 | 13031.2 | 324 |  | 13370.2
22:00 | 12736.2 | 300 |  | 13050.2
23:00 | 12760 | 201 |  | 12970
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 30-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5935 | 5831.82 | 11766.82 | DAILY GENERATION CURVE
00:30 | 5892.5 | 5702.16 | 11594.66
01:00 | 5850 | 5572.5 | 11422.5 | 30-03-2026
01:30 | 5818.5 | 5390.835 | 11209.335
02:00 | 5787 | 5209.17 | 10996.17
02:30 | 5769.5 | 5083.655 | 10853.155
03:00 | 5752 | 4958.14 | 10710.14
03:30 | 5716 | 4904.6 | 10620.6
04:00 | 5680 | 4851.06 | 10531.06
04:30 | 5585.5 | 4831.975 | 10417.475
05:00 | 5491 | 4812.89 | 10303.89
05:30 | 5499.505 | 4828.265 | 10327.77
06:00 | 5508.01 | 4843.64 | 10351.65
06:30 | 5673.955 | 4999.775 | 10673.73
07:00 | 5839.9 | 5155.91 | 10995.81
07:30 | 5874.395 | 5328.7 | 11203.095
08:00 | 5908.89 | 5501.49 | 11410.38
08:30 | 5875.495 | 5686.81 | 11562.305
09:00 | 5842.1 | 5872.13 | 11714.23
09:30 | 5963.75 | 5889 | 11852.75
10:00 | 6085.4 | 5905.87 | 11991.27
10:30 | 6135.225 | 6030.625 | 12165.85
11:00 | 6185.05 | 6155.38 | 12340.43
11:30 | 6274.145 | 6113.82 | 12387.965
12:00 | 6363.24 | 6072.26 | 12435.5
12:30 | 6570.82 | 6166.585 | 12737.405
13:00 | 6778.4 | 6260.91 | 13039.31
13:30 | 6791.04 | 6197.045 | 12988.085
14:00 | 6803.68 | 6133.18 | 12936.86
14:30 | 6763.14 | 6154.285 | 12917.425
15:00 | 6722.6 | 6175.39 | 12897.99
15:30 | 6694.225 | 6086.595 | 12780.82
16:00 | 6665.85 | 5997.8 | 12663.65
16:30 | 6702.63 | 5942.69 | 12645.32
17:00 | 6739.41 | 5887.58 | 12626.99
17:30 | 6787.705 | 5806.185 | 12593.89
18:00 | 6836 | 5724.79 | 12560.79
18:30 | 6928 | 5778.395 | 12706.395
19:00 | 7020 | 5832 | 12852
19:30 | 7014 | 6021 | 13035
20:00 | 6958 | 6065.2 | 13023.2
20:30 | 6944 | 6083.2 | 13027.2 |  | Executive Engineer
21:00 | 6930 | 6101.2 | 13031.2 |  | Network Operation Division
21:30 | 6858.5 | 6025.2 | 12883.7
22:00 | 6787 | 5949.2 | 12736.2
22:30 | 6809.5 | 5938.6 | 12748.1
23:00 | 6832 | 5928 | 12760

## En-Curve
QF-LDC-12
Date | 30-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3396 | 1422 | 902 | 0 | 158 | 1022.82 | 80 | 4627 | 0 | 51 | 107 | 0 | 0 | 1 | 0 | DAILY ENERGY CURVE
00:30 | 3395.5 | 1415.5 | 901 | 0 | 153 | 1020.16 | 80 | 4476 | 0 | 51 | 102 | 0 | 0 | 0.5 | 0 | 30-03-2026
01:00 | 3395 | 1409 | 900 | 0 | 148 | 1017.5 | 80 | 4325 | 0 | 51 | 97 | 0 | 0 | 0 | 0
01:30 | 3355.5 | 1408.5 | 900 | 0 | 146 | 1004.835 | 80 | 4189.5 | 0 | 51 | 74 | 0 | 0 | 0 | 0 | Energy Generated | 291.0832 |  | MKWHr
02:00 | 3316 | 1408 | 900 | 0 | 144 | 992.17 | 80 | 4054 | 0 | 51 | 51 | 0 | 0 | 0 | 0 | Energy not Served | 3.331 |  | MKWHr
02:30 | 3329.5 | 1414 | 900 | 0 | 140 | 877.155 | 80 | 4036 | 0 | 51 | 25.5 | 0 | 0 | 0 | 0 | Total Energy Requirement | 294.4142 |  | MKWHr
03:00 | 3343 | 1420 | 900 | 0 | 136 | 762.14 | 80 | 4018 | 0 | 51 | 0 | 0 | 0 | 0 | 0
03:30 | 3311 | 1418 | 900 | 0 | 134 | 761.6 | 80 | 3973 | 0 | 43 | 0 | 0 | 0 | 0 | 0
04:00 | 3279 | 1416 | 900 | 0 | 132 | 761.06 | 80 | 3928 | 0 | 35 | 0 | 0 | 0 | 0 | 0
04:30 | 3299.5 | 1412.5 | 900 | 0 | 132 | 723.475 | 80 | 3844 | 0 | 26 | 0 | 0 | 0 | 0 | 0
05:00 | 3320 | 1409 | 900 | 0 | 132 | 685.89 | 80 | 3760 | 0 | 17 | 0 | 0 | 0 | 0 | 0
05:30 | 3336.5 | 1421 | 900 | 0 | 131 | 688.765 | 80 | 3758 | 0.005 | 8.5 | 2 | 0 | 0 | 2 | 0
06:00 | 3353 | 1433 | 900 | 0 | 130 | 691.64 | 80 | 3756 | 0.01 | 0 | 4 | 0 | 0 | 4 | 0
06:30 | 3419.5 | 1428.5 | 900 | 0 | 130 | 718.775 | 80 | 3889 | 36.955 | 5 | 64 | 0 | 0 | 2 | 0
07:00 | 3486 | 1424 | 900 | 0 | 130 | 745.91 | 80 | 4022 | 73.9 | 10 | 124 | 0 | 0 | 0 | 0
07:30 | 3403 | 1414 | 901.5 | 0 | 134 | 755.745 | 80 | 4192 | 132.85 | 30 | 159.5 | 0 | 0 | 0.5 | 0
08:00 | 3320 | 1404 | 903 | 0 | 138 | 765.58 | 80 | 4362 | 191.8 | 50 | 195 | 0 | 0 | 1 | 0
08:30 | 3116 | 1458 | 904 | 0 | 141 | 765.29 | 80 | 4555.5 | 286.515 | 52 | 203.5 | 0 | 0 | 0.5 | 0
09:00 | 2912 | 1512 | 905 | 0 | 144 | 765 | 80 | 4749 | 381.23 | 54 | 212 | 0 | 0 | 0 | 0
09:30 | 2909 | 1589.5 | 907 | 0 | 147 | 766 | 80 | 4747 | 429.75 | 64.5 | 213 | 0 | 0 | 0 | 29
10:00 | 2906 | 1667 | 909 | 0 | 150 | 767 | 80 | 4745 | 478.27 | 75 | 214 | 0 | 0 | 0 | 58
10:30 | 2884 | 1723.5 | 909 | 0 | 163 | 766.5 | 80 | 4795.5 | 555.35 | 75 | 214 | 0 | 0 | 0 | 140.5
11:00 | 2862 | 1780 | 909 | 0 | 176 | 766 | 80 | 4846 | 632.43 | 75 | 214 | 0 | 0 | 0 | 223
11:30 | 2857.5 | 1796 | 908.5 | 0 | 180 | 768 | 80 | 4881.5 | 553.465 | 83.5 | 277 | 0 | 0 | 2.5 | 239
12:00 | 2853 | 1812 | 908 | 0 | 184 | 770 | 80 | 4917 | 474.5 | 92 | 340 | 0 | 0 | 5 | 255
12:30 | 2856 | 1801 | 912 | 0 | 182 | 762.5 | 80 | 4871.5 | 543.405 | 92 | 632.5 | 0 | 0 | 4.5 | 311.5
13:00 | 2859 | 1790 | 916 | 0 | 180 | 755 | 80 | 4826 | 612.31 | 92 | 925 | 0 | 0 | 4 | 368
13:30 | 2852.5 | 1706 | 916 | 0 | 181 | 755 | 80 | 4855 | 545.585 | 84 | 1008.5 | 0 | 0 | 4.5 | 345.5
14:00 | 2846 | 1622 | 916 | 0 | 182 | 755 | 80 | 4884 | 478.86 | 76 | 1092 | 0 | 0 | 5 | 323
14:30 | 2876.5 | 1594 | 916 | 0 | 178 | 751.5 | 80 | 4887.5 | 447.775 | 75.5 | 1104.65 | 0 | 0 | 6 | 336.5
15:00 | 2907 | 1566 | 916 | 0 | 174 | 748 | 80 | 4891 | 416.69 | 75 | 1117.3 | 0 | 0 | 7 | 350
15:30 | 2897 | 1561 | 916 | 0 | 176 | 748 | 80 | 4896.6 | 316.57 | 88.5 | 1092.15 | 0 | 0 | 9 | 338
16:00 | 2887 | 1556 | 916 | 0 | 178 | 748 | 80 | 4902.2 | 216.45 | 102 | 1067 | 0 | 0 | 11 | 326
16:30 | 2908.5 | 1562.5 | 915.5 | 0 | 173 | 752 | 80 | 4888.6 | 160.22 | 117.5 | 1079 | 0 | 0 | 8.5 | 242.5
17:00 | 2930 | 1569 | 915 | 0 | 168 | 756 | 80 | 4875 | 103.99 | 133 | 1091 | 0 | 0 | 6 | 159
17:30 | 2916 | 1521 | 901.5 | 0 | 169 | 750 | 80 | 4838 | 53.39 | 178 | 1181.5 | 0 | 0 | 5.5 | 146.5
18:00 | 2902 | 1473 | 888 | 0 | 170 | 744 | 80 | 4801 | 2.79 | 223 | 1272 | 0 | 0 | 5 | 134
18:30 | 2916.5 | 1437 | 888 | 0 | 175 | 747 | 80 | 4787.5 | 1.395 | 252.5 | 1417 | 0 | 0 | 4.5 | 121
19:00 | 2931 | 1401 | 888 | 0 | 180 | 750 | 80 | 4774 | 0 | 282 | 1562 | 0 | 0 | 4 | 108
19:30 | 2979 | 1445 | 888 | 0 | 180 | 769 | 80 | 4886 | 0 | 337 | 1465 | 0 | 0 | 6 | 100
20:00 | 3051 | 1509 | 862 | 0 | 136 | 749 | 80 | 4921.2 | 0 | 367 | 1343 | 0 | 0 | 5 | 202
20:30 | 3059.5 | 1511 | 862 | 0 | 141 | 749.5 | 80 | 4927.2 | 0 | 364 | 1325 | 0 | 0 | 8 | 263
21:00 | 3068 | 1513 | 862 | 0 | 146 | 750 | 80 | 4933.2 | 0 | 361 | 1307 | 0 | 0 | 11 | 324
21:30 | 3069 | 1485 | 862 | 0 | 153 | 751 | 80 | 4931.2 | 0 | 271.5 | 1274 | 0 | 0 | 7 | 312
22:00 | 3070 | 1457 | 862 | 0 | 160 | 752 | 80 | 4929.2 | 0 | 182 | 1241 | 0 | 0 | 3 | 300
22:30 | 3104 | 1453.5 | 862 | 0 | 163 | 753.5 | 80 | 4918.1 | 0 | 177 | 1235.5 | 0 | 0 | 1.5 | 250.5
23:00 | 3138 | 1450 | 862 | 0 | 166 | 755 | 80 | 4907 | 0 | 172 | 1230 | 0 | 0 | 0 | 201
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 30-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 395 | 04:00 | 378 | 09:00 | Madunaghat | 401 | 19:00 | 389 | 10:00
Amtali | 414 | 04:00 | 408 | 00:00 | Meghnaghat | 400 | 04:00 | 384 | 12:00
Ashuganj | 402 | 19:30 | 376 | 12:00 | Payra | 415 | 03:00 | 410 | 09:00
Bhulta | 396 | 19:00 | 371 | 11:00 | Rahanpur | 411 | 05:00 | 398 | 12:00
Bibiana | 408 | 18:00 | 395 | 12:00 | Rampal | 405 | 05:00 | 391 | 12:00
BIPTC | 399 | 22:00 | 387 | 15:00
Bogura | 406 | 05:00 | 391 | 12:00
Gopalganj | 404 | 04:00 | 389 | 12:00
Kaliakoir | 393 | 18:30 | 369 | 12:00
Korerhat | 404 | 19:00 | 390 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 04:00 | 217 | 12:00 | Jhenaidah | 233 | 04:00 | 217 | 12:00
AKSML | 236 | 19:00 | 223 | 10:00 | Kachua | 229 | 18:00 | 219 | 00:00
Aminbazar | 232 | 04:00 | 219 | 09:00 | Kaliakoir | 238 | 18:30 | 221 | 12:00
Ashuganj | 230 | 19:30 | 217 | 12:00 | Keranigonj | 229 | 04:00 | 215 | 12:00
Ashuganj-400 | 230 | 19:30 | 217 | 12:00 | Khulna(S) | 233 | 04:00 | 220 | 12:00
Baghabari | 233 | 04:00 | 224 | 12:00 | Korerhat | 230 | 18:00 | 220 | 09:00
Barapukuria | 228 | 22:00 | 218 | 10:00 | Madunaghat | 239 | 18:30 | 224 | 09:00
Barapukuria-230 | 228 | 22:00 | 218 | 10:00 | Madunaghat-400 | 239 | 19:00 | 225 | 10:00
Barishal | 229 | 06:00 | 224 | 00:00 | Maniknagar | 226 | 19:00 | 211 | 12:00
Bheramara | 234 | 02:00 | 221 | 12:00 | Meghnaghat | 234 | 04:00 | 220 | 11:00
Bhulta | 228 | 19:00 | 213 | 11:00 | Meghnaghat-400 | 228 | 19:00 | 215 | 12:00
Bibiana | 235 | 18:00 | 227 | 12:00 | Mirsorai | 235 | 19:00 | 227 | 09:00
BIPTC | 237 | 03:00 | 221 | 12:00 | Purbasadipur | 229 | 22:00 | 216 | 10:00
Bogura | 234 | 04:00 | 224 | 12:00 | Rajshahi | 233 | 04:00 | 220 | 12:00
Bogura-400 | 233 | 04:00 | 225 | 11:00 | Rampal | 233 | 05:00 | 220 | 12:00
Borhanuddin | 232 | 04:00 | 229 | 00:00 | Rampur | N/A | N/A | N/A | N/A
BSRM | 232 | 19:00 | 221 | 09:00 | Rampura | 227 | 05:00 | 216 | 12:00
Chowmuhani | 226 | 06:00 | 220 | 09:00 | Shikalbaha | 238 | 20:00 | 222 | 10:00
Cumilla(N) | 228 | 19:30 | 216 | 11:00 | Shyampur | 227 | 04:00 | 214 | 12:00
Faridpur | 227 | 06:00 | 218 | 11:00 | Siddhirganj | 228 | 18:30 | 213 | 10:00
Fenchuganj | 239 | 06:00 | 233 | 10:00 | Sirajgonj | 239 | 04:00 | 231 | 12:00
Feni | 230 | 19:30 | 219 | 11:00 | Sreepur | 226 | 04:00 | 216 | 11:00
Ghorashal | 232 | 05:00 | 220 | 09:00 | Tongi | 235 | 20:00 | 218 | 11:00
Ghorashal-230 | 230 | 19:00 | 213 | 12:00
Gopalganj | 226 | 00:00 | 218 | 11:00
GPH | 230 | 00:00 | 226 | 18:30
Haripur | 227 | 05:00 | 213 | 11:00
Hasnabad | 228 | 05:00 | 214 | 12:00
Hathazari | 236 | 22:00 | 227 | 12:00
Ishurdi | 237 | 03:00 | 224 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 132 | 02:00 | 122 | 11:00 | Madunaghat | 138 | 18:30 | 129 | 11:00
Agargaon | 137 | 04:00 | 126 | 12:00 | Magura | 134 | 04:00 | 120 | 13:00
Agrabad | 135 | 18:00 | 126 | 09:00 | Mahasthangarh | 133 | 04:00 | 127 | 12:00
AKS | 134 | 21:00 | 125 | 10:00 | Maijdee | 127 | 19:00 | 122 | 00:00
Aminbazar | 133 | 04:00 | 123 | 09:00 | Manikganj | 132 | 05:00 | 121 | 12:00
Amnura | 136 | 02:00 | 127 | 12:00 | Maniknagar | 133 | 03:00 | 122 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 119 | 13:00 | 108 | 00:00
Ashuganj-230 | 137 | 04:00 | 133 | 09:00 | Matuail | 132 | 19:00 | 122 | 10:00
Bagerhat | 131 | 04:00 | 117 | 12:00 | Metrorail_Motijheel | 133 | 03:00 | 122 | 12:00
Bajitpur | 134 | 22:00 | 125 | 11:00 | Metrorail_Uttara | 133 | 18:30 | 121 | 11:00
Bakerganj | 133 | 05:00 | 129 | 12:00 | Millgate | 137 | 18:30 | 124 | 12:00
Bakulia | 136 | 18:00 | 127 | 10:00 | Mirpur | 133 | 18:30 | 122 | 12:00
Banani | 137 | 18:30 | 123 | 12:00 | Mirzapur | 133 | 18:00 | 123 | 12:00
Bangabhaban | 133 | 04:00 | 123 | 11:00 | Mithapukur | 132 | 06:00 | 124 | 10:00
Barapukuria | 130 | 22:00 | 124 | 07:00 | MI_Cement | 131.1 | 04:00 | 119 | 12:00
Barguna | 133 | 06:00 | 125 | 12:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 133 | 05:00 | 129 | 00:00 | Mogbazar | 133 | 03:00 | 123 | 12:00
Barishal-230 | 133 | 05:00 | 129 | 00:00 | Mongla | 129 | 05:00 | 116 | 12:00
Baroaulia | 135 | 18:00 | 128 | 10:00 | Motijheel | 133 | 04:00 | 123 | 11:00
Baroirhat | 131 | 18:00 | 126 | 09:00 | Muktagacha | 133 | 22:00 | 124 | 05:00
Bashundhara | 137 | 18:30 | 120 | 12:00 | Munshiganj | 132 | 19:30 | 119 | 09:00
BashundharaCement | 132 | 19:00 | 122 | 09:00 | Muradnagar | 130 | 20:00 | 120 | 11:00
Beanibazar | 131 | 02:00 | 127 | 11:00 | Mymensingh | 133 | 18:30 | 121 | 09:00
Benapole | 129 | 04:00 | 115 | 12:00 | Nabinagar | 145 | 18:00 | 129 | 10:00
Bhaluka | 133 | 22:00 | 123 | 11:00 | Naogaon | 138 | 18:00 | 125 | 12:00
Bhandaria | 129 | 07:00 | 113 | 15:00 | Narail | 135 | 04:00 | 121 | 14:00
Bhangura | 134 | 04:00 | 127 | 12:00 | Narinda | 133 | 03:00 | 122 | 12:00
Bheramara | 136 | 02:00 | 131 | 12:00 | Narshingdi | 133 | 19:30 | 117 | 10:00
Bheramara(GK) | 136 | 03:00 | 131 | 12:00 | Natore | 134 | 04:00 | 126 | 12:00
Bhulta | 128 | 19:00 | 118 | 10:00 | Nawabganj | 134 | 04:00 | 125 | 12:00
Bog-Sherpur | 134 | 03:00 | 127 | 12:00 | Netrakona | 132 | 22:00 | 120 | 11:00
Bogura | 136 | 23:00 | 129 | 11:00 | New | 140 | 18:30 | 125 | 12:00
Bogura-230 | 136 | 04:00 | 129 | 12:00 | Niamatpur | 137 | 02:00 | 133 | 09:00
Brahmanbaria | 131 | 19:30 | 123 | 12:00 | Noapara | 132 | 05:00 | 120 | 16:00
Cantonment | 137 | 04:00 | 126 | 12:00 | Pabna | 135 | 03:00 | 129 | 12:00
Chandina | 132 | 19:30 | 124 | 11:00 | Palashbari | 130 | 04:00 | 122 | 11:00
Chandpur | 132 | 14:00 | 122 | 00:00 | Panchagarh | 137 | 22:00 | 127 | 02:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 138 | 21:00 | 129 | 09:00 | Patiya | 135 | 19:00 | 124 | 09:00
Chapai | 136 | 04:00 | 131 | 12:00 | Patuakhali | 133 | 18:00 | 129 | 00:00
Charsaidpur | 133 | 19:30 | 121 | 09:00 | Payra | 136 | 04:00 | 132 | 12:00
Chauddagram | 129 | 19:00 | 123 | 09:00 | PHP | 131 | 19:00 | 125 | 09:00
Chhatak | 131 | 04:00 | 125 | 13:00 | Postogola | 133 | 09:00 | 122 | 12:00
Chowmuhani | 128 | 15:00 | 122 | 10:00 | Pubail | 140 | 18:30 | 125 | 12:00
Chuadanga | 133 | 05:00 | 119 | 13:00 | Purbachal | 137 | 18:30 | 123 | 12:00
Coxsbazar | 117 | 12:00 | 108 | 00:00 | Purbasadipur | 132 | 22:00 | 124 | 10:00
Cumilla(N) | 133 | 19:30 | 124 | 11:00 | Rahanpur | 137 | 00:00 | 134 | 09:00
Cumilla(S) | 132 | 19:30 | 120 | 08:00 | Rahanpur-400 | 138 | 02:00 | 133 | 12:00
Daganbhuiyan | 129 | 19:00 | 123 | 09:00 | Rahim | 133 | 19:00 | 122 | 10:00
Daudkandi | 127 | 19:30 | 117 | 09:00 | Rajbari | 130 | 05:00 | 124 | 11:00
DhakaUniversity | 133 | 04:00 | 123 | 11:00 | Rajendrapur | 133 | 22:00 | 125 | 10:00
Dhamrai | 144 | 18:00 | 129 | 09:00 | Rajshahi | 132 | 02:00 | 125 | 12:00
Dhanmondi | 135 | 21:00 | 124 | 09:00 | Rajshahi-230 | 134 | 03:00 | 126 | 12:00
Dohazari | 131 | 21:00 | 121 | 00:00 | Ramganj | 128 | 14:00 | 119 | 00:00
Faridpur | 131 | 06:00 | 125 | 12:00 | Rampur | 135 | 18:00 | 127 | 00:00
Fatullah | 132 | 19:30 | 120 | 12:00 | Rampura | 133 | 05:00 | 122 | 12:00
Fenchuganj | 136 | 06:00 | 132 | 12:00 | Rangamati | 136 | 19:00 | 128 | 10:00
Feni | 129 | 19:30 | 123 | 00:00 | Rangpur | 132 | 22:00 | 123 | 11:00
Feni-230 | 129 | 19:30 | 122 | 11:00 | Ruppur | 137 | 01:00 | 131 | 12:00
Ghatail | 129 | 00:00 | 120 | 15:00 | Saidpur | 132 | 05:00 | 123 | 11:00
Ghorashal | 140 | 19:00 | 129 | 09:00 | Satkhira | 131 | 05:00 | 119 | 18:30
Goalpara | 134 | 05:00 | 126 | 12:00 | Satmasjid | 137 | 04:00 | 126 | 12:00
Gollamari | 134 | 05:00 | 125 | 12:00 | Savar | 134 | 18:30 | 120 | 10:00
Gopalganj | 133 | 05:00 | 125 | 12:00 | SevenRings | 140 | 18:30 | 128 | 12:00
Gopalganj-400 | 134 | 04:00 | 129 | 12:00 | ShahCement | 133 | 19:30 | 121 | 09:00
Gulshan | 132 | 04:00 | 122 | 12:00 | Shahjadpur | 137 | 05:00 | 132 | 12:00
Halishahar | 137 | 19:00 | 126 | 10:00 | Shahjibazar | 132 | 07:00 | 126 | 12:00
Haripur | 133 | 19:30 | 122 | 10:00 | Shahmirpur | 138 | 21:00 | 128 | 00:00
HaripurSBU | 133 | 20:00 | 122 | 10:00 | Shariatpur | 132 | 06:00 | 126 | 12:00
Hasnabad | 133 | 05:00 | 122 | 12:00 | Sherpur | 132 | 20:00 | 118 | 04:00
Hathazari | 137 | 18:00 | 129 | 10:00 | Shikalbaha | 126 | 18:00 | 117 | 00:00
Hatirjheel | 135 | 03:00 | 122 | 12:00 | Shikalbaha-230 | 138 | 18:00 | 129 | 00:00
Ishurdi | 138 | 02:00 | 132 | 12:00 | Shitalakhya | 131.3 | 05:00 | 119 | 12:00
Jaldhaka | 129 | 22:00 | 121 | 07:00 | Sholosohor | 137 | 19:00 | 129 | 00:00
Jamalpur | 135 | 22:00 | 119 | 05:00 | Shyampur | 130 | 02:00 | 122 | 12:00
Jashore | 130 | 05:00 | 118 | 13:00 | Shyampur-230 | 131 | 06:00 | 123 | 11:00
Jhenaidah | 135 | 03:00 | 124 | 12:00 | Siddhirganj | 132 | 19:00 | 122 | 09:00
Jhenaidah-230 | 135 | 04:00 | 123 | 12:00 | Sirajganj | 135 | 04:00 | 126 | 12:00
Joydebpur | 140 | 18:30 | 123 | 11:00 | Sonargaon | 132 | 19:00 | 120 | 09:00
Joypurhat | 131 | 04:00 | 123 | 12:00 | Sreemongol | 132 | 15:00 | 128 | 00:00
Juldah | 137 | 18:00 | 128 | 00:00 | Sreepur | 135 | 04:00 | 128 | 09:00
Kabirpur | 140 | 18:00 | 123 | 11:00 | Srinagar | 135 | 05:00 | 125 | 12:00
Kachua | 130 | 18:00 | 124 | 00:00 | SSM | 138 | 18:30 | 130 | 10:00
Kaliakoir | 145 | 18:00 | 129 | 12:00 | Sunamganj | 130 | 05:00 | 124 | 14:00
Kaliganj | 133 | 02:00 | 122 | 13:00 | Sylhet | 132 | 04:00 | 128 | 13:00
Kallyanpur | 133 | 05:00 | 123 | 12:00 | Sylhet-132 | 132 | 05:00 | 129 | 13:00
Kalurghat | 138 | 21:00 | 129 | 09:00 | Tangail | 130 | 18:00 | 120 | 12:00
Kamrangirchar | 135 | 04:00 | 120 | 12:00 | Taraganj | 130 | 15:00 | 122 | 09:00
Kaptai | N/A | N/A | N/A | N/A | Tasnim | 132 | 19:00 | 120 | 09:00
Kasba | 129 | 19:30 | 119 | 11:00 | Thakurgaon | 135 | 22:00 | 125 | 07:00
Kazla | 133 | 05:00 | 122 | 12:00 | TK | 137 | 18:00 | 129 | 09:00
Keranigonj | 135 | 04:00 | 126 | 12:00 | Tongi | 138 | 18:30 | 127 | 11:00
Khagrachori | 136 | 19:30 | 128 | 10:00 | Ullahpara | 134 | 01:00 | 128 | 12:00
Khulna | 133 | 05:00 | 123 | 13:00 | Ullon | 133 | 03:00 | 122 | 11:00
Khulna(S) | 134 | 04:00 | 124 | 12:00 | Uttara | 133 | 05:00 | 121 | 12:00
Khulshi | 135 | 19:00 | 125 | 10:00 | UttaraNew | 133 | 04:00 | 121 | 11:00
Kishoreganj | 133 | 00:00 | 125 | 11:00 | Zigatola | 136 | 05:00 | 126 | 12:00
Kodda | 139 | 18:30 | 121 | 09:00
Korerhat | 134 | 19:00 | 127 | 09:00
KSRM | 136 | 18:30 | 127 | 09:00
Kulaura | 135 | 05:00 | 131 | 13:00
Kurigram | 130 | 22:00 | 121 | 07:00
Kushtia | 135 | 02:00 | 127 | 14:00
Laksam | 130 | 19:30 | 124 | 00:00
Lakshmipur | 127 | 19:00 | 119 | 12:00
Lalbag | 133 | 04:00 | 126 | 12:00
Lalmonirhat | 158 | 15:00 | 120 | 07:00
Madanganj | 132 | 19:00 | 122 | 09:00
Madaripur | 132 | 11:00 | 129 | 00:00
Madartek | 132 | 03:00 | 122 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division