## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 01-04-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 31-03-2026 | during | 01-04-2026 | during | 01-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 115 | 115 | 180 | 180 | 116 | 116 | GBC-3 Under maintenance.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 409 | 412 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 450 | 450 | 226 | 226 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 50 | 53.97 | 53.97 | 49 | 49 | FGMO
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 108 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 30 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 0 | 20 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 7 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 51 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 195 | 245 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 21 | 114 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 95 | 54 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 16 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 420 | 500 | 584 | 584 | 526 | 526 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage (BPDB)
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 70 | 160 | 160 | 160 | 160 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1687 | 2165 | 5865.22 | 5835.22 | 2815 | 2785
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 12 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 24 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 226 | 220 | 220 | 220 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 16 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 32 | 56 | 64 | 56 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 | 51 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 50 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 9 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.5 | 0 | 3.87 | 0 | 3.87 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 15 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 50 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 13 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1224 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 14 | 0 | 3 | 1 | 3 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 950 | 950 | 950 | 950 | 950 | 950 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2486.5 | 2774 | 3842.73 | 3833.86 | 3842.73 | 3833.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 197 | 195 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 9 | 102 | 240 | 240 | 240 | 240 | STG Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 345 | 345 | 342.01 | 342.01 | 342.01 | 342.01
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 393 | 393 | FGMO
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 35 | 43 | 41.65 | 41.65 | 41.65 | 41.65 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 10 | 55 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 16 | 53 | 195 | 195 | 9 | 9 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 88 | 143 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 22 | 24 | 24 | 24 | 24 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 100 | 163 | 163 | 101 | 101 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 38 | 100 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 150 | 144 | 84 | 82 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 20 | 93 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 71 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2872.921 | 1244 | 1430 | 2643.36 | 2576.36 | 2400.36 | 2335.36
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 31-03-2026 | during | 01-04-2026 | during | 01-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 26 | 20 | 157.5 | 157.5 | 60 | 60 | Gas shortage
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.9 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 24 | 76 | 60 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 78 | 70 | 80 | 70 | 80 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 16.79 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 22 | 22 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 135.69 | 186 | 407.9 | 394 | 310.4 | 296.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 41 | 41 | 41 | 41 | 41 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 159 | 156 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 110 | 110 | 110 | 110 | 105 | 105 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 5 | 83 | 83 | 6 | 6 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 98 | 97 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 20 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 358 | 380 | 400 | 400 | 372 | 372 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1126 | 1144 | 1313 | 1313 | 1130 | 1130
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 868 | 868 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 31 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 28 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 241 | 194 | 410 | 410 | 300 | 300 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 16 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 29 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1229 | 1234.2 | 1234.2 | 1234.2 | 1024.2 | 1024.2 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2367 | 2371.2 | 3587.2 | 3512.2 | 2911.2 | 2836.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1240 | 1205 | 892 | 892 | 882 | 882 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 150 | 150 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 301 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.22 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1897.22 | 1926 | 1809 | 1809 | 1779 | 1779
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 49.61 | 0 | 52 | 0 | 52 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 41 | 40 | 40 | 40 | 40 | 1 unit is under maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 185 | 180 | 220 | 220 | 198 | 198 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 398 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 15 | 22 | 22 | 22 | 22 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 50 | 80 | 80 | 80 | 80 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.66 | 0 | 6 | 0 | 6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 763.69 | 755.65 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 36.88 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 17 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1470.84 | 1580.65 | 2518.99 | 2299.99 | 2021.61 | 1802.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 55 | 53 | 55 | 55 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 32 | 95 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.9 | 0 | 6.2 | 0 | 6.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 14 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 13 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 35 | 0 | 112 | 0 | 112 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 155.9 | 263 | 451.2 | 303 | 431.2 | 283
System Total |  |  |  |  | 28823.2 | 29272.163 | 12570.15 | 13839.85 | 22438.6 | 21876.63 | 17431.75 | 16871.78
Forecast Scenario (01-04-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12610 |  | 0 |  | 12610
|  |  |  | 1:00 | 12100 |  | 0 |  | 12100
|  |  |  | 2:00 | 11520 |  | 0 |  | 11520
|  |  |  | 3:00 | 11240 |  | 0 |  | 11240
|  |  |  | 4:00 | 10930 |  | 0 |  | 10930
|  |  |  | 5:00 | 10680 |  | 0 |  | 10680
|  |  |  | 6:00 | 10670 |  | 0 |  | 10670
|  |  |  | 7:00 | 11190 |  | 0 |  | 11190
|  |  |  | 8:00 | 11720 |  | 0 |  | 11720
|  |  |  | 9:00 | 12150 |  | 0 |  | 12150
|  |  |  | 10:00 | 12110 |  | 0 |  | 12110
|  |  |  | 11:00 | 12480 |  | 0 |  | 12480
|  |  |  | 12:00 | 13000 |  | 0 |  | 13000
|  |  |  | 13:00 | 13100 |  | 0 |  | 13100
|  |  |  | 14:00 | 12780 |  | 0 |  | 12780
|  |  |  | 15:00 | 12800 |  | 0 |  | 12800
|  |  |  | 16:00 | 12650 |  | 0 |  | 12650
|  |  |  | 17:00 | 12320 |  | 0 |  | 12320
|  |  |  | 18:00 | 12750 |  | 0 |  | 12750
|  |  |  | 18:30 | 13300 |  | 0 |  | 13300
|  |  |  | 19:00 | 14090 |  | 0 |  | 14090
|  |  |  | 19:30 | 13980 |  | 0 |  | 13980
|  |  |  | 20:00 | 13930 |  | 0 |  | 13930
|  |  |  | 21:00 | 13820 |  | 0 |  | 13820
|  |  |  | 22:00 | 13500 |  | 0 |  | 13500
|  |  |  | 23:00 | 13100 |  | 0 |  | 13100
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 13000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14090.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13970.24 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 297.10924 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:08 hrs on 01-04-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 31-03-2026 | [28 empty] | Date: | 31-03-2026 | [28 empty] | Date: | 31-03-2026 | [28 empty] | Date: | 31-03-2026 | [28 empty] | Date: | 31-03-2026 | [17 empty] | Date: | 31-03-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 24 | 115 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 70 | 0 | 95 | 30 | 17 | 17 | 0 | 225 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 24 | 22 | 0 | 400 | 26 | 30 | 0 | 0 | 0 | 23 | 7 | 0 | 0 | 36 | 0 | 80 | 47 | 14 | 950 | 0 | 0 | 39 | 0 | 63 | 223 | 0 | 0 | 0 | 1160 | 0 | 70 | 8 | 0 | 252 | 190 | 51 | 5 | 201 | 42 | 17 | 100 | 63 | 0 | 20 | 0 | 162 | 25 | 0 | 0 | 300 | 0 | 302 | 41 | 0 | 133 | 0 | 17 | 0 | 5 | 30 | 112 | 0 | 98 | 17 | 78 | 77 | 35 | 0 | 0 | 6 | 6674 | 863 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1190 | 16 | 0 | 0 | 756 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 344 | 0 | 0 | 0 | 55 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 130 | 220 | 0 | 0 | 1225 | 54 | 5840 | 12514 | 84.85
01:00 | 0 | 0 | 0 | 116 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 10 | 0 | 50 | 0 | 45 | 30 | 17 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 36 | 0 | 80 | 17 | 15 | 950 | 0 | 0 | 39 | 0 | 17 | 224 | 0 | 0 | 0 | 1134 | 0 | 70 | 8 | 0 | 251 | 280 | 51 | 0 | 183 | 10 | 17 | 99 | 62 | 0 | 20 | 0 | 162 | 0 | 0 | 0 | 305 | 0 | 306 | 41 | 0 | 133 | 0 | 17 | 0 | 5 | 30 | 110 | 0 | 98 | 0 | 68 | 57 | 35 | 0 | 0 | 0 | 6320.5 | 864 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1202 | 0 | 0 | 0 | 740 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 345 | 0 | 0 | 0 | 55 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 1220 | 0 | 5644 | 11964.5 | 84.83
02:00 | 0 | 0 | 0 | 116 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 14.3 | 0 | 16 | 0 | 0 | 15 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 17 | 950 | 0 | 0 | 39 | 0 | 0 | 224 | 0 | 0 | 0 | 1162 | 0 | 0 | 0 | 0 | 200 | 345 | 51 | 0 | 184 | 10 | 0 | 100 | 0 | 0 | 20 | 0 | 152 | 0 | 0 | 0 | 305 | 0 | 330 | 41 | 0 | 133 | 0 | 17 | 0 | 5 | 30 | 109 | 0 | 98 | 0 | 45 | 8 | 35 | 0 | 0 | 0 | 5932.8 | 859 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1196 | 0 | 0 | 0 | 745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 364 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 130 | 220 | 0 | 0 | 1200 | 0 | 5492 | 11424.8 | 84.81
03:00 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 15.8 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 17 | 950 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 0 | 200 | 345 | 51 | 0 | 175 | 10 | 0 | 100 | 0 | 0 | 20 | 0 | 152 | 0 | 0 | 0 | 305 | 0 | 312 | 41 | 0 | 139 | 0 | 17 | 0 | 5 | 30 | 110 | 0 | 98 | 0 | 24 | 8 | 48 | 0 | 0 | 0 | 5848.3 | 858 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085 | 0 | 0 | 0 | 748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 355 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 130 | 220 | 0 | 0 | 1120 | 0 | 5297 | 11145.3 | 84.79
04:00 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 21 | 950 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1093 | 0 | 0 | 0 | 0 | 200 | 345 | 51 | 0 | 171 | 10 | 0 | 100 | 0 | 0 | 20 | 0 | 146 | 0 | 0 | 0 | 300 | 0 | 325 | 41 | 0 | 136 | 0 | 17 | 0 | 5 | 30 | 110 | 0 | 98 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 5764.5 | 859 | 271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 0 | 0 | 0 | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 357 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226 | 130 | 220 | 0 | 0 | 1106 | 0 | 5070 | 10834.5 | 84.87
05:00 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 415 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 22 | 950 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1008 | 0 | 0 | 0 | 0 | 200 | 345 | 51 | 0 | 173 | 10 | 0 | 99 | 0 | 0 | 20 | 0 | 146 | 0 | 0 | 0 | 310 | 0 | 342 | 41 | 0 | 138 | 0 | 17 | 0 | 5 | 30 | 110 | 0 | 98 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 5698 | 859 | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 846 | 0 | 0 | 0 | 747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 389 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 130 | 220 | 0 | 0 | 1000 | 0 | 4890 | 10588 | 84.75
06:00 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 0 | 415 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 18 | 950 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1133 | 0 | 0 | 0 | 0 | 200 | 345 | 51 | 0 | 173 | 10 | 0 | 99 | 0 | 0 | 20 | 0 | 144 | 0 | 0 | 0 | 300 | 0 | 379 | 41 | 0 | 154 | 0 | 17 | 0 | 5 | 30 | 112 | 0 | 98 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 5824 | 567 | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 414 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 130 | 220 | 0 | 0 | 1000 | 0 | 4746 | 10570 | 84.73
07:00 | 0 | 0 | 2 | 115 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 10 | 22 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 22 | 15 | 0 | 370 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0.32 | 80 | 0 | 25 | 950 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1175 | 3 | 0 | 0 | 0 | 220 | 345 | 51 | 0 | 157 | 10 | 0 | 100 | 0 | 0 | 20 | 0 | 136 | 0 | 0 | 0 | 300 | 0 | 379 | 41 | 0 | 159 | 0 | 17 | 0 | 5 | 30 | 111 | 0 | 98 | 0 | 15 | 24 | 45 | 0.2 | 1.94 | 0 | 5939.46 | 566 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 1008 | 0 | 0 | 0 | 754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.28 | 8 | 0 | 0 | 5.93 | 0 | 0 | 0 | 0 | 192 | 0 | 414 | 0 | 0.57 | 0 | 54 | 0 | 3 | 0 | 0 | 0 | 0 | 0.2 | 18 | 0.05 | 0 | 307 | 130 | 220 | 0 | 0 | 1050 | 0 | 5027.03 | 10966.49 | 84.71
08:00 | 0 | 16 | 16 | 115 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 36 | 35 | 0 | 0 | 80 | 55 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 24 | 15 | 0 | 330 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0.42 | 80 | 0 | 8 | 950 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1160 | 8 | 45 | 0 | 0 | 220 | 345 | 51 | 0 | 158 | 0 | 0 | 98 | 0 | 0 | 20 | 0 | 154 | 0 | 5 | 0 | 300 | 0 | 408 | 41 | 0 | 159 | 0 | 17 | 0 | 5 | 30 | 111 | 0 | 98 | 0 | 45 | 24 | 34 | 0.7 | 4.16 | 0 | 6134.28 | 556 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 1112 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.1 | 42 | 0 | 0 | 9.3 | 0 | 0 | 0 | 0 | 192 | 0 | 414 | 0 | 0.77 | 0 | 55 | 0 | 4 | 0 | 0 | 0 | 0 | 1.5 | 31 | 0.09 | 0 | 307 | 130 | 220 | 0 | 0 | 1150 | 0 | 5267.76 | 11402.04 | 84.69
09:00 | 0 | 34 | 16 | 115 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 36 | 35 | 12 | 0 | 80 | 55 | 0 | 0 | 4 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 23 | 15 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.25 | 80 | 0 | 2 | 950 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1160 | 13 | 50 | 0 | 0 | 220 | 345 | 51 | 0 | 158 | 0 | 0 | 98 | 0 | 0 | 20 | 52 | 158 | 0 | 28 | 0 | 295 | 0 | 322 | 41 | 0 | 148 | 6 | 17 | 0 | 5 | 30 | 111 | 0 | 98 | 0 | 45 | 24 | 34 | 0.6 | 10.14 | 0 | 6137.99 | 863 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 1212 | 0 | 0 | 0 | 765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.23 | 29 | 0 | 0 | 29.45 | 0 | 0 | 0 | 0 | 192 | 0 | 346 | 0 | 2.94 | 0 | 55 | 0 | 7 | 0 | 0 | 0 | 0 | 3.6 | 52 | 0.51 | 0 | 307 | 130 | 180 | 0 | 0 | 1200 | 0 | 5688.73 | 11826.72 | 84.67
10:00 | 0 | 34 | 24 | 115 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 35 | 17 | 0 | 80 | 55 | 0 | 0 | 14 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 15 | 0 | 310 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1.18 | 80 | 0 | 3 | 950 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1160 | 15 | 50 | 0 | 0 | 133 | 345 | 51 | 0 | 160 | 0 | 0 | 97 | 0 | 0 | 20 | 114 | 152 | 0 | 52 | 0 | 305 | 0 | 322 | 41 | 0 | 135 | 3 | 17 | 0 | 5 | 30 | 111 | 0 | 98 | 0 | 45 | 24 | 33 | 1.2 | 15.55 | 0 | 6109.93 | 863 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1224 | 0 | 0 | 0 | 765.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.05 | 77 | 0 | 0 | 41.88 | 0 | 0 | 0 | 0 | 191 | 0 | 300 | 0 | 2.57 | 0 | 55 | 0 | 13 | 0 | 0 | 0 | 0 | 2.7 | 85 | 0.53 | 0 | 307 | 120 | 180 | 0 | 0 | 1190 | 0 | 5731.99 | 11841.92 | 84.66
11:00 | 0 | 34 | 24 | 115 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 0 | 17 | 0 | 80 | 55 | 0 | 0 | 15 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 15 | 0 | 480 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 2 | 0 | 1.97 | 80 | 0 | 3 | 950 | 0 | 0 | 10 | 0 | 0 | 218 | 0 | 0 | 0 | 1183 | 18 | 50 | 0 | 0 | 10 | 342 | 51 | 0 | 213 | 0 | 0 | 97 | 0 | 0 | 20 | 114 | 150 | 0 | 29 | 0 | 290 | 0 | 392 | 42 | 0 | 152 | 5 | 17 | 0 | 5 | 28 | 111 | 0 | 98 | 0 | 45 | 24 | 30 | 1.8 | 10.11 | 0 | 6288.88 | 868 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 1234.2 | 0 | 0 | 0 | 772.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.02 | 88 | 0 | 0 | 18.51 | 0 | 0 | 0 | 0 | 189 | 0 | 414 | 0 | 2.08 | 0 | 55 | 0 | 14 | 0 | 0 | 0 | 0 | 6.7 | 49 | 0.31 | 0 | 307 | 127 | 220 | 0 | 0 | 1190 | 0 | 5894.9 | 12183.78 | 84.65
12:00 | 0 | 34 | 24 | 115 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 0 | 21 | 0 | 195 | 55 | 30 | 95 | 16 | 225 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 16 | 0 | 0 | 15 | 0 | 420 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 12 | 12 | 1.5 | 80 | 0 | 2 | 950 | 0 | 0 | 24 | 0 | 0 | 219 | 0 | 0 | 0 | 1160 | 12 | 88 | 16 | 0 | 9 | 345 | 51 | 0 | 197 | 35 | 20 | 96 | 38 | 0 | 14 | 114 | 150 | 0 | 71 | 0 | 295 | 0 | 358 | 42 | 0 | 159 | 12 | 17 | 0 | 5 | 30 | 110 | 0 | 98 | 0 | 67 | 24 | 26 | 1.9 | 16.79 | 0 | 6679.19 | 868 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 1229 | 0 | 0 | 0 | 763.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.61 | 17 | 0 | 0 | 36.88 | 0 | 0 | 0 | 0 | 185 | 0 | 414 | 0 | 4.66 | 0 | 55 | 14 | 13 | 32 | 0 | 0 | 0 | 6.9 | 35 | 0.22 | 0 | 307 | 130 | 220 | 0 | 0 | 1240 | 0 | 5890.96 | 12570.15 | 84.64
13:00 | 0 | 34 | 24 | 115 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 69 | 0 | 245 | 55 | 35 | 100 | 0 | 225 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 14 | 0 | 0 | 15 | 0 | 350 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 12 | 12 | 1.41 | 80 | 7 | 2 | 950 | 0 | 0 | 25 | 0 | 9 | 220 | 0 | 0 | 0 | 1120 | 18 | 100 | 16 | 0 | 6 | 345 | 51 | 0 | 184 | 37 | 34 | 96 | 51 | 0 | 14 | 114 | 132 | 0 | 69 | 0 | 295 | 0 | 358 | 42 | 0 | 136 | 2 | 17 | 0 | 5 | 30 | 110 | 0 | 98 | 0 | 67 | 24 | 15 | 1.2 | 37.45 | 0 | 6685.06 | 868 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 1211 | 0 | 0 | 0 | 731.29 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 13.02 | 13 | 0 | 0 | 14.3 | 0 | 0 | 0 | 0 | 197 | 0 | 414 | 0 | 1.51 | 0 | 55 | 50 | 13 | 46 | 0 | 0 | 0 | 6.8 | 142 | 0.19 | 0 | 307 | 125 | 180 | 0 | 0 | 1244 | 0 | 5921.11 | 12606.17 | 84.63
14:00 | 0 | 34 | 24 | 115 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 70 | 0 | 145 | 55 | 35 | 88 | 0 | 180 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 12 | 12 | 3.21 | 80 | 0 | 6 | 950 | 0 | 0 | 25 | 0 | 0 | 218 | 0 | 0 | 0 | 1160 | 16 | 100 | 53 | 0 | 6 | 280 | 51 | 8 | 198 | 40 | 16 | 96 | 0 | 9 | 14 | 114 | 140 | 0 | 54 | 0 | 300 | 0 | 379 | 42 | 0 | 132 | 2 | 17 | 0 | 5 | 30 | 110 | 0 | 98 | 0 | 68 | 24 | 15 | 1.4 | 31.98 | 0 | 6424.59 | 868 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 1201 | 0 | 0 | 0 | 767.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.42 | 55 | 0 | 0 | 31.77 | 0 | 0 | 0 | 0 | 191 | 0 | 369 | 0 | 2.92 | 0 | 55 | 35 | 17 | 34 | 0 | 0 | 0 | 5.3 | 143 | 0.35 | 0 | 284 | 125 | 180 | 0 | 0 | 1244 | 0 | 5863.8 | 12288.39 | 84.62
15:00 | 0 | 34 | 24 | 115 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 0 | 54 | 0 | 145 | 55 | 35 | 84 | 0 | 180 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 22 | 0 | 14 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 12 | 12 | 2.48 | 80 | 0 | 2 | 950 | 0 | 0 | 25 | 0 | 0 | 218 | 0 | 0 | 0 | 1160 | 12 | 100 | 53 | 0 | 6 | 280 | 51 | 10 | 196 | 43 | 15 | 95 | 0 | 9 | 5 | 114 | 128 | 0 | 40 | 0 | 305 | 0 | 374 | 42 | 0 | 153 | 4 | 17 | 0 | 5 | 30 | 110 | 0 | 97 | 0 | 68 | 24 | 15 | 0.8 | 14.77 | 0 | 6465.05 | 868 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.95 | 1237 | 0 | 0 | 0 | 759.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.29 | 77 | 0 | 0 | 40.31 | 0 | 0 | 0 | 0 | 189 | 0 | 401 | 0 | 2.09 | 0 | 54 | 35 | 10 | 34 | 0 | 0 | 0 | 4.1 | 82 | 0.43 | 0 | 276 | 128 | 220 | 0 | 0 | 1220 | 0 | 5891.71 | 12356.76 | 84.61
16:00 | 0 | 34 | 24 | 115 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 34 | 45 | 145 | 55 | 35 | 51 | 0 | 225 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 15 | 0 | 21 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 950 | 0 | 0 | 25 | 0 | 0 | 217 | 0 | 0 | 0 | 1160 | 8 | 30 | 100 | 0 | 6 | 345 | 51 | 10 | 194 | 43 | 16 | 94 | 0 | 9 | 5 | 114 | 124 | 0 | 2 | 0 | 300 | 0 | 380 | 42 | 0 | 154 | 2 | 17 | 0 | 5 | 30 | 110 | 0 | 97 | 0 | 68 | 56 | 18 | 0.8 | 8.26 | 0 | 6569.06 | 868 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 1217 | 0 | 0 | 0 | 763.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.82 | 51 | 0 | 0 | 22.68 | 0 | 0 | 0 | 0 | 188 | 0 | 400 | 0 | 2.12 | 0 | 54 | 35 | 7 | 34 | 0 | 0 | 0 | 2.3 | 71 | 0.15 | 0 | 276 | 128 | 220 | 0 | 0 | 1230 | 0 | 5825.12 | 12394.18 | 84.6
17:00 | 0 | 34 | 24 | 115 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 11 | 48 | 78 | 145 | 55 | 35 | 47 | 0 | 225 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 5 | 0 | 21 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 7 | 0 | 4 | 0 | 0 | 0 | 0.3 | 80 | 0 | 0 | 950 | 0 | 0 | 25 | 0 | 0 | 217 | 0 | 0 | 0 | 1150 | 0 | 20 | 108 | 0 | 38 | 345 | 51 | 10 | 194 | 40 | 16 | 95 | 0 | 8 | 19 | 17 | 132 | 0 | 5 | 0 | 305 | 0 | 375 | 42 | 0 | 155 | 1 | 20 | 0 | 5 | 30 | 110 | 0 | 97 | 0 | 68 | 55 | 18 | 0.2 | 6.04 | 0 | 6541.54 | 869 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 1124 | 0 | 0 | 0 | 762.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.55 | 18 | 0 | 0 | 9.7 | 0 | 0 | 0 | 0 | 185 | 0 | 401 | 0 | 0.9 | 0 | 53 | 35 | 3 | 34 | 0 | 0 | 0 | 1.3 | 25 | 0.86 | 0 | 201 | 128 | 220 | 0 | 0 | 1210 | 0 | 5512.5 | 12054.04 | 84.59
18:00 | 0 | 48 | 30 | 115 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 17 | 52 | 91 | 146 | 55 | 17 | 54 | 0 | 225 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 70 | 20 | 7 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 51 | 32 | 0 | 36 | 40 | 0 | 80 | 0 | 3 | 950 | 16 | 0 | 29 | 0 | 0 | 217 | 0 | 0 | 0 | 1160 | 0 | 30 | 108 | 0 | 58 | 345 | 51 | 10 | 192 | 40 | 21 | 98 | 10 | 9 | 20 | 17 | 146 | 1 | 0 | 15 | 300 | 0 | 374 | 41 | 0 | 159 | 0 | 20 | 0 | 5 | 30 | 110 | 0 | 97 | 0 | 79 | 73 | 18 | 0 | 0 | 1 | 6931 | 868 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 1082 | 0 | 0 | 0 | 756.21 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 0.26 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 184 | 0 | 404 | 0 | 0.04 | 0 | 53 | 90 | 1 | 65 | 0 | 0 | 0 | 0.1 | 2 | 0.12 | 0 | 197 | 130 | 220 | 0 | 0 | 1206 | 0 | 5475.83 | 12406.83 | 84.58
19:00 | 0 | 70 | 51 | 115 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 22 | 17 | 114 | 108 | 245 | 55 | 17 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 70 | 21 | 12 | 0 | 500 | 10 | 0 | 0 | 0 | 0 | 51 | 32 | 0 | 50 | 50 | 0 | 80 | 14 | 5 | 950 | 16 | 0 | 43 | 0 | 12 | 223 | 0 | 0 | 0 | 1224 | 0 | 108 | 53 | 0 | 83 | 345 | 51 | 10 | 190 | 43 | 81 | 98 | 84 | 9 | 20 | 17 | 150 | 16 | 0 | 16 | 295 | 0 | 350 | 41 | 0 | 148 | 0 | 20 | 0 | 5 | 30 | 110 | 0 | 97 | 0 | 78 | 76 | 19 | 0 | 0 | 11 | 7557 | 868 | 194 | 0 | 16 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1210 | 16 | 0 | 0 | 756.38 | 0 | 42 | 0 | 70 | 47 | 0 | 35 | 21 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 401 | 0 | 0 | 0 | 53 | 115 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 301 | 130 | 220 | 0 | 0 | 1206 | 40 | 6065.38 | 13622.38 | 84.57
19:30 | 0 | 70 | 51 | 115 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 50 | 17 | 114 | 108 | 245 | 55 | 17 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 70 | 20 | 7 | 0 | 500 | 13 | 0 | 0 | 0 | 0 | 51 | 32 | 0 | 50 | 50 | 0 | 80 | 15 | 9 | 950 | 0 | 0 | 50 | 8 | 16 | 226 | 0 | 0 | 0 | 1224 | 0 | 143 | 53 | 0 | 102 | 345 | 51 | 10 | 195 | 43 | 93 | 100 | 100 | 9 | 20 | 0 | 144 | 0 | 0 | 22 | 305 | 0 | 380 | 41 | 0 | 156 | 0 | 20 | 0 | 5 | 30 | 110 | 0 | 97 | 0 | 78 | 76 | 20 | 0 | 0 | 12 | 7699 | 868 | 194 | 0 | 31 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 16 | 0 | 0 | 755.65 | 0 | 41 | 0 | 70 | 50 | 0 | 50 | 21 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 398 | 0 | 0 | 0 | 53 | 115 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 301 | 130 | 220 | 0 | 0 | 1205 | 54 | 6140.85 | 13839.85
20:00 | 0 | 70 | 51 | 115 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 52.5 | 17 | 120 | 108 | 245 | 55 | 17 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 70 | 20 | 7 | 0 | 500 | 13 | 0 | 0 | 0 | 0 | 51 | 32 | 0 | 50 | 50 | 0 | 80 | 16 | 6 | 950 | 0 | 0 | 49 | 8 | 15 | 226 | 0 | 0 | 0 | 1224 | 0 | 143 | 53 | 0 | 102 | 345 | 51 | 10 | 185 | 43 | 100 | 100 | 100 | 9 | 20 | 0 | 140 | 0 | 0 | 22 | 290 | 0 | 359 | 41 | 0 | 156 | 0 | 20 | 0 | 5 | 30 | 110 | 0 | 97 | 0 | 78 | 71 | 21 | 0 | 0 | 12 | 7656.5 | 868 | 193 | 0 | 31 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1216 | 17 | 0 | 0 | 759.91 | 0 | 41 | 0 | 70 | 50 | 0 | 50 | 30 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 404 | 0 | 0 | 0 | 53 | 115 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 130 | 220 | 0 | 0 | 1210 | 54 | 6175.91 | 13832.41 | 84.56
21:00 | 0 | 34 | 51 | 115 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17 | 17 | 103 | 78 | 245 | 55 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 70 | 20 | 7 | 0 | 500 | 15 | 0 | 0 | 0 | 0 | 51 | 32 | 0 | 50 | 50 | 0 | 80 | 16 | 9 | 950 | 0 | 0 | 47 | 8 | 15 | 224 | 0 | 0 | 0 | 1224 | 0 | 142 | 53 | 0 | 121 | 345 | 51 | 10 | 170 | 43 | 85 | 100 | 100 | 9 | 20 | 0 | 134 | 0 | 0 | 23 | 300 | 0 | 394 | 41 | 0 | 158 | 0 | 20 | 0 | 5 | 30 | 110 | 0 | 97 | 0 | 79 | 77 | 21 | 0 | 0 | 12 | 7559 | 862 | 189 | 0 | 31 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1185 | 17 | 0 | 0 | 762.65 | 0 | 41 | 0 | 70 | 50 | 0 | 51 | 30 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 414 | 0 | 0 | 0 | 52 | 115 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 130 | 220 | 0 | 0 | 1244 | 54 | 6160.65 | 13719.65 | 84.55
22:00 | 0 | 34 | 51 | 115 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 17 | 82 | 46 | 245 | 55 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 20 | 7 | 0 | 450 | 15 | 0 | 0 | 0 | 0 | 51 | 32 | 0 | 50 | 50 | 0 | 80 | 16 | 12 | 950 | 0 | 0 | 47 | 8 | 33 | 226 | 0 | 0 | 0 | 1224 | 0 | 143 | 53 | 0 | 127 | 345 | 51 | 10 | 190 | 43 | 50 | 102 | 115 | 9 | 20 | 0 | 144 | 0 | 0 | 23 | 295 | 0 | 394 | 41 | 0 | 156 | 0 | 20 | 0 | 5 | 30 | 111 | 0 | 97 | 0 | 79 | 77 | 19 | 0 | 0 | 12 | 7384 | 862 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1199 | 16 | 0 | 0 | 756.3 | 0 | 0 | 0 | 100 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 400 | 0 | 0 | 0 | 52 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 1244 | 81 | 6024.3 | 13408.3 | 84.54
23:00 | 0 | 17 | 34 | 115 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 17 | 52 | 46 | 145 | 55 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 20 | 15 | 0 | 450 | 15 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 50 | 50 | 0 | 80 | 14 | 19 | 950 | 0 | 0 | 47 | 8 | 48 | 225 | 0 | 0 | 0 | 1160 | 0 | 135 | 8 | 0 | 155 | 345 | 51 | 10 | 198 | 43 | 34 | 102 | 117 | 0 | 20 | 0 | 146 | 0 | 0 | 23 | 295 | 0 | 394 | 41 | 0 | 138 | 0 | 22 | 0 | 5 | 30 | 110 | 0 | 97 | 0 | 79 | 77 | 18 | 0 | 0 | 12 | 7077 | 861 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 762.94 | 0 | 0 | 0 | 70 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 367 | 0 | 0 | 0 | 53 | 90 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 130 | 220 | 0 | 0 | 1244 | 50 | 5859.14 | 12936.14 | 84.53
Total KWH | 0 | 648960 | 538560 | 2765100 | 0 | 0 | 0 | 0 | 9972000 | 0 | 0 | 259920 | 286920 | 1028880 | 578400 | 2834018 | 1101018 | 266816 | 806400 | 55680 | 5088500 | 0 | 0 | 0 | 269671 | 0 | 0 | 0 | 144636 | 320400 | 409200 | 293040 | 0 | 9794090.91 | 92836 | 7527 | 0 | 0 | 170400 | 350086 | 151745 | 0 | 351360 | 432960 | 14406 | 1922040 | 158900 | 310080 | 22916363.64 | 18400 | 0 | 570240 | 42051.6 | 249236 | 5319705 | 0 | 0 | 0 | 27730906 | 125550 | 1706181 | 702545 | 0 | 3284500 | 8000000 | 1230916 | 117600 | 4564000 | 618192 | 563520 | 2458120 | 832800 | 83160 | 456270 | 941640 | 3463680 | 25781 | 336845 | 132176 | 7254000 | 0 | 8872000 | 981000 | 0 | 3541581.82 | 43110 | 418488 | 0 | 125760 | 718848 | 2599000 | 0 | 2346750 | 18720 | 1342800 | 960000 | 644160 | 10250 | 196630 | 76560 | 158064585.97 | 20301090 | 5708160 | 0 | 85920 | 81280 | 0 | 0 | 0 | 0 | 0 | 0 | 248400 | 27629090 | 89280 | 0 | 0 | 18256364 | 0 | 118298 | 0 | 466176 | 494400 | 0 | 139872 | 62853 | 0 | 246160 | 474160 | 60915 | 0 | 268496 | 0 | 0 | 0 | 0 | 4697373 | 0 | 9412436 | 0 | 22920 | 0 | 1234472 | 975730 | 108151 | 902371 | 0 | 0 | 0 | 42734.76 | 743040 | 2998 | 60672 | 6764000 | 3100000 | 5506770 | 0 | 0 | 28704000 | 366000 | 137374581.76 | 295439167.73

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 31-03-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12570.15 | MW | 12:00 Hr. | Energy Generated |  |  | 295.4392 |  | MKWHr.
| Day Peak Demand |  |  | 12905.15 | MW | 12:00 Hr. | Energy Unserverd |  |  | 3.221 |  | MKWHr.
| Evening Peak Generation |  |  | 13839.85 | MW | 19:30 Hr. | Energy Demand |  |  | 298.6602 |  | MKWHr.
| Evening Peak Demand |  |  | 13999.38 | MW | 19:00 Hr. | Maximum Temperature |  |  | 32.9 |  | °C
| Minimum Generation of the Day |  |  | 10570 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 844.04 |  | MMCFD
| Maximum Generation of the Day |  |  | 13839.85 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.1662 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 28.3219 | 0 | 8.9956 | 0 | 0 | 0.14464 | 0 | 0 | 37.4622 | Gas | 111.3102 | Gas | 388018425.5491
| Chattogram Zone |  |  | 5.6298 | 50.6473 | 2.4253 | 0 | 1.922 | 0.13996 | 0 | 0.1704 | 60.9348 | Coal | 114.9788 | Coal | 775669149.3292
| Cumilla Zone |  |  | 21.4321 | 0 | 4.2853 | 0 | 0 | 0.33685 | 3.4637 | 0 | 29.5179 | HFO | 22.0081 | HFO | 375099417.92
| Mymensingh Zone |  |  | 0.64416 | 0 | 2.3981 | 0 | 0 | 0.20688 | 0 | 0 | 3.2491 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.8574 | 0 | 0 | 0 | 0 | 0.04311 | 0 | 0 | 26.9005 | Hydro | 1.922 | Hydro | 192204
| Khulna Zone |  |  | 5.7082 | 27.6291 | 0.25648 | 0 | 0 | 0.2484 | 20.3011 | 0 | 54.1432 | Solar | 3.0285 | Solar | 47951394.752
| Barishal Zone |  |  | 8.6068 | 35.468 | 0.42667 | 0 | 0 | 0.002998 | 0 | 0 | 44.5044 | Import | 42.0211 | Import | 232298674.86
| Rajshahi Zone |  |  | 14.1098 | 0 | 1.3425 | 0 | 0 | 1.0117 | 18.2564 | 0 | 34.7204 | Wind | 0.1704 | Wind | 2506584
| Rangpur Zone |  |  | 0 | 1.2345 | 1.8781 | 0 | 0 | 0.89393 | 0 | 0 | 4.0065
| Total |  |  | 111.3102 | 114.9788 | 22.0081 | 0 | 1.922 | 3.0285 | 42.0211 | 0.1704 | 295.4392
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 388018425.5491 |  | Hydro | 192204
|  |  |  | Coal | 775669149.3292 |  | Solar | 47951394.752
|  |  |  | HFO | 375099417.92 |  | Import | 232298674.86
|  |  |  | HSD | 0 |  | Wind | 2506584
[5 empty] | Total: | 182,17,35,850 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.3011 | Peak Hr Flow | 868.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 36028872.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 18.2564 | Peak Hr Flow | 755.65 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1622 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.4637 | Peak Hr Flow | 144.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2357 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 42.0211 | Peak Hr Flow | 1767.65 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5048
|  |  |  | Chattogram |  | 0 |  | 1354
|  |  |  | Cumilla |  | 8 |  | 1172
|  |  |  | Mymensingh |  | 31 |  | 1108
|  |  |  | Sylhet |  | 0 |  | 447
|  |  |  | Khulna |  | 0 |  | 1695
|  |  |  | Barishal |  | 0 |  | 449
|  |  |  | Rajshahi |  | 0 |  | 1347
|  |  |  | Rangpur |  | 0 |  | 818
|  |  |  | Total |  | 39 |  | 13438
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:30 | 15:08 | Bogura-Natore 132 kV Ckt-1 Scheduled S/D from Bogura 132/33kV end Due to maitenance work
and from Natore 132/33kVend.
| 09:05 | 10:26 | BIPTC S/S 20DF22 Forced S/D Due to 20DF22 tripped at 05:22 today.
| 09:12 | 12:56 | Daudkandi 132/33kV S/S Titas 50 MW Power Plant Line Scheduled S/D Due to Titas power
plant end ground CT work
|  | 09:32 | Haripur-Meghnaghat 230kV Ckt-1 is restored.
| 09:40 |  | Bibiyana-Kaliakoir 400 kV Ckt-2 Scheduled S/D from Bibiana 400/230kV end Due to Emergency
Maintenance
| 09:53 | 10:16 | Kabirpur 132/33kV S/S XFR, T-I LT Tripped showing Micom P-127 relays Due to 33 kV | [7 empty] | 67.0MW load
|  |  | baroibari feeder CT and CB blast | [7 empty] | interrup.
| 09:53 | 09:58 | Kabirpur 132/33kV S/S XFR, T-2 LT Tripped showing Micom p-127 relays Due to Baroibari 33 | [7 empty] | 67.0MW load
|  |  | kV feeder CT and CB blast | [7 empty] | interrup.
| 09:53 |  | Kachua 230/132/33kV S/S Laksam CKT-1 Project Work S/D Due to DFDR Test.
| 09:58 | 09:58 | Kabirpur 132/33kV S/S XFR, T-2 LT Forced S/D Due to 33 kV boroibari feeder bus DS loop
connecting work
| 10:07 |  | BIPTC S/S 20DF24 Forced S/D Due to Flashing spot at some location has been noticed.
| 10:25 | 17:09 | Bibiyana-Kaliakoir 400 kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
Tree Trimming and Disc Cleaning
| 10:34 | 12:14 | BIPTC S/S 20DF11 Forced S/D
| 10:34 | 14:37 | Juldah-Sikalbaha 132kV Ckt-1 Forced S/D from Juldah 132/33kV end Due to Conductor
Armouring is required between towers 45-46 R Phase.There will be no Load shedding.
| 12:00 |  | Day peak generation 12564 MW
| 13:54 | 16:23 | Bajitpur 132/33kV S/S Tr-2(414T) LT Scheduled S/D Due to Due to Tr-02 PDB 33kV Spare
feeder DS Maintenance and BPDB Feeder isolator Maintenance. Load shed 12MW for BPDB
| 14:40 | 19:26 | Khulna(C )-Noapara 132kV Ckt-1 Scheduled S/D from Noapara 132/33kV end Due to Instructed
By ALDC and from Khulna (C) end Due to near phultala lilo line OTG wire maintenance.
| 14:43 | 20:32 | Khulna(C )-Noapara 132kV Ckt-2 Scheduled S/D from Noapara 132/33kV end Due to Instructed
By ALDC and from Khulna (C) end Due to near phultala lilo line OPG wire maintenance.
| 16:17 | 17:03 | Baroirhat-Hathazari 132 kV Ckt-1 Tripped from Hathazari 230/132/33kV end showing
Quadrahmo relays Due to Tripped
| 16:46 | 16:46 | Chowmuhani-Ramganj 132 kV Ckt-2 Tripped from Chowmuhani 230/132/33kV end showing SIPROTEC
7SA87 relays Due to Stormy wind.
|  | 16:47 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 HT is restored.
|  | 16:47 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 LT is restored.
|  | 19:26 | Khulna(C )-Noapara 132kV Ckt-1 is restored.
|  | 19:26 | Khulna(C )-Noapara 132kV Ckt-1 is restored.
| 19:30 |  | Evening Peak Generation: 13839 MW.
| 20:23 | 21:11 | Bhangura 132/33kV S/S Tr-1(403T) LT Forced S/D Due to 33 KV TR-1 CT Y phase Red Hot
| 20:25 | 21:09 | Bhangura 132/33kV S/S Tr-1(403T) HT Forced S/D Due to 33 KV TR-1 CT Y phase Red Hot
|  | 21:01 | Kallyanpur 132/33kV S/S GT-3 (132kV) HT is restored.
| 00:19 |  | Siddhirganj 335 MW CCPP GT was sync.
| 03:16 |  | Siddhirganj 335 MW CCPP ST was sync.
| 06:45 |  | Chattak-Sylhet 132 kV Ckt-1 Scheduled S/D from Sylhet 132/33kV end Due to Breaker Change | [7 empty] | 24.0MW load
|  |  | at Chatak | [7 empty] | interrup. Sylhet
132/33kV end
| 06:45 |  | Chattak-Sylhet 132 kV Ckt-2 Scheduled S/D from Sylhet 132/33kV end Due to Breaker Change | [7 empty] | 27.0MW load
|  |  | at Chhatak | [7 empty] | interrup. Sylhet
132/33kV end
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 31-03-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 115 | 2765100 | GBC-3 Under maintenance.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 412 | 9972000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5088500 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1101018 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 50 | 259920 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 108 | 578400 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 266816 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 269671 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 409200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 7 | 293040 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 51 | 538560 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 245 | 2834018 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 114 | 1028880 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 648960 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 55680 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 806400 | FGMO
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 144636 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 286920 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 500 | 9794090.91 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage (BPDB)
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 70 | 320400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2165 | 37462209.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 42051.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 125550 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 570240 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1922040 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 226 | 5319705 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 16 | 249236 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 32 | 151745 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 350086 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 351360 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 9 | 310080 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 14406 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 7527 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 15 | 158900 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 432960 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 13 | 92836 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 18400 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 27730906 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 170400 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 950 | 22916363.64 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 2774 | 60934792.24
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 195 | 4564000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 102 | 3284500 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 345 | 8000000 | Able to ON FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 43 | 618192 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 10 | 117600 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 53 | 702545 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1230916 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 143 | 1706181 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 22 | 132176 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2458120 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 832800 | -
| Import (Tripura) |  | Import | 0 | 160 | 144 | 3463680 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 25781 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 456270 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 941640 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 83160 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 93 | 563520 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 336845 | -
Cumilla Area Total |  |  |  |  | 2872.921 | 1430 | 29517926
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 20 | 644160 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 76 | 960000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1342800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 196630 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 76560 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 18720 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 186 | 3249120
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 43110 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 981000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3541581.82 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 110 | 2599000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 718848 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 5 | 125760 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 97 | 2346750 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 20 | 418488 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7254000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 380 | 8872000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1144 | 26900537.82
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 868 | 20301090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 31 | 85920 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 28 | 81280 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 194 | 5708160 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 16 | 89280 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 248400 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 27629090 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2371.2 | 54143220
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 60672 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3100000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1205 | 28704000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5506770 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 366000 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 301 | 6764000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2998 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1926 | 44504440
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 246160 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Machine Problem
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 41 | 118298 | Under Maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 62853 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 180 | 4697373 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 398 | 9412436 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 15 | 60915 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 139872 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 494400 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 70 | 466176 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 22920 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 755.65 | 18256364 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 268496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 474160 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1580.65 | 34720423
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 53 | 1234472 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 95 | 902371 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 42734.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 975730 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 108151 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 743040 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 263 | 4006498.76
Eastern Grid Total |  |  |  |  | 17419.968 | 7699 | 158064585.97
Western Grid Total |  |  |  |  | 11852.195 | 6140.85 | 137374581.76
National Grid Total |  |  |  |  | 29272.163 | 13839.85 | 295439167.73
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 31-03-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9090.32 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4309.3 | MW
i) Dhaka area |  |  | 5048.32 |  | MW | i) Khulna area |  |  |  | 1695 | MW
ii) Chattogram area |  |  | 1354 |  | MW | ii) Barishal area |  |  |  | 449.1 | MW
iii) Cumilla area |  |  | 1164 |  | MW | iii) Rajshahi area |  |  |  | 1347.2 | MW
iv) Mymensingh area |  |  | 1077 |  | MW | iv) Rangpur area |  |  |  | 818 | MW
v) Sylhet area |  |  | 447 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13399.62 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 84 | 22:00 | 133 | Natore | 140 | 19:00
2 | AKSML | 13 | 04:00 | 68 | Hathazari | 77 | 00:00 | 134 | Nawabganj | 53.6 | 16:00
3 | Aftabnagar | 36 | 13:00 | 69 | Hatirjheel | 36 | 11:00 | 135 | Netrakona | 121 | 18:30
4 | Agargaon | 121 | 13:00 | 70 | Ishurdi | 71 | 19:00 | 136 | New | 72 | 14:00
5 | Agrabad | 64 | 19:30 | 71 | Jaldhaka | 66 | 19:30 | 137 | Niamatpur | 67 | 20:00
6 | Amnura | 39 | 14:00 | 72 | Jamalpur | 116 | 20:00 | 138 | Noapara | 45 | 20:00
7 | Ashuganj | 78 | 00:00 | 73 | Jashore | 143 | 20:00 | 139 | PHP | 9 | 10:00
8 | BSRM | 196 | 23:00 | 74 | Jhenaidah | 97 | 21:00 | 140 | Pabna | 88 | 19:30
9 | Bagerhat | 83 | 00:00 | 75 | Joydebpur | 130 | 20:00 | 141 | Palashbari | 109 | 19:30
10 | Bajitpur | 69 | 01:00 | 76 | Joypurhat | 64 | 19:30 | 142 | Panchagarh | 46 | 19:00
11 | Bakerganj | 10.4 | 19:00 | 77 | Juldah | 18 | 16:00 | 143 | Patiya | 9.5 | 23:00
12 | Bakulia | 86 | 15:00 | 78 | KSRM | 12 | 03:00 | 144 | Patuakhali | 64 | 22:00
13 | Banani | 40 | 12:00 | 79 | Kabirpur | 238 | 18:00 | 145 | Payra | 32 | 22:00
14 | Bangabhaban | 19 | 11:00 | 80 | Kachua | 92 | 00:00 | 146 | Postogola | 48 | 13:00
15 | Barapukuria | 57 | 19:00 | 81 | Kaliganj | 29 | 19:00 | 147 | Pubail | 27 | 12:00
16 | Barguna | 20 | 00:00 | 82 | Kallyanpur | 86 | 13:00 | 148 | Purbachal | 30 | 13:00
17 | Barishal | 98 | 19:00 | 83 | Kalurghat | 41 | 12:00 | 149 | Purbasadipur | 103 | 19:30
18 | Barishal-230 | 100 | 19:30 | 84 | Kamrangirchar | 79 | 13:00 | 150 | Rahanpur | 29 | 19:30
19 | Baroaulia | 63 | 16:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 22 | 23:00
20 | Baroirhat | 58 | 00:00 | 86 | Kasba | 31 | 00:00 | 152 | Rajbari | 70 | 21:00
21 | Bashundhara | 172 | 13:00 | 87 | Kazla | 110 | 13:00 | 153 | Rajendrapur | 119 | 18:30
22 | BashundharaCement | 7 | 00:00 | 88 | Keranigonj | 72 | 19:30 | 154 | Rajshahi | 96 | 18:30
23 | Beanibazar | 54 | 21:00 | 89 | Khagrachori | 26 | 12:00 | 155 | Rajshahi-230 | 92 | 22:00
24 | Benapole | 63 | 20:00 | 90 | Khulna | 55 | 13:00 | 156 | Ramganj | 106 | 00:00
25 | Bhaluka | 141 | 15:00 | 91 | Khulshi | 182 | 15:00 | 157 | Rampur | 39 | 00:00
26 | Bhandaria | 53 | 21:00 | 92 | Kishoreganj | 104 | 19:00 | 158 | Rangamati | 15 | 20:00
27 | Bhangura | 34 | 21:00 | 93 | Kodda | 312 | 19:00 | 159 | Rangpur | 116 | 20:00
28 | Bheramara(GK) | 55 | 19:30 | 94 | Kulaura | 33 | 21:00 | 160 | Ruppur | 3.8 | 15:00
29 | Bhulta | 196 | 21:00 | 95 | Kurigram | 56 | 18:30 | 161 | SSM | 10 | 02:00
30 | Bog-Sherpur | 76 | 21:00 | 96 | Kushtia | 136 | 19:30 | 162 | Saidpur | 87 | 12:00
31 | Bogura | 156 | 21:00 | 97 | Laksam | 22 | 02:00 | 163 | Satkhira | 134 | 19:00
32 | Borhanuddin | 88 | 00:00 | 98 | Lakshmipur | 40 | 23:00 | 164 | Satmasjid | 95 | 14:00
33 | Brahmanbaria | 104 | 21:00 | 99 | Lalbag | 63 | 12:00 | 165 | Savar | 212 | 16:00
34 | Cantonment | 148 | 13:00 | 100 | Lalmonirhat | 54 | 19:00 | 166 | SevenRings | 6.5 | 21:00
35 | Chandina | 16 | 16:00 | 101 | MI_Cement | 11.2 | 00:00 | 167 | ShahCement | 36 | 10:00
36 | Chandpur | 76 | 00:00 | 102 | Madanganj | 42 | 20:00 | 168 | Shahjadpur | 71 | 19:00
37 | Chandraghona | 36 | 18:30 | 103 | Madaripur | 102 | 00:00 | 169 | Shahjibazar | 97 | 21:00
38 | Chapai | 65 | 12:00 | 104 | Madartek | 68 | 14:00 | 170 | Shahmirpur | 53 | 18:00
39 | Charsaidpur | 43 | 16:00 | 105 | Madunaghat | 53 | 18:30 | 171 | Shariatpur | 82 | 00:00
40 | Chauddagram | 69 | 01:00 | 106 | Magura | 64 | 19:30 | 172 | Sherpur | 136 | 19:00
41 | Chhatak | 31 | 20:00 | 107 | Mahasthangarh | 73 | 19:00 | 173 | Shikalbaha | 26.5 | 19:30
42 | Chowmuhani | 134 | 00:00 | 108 | Maijdee | 50 | 00:00 | 174 | Shitalakhya | 81 | 12:00
43 | Chuadanga | 109 | 19:30 | 109 | Manikganj | 129 | 19:00 | 175 | Sholosohor | 48 | 15:00
44 | Coxsbazar | 145 | 19:30 | 110 | Maniknagar | 74 | 13:00 | 176 | Shyampur | 150 | 13:00
45 | Cumilla(N) | 114 | 11:00 | 111 | Matarbari | 55 | 18:30 | 177 | Siddhirganj | 118 | 14:00
46 | Cumilla(S) | 162 | 00:00 | 112 | Matuail | 60 | 09:00 | 178 | Sirajganj | 100 | 13:00
47 | Daganbhuiyan | 33 | 00:00 | 113 | Metrorail_Motijheel | 24 | 19:30 | 179 | Sonargaon | 142 | 16:00
48 | Daudkandi | 133 | 19:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreemongol | 61 | 18:30
49 | DhakaUniversity | 72 | 13:00 | 115 | Millgate | 97 | 12:00 | 181 | Sreepur | 110 | 18:30
50 | Dhamrai | 132 | 19:00 | 116 | Mirpur | 133 | 12:00 | 182 | Srinagar | 48 | 16:00
51 | Dhanmondi | 102 | 13:00 | 117 | Mirsorai | 49 | 12:00 | 183 | Sunamganj | 48 | 19:30
52 | Dohazari | 106 | 20:00 | 118 | Mirzapur | 56 | 18:30 | 184 | Sylhet | 50 | 19:30
53 | Faridpur | 154 | 00:00 | 119 | Mithapukur | 50 | 19:00 | 185 | Sylhet-132 | 87 | 13:00
54 | Fatullah | 98 | 15:00 | 120 | Modern | N/A | N/A | 186 | TK | 24 | 00:00
55 | Fenchuganj | 34 | 22:00 | 121 | Mogbazar | 55.6 | 16:00 | 187 | Tangail | 184 | 19:30
56 | Feni | 92 | 00:00 | 122 | Mongla | 48 | 15:00 | 188 | Taraganj | 20 | 18:30
57 | GPH | 4 | 17:00 | 123 | Motijheel | 47 | 13:00 | 189 | Tasnim | 25 | 01:00
58 | Ghatail | 98 | 20:00 | 124 | Muktagacha | 40 | 18:30 | 190 | Thakurgaon | 86 | 19:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 125 | 21:00 | 191 | Tongi | 131 | 11:00
60 | Ghorashal-230 | 97 | 19:00 | 126 | Muradnagar | 39 | 22:00 | 192 | Ullahpara | 36 | 18:30
61 | Goalpara | 39 | 15:00 | 127 | Mymensingh | 171 | 18:00 | 193 | Ullon | 59 | 13:00
62 | Gollamari | 96 | 21:00 | 128 | Nabinagar | 8 | 20:00 | 194 | Uttara | 82 | 12:00
63 | Gopalganj | 103 | 19:30 | 129 | Naogaon | 116 | 21:00 | 195 | UttaraNew | 29 | 14:00
64 | Gulshan | 122 | 12:00 | 130 | Narail | 60 | 20:00 | 196 | Zigatola | 86 | 13:00
65 | Halishahar | 99 | 16:00 | 131 | Narinda | 65 | 13:00
66 | HaripurSBU | 116 | 23:00 | 132 | Narshingdi | 153 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 31-03-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 12514 | 0 |  | 12514
1:00 | 11964.5 | 0 |  | 11964.5
2:00 | 11424.8 | 0 |  | 11424.8
3:00 | 11145.3 | 0 |  | 11145.3
4:00 | 10834.5 | 0 |  | 10834.5
5:00 | 10588 | 0 |  | 10588
6:00 | 10570 | 0 |  | 10570
7:00 | 10966.49 | 121 |  | 11092.49
8:00 | 11402.04 | 211 |  | 11622.04
9:00 | 11826.72 | 217 |  | 12053.72
10:00 | 11841.92 | 162 |  | 12010.92
11:00 | 12183.78 | 191 |  | 12383.78
12:00 | 12570.15 | 321 |  | 12905.15
13:00 | 12606.17 | 379 |  | 13002.17
14:00 | 12288.39 | 378 |  | 12683.39
15:00 | 12356.76 | 332 |  | 12703.76
16:00 | 12394.18 | 152 |  | 12553.18
17:00 | 12054.04 | 162 |  | 12223.04
18:00 | 12406.83 | 234 |  | 12651.83
19:00 | 13622.38 | 361 |  | 13999.38
19:30 | 13839.85 | 39 |  | 13880.85
20:00 | 13832.41 | 0 |  | 13832.41
21:00 | 13719.65 | 0 |  | 13719.65
22:00 | 13408.3 | 0 |  | 13408.3
23:00 | 12936.14 | 0 |  | 12936.14
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 31-03-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6674 | 5840 | 12514 | DAILY GENERATION CURVE
00:30 | 6497.25 | 5742 | 12239.25
01:00 | 6320.5 | 5644 | 11964.5 | 31-03-2026
01:30 | 6126.65 | 5568 | 11694.65
02:00 | 5932.8 | 5492 | 11424.8
02:30 | 5890.55 | 5394.5 | 11285.05
03:00 | 5848.3 | 5297 | 11145.3
03:30 | 5806.4 | 5183.5 | 10989.9
04:00 | 5764.5 | 5070 | 10834.5
04:30 | 5731.25 | 4980 | 10711.25
05:00 | 5698 | 4890 | 10588
05:30 | 5761 | 4818 | 10579
06:00 | 5824 | 4746 | 10570
06:30 | 5881.73 | 4886.515 | 10768.245
07:00 | 5939.46 | 5027.03 | 10966.49
07:30 | 6036.87 | 5147.395 | 11184.265
08:00 | 6134.28 | 5267.76 | 11402.04
08:30 | 6136.135 | 5478.245 | 11614.38
09:00 | 6137.99 | 5688.73 | 11826.72
09:30 | 6123.96 | 5710.36 | 11834.32
10:00 | 6109.93 | 5731.99 | 11841.92
10:30 | 6199.405 | 5813.445 | 12012.85
11:00 | 6288.88 | 5894.9 | 12183.78
11:30 | 6484.035 | 5892.93 | 12376.965
12:00 | 6679.19 | 5890.96 | 12570.15
12:30 | 6682.125 | 5906.035 | 12588.16
13:00 | 6685.06 | 5921.11 | 12606.17
13:30 | 6554.825 | 5892.455 | 12447.28
14:00 | 6424.59 | 5863.8 | 12288.39
14:30 | 6444.82 | 5877.755 | 12322.575
15:00 | 6465.05 | 5891.71 | 12356.76
15:30 | 6517.055 | 5858.415 | 12375.47
16:00 | 6569.06 | 5825.12 | 12394.18
16:30 | 6555.3 | 5668.81 | 12224.11
17:00 | 6541.54 | 5512.5 | 12054.04
17:30 | 6736.27 | 5494.165 | 12230.435
18:00 | 6931 | 5475.83 | 12406.83
18:30 | 7244 | 5770.605 | 13014.605
19:00 | 7557 | 6065.38 | 13622.38
19:30 | 7699 | 6140.85 | 13839.85
20:00 | 7656.5 | 6175.91 | 13832.41
20:30 | 7607.75 | 6168.28 | 13776.03 |  | Executive Engineer
21:00 | 7559 | 6160.65 | 13719.65 |  | Network Operation Division
21:30 | 7471.5 | 6092.475 | 13563.975
22:00 | 7384 | 6024.3 | 13408.3
22:30 | 7230.5 | 5941.72 | 13172.22
23:00 | 7077 | 5859.14 | 12936.14

## En-Curve
QF-LDC-12
Date | 31-03-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3066 | 1444 | 863 | 0 | 162 | 756 | 80 | 4887 | 0 | 120 | 1136 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3089 | 1443.75 | 863.5 | 0 | 162 | 748 | 80 | 4877.5 | 0 | 72 | 903.5 | 0 | 0 | 0 | 0 | 31-03-2026
01:00 | 3112 | 1443.5 | 864 | 0 | 162 | 740 | 80 | 4868 | 0 | 24 | 671 | 0 | 0 | 0 | 0
01:30 | 3143.5 | 1440.5 | 861.5 | 0 | 157 | 742.5 | 80 | 4853.5 | 0 | 12 | 404.15 | 0 | 0 | 0 | 0 | Energy Generated | 295.4392 |  | MKWHr
02:00 | 3175 | 1437.5 | 859 | 0 | 152 | 745 | 80 | 4839 | 0 | 0 | 137.3 | 0 | 0 | 0 | 0 | Energy not Served | 3.221 |  | MKWHr
02:30 | 3165 | 1440.5 | 858.5 | 0 | 152 | 746.5 | 80 | 4742.5 | 0 | 0 | 100.05 | 0 | 0 | 0 | 0 | Total Energy Requirement | 298.6602 |  | MKWHr
03:00 | 3155 | 1443.5 | 858 | 0 | 152 | 748 | 80 | 4646 | 0 | 0 | 62.8 | 0 | 0 | 0 | 0
03:30 | 3164 | 1441.5 | 858.5 | 0 | 149 | 749 | 80 | 4493.5 | 0 | 0 | 54.4 | 0 | 0 | 0 | 0
04:00 | 3173 | 1439.5 | 859 | 0 | 146 | 750 | 80 | 4341 | 0 | 0 | 46 | 0 | 0 | 0 | 0
04:30 | 3201.5 | 1453.25 | 859 | 0 | 146 | 748.5 | 80 | 4190.5 | 0 | 0 | 30.5 | 0 | 0 | 2 | 0
05:00 | 3230 | 1467 | 859 | 0 | 146 | 747 | 80 | 4040 | 0 | 0 | 15 | 0 | 0 | 4 | 0
05:30 | 3263 | 1442 | 713 | 0 | 145 | 751 | 80 | 4159 | 0 | 0 | 15 | 0 | 0 | 11 | 0
06:00 | 3296 | 1417 | 567 | 0 | 144 | 755 | 80 | 4278 | 0 | 0 | 15 | 0 | 0 | 18 | 0
06:30 | 3295 | 1400.5 | 566.5 | 0 | 140 | 754.5 | 80 | 4411 | 35.745 | 1 | 60.5 | 0 | 0 | 23.5 | 60.5
07:00 | 3294 | 1384 | 566 | 0 | 136 | 754 | 80 | 4544 | 71.49 | 2 | 106 | 0 | 0 | 29 | 121
07:30 | 3293 | 1356.5 | 561 | 0 | 145 | 756 | 80 | 4639 | 104.265 | 17 | 213 | 0 | 0 | 19.5 | 166
08:00 | 3292 | 1329 | 556 | 0 | 154 | 758 | 80 | 4734 | 137.04 | 32 | 320 | 0 | 0 | 10 | 211
08:30 | 3212 | 1287.5 | 709.5 | 0 | 156 | 761.5 | 80 | 4809 | 196.38 | 41 | 356.5 | 0 | 0 | 5 | 214
09:00 | 3132 | 1246 | 863 | 0 | 158 | 765 | 80 | 4884 | 255.72 | 50 | 393 | 0 | 0 | 0 | 217
09:30 | 3057.5 | 1233.5 | 863 | 0 | 155 | 765.13 | 80 | 4885 | 326.69 | 54 | 413.5 | 0 | 0 | 1 | 189.5
10:00 | 2983 | 1221 | 863 | 0 | 152 | 765.26 | 80 | 4886 | 397.66 | 58 | 434 | 0 | 0 | 2 | 162
10:30 | 3033.5 | 1349.5 | 865.5 | 0 | 151 | 768.67 | 80 | 4902.6 | 373.58 | 58 | 423 | 0 | 0 | 7.5 | 176.5
11:00 | 3084 | 1478 | 868 | 0 | 150 | 772.08 | 80 | 4919.2 | 349.5 | 58 | 412 | 0 | 0 | 13 | 191
11:30 | 3071.5 | 1458.5 | 868 | 0 | 150 | 767.885 | 80 | 4930.1 | 336.48 | 58 | 643 | 0 | 0 | 13.5 | 256
12:00 | 3059 | 1439 | 868 | 0 | 150 | 763.69 | 80 | 4941 | 323.46 | 58 | 874 | 0 | 0 | 14 | 321
12:30 | 3046.5 | 1372.5 | 868 | 0 | 141 | 747.49 | 80 | 4914 | 351.17 | 58 | 994.5 | 0 | 0 | 15 | 350
13:00 | 3034 | 1306 | 868 | 0 | 132 | 731.29 | 80 | 4887 | 378.88 | 58 | 1115 | 0 | 0 | 16 | 379
13:30 | 2988 | 1281 | 868 | 0 | 136 | 749.165 | 80 | 4890.5 | 395.115 | 58 | 987 | 0 | 0 | 14.5 | 378.5
14:00 | 2942 | 1256 | 868 | 0 | 140 | 767.04 | 80 | 4894 | 411.35 | 58 | 859 | 0 | 0 | 13 | 378
14:30 | 2953 | 1325.5 | 868 | 0 | 134 | 763.29 | 80 | 4895.5 | 380.285 | 58 | 848.5 | 0 | 0 | 16.5 | 355
15:00 | 2964 | 1395 | 868 | 0 | 128 | 759.54 | 80 | 4897 | 349.22 | 58 | 838 | 0 | 0 | 20 | 332
15:30 | 2996 | 1476.5 | 868 | 0 | 126 | 761.295 | 80 | 4892 | 294.675 | 80.5 | 781 | 0 | 0 | 19.5 | 242
16:00 | 3028 | 1558 | 868 | 0 | 124 | 763.05 | 80 | 4887 | 240.13 | 103 | 724 | 0 | 0 | 19 | 152
16:30 | 3039.5 | 1573.5 | 868.5 | 0 | 128 | 762.62 | 80 | 4787.5 | 169.99 | 121.5 | 680 | 0 | 0 | 13 | 157
17:00 | 3051 | 1589 | 869 | 0 | 132 | 762.19 | 80 | 4688 | 99.85 | 140 | 636 | 0 | 0 | 7 | 162
17:30 | 3057.5 | 1593.5 | 868.5 | 0 | 139 | 759.2 | 80 | 4668 | 52.735 | 238.5 | 770 | 0 | 0 | 3.5 | 198
18:00 | 3064 | 1598 | 868 | 0 | 146 | 756.21 | 80 | 4648 | 5.62 | 337 | 904 | 0 | 0 | 0 | 234
18:30 | 3063.5 | 1591.5 | 868 | 0 | 148 | 756.295 | 80 | 4796 | 2.81 | 442 | 1266.5 | 0 | 0 | 0 | 297.5
19:00 | 3063 | 1585 | 868 | 0 | 150 | 756.38 | 80 | 4944 | 0 | 547 | 1629 | 0 | 0 | 0 | 361
19:30 | 3118 | 1601 | 868 | 0 | 144 | 755.65 | 80 | 4967.2 | 0 | 590 | 1716 | 0 | 0 | 0 | 39
20:00 | 3093 | 1583 | 868 | 0 | 140 | 759.91 | 80 | 4960 | 0 | 623 | 1725.5 | 0 | 0 | 0 | 0
20:30 | 3112 | 1590.5 | 865 | 0 | 137 | 761.28 | 80 | 4961 | 0 | 582 | 1687.25 | 0 | 0 | 0 | 0
21:00 | 3131 | 1598 | 862 | 0 | 134 | 762.65 | 80 | 4962 | 0 | 541 | 1649 | 0 | 0 | 0 | 0
21:30 | 3135 | 1571 | 862 | 0 | 139 | 759.475 | 80 | 4969 | 0 | 406.5 | 1642 | 0 | 0 | 0 | 0
22:00 | 3139 | 1544 | 862 | 0 | 144 | 756.3 | 80 | 4976 | 0 | 272 | 1635 | 0 | 0 | 0 | 0
22:30 | 3133.5 | 1521 | 861.5 | 0 | 145 | 759.62 | 80 | 4946.6 | 0 | 230 | 1495 | 0 | 0 | 0 | 0
23:00 | 3128 | 1498 | 861 | 0 | 146 | 762.94 | 80 | 4917.2 | 0 | 188 | 1355 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 31-03-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 394 | 05:00 | 371 | 11:00 | Madunaghat | 401 | 23:00 | 390 | 12:00
Amtali | 414 | 04:00 | 408 | 15:00 | Meghnaghat | 398 | 05:00 | 376 | 11:00
Ashuganj | 402 | 8:00 | 366 | 11:00 | Payra | 415 | 04:00 | 408 | 11:00
Bhulta | 396 | 08:00 | 362 | 11:00 | Rahanpur | 410 | 06:00 | 399 | 08:00
Bibiana | 407 | 19:00 | 399 | 11:00 | Rampal | 407 | 05:00 | 393 | 11:00
BIPTC | 406 | 06:00 | 392 | 11:00
Bogura | 404 | 00:00 | 391 | 12:00
Gopalganj | 404 | 05:00 | 388 | 11:00
Kaliakoir | 387 | 05:00 | 361 | 11:00
Korerhat | 402 | 00:00 | 327 | 03:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 04:00 | 213 | 11:00 | Jhenaidah | 233 | 04:00 | 218 | 19:00
AKSML | 236 | 00:00 | 226 | 11:00 | Kachua | 231 | 18:30 | 219 | 11:00
Aminbazar | 231 | 03:00 | 214 | 11:00 | Kaliakoir | 234 | 00:00 | 218 | 11:00
Ashuganj | 230 | 04:00 | 218 | 11:00 | Keranigonj | 228 | 04:00 | 211 | 11:00
Ashuganj-400 | 230 | 8:00 | 205 | 11:00 | Khulna(S) | 233 | 05:00 | 223 | 19:30
Baghabari | 235 | 03:00 | 226 | 15:00 | Korerhat | 229 | 00:00 | 222 | 10:00
Barapukuria | 229 | 00:00 | 215 | 08:00 | Madunaghat | 238 | 00:00 | 230 | 11:00
Barapukuria-230 | 229 | 23:00 | 210 | 7:00 | Madunaghat-400 | 238 | 00:00 | 231 | 11:00
Barishal | 229 | 06:00 | 223 | 15:00 | Maniknagar | 225 | 07:00 | 212 | 16:00
Bheramara | 234 | 00:00 | 223 | 15:00 | Meghnaghat | 233 | 02:00 | 217 | 11:00
Bhulta | 229 | 08:00 | 210 | 11:00 | Meghnaghat-400 | 227 | 04:00 | 213 | 11:00
Bibiana | 234 | 00:00 | 229 | 10:00 | Mirsorai | 234 | 19:00 | 225 | 11:00
BIPTC | 237 | 00:00 | 223 | 15:00 | Purbasadipur | 230 | 00:00 | 215 | 08:00
Bogura | 234 | 00:00 | 225 | 08:00 | Rajshahi | 232 | 00:00 | 220 | 15:00
Bogura-400 | 233 | 00:00 | 224 | 12:00 | Rampal | 233 | 04:00 | 223 | 11:00
Borhanuddin | 233 | 06:00 | 230 | 00:00 | Rampur | N/A | N/A | N/A | N/A
BSRM | 230 | 00:00 | 221 | 11:00 | Rampura | 228 | 08:00 | 209 | 11:00
Chowmuhani | 0 | 00:00 | N/A | N/A | Shikalbaha | 237 | 10:00 | 227 | 10:00
Cumilla(N) | 228 | 05:00 | 216 | 11:00 | Shyampur | 227 | 05:00 | 211 | 12:00
Faridpur | 226 | 06:00 | 218 | 11:00 | Siddhirganj | 225 | 04:00 | 211 | 11:00
Fenchuganj | 239 | 04:00 | 232 | 11:00 | Sirajgonj | 238 | 04:00 | 229 | 10:00
Feni | 230 | 19:00 | 220 | 11:00 | Sreepur | 226 | 04:00 | 218 | 11:00
Ghorashal | 230 | 00:00 | 225 | 14:00 | Tongi | 232 | 01:00 | 219 | 15:00
Ghorashal-230 | 228 | 08:00 | 212 | 11:00
Gopalganj | 225 | 04:00 | 218 | 11:00
GPH | 235 | 19:00 | 226 | 11:00
Haripur | 226 | 05:00 | 211 | 11:00
Hasnabad | 228 | 05:00 | 211 | 11:00
Hathazari | 236 | 19:00 | 224 | 11:00
Ishurdi | 237 | 00:00 | 225 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 07:00 | 124 | 10:00 | Madunaghat | 138 | 00:00 | 132 | 11:00
Agargaon | 136 | 04:00 | 124 | 11:00 | Magura | 134 | 01:00 | 118 | 18:30
Agrabad | 136 | 18:00 | 129 | 11:00 | Mahasthangarh | 134 | 00:00 | 126 | 08:00
AKS | 134 | 18:30 | 128 | 11:00 | Maijdee | 129 | 19:00 | 121 | 11:00
Aminbazar | 133 | 03:00 | 120 | 11:00 | Manikganj | 131 | 04:00 | 118 | 11:00
Amnura | 134 | 06:00 | 127 | 23:00 | Maniknagar | 133 | 04:00 | 121 | 11:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 120 | 17:00 | 112 | 01:00
Ashuganj-230 | 138 | 04:00 | 133 | 11:00 | Matuail | 131 | 04:00 | 123.5 | 11:00
Bagerhat | 130 | 05:00 | 118 | 19:30 | Metrorail_Motijheel | 133 | 04:00 | 121 | 11:00
Bajitpur | 134 | 02:00 | 129 | 15:00 | Metrorail_Uttara | 132 | 04:00 | 118 | 11:00
Bakerganj | 133 | 18:00 | 129 | 11:00 | Millgate | 135 | 06:00 | 122 | 11:00
Bakulia | 138 | 18:00 | 131 | 11:00 | Mirpur | 131 | 00:00 | 119 | 11:00
Banani | 134 | 03:00 | 122 | 11:00 | Mirzapur | 130 | 00:00 | 117 | 11:00
Bangabhaban | 134 | 07:00 | 121 | 11:00 | Mithapukur | 132 | 00:00 | 122 | 08:00
Barapukuria | 131 | 00:00 | 124 | 10:00 | MI_Cement | 131 | 04:00 | 118 | 11:00
Barguna | 133 | 07:00 | 128 | 11:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 134 | 04:00 | 128 | 11:00 | Mogbazar | 134 | 21:00 | 125 | 10:00
Barishal-230 | 132 | 04:00 | 129 | 11:00 | Mongla | 127 | 18:00 | 119 | 19:30
Baroaulia | 136 | 18:30 | 132 | 10:00 | Motijheel | 134 | 07:00 | 121 | 11:00
Baroirhat | 132 | 19:00 | 127 | 11:00 | Muktagacha | 136 | 00:00 | 121 | 11:00
Bashundhara | 135 | 05:00 | 121 | 10:00 | Munshiganj | 132 | 07:00 | 123 | 11:00
BashundharaCement | 131 | 09:00 | 124 | 11:00 | Muradnagar | 127 | 04:00 | 119 | 11:00
Beanibazar | 132 | 04:00 | 127 | 15:00 | Mymensingh | 134 | 00:00 | 119 | 13:00
Benapole | 132 | 04:00 | 112 | 18:30 | Nabinagar | 130 | 01:00 | 120 | 11:00
Bhaluka | 132 | 00:00 | 125 | 15:00 | Naogaon | 138 | 00:00 | 125 | 08:00
Bhandaria | 128 | 05:00 | 124 | 15:00 | Narail | 135 | 01:00 | 120 | 19:30
Bhangura | 134 | 04:00 | 128 | 11:00 | Narinda | 133 | 4:00 | 121 | 11:00
Bheramara | 136 | 00:00 | 131 | 16:00 | Narshingdi | 132 | 07:00 | 118 | 09:00
Bheramara(GK) | 137 | 00:00 | 131 | 15:00 | Natore | 133 | 00:00 | 127 | 15:00
Bhulta | 127 | 07:00 | 118 | 12:00 | Nawabganj | 133 | 04:00 | 123 | 11:00
Bog-Sherpur | 134 | 00:00 | 128 | 11:00 | Netrakona | 132 | 02:00 | 119 | 18:30
Bogura | 136 | 00:00 | 129 | 11:00 | New | 136 | 03:00 | 127 | 10:00
Bogura-230 | 136 | 00:00 | 129 | 08:00 | Niamatpur | 136 | 00:00 | 132 | 08:00
Brahmanbaria | 132 | 13:00 | 122 | 11:00 | Noapara | 131 | 04:00 | 115 | 19:00
Cantonment | 136 | 04:00 | 123 | 11:00 | Pabna | 135 | 04:00 | 129 | 15:00
Chandina | 131 | 05:00 | 124 | 11:00 | Palashbari | 130 | 00:00 | 121 | 08:00
Chandpur | 133 | 18:30 | 122 | 11:00 | Panchagarh | 140 | 18:00 | 127 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 139 | 18:00 | 132 | 11:00 | Patiya | 135 | 23:00 | 129 | 11:00
Chapai | 136 | 03:00 | 130 | 11:00 | Patuakhali | 132 | 05:00 | 129 | 12:00
Charsaidpur | 133 | 07:00 | 123 | 11:00 | Payra | 135 | 05:00 | 131 | 11:00
Chauddagram | 129 | 18:30 | 123 | 11:00 | PHP | 131 | 19:00 | 127 | 11:00
Chhatak | 133 | 07:00 | 125 | 21:00 | Postogola | 132 | 06:00 | 120 | 11:00
Chowmuhani | 129 | 18:30 | 123 | 11:00 | Pubail | 135 | 18:30 | 127 | 16:00
Chuadanga | 133 | 05:00 | 119 | 18:30 | Purbachal | 134 | 00:00 | 121 | 11:00
Coxsbazar | 118 | 18:00 | 113 | 01:00 | Purbasadipur | 134 | 18:00 | 123 | 08:00
Cumilla(N) | 131 | 05:00 | 127 | 10:00 | Rahanpur | 137 | 02:00 | 133 | 08:00
Cumilla(S) | 130 | 00:00 | 124 | 09:00 | Rahanpur-400 | 138 | 05:00 | 133 | 08:00
Daganbhuiyan | 129 | 18:00 | 124 | 11:00 | Rahim | 132 | 07:00 | 124 | 11:00
Daudkandi | 125 | 05:00 | 115 | 11:00 | Rajbari | 130 | 06:00 | 124 | 13:00
DhakaUniversity | 134 | 22:00 | 124 | 10:00 | Rajendrapur | 133 | 05:00 | 125 | 16:00
Dhamrai | 131 | 04:00 | 120 | 11:00 | Rajshahi | 133 | 00:00 | 127 | 08:00
Dhanmondi | 134 | 07:00 | 124.5 | 11:00 | Rajshahi-230 | 134 | 00:00 | 127 | 15:00
Dohazari | 131 | 18:00 | 125 | 11:00 | Ramganj | 129 | 19:00 | 120 | 11:00
Faridpur | 131 | 04:00 | 126 | 12:00 | Rampur | 136 | 19:00 | 128 | 11:00
Fatullah | 131 | 06:00 | 119 | 11:00 | Rampura | 134 | 23:00 | 124 | 11:00
Fenchuganj | 136 | 04:00 | 131 | 11:00 | Rangamati | 138 | 18:00 | 131 | 11:00
Feni | 128 | 13:00 | 126 | 02:00 | Rangpur | 133 | 01:00 | 123 | 08:00
Feni-230 | 129 | 19:00 | 124 | 11:00 | Ruppur | 137 | 02:00 | 131 | 15:00
Ghatail | 130 | 00:00 | 115 | 11:00 | Saidpur | 132 | 02:00 | 122 | 08:00
Ghorashal | 137 | 00:00 | 130 | 11:00 | Satkhira | 129 | 04:00 | 120 | 19:30
Goalpara | 132 | 06:00 | 125 | 19:30 | Satmasjid | 136 | 05:00 | 124 | 11:00
Gollamari | 133 | 05:00 | 126 | 19:30 | Savar | 130 | 00:00 | 117 | 11:00
Gopalganj | 132 | 05:00 | 127 | 11:00 | SevenRings | 137 | 00:00 | 128 | 11:00
Gopalganj-400 | 134 | 05:00 | 129 | 11:00 | ShahCement | 133 | 07:00 | 123 | 11:00
Gulshan | 133 | 20:00 | 123 | 10:00 | Shahjadpur | 140 | 04:00 | 132 | 10:00
Halishahar | 137 | 19:00 | 129 | 11:00 | Shahjibazar | 131 | 05:00 | 124 | 11:00
Haripur | 132 | 07:00 | 130 | 23:00 | Shahmirpur | 137 | 18:00 | 131 | 11:00
HaripurSBU | 135 | 00:00 | 124 | 11:00 | Shariatpur | 131 | 04:00 | 126 | 15:00
Hasnabad | 134 | 02:00 | 122 | 11:00 | Sherpur | 132 | 01:00 | 116 | 06:00
Hathazari | 137 | 00:00 | 132 | 11:00 | Shikalbaha | 127 | 22:00 | 121 | 11:00
Hatirjheel | 134 | 22:00 | 124 | 10:00 | Shikalbaha-230 | 138 | 01:00 | 132 | 11:00
Ishurdi | 138 | 00:00 | 132 | 19:00 | Shitalakhya | 131 | 04:00 | 118 | 11:00
Jaldhaka | 129 | 18:00 | 119 | 08:00 | Sholosohor | 137 | 18:00 | 132 | 11:00
Jamalpur | 136 | 00:00 | 118 | 06:00 | Shyampur | 130 | 01:00 | 120 | 11:00
Jashore | 132 | 05:00 | 115 | 19:00 | Shyampur-230 | 131 | 04:00 | 121 | 12:00
Jhenaidah | 136 | 00:00 | 123 | 19:00 | Siddhirganj | 133 | 07:00 | 124 | 11:00
Jhenaidah-230 | 135 | 01:00 | 121 | 19:30 | Sirajganj | 133 | 01:00 | 127 | 08:00
Joydebpur | 134 | 00:00 | 123 | 16:00 | Sonargaon | 132 | 07:00 | 123 | 11:00
Joypurhat | 130 | 00:00 | 122 | 08:00 | Sreemongol | 132 | 05:00 | 126 | 11:00
Juldah | 138 | 22:00 | 129 | 11:00 | Sreepur | 135 | 04:00 | 128 | 16:00
Kabirpur | 136 | 19:00 | 118 | 11:00 | Srinagar | 134 | 04:00 | 124 | 11:00
Kachua | 131 | 18:30 | 124 | 11:00 | SSM | 140 | 18:30 | 135 | 10:00
Kaliakoir | 136 | 19:00 | 123 | 11:00 | Sunamganj | 130 | 04:00 | 124 | 21:00
Kaliganj | 135 | 04:00 | 121 | 18:30 | Sylhet | 132 | 04:00 | 128 | 12:00
Kallyanpur | 136 | 19:30 | 120 | 11:00 | Sylhet-132 | 132 | 03:00 | 129 | 11:00
Kalurghat | 138 | 18:00 | 132 | 11:00 | Tangail | 128 | 00:00 | 117 | 11:00
Kamrangirchar | 135 | 06:00 | 117 | 11:00 | Taraganj | 131 | 00:00 | 121 | 08:00
Kaptai | N/A | N/A | N/A | N/A | Tasnim | 131 | 07:00 | 123 | 11:00
Kasba | 126 | 04:00 | 119 | 11:00 | Thakurgaon | 139 | 18:00 | 124 | 07:00
Kazla | 132 | 04:00 | 122 | 12:00 | TK | 138 | 18:00 | 132 | 10:00
Keranigonj | 134 | 04:00 | 124 | 11:00 | Tongi | 137 | 01:00 | 129 | 11:00
Khagrachori | 138 | 16:00 | 130 | 11:00 | Ullahpara | 134 | 00:00 | 128 | 11:00
Khulna | 133 | 06:00 | 125 | 19:30 | Ullon | 134 | 22:00 | 123 | 10:00
Khulna(S) | 134 | 05:00 | 127 | 19:30 | Uttara | 132 | 04:00 | 118 | 11:00
Khulshi | 136 | 18:30 | 128 | 11:00 | UttaraNew | 132 | 04:00 | 118 | 11:00
Kishoreganj | 134 | 03:00 | 126 | 18:30 | Zigatola | 135 | 05:00 | 124 | 12:00
Kodda | 136 | 19:00 | 118 | 11:00
Korerhat | 133 | 19:30 | 129 | 10:00
KSRM | 137 | 19:00 | 130 | 11:00
Kulaura | 135 | 03:00 | 131 | 11:00
Kurigram | 132 | 22:00 | 117 | 08:00
Kushtia | 136 | 00:00 | 127 | 18:30
Laksam | 131 | 18:30 | 123 | 11:00
Lakshmipur | 128 | 19:00 | 121 | 11:00
Lalbag | 134 | 06:00 | 124 | 10:00
Lalmonirhat | 129 | 03:00 | 119 | 08:00
Madanganj | 131 | 09:00 | 124 | 11:00
Madaripur | 131 | 03:00 | 128 | 13:00
Madartek | 132 | 08:00 | 124 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division