## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 02-04-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-04-2026 | during | 02-04-2026 | during | 02-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 81 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 380 | 402 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 160 | 160 | 450 | 450 | 226 | 226 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 326 | 326 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 18 | 25 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 62 | 122 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 19 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 20 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 41 | 34 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 145 | 195 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 104 | 140 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 40 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 54 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 33 | 0 | 33 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 20 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 365 | 350 | 584 | 584 | 450 | 450 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 142 | 160 | 160 | 160 | 160
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1965 | 2239 | 5948.22 | 5915.22 | 2966.52 | 2933.52
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 13 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 42 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 75 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 221 | 220 | 220 | 220 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 67 | 102 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 30 | 56 | 64 | 56 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 | 51 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 20 | 50 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 9 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 58 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.77 | 0 | 1.5 | 0 | 1.5 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 49 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 20 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 7 | 79 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 36 | 38 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 5 | 43 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 10 | 136 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1170 | 1160 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 4 | 0 | 5 | 1 | 5 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 950 | 950 | 950 | 950 | 950 | 950 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2619.77 | 3151.5 | 3842.36 | 3833.86 | 3842.36 | 3833.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 167 | 190 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 365 | 360 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 342 | 345 | 342.01 | 342.01 | 342.01 | 342.01 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 10 | 0 | 41.65 | 41.65 | 41.65 | 41.65 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 10 | 0 | 55 | 55 | 11 | 11 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 9 | 9 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 108 | 127 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 22 | 24 | 24 | 24 | 24 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 96 | 163 | 163 | 101 | 101 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 83 | 167 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 156 | 184 | 84 | 82 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 101 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 47 | 27 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 73 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2872.921 | 1528 | 1751.2 | 2748.37 | 2686.37 | 2123.37 | 2063.37
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-04-2026 | during | 02-04-2026 | during | 02-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 12 | 157.5 | 157.5 | 60 | 60 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.1 | 0 | 0 | 0 | 0 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 78 | 60 | 80 | 60 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 69 | 78 | 70 | 80 | 70 | 80 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 21.35 | 0 | 45.12 | 0 | 45.12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 0 | 22 | 22 | 22 | 22 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 172.45 | 203 | 409.12 | 394 | 311.62 | 296.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 41 | 41 | 41 | 41 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 152 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 110 | 0 | 110 | 110 | 110 | 110 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 80 | 83 | 83 | 6 | 6 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 98 | 98 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 23 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 356 | 321 | 400 | 400 | 372 | 372 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1126 | 1040 | 1313 | 1313 | 1135 | 1135
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 868 | 841 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 31 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 30 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 162 | 134 | 410 | 410 | 190 | 190 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 16 | 105 | 105 | 105 | 105 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 99 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1188 | 1200 | 1234.2 | 1234.2 | 1204 | 1204 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2317 | 2252 | 3591.2 | 3506.2 | 2676 | 2591
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 897 | 900 | 902 | 902 | 902 | 902 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 150 | 150 | 150 | 150 | 150 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.69 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1544.69 | 1683 | 1820 | 1819 | 1820 | 1819
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 59.3 | 0 | 52 | 0 | 52 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 32 | 32 | 32 | 32 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 163 | 154 | 220 | 220 | 180 | 180 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 380 | 370 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 22 | 22 | 22 | 22 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 67 | 80 | 80 | 80 | 80 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 70 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 80 | 80 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.56 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 764 | 755 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 63.92 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 111 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1676.78 | 1634.2 | 2518.69 | 2299.99 | 2044.69 | 1825.99
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 51 | 51 | 53 | 53 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 85 | 99 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.3 | 0 | 6.2 | 0 | 6.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 93 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 140 | 0 | 189.16 | 0 | 189.16 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 404.3 | 265 | 526.36 | 301 | 508.36 | 283
System Total |  |  |  |  | 28823.2 | 29272.163 | 13353.99 | 14218.9 | 22717.32 | 22068.64 | 17427.92 | 16781.24
Forecast Scenario (02-04-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12790 |  | 0 |  | 12790
|  |  |  | 1:00 | 12230 |  | 0 |  | 12230
|  |  |  | 2:00 | 11820 |  | 0 |  | 11820
|  |  |  | 3:00 | 11510 |  | 0 |  | 11510
|  |  |  | 4:00 | 11190 |  | 0 |  | 11190
|  |  |  | 5:00 | 11020 |  | 0 |  | 11020
|  |  |  | 6:00 | 10970 |  | 0 |  | 10970
|  |  |  | 7:00 | 11600 |  | 0 |  | 11600
|  |  |  | 8:00 | 11970 |  | 0 |  | 11970
|  |  |  | 9:00 | 12090 |  | 0 |  | 12090
|  |  |  | 10:00 | 12560 |  | 0 |  | 12560
|  |  |  | 11:00 | 12940 |  | 0 |  | 12940
|  |  |  | 12:00 | 13550 |  | 0 |  | 13550
|  |  |  | 13:00 | 14080 |  | 0 |  | 14080
|  |  |  | 14:00 | 14170 |  | 0 |  | 14170
|  |  |  | 15:00 | 14320 |  | 0 |  | 14320
|  |  |  | 16:00 | 14110 |  | 0 |  | 14110
|  |  |  | 17:00 | 13670 |  | 0 |  | 13670
|  |  |  | 18:00 | 13550 |  | 0 |  | 13550
|  |  |  | 18:30 | 14000 |  | 0 |  | 14000
|  |  |  | 19:00 | 14410 |  | 0 |  | 14410
|  |  |  | 19:30 | 14230 |  | 0 |  | 14230
|  |  |  | 20:00 | 14050 |  | 0 |  | 14050
|  |  |  | 21:00 | 13700 |  | 0 |  | 13700
|  |  |  | 22:00 | 13440 |  | 0 |  | 13440
|  |  |  | 23:00 | 13200 |  | 0 |  | 13200
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 13550.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14410.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14410.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 306.56893 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:17 hrs on 02-04-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 01-04-2026 | [28 empty] | Date: | 01-04-2026 | [28 empty] | Date: | 01-04-2026 | [28 empty] | Date: | 01-04-2026 | [28 empty] | Date: | 01-04-2026 | [17 empty] | Date: | 01-04-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 55.000 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 24 | 115 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 18 | 52 | 15 | 45 | 55 | 17 | 35 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 0 | 450 | 15 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 24 | 50 | 0 | 80 | 15 | 12 | 950 | 0 | 0 | 46 | 8 | 49 | 225 | 0 | 0 | 0 | 1160 | 0 | 90 | 8 | 0 | 280 | 345 | 51 | 10 | 193 | 42 | 23 | 101 | 84 | 0 | 20 | 0 | 144 | 0 | 0 | 23 | 295 | 0 | 380 | 41 | 0 | 140 | 0 | 22 | 0 | 5 | 30 | 110 | 0 | 97 | 0 | 79 | 77 | 18 | 0 | 0 | 12 | 6920 | 861 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 759.56 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 358 | 0 | 0 | 0 | 52 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 130 | 220 | 0 | 0 | 1244 | 15 | 5669.76 | 12589.76 | 84.52
01:00 | 0 | 10 | 25 | 115 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 52 | 15 | 0 | 55 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 20 | 15 | 0 | 420 | 0 | 0 | 0 | 0 | 3 | 17 | 0 | 0 | 12 | 12 | 0 | 80 | 0 | 23 | 950 | 0 | 0 | 33 | 0 | 46 | 225 | 0 | 0 | 0 | 1160 | 0 | 20 | 3 | 0 | 305 | 345 | 51 | 10 | 203 | 10 | 17 | 102 | 17 | 0 | 20 | 0 | 128 | 0 | 0 | 0 | 300 | 0 | 394 | 41 | 0 | 137 | 0 | 17 | 0 | 5 | 30 | 110 | 0 | 97 | 0 | 69 | 57 | 18 | 0 | 0 | 12 | 6480 | 868 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 753.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 389 | 0 | 0 | 0 | 53 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 130 | 220 | 0 | 0 | 1244 | 0 | 5552.61 | 12032.61 | 84.51
02:00 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 15 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 20 | 15 | 0 | 400 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 24 | 950 | 0 | 0 | 5 | 0 | 0 | 225 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 0 | 305 | 345 | 51 | 10 | 200 | 10 | 0 | 102 | 0 | 0 | 20 | 0 | 126 | 0 | 0 | 0 | 305 | 0 | 380 | 41 | 0 | 143 | 0 | 17 | 0 | 5 | 30 | 110 | 0 | 97 | 0 | 69 | 57 | 18 | 0 | 0 | 0 | 6125 | 869 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 756.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 378 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 130 | 220 | 0 | 0 | 1244 | 0 | 5503.83 | 11628.83 | 84.5
03:00 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 20 | 15 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 26 | 950 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1107 | 0 | 0 | 0 | 0 | 305 | 345 | 51 | 10 | 205 | 10 | 0 | 102 | 0 | 0 | 20 | 0 | 130 | 0 | 0 | 0 | 305 | 0 | 380 | 41 | 0 | 141 | 0 | 17 | 0 | 5 | 30 | 112 | 0 | 97 | 0 | 69 | 57 | 23 | 0 | 0 | 0 | 6083 | 869 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 0 | 0 | 0 | 756.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 394 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 130 | 220 | 0 | 0 | 1170 | 0 | 5228.79 | 11311.79 | 84.49
04:00 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 20 | 15 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 26 | 950 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1036 | 0 | 0 | 0 | 0 | 305 | 345 | 51 | 10 | 193 | 10 | 0 | 102 | 0 | 0 | 20 | 0 | 124 | 0 | 0 | 0 | 305 | 0 | 378 | 41 | 0 | 140 | 0 | 17 | 0 | 5 | 30 | 110 | 0 | 98 | 0 | 69 | 58 | 23 | 0 | 0 | 0 | 5958 | 869 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 0 | 0 | 0 | 760.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 359 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 130 | 220 | 0 | 0 | 1022 | 0 | 5036.48 | 10994.48 | 84.48
05:00 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 20 | 15 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 27 | 950 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 0 | 305 | 345 | 51 | 10 | 202 | 10 | 0 | 102 | 0 | 0 | 20 | 0 | 124 | 0 | 0 | 0 | 305 | 0 | 379 | 41 | 0 | 142 | 0 | 17 | 0 | 5 | 30 | 109 | 0 | 98 | 0 | 55 | 45 | 23 | 0 | 0 | 0 | 5963 | 868 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 965 | 0 | 0 | 0 | 665.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 389 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 130 | 220 | 0 | 0 | 942 | 0 | 4860.64 | 10823.64 | 84.47
06:00 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 20 | 15 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 26 | 950 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1007 | 0 | 0 | 0 | 0 | 305 | 345 | 51 | 10 | 197 | 10 | 0 | 102 | 0 | 0 | 20 | 0 | 120 | 0 | 0 | 0 | 300 | 0 | 379 | 41 | 0 | 140 | 0 | 17 | 0 | 5 | 30 | 110 | 0 | 98 | 0 | 55 | 45 | 23 | 0 | 0 | 0 | 5950 | 868 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 0 | 0 | 0 | 663.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 385 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 130 | 220 | 0 | 0 | 922 | 0 | 4821.09 | 10771.09 | 84.46
07:00 | 0 | 9 | 11 | 115 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 35 | 45 | 0 | 4 | 0 | 15 | 0 | 160 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 1 | 17 | 20 | 15 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 20 | 950 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1170 | 3 | 1 | 0 | 0 | 305 | 345 | 51 | 10 | 204 | 10 | 0 | 102 | 0 | 0 | 20 | 0 | 116 | 0 | 11 | 0 | 305 | 0 | 379 | 41 | 0 | 152 | 2 | 17 | 0 | 5 | 30 | 110 | 0 | 98 | 0 | 69 | 57 | 21 | 0.1 | 3.52 | 0 | 6300.62 | 868 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.99 | 1107 | 0 | 0 | 0 | 752.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.14 | 4 | 0 | 0 | 3.27 | 0 | 0 | 0 | 0 | 168 | 0 | 414 | 0 | 0.32 | 0 | 51 | 0 | 1 | 0 | 0 | 0 | 0 | 0.4 | 1 | 0.06 | 0 | 279 | 130 | 220 | 0 | 0 | 910 | 0 | 5108.65 | 11409.27 | 84.45
08:00 | 0 | 17 | 16 | 115 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 61 | 45 | 0 | 15 | 0 | 14 | 0 | 160 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 4 | 17 | 20 | 15 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 8 | 950 | 0 | 0 | 12 | 0 | 12 | 222 | 0 | 0 | 0 | 1180 | 6 | 12 | 0 | 0 | 305 | 345 | 51 | 10 | 206 | 10 | 12 | 100 | 4 | 0 | 20 | 0 | 134 | 0 | 33 | 0 | 305 | 0 | 410 | 41 | 0 | 159 | 4 | 16 | 0 | 5 | 30 | 110 | 0 | 98 | 0 | 68 | 58 | 16 | 0.2 | 2.45 | 0 | 6478.65 | 868 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.67 | 1234.2 | 0 | 0 | 0 | 762.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.38 | 16 | 0 | 0 | 13.69 | 0 | 0 | 0 | 0 | 168 | 0 | 414 | 0 | 1.01 | 0 | 52 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 17 | 0.2 | 0 | 280 | 130 | 220 | 0 | 0 | 902 | 0 | 5300.07 | 11778.72 | 84.44
09:00 | 0 | 25 | 33 | 100 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 72 | 60 | 0 | 25 | 0 | 35 | 0 | 160 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 8 | 17 | 20 | 15 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.66 | 80 | 0 | 3 | 950 | 0 | 0 | 24 | 0 | 34 | 221 | 0 | 0 | 0 | 1224 | 5 | 36 | 0 | 0 | 305 | 320 | 51 | 10 | 186 | 10 | 25 | 100 | 29 | 0 | 20 | 0 | 138 | 0 | 28 | 0 | 305 | 0 | 337 | 41 | 0 | 158 | 8 | 0 | 0 | 5 | 30 | 110 | 0 | 98 | 0 | 69 | 58 | 16 | 0.2 | 7.99 | 0 | 6528.85 | 868 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.42 | 1166 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 27.63 | 71 | 0 | 0 | 19.19 | 0 | 0 | 0 | 0 | 165 | 0 | 360 | 0 | 1.54 | 0 | 52 | 35 | 7 | 34 | 0 | 0 | 0 | 0.9 | 16 | 0.21 | 0 | 307 | 130 | 220 | 0 | 0 | 882 | 0 | 5363.89 | 11892.74 | 84.43
10:00 | 0 | 34 | 33 | 81 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 18 | 0 | 104 | 60 | 0 | 55 | 0 | 35 | 0 | 160 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 28 | 0 | 20 | 15 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.45 | 80 | 0 | 0 | 950 | 0 | 0 | 39 | 0 | 68 | 219 | 0 | 0 | 0 | 1160 | 16 | 70 | 0 | 0 | 370 | 320 | 51 | 10 | 205 | 10 | 46 | 100 | 50 | 0 | 20 | 0 | 148 | 0 | 63 | 0 | 310 | 0 | 371 | 41 | 0 | 156 | 0 | 0 | 0 | 5 | 30 | 111 | 0 | 98 | 0 | 69 | 58 | 10 | 0.4 | 21.75 | 1 | 6828.6 | 869 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 1201 | 0 | 0 | 0 | 764 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 48.94 | 94 | 0 | 0 | 29.16 | 0 | 0 | 0 | 0 | 155 | 0 | 414 | 0 | 3.68 | 0 | 53 | 35 | 4 | 34 | 0 | 0 | 0 | 2 | 34 | 0.24 | 0 | 273 | 130 | 220 | 0 | 0 | 892 | 0 | 5540.02 | 12368.62 | 84.42
11:00 | 0 | 34 | 33 | 80 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 18 | 0 | 104 | 60 | 0 | 55 | 4 | 35 | 0 | 160 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 31 | 0 | 20 | 15 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.59 | 75 | 0 | 4 | 950 | 0 | 0 | 39 | 0 | 62 | 217 | 0 | 0 | 0 | 1180 | 14 | 70 | 0 | 0 | 365 | 345 | 51 | 10 | 206 | 10 | 46 | 97 | 51 | 0 | 20 | 0 | 156 | 0 | 69 | 0 | 300 | 0 | 414 | 41 | 0 | 155 | 12 | 17 | 0 | 5 | 30 | 110 | 0 | 98 | 0 | 69 | 57 | 10 | 1.3 | 32.6 | 12 | 7038.49 | 868 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 1200 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 58.56 | 107 | 0 | 0 | 47.36 | 0 | 0 | 0 | 0 | 163 | 0 | 414 | 0 | 4.86 | 0 | 52 | 35 | 12 | 34 | 0 | 0 | 0 | 5.1 | 134 | 0.68 | 0 | 283 | 120 | 220 | 0 | 0 | 900 | 0 | 5703.56 | 12742.05 | 84.41
12:00 | 0 | 40 | 41 | 81 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 18 | 0 | 104 | 62 | 145 | 55 | 17 | 54 | 0 | 160 | 0 | 0 | 0 | 17 | 326 | 0 | 0 | 30 | 35 | 20 | 15 | 0 | 365 | 5 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 20 | 36 | 1.77 | 75 | 7 | 4 | 950 | 10 | 0 | 42 | 0 | 67 | 215 | 0 | 0 | 0 | 1170 | 13 | 108 | 0 | 0 | 365 | 342 | 51 | 10 | 167 | 10 | 47 | 96 | 83 | 0 | 20 | 0 | 156 | 0 | 73 | 0 | 300 | 0 | 356 | 41 | 0 | 157 | 12 | 17 | 0 | 5 | 30 | 110 | 0 | 98 | 0 | 69 | 58 | 10 | 2.1 | 21.35 | 12 | 7411.22 | 868 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 1188 | 0 | 0 | 0 | 764 | 0 | 0 | 0 | 80 | 50 | 0 | 0 | 0 | 0 | 59.3 | 111 | 0 | 0 | 63.92 | 0 | 0 | 0 | 0 | 163 | 0 | 380 | 0 | 5.56 | 0 | 51 | 93 | 33 | 85 | 0 | 0 | 0 | 2.3 | 140 | 0.69 | 0 | 307 | 120 | 220 | 0 | 0 | 897 | 0 | 5942.77 | 13353.99 | 84.4
13:00 | 0 | 68 | 41 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 18 | 17 | 80 | 93 | 245 | 55 | 17 | 54 | 0 | 160 | 0 | 0 | 0 | 17 | 324 | 0 | 0 | 31 | 94 | 20 | 15 | 0 | 350 | 16 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 50 | 50 | 0 | 71 | 16 | 9 | 950 | 48 | 0 | 46 | 8 | 66 | 219 | 0 | 0 | 0 | 1172 | 18 | 150 | 0 | 0 | 360 | 330 | 51 | 10 | 147 | 10 | 33 | 94 | 149 | 7 | 20 | 0 | 178 | 16 | 70 | 0 | 300 | 0 | 331 | 42 | 0 | 157 | 12 | 17 | 0 | 5 | 30 | 80 | 0 | 98 | 10 | 69 | 57 | 7 | 2 | 42.52 | 12 | 7723.52 | 868 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 1234.2 | 0 | 0 | 0 | 765 | 0 | 0 | 0 | 113 | 111 | 0 | 0 | 0 | 0 | 57.64 | 109 | 0 | 0 | 38.83 | 0 | 0 | 0 | 0 | 163 | 0 | 411 | 0 | 4.5 | 0 | 52 | 110 | 21 | 94 | 0 | 0 | 0 | 2.4 | 144 | 0.7 | 11 | 307 | 110 | 220 | 0 | 0 | 892 | 70 | 6165.27 | 13888.79 | 84.39
14:00 | 0 | 88 | 41 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 18 | 17 | 0 | 122 | 245 | 55 | 17 | 54 | 0 | 160 | 0 | 0 | 0 | 17 | 324 | 0 | 0 | 28 | 108 | 20 | 15 | 0 | 350 | 15 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 50 | 50 | 1.49 | 75 | 16 | 0 | 950 | 48 | 0 | 50 | 25.5 | 66 | 217 | 0 | 0 | 0 | 1164 | 15 | 137 | 0 | 0 | 350 | 300 | 51 | 0 | 190 | 0 | 34 | 94 | 179 | 9 | 20 | 0 | 170 | 34 | 51 | 13 | 310 | 0 | 379 | 42 | 0 | 155 | 11 | 17 | 0 | 77 | 30 | 0 | 0 | 98 | 35 | 69 | 58 | 7 | 1.7 | 40.61 | 12 | 7785.3 | 868 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 1234.2 | 6 | 0 | 0 | 762 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 50.82 | 95 | 0 | 0 | 53.22 | 0 | 0 | 0 | 0 | 157 | 0 | 414 | 0 | 4.57 | 0 | 52 | 115 | 23 | 97 | 0 | 0 | 0 | 5.6 | 160 | 0.22 | 16 | 276 | 110 | 220 | 0 | 0 | 882 | 119 | 6185.63 | 13970.93 | 84.38
15:00 | 0 | 88 | 41 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 18 | 17 | 0 | 117 | 278 | 55 | 35 | 54 | 0 | 160 | 0 | 0 | 0 | 17 | 324 | 0 | 0 | 21 | 142 | 19 | 15 | 0 | 420 | 16 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 50 | 50 | 0.99 | 75 | 18 | 3 | 950 | 95 | 0 | 50 | 25.5 | 78 | 214 | 0 | 0 | 0 | 1224 | 12 | 118 | 0 | 0 | 290 | 340 | 51 | 0 | 205 | 0 | 23 | 93 | 185 | 9 | 20 | 0 | 182 | 38 | 49 | 14 | 310 | 0 | 384 | 42 | 0 | 155 | 8 | 17 | 0 | 80 | 30 | 0 | 0 | 98 | 35 | 67 | 58 | 8 | 1.4 | 21.95 | 12 | 8014.84 | 868 | 145 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 1234.2 | 16 | 0 | 0 | 762 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 39.21 | 60 | 0 | 0 | 36.49 | 0 | 0 | 0 | 0 | 155 | 0 | 414 | 0 | 3.61 | 0 | 52 | 115 | 20 | 99 | 0 | 0 | 0 | 4.7 | 124 | 0.48 | 7 | 307 | 120 | 220 | 0 | 0 | 870 | 136 | 6108.69 | 14123.53 | 84.37
16:00 | 0 | 100 | 41 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 18 | 17 | 6 | 118 | 278 | 55 | 35 | 54 | 0 | 160 | 0 | 0 | 0 | 17 | 324 | 0 | 0 | 14 | 142 | 19 | 19 | 0 | 400 | 16 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 50 | 38 | 1.37 | 75 | 47 | 2 | 950 | 93 | 0 | 50 | 25.5 | 88 | 223 | 0 | 0 | 0 | 1224 | 7 | 117 | 0 | 0 | 310 | 343 | 51 | 0 | 195 | 0 | 16 | 94 | 177 | 0 | 20 | 0 | 176 | 52.2 | 29 | 20 | 310 | 0 | 380 | 42 | 0 | 155 | 3 | 17 | 0 | 78 | 30 | 0 | 0 | 98 | 35 | 67 | 58 | 9 | 0.4 | 15.81 | 12 | 8005.28 | 868 | 140 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 1234.2 | 16 | 0 | 0 | 767 | 0 | 0 | 0 | 70 | 70 | 0 | 0 | 0 | 25 | 25.8 | 13 | 0 | 0 | 7.22 | 0 | 0 | 0 | 0 | 155 | 0 | 414 | 0 | 0.72 | 0 | 50 | 101 | 13 | 99 | 0 | 0 | 0 | 4.1 | 80 | 0.18 | 16 | 307 | 130 | 220 | 0 | 0 | 880 | 150 | 5908.22 | 13913.5 | 84.36
17:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 18 | 17 | 95 | 90 | 278 | 55 | 35 | 54 | 0 | 160 | 0 | 0 | 0 | 17 | 327 | 0 | 0 | 6 | 142 | 19 | 19 | 0 | 350 | 15 | 0 | 0 | 0 | 9 | 0 | 20 | 0 | 50 | 38 | 0.6 | 75 | 48 | 2 | 950 | 90 | 0 | 50 | 25.5 | 88 | 218 | 0 | 0 | 0 | 1100 | 3 | 118 | 0 | 0 | 355 | 345 | 51 | 0 | 180 | 0 | 17 | 94 | 136 | 0 | 20 | 0 | 166 | 52.2 | 14 | 20 | 305 | 0 | 316 | 42 | 0 | 152 | 2 | 17 | 0 | 79 | 30 | 0 | 0 | 98 | 35 | 64 | 58 | 10 | 0.2 | 2.41 | 12 | 7796.91 | 868 | 138 | 0 | 5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 1158 | 16 | 0 | 0 | 754 | 0 | 0 | 0 | 50 | 50 | 0 | 50 | 0 | 25 | 9.62 | 21 | 0 | 0 | 0.41 | 0 | 0 | 0 | 0 | 154 | 0 | 414 | 0 | 0 | 0 | 50 | 50 | 5 | 49 | 0 | 0 | 0 | 1.1 | 26 | 0.18 | 16 | 307 | 130 | 220 | 0 | 0 | 880 | 150 | 5629.31 | 13426.22 | 84.35
18:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 18 | 17 | 120 | 90 | 278 | 55 | 35 | 54 | 0 | 160 | 0 | 0 | 0 | 35 | 280 | 0 | 0 | 1 | 142 | 19 | 19 | 0 | 350 | 15 | 20 | 6 | 0 | 2 | 51 | 23 | 11 | 50 | 38 | 0 | 80 | 45 | 10 | 950 | 93 | 0 | 50 | 25.5 | 94 | 218 | 0 | 0 | 0 | 1100 | 0 | 103 | 0 | 0 | 355 | 280 | 51 | 0 | 192 | 0 | 17 | 95 | 131 | 8 | 20 | 17 | 172 | 52.2 | 0 | 20 | 300 | 0 | 324 | 42 | 0 | 154 | 0 | 21 | 0 | 80 | 30 | 0 | 0 | 98 | 35 | 76 | 77 | 10 | 0 | 0.41 | 0 | 7881.11 | 842 | 137 | 0 | 24 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 1100 | 16 | 0 | 0 | 756 | 0 | 38 | 0 | 50 | 50 | 0 | 57 | 15 | 25 | 0.63 | 1 | 20 | 0 | 0.82 | 0 | 0 | 0 | 0 | 154 | 0 | 380 | 0 | 0 | 0 | 50 | 50 | 0 | 49 | 0 | 0 | 0 | 0.2 | 3 | 0.07 | 16 | 275 | 130 | 180 | 0 | 0 | 880 | 150 | 5478.35 | 13359.46 | 84.34
19:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 25 | 20 | 140 | 122 | 195 | 55 | 35 | 54 | 0 | 160 | 0 | 0 | 0 | 35 | 326 | 0 | 0 | 0 | 142 | 19 | 20 | 0 | 350 | 43 | 49 | 58 | 0 | 0 | 51 | 30 | 20 | 50 | 38 | 0 | 80 | 79 | 9 | 950 | 136 | 0 | 50 | 25.5 | 102 | 221 | 0 | 0 | 0 | 1160 | 0 | 127 | 0 | 0 | 360 | 345 | 51 | 0 | 190 | 0 | 27 | 96 | 167 | 9 | 20 | 101 | 184 | 52.2 | 0 | 22 | 295 | 0 | 321 | 41 | 0 | 152 | 0 | 23 | 0 | 80 | 30 | 0 | 0 | 98 | 35 | 78 | 78 | 12 | 0 | 0 | 0 | 8384.7 | 841 | 134 | 0 | 31 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 16 | 0 | 0 | 755 | 0 | 40 | 0 | 80 | 70 | 0 | 67 | 26 | 52.2 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 370 | 0 | 0 | 0 | 51 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 130 | 180 | 0 | 0 | 900 | 150 | 5834.2 | 14218.9 | 84.33
19:30 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 45.8 | 35 | 104 | 90 | 95 | 55 | 35 | 54 | 0 | 160 | 0 | 0 | 0 | 35 | 328 | 0 | 0 | 0 | 125 | 0 | 20 | 0 | 350 | 84 | 49 | 60 | 0 | 0 | 51 | 30 | 54.36 | 50 | 38 | 0 | 80 | 99 | 12 | 950 | 140 | 0 | 33 | 8 | 94 | 220 | 0 | 0 | 0 | 1160 | 0 | 80 | 0 | 0 | 360 | 345 | 51 | 0 | 195 | 0 | 51 | 97 | 182 | 9 | 20 | 105 | 178 | 25 | 0 | 22 | 300 | 0 | 340 | 41 | 0 | 135 | 0 | 23 | 0 | 80 | 30 | 0 | 0 | 98 | 35 | 78 | 78 | 11 | 0 | 0 | 4 | 8148.16 | 842 | 133 | 0 | 35 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 16 | 0 | 0 | 757 | 0 | 41 | 0 | 113 | 113 | 0 | 67 | 23 | 52.2 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 370 | 0 | 0 | 0 | 51 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 130 | 180 | 0 | 0 | 900 | 87 | 5888.4 | 14036.56 | 84.32
20:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 46.8 | 35 | 110 | 60 | 95 | 55 | 17 | 54 | 0 | 160 | 0 | 0 | 0 | 35 | 329 | 0 | 0 | 0 | 125 | 0 | 21 | 0 | 350 | 87 | 48 | 63 | 0 | 0 | 34 | 30 | 54 | 50 | 38 | 0 | 80 | 103 | 20 | 950 | 78 | 0 | 33 | 8 | 96 | 221 | 0 | 0 | 0 | 1161 | 0 | 80 | 0 | 0 | 360 | 345 | 51 | 0 | 200 | 0 | 51 | 97 | 181 | 9 | 20 | 67 | 176 | 25 | 0 | 22 | 300 | 0 | 379 | 41 | 0 | 143 | 0 | 23 | 0 | 80 | 30 | 0 | 0 | 98 | 33 | 78 | 78 | 11 | 0 | 0 | 4 | 8057.8 | 842 | 133 | 0 | 31 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 16 | 0 | 0 | 763 | 0 | 41 | 0 | 70 | 70 | 0 | 67 | 23 | 25 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 370 | 0 | 0 | 0 | 50 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 130 | 220 | 0 | 0 | 900 | 65 | 5801.2 | 13859 | 84.32
21:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 18 | 17 | 50 | 30 | 15 | 30 | 17 | 35 | 0 | 160 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 108 | 0 | 21 | 0 | 430 | 45 | 48 | 44 | 0 | 0 | 41 | 30 | 17 | 12 | 38 | 0 | 80 | 85 | 15 | 950 | 0 | 0 | 32 | 8 | 95 | 221 | 0 | 0 | 0 | 1163 | 0 | 30 | 0 | 0 | 360 | 345 | 51 | 0 | 210 | 0 | 51 | 97 | 85 | 9 | 20 | 0 | 174 | 8 | 0 | 15 | 310 | 0 | 408 | 30 | 0 | 155 | 0 | 23 | 0 | 80 | 30 | 0 | 0 | 98 | 17 | 78 | 78 | 17 | 0 | 0 | 0 | 7415 | 841 | 133 | 0 | 30 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1230 | 16 | 0 | 0 | 761 | 0 | 0 | 0 | 35 | 35 | 0 | 67 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 414 | 0 | 0 | 0 | 51 | 70 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 900 | 34 | 5580 | 12995 | 84.31
22:00 | 0 | 47 | 4 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 18 | 17 | 34 | 60 | 65 | 30 | 0 | 35 | 0 | 160 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 108 | 12 | 21 | 0 | 430 | 51 | 60 | 38 | 0 | 0 | 51 | 30 | 17 | 24 | 38 | 0 | 80 | 72 | 23 | 950 | 0 | 0 | 33 | 8 | 102 | 222 | 0 | 0 | 0 | 1220 | 0 | 36 | 0 | 0 | 355 | 345 | 51 | 0 | 197 | 0 | 37 | 98 | 93 | 9 | 20 | 0 | 174 | 9 | 0 | 22 | 310 | 0 | 384 | 30 | 0 | 158 | 0 | 23 | 0 | 80 | 30 | 0 | 0 | 98 | 17 | 78 | 78 | 16 | 0 | 0 | 0 | 7574 | 841 | 134 | 0 | 29 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1233 | 16 | 0 | 0 | 762 | 0 | 0 | 0 | 70 | 50 | 0 | 67 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 414 | 0 | 0 | 0 | 50 | 90 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 900 | 67 | 5687 | 13261 | 84.3
23:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 17 | 60 | 60 | 95 | 30 | 0 | 35 | 0 | 160 | 0 | 0 | 0 | 17 | 332 | 0 | 0 | 0 | 108 | 17 | 21 | 0 | 380 | 86 | 60 | 38 | 0 | 0 | 51 | 30 | 17 | 24 | 38 | 0 | 80 | 108 | 24 | 950 | 0 | 0 | 32 | 8 | 96 | 222 | 0 | 0 | 0 | 1224 | 0 | 80 | 0 | 0 | 360 | 345 | 51 | 0 | 192 | 0 | 31 | 99 | 129 | 5 | 20 | 0 | 178 | 32 | 0 | 23 | 305 | 0 | 374 | 30 | 0 | 158 | 0 | 17 | 0 | 80 | 30 | 0 | 0 | 98 | 17 | 77 | 78 | 13 | 0 | 0 | 0 | 7722 | 842 | 134 | 0 | 27 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1219 | 16 | 0 | 0 | 759 | 0 | 0 | 0 | 70 | 110 | 0 | 67 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 414 | 0 | 0 | 0 | 50 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 0 | 902 | 61 | 5746 | 13468 | 84.29
Total KWH | 0 | 1076774 | 547402 | 0 | 0 | 0 | 0 | 0 | 9388800 | 0 | 0 | 259632 | 250560 | 1496592 | 1332000 | 2241622 | 896206 | 270926 | 807840 | 0 | 4282500 | 0 | 0 | 0 | 251742 | 5761293 | 0 | 0 | 201638 | 1468800 | 421800 | 395280 | 0 | 8921363.64 | 536331 | 364320 | 283200 | 0 | 51840 | 328179 | 200894 | 176703 | 518400 | 534720 | 20164 | 1897380 | 787854 | 342240 | 22887272.73 | 647345 | 0 | 747360 | 202962.6 | 1425163 | 5015370 | 0 | 0 | 0 | 27845452 | 104085 | 1659345 | 3000 | 0 | 8342500 | 8156000 | 1246816 | 140640 | 4839000 | 183168 | 565440 | 2253772 | 2104800 | 84840 | 486500 | 167580 | 3709440 | 413203 | 506836 | 213488 | 7389000 | 0 | 9133000 | 940000 | 0 | 3641318.18 | 69440 | 414792 | 0 | 899520 | 733344 | 1441500 | 0 | 2356050 | 330120 | 1687200 | 1495200 | 324480 | 10300 | 204720 | 124320 | 171460678.15 | 20715636 | 3935232 | 0 | 163200 | 217600 | 0 | 0 | 0 | 0 | 0 | 0 | 606960 | 28043630 | 161616 | 0 | 0 | 18042292 | 0 | 148214 | 0 | 1043712 | 1278624 | 0 | 461968 | 64274 | 144307 | 392952 | 737160 | 131520 | 0 | 333744 | 0 | 0 | 0 | 0 | 4095018 | 0 | 9566327 | 0 | 29820 | 0 | 1204363 | 1403742 | 141542 | 1320595 | 0 | 0 | 0 | 25348.68 | 910800 | 3972 | 132864 | 7047000 | 3042000 | 5394720 | 0 | 0 | 23181090.91 | 1238400 | 135360243.59 | 306820921.74

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 01-04-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13353.99 | MW | 12:00 Hr. | Energy Generated |  |  | 306.8209 |  | MKWHr.
| Day Peak Demand |  |  | 13353.99 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.045 |  | MKWHr.
| Evening Peak Generation |  |  | 14218.9 | MW | 19:00 Hr. | Energy Demand |  |  | 306.8659 |  | MKWHr.
| Evening Peak Demand |  |  | 14218.9 | MW | 19:00 Hr. | Maximum Temperature |  |  | 34.5 |  | °C
| Minimum Generation of the Day |  |  | 10771.09 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 844.52 |  | MMCFD
| Maximum Generation of the Day |  |  | 14218.9 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.6273 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 29.171 | 0 | 10.9001 | 0 | 0 | 0.20164 | 0 | 0 | 40.2728 | Gas | 113.4863 | Gas | 394340452.8744
| Chattogram Zone |  |  | 5.3576 | 50.7327 | 6.7534 | 0 | 1.8974 | 0.12425 | 0 | 0.05184 | 64.9172 | Coal | 110.2088 | Coal | 745899279.4272
| Cumilla Zone |  |  | 25.6514 | 0 | 5.2087 | 0 | 0 | 0.50684 | 3.7094 | 0 | 35.0764 | HFO | 34.4097 | HFO | 590260829.7
| Mymensingh Zone |  |  | 0.32448 | 0 | 3.6368 | 0 | 0 | 0.21502 | 0 | 0 | 4.1763 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.9485 | 0 | 0 | 0 | 0 | 0.06944 | 0 | 0 | 27.018 | Hydro | 1.8974 | Hydro | 189738
| Khulna Zone |  |  | 3.9352 | 28.0436 | 0.54242 | 0 | 0 | 0.60696 | 20.7156 | 0 | 53.8439 | Solar | 4.2995 | Solar | 67222169.566
| Barishal Zone |  |  | 8.4367 | 30.2281 | 1.3713 | 0 | 0 | 0.003972 | 0 | 0 | 40.04 | Import | 42.4674 | Import | 234733357.68
| Rajshahi Zone |  |  | 13.6613 | 0 | 3.2726 | 0 | 0 | 1.4937 | 18.0423 | 0 | 36.4699 | Wind | 0.05184 | Wind | 762566.4
| Rangpur Zone |  |  | 0 | 1.2044 | 2.7243 | 0 | 0 | 1.0777 | 0 | 0 | 5.0064
| Total |  |  | 113.4863 | 110.2088 | 34.4097 | 0 | 1.8974 | 4.2995 | 42.4674 | 0.05184 | 306.8209
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 394340452.8744 |  | Hydro | 189738
|  |  |  | Coal | 745899279.4272 |  | Solar | 67222169.566
|  |  |  | HFO | 590260829.7 |  | Import | 234733357.68
|  |  |  | HSD | 0 |  | Wind | 762566.4
[5 empty] | Total: | 203,34,08,393 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.7156 | Peak Hr Flow | 841.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 33130400 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 18.0423 | Peak Hr Flow | 755.00 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 995 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.7094 | Peak Hr Flow | 184.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1867 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 42.4674 | Peak Hr Flow | 1780.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4662
|  |  |  | Chattogram |  | 0 |  | 1512
|  |  |  | Cumilla |  | 0 |  | 1490
|  |  |  | Mymensingh |  | 0 |  | 966
|  |  |  | Sylhet |  | 0 |  | 508
|  |  |  | Khulna |  | 0 |  | 1901
|  |  |  | Barishal |  | 0 |  | 462
|  |  |  | Rajshahi |  | 0 |  | 1402
|  |  |  | Rangpur |  | 0 |  | 886
|  |  |  | Total |  | 0 |  | 13789
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:38 | 02:02 | Fatullah-Shyampur(New) 132 kV Ckt-2 Tripped from Shyampur 230/132kV end showing 86.1
Operated relays Due to Stormy weather
| 08:38 | 09:04 | Shyampur-Shyampur(New) 132kV Ckt-2 Tripped from Shyampur 230/132kV end showing 86 relay
operated relays Due to Stormy weather
| 08:48 | 09:53 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Shutdown Taken by pdb for redhot | [7 empty] | 60.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 08:48 | 09:50 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Shutdown Taken by pdb for redhot | [7 empty] | 60.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 09:15 | 13:30 | Chauddagram 132/33kV S/S 132 kv T-2 HT Scheduled S/D Due to Leakage repair of NIFPS
valve.
| 09:15 | 13:30 | Chauddagram 132/33kV S/S 132 kv T-2 LT Scheduled S/D Due to Leakage repair of NIFPS
valve.
| 09:18 | 13:24 | Feni 132/33kV S/S T-1(405T) HT Scheduled S/D Due to T-2,132kV GCB Replace work
| 09:20 |  | Kushtia 132/33kV S/S T-3 HT Project Work S/D
| 09:21 |  | Kushtia 132/33kV S/S T-3 LT Project Work S/D
| 09:29 | 13:36 | Chauddagram-Feni 132 kV Ckt-1 Scheduled S/D from Feni 230/132kV end Due to Braker
replacement at Feni 132/33kV Grid end. and from Feni 132/33kV end Due to For T2 132KV
breaker replacement work
| 09:30 | 13:39 | Chauddagram-Feni 132 kV Ckt-2 Scheduled S/D from Feni 230/132kV end Due to Braker
replacement at Feni 132/33kV Grid end. and from Feni 132/33kV end Due to For T2 132KV
breaker replacement work
| 09:35 | 13:57 | Feni 132/33kV S/S Feni-Lanka HFO PS Scheduled S/D Due to For T2 132KV breaker replacement
work
| 09:38 | 17:22 | Bibiyana-Kaliakoir 400 kV Ckt-1 Scheduled S/D from Bibiana 400/230kV end Due to Emergency
Maintenance
| 09:40 | 12:36 | Feni 132/33kV S/S Bus-1 Scheduled S/D Due to For T2 132KV breaker replacement work
| 09:44 | 12:05 | Chandraghona-Rangamati 132 kV Ckt-2 Scheduled S/D from Rangamati 132/33kV end Due to Red
hot temperature maintenance.
| 10:05 | 16:29 | Gopalganj 400/132kV S/S ATR-02 HT Scheduled S/D
| 10:05 | 16:30 | Gopalganj 400/132kV S/S ATR-02 LT Scheduled S/D
| 10:15 | 11:55 | Saidpur 132/33kV S/S TR-01 HT Scheduled S/D Due to QF- GMD-39 and as the instruction of
ALDC Bogura (499264)
| 10:17 | 10:51 | Bashundhara-Tongi 132 kV Ckt-1 Tripped from Tongi 230/132/33kV end showing Distance
Relay, Phase -c(A,B,C), Distance -7 km from Bashundhara End. relays.
| 10:50 | 18:01 | Kachua 230/132/33kV S/S Laksam CKT-2 Project Work S/D Due to DFDR Test.
| 11:01 |  | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-01 LT Scheduled S/D Due to
Maintenance
|  | 11:01 | Chattak-Sylhet 132 kV Ckt-1 is restored.
| 11:01 | 14:50 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-01 HT Scheduled S/D Due to
Maintenance
| 11:28 | 18:24 | Candpur- Kachua 132kV Ckt-1 Scheduled S/D from Chandpur 132/33kV end Due to Due to kachua
ss maintenance work
| 11:40 | 18:24 | Candpur- Kachua 132kV Ckt-1 Project Work S/D from Kachua 230/132/33kV end Due to DFDR
Test.
| 11:49 |  | Kishoreganj 132/33kV S/S Tr-2 (414T) HT Scheduled S/D Due to Transformer Painting work
| 12:00 |  | Day Peak Generation: 13350 MW.
| 12:13 | 14:04 | Narshingdi 132/33kV S/S T-3 LT Scheduled S/D Due to Bus-1 DS Maintennace
| 12:13 | 14:04 | Narshingdi 132/33kV S/S T-3 HT Scheduled S/D Due to Bus-1 DS Maintanance
| 12:13 | 15:15 | Sholosohor 132/33kV S/S TRAFO-02 LT Forced S/D Due to Disk replacement work at 33kV
feeder sholoshahar-2 isolator by BPDB
|  | 12:41 | BIPTC S/S 20DF24 is restored.
|  | 13:24 | Feni 132/33kV S/S T-1(405T) LT is restored.
| 13:36 |  | Kodda 132/33kV S/S Summit 149 MW PS Scheduled S/D Due to Red hot maintenance
| 13:40 | 16:39 | Chauddagram 132/33kV S/S 132 kv T-2 HT Forced S/D Due to 33 kV DS Problem. | [7 empty] | 30.0MW load
interrup.
| 13:40 | 16:39 | Chauddagram 132/33kV S/S 132 kv T-2 LT Forced S/D Due to 33 kV DS Problem. | [7 empty] | 30.0MW load
interrup.
| 14:33 | 15:20 | BIPTC S/S 10CF25 Tripped showing 87 Differential Relay relays Due to Tripped by Capacitor
bank 1 T1 Current Unbalance at B & Y Phase.
| 15:15 | 17:54 | Amtali 400/132kV S/S Amtali - RNPL 400 kV Ckt - 1 Project Work S/D Due to DS problem
| 17:30 | 17:57 | Sirajganj 132/33kV S/S T3-(435) LT Tripped showing O/C Relay R & Y & B Phase relays Due | [7 empty] | 22.0MW load
|  |  | to 33KV T2-T3 Bus Coupler Sky Wire depart or fall on. | [7 empty] | interrup.
| 17:30 | 18:01 | Sirajganj 132/33kV S/S T4-(445) LT Tripped showing O/C R & Y & B Phase relays Due to | [7 empty] | 22.0MW load
|  |  | 33KV T2-T3 Bus Coupler Sky Wire depart or fall on. | [7 empty] | interrup.
| 17:30 | 17:57 | Sirajganj 132/33kV S/S T2-(425) LT Tripped showing O/C IDMT R & Y & B Phase relays Due to | [7 empty] | 20.0MW load
|  |  | 33KV T2-T3 Bus Coupler Sky Wire depart or fall on. | [7 empty] | interrup.
| 17:30 | 17:57 | Sirajganj 132/33kV S/S T1-(415) LT Tripped showing O/C IDMT R & Y Phase relays Due to | [7 empty] | 20.0MW load
|  |  | 33KV T2-T3 Bus Coupler Sky Wire depart or fall on. | [7 empty] | interrup.
| 17:31 | 18:34 | Baghabari-Ullahpara 132 kV Ckt-1 Tripped from Ullahpara 132/33kV end showing REL650 &
REL670 relays Due to Storm and rain
| 17:31 | 18:32 | Shahjadpur-Ullahpara 132kV Ckt-1 Tripped from Ullahpara 132/33kV end showing REL650 &
REL670 relays Due to Storm and Rain
|  | 17:56 | Sirajganj 132/33kV S/S T2-(425) HT is restored.
| 18:03 | 20:18 | Amtali 400/132kV S/S Amtali - RNPL 400 kV Ckt - 2 Project Work S/D Due to DS Checking
| 18:27 | 19:29 | Sirajganj 132/33kV S/S T2-(425) HT Forced S/D Due to 33KV T2-T3 Bus Coupler Sky Wire | [7 empty] | 25.0MW load
|  |  | depart or fall on work | [7 empty] | interrup.
| 18:27 | 19:31 | Sirajganj 132/33kV S/S T3-(435) HT Forced S/D Due to 33KV T2-T3 Bus Coupler Sky Wire | [7 empty] | 25.0MW load
|  |  | depart or fall on work. | [7 empty] | interrup.
| 18:28 | 19:32 | Sirajganj 132/33kV S/S T3-(435) LT Forced S/D Due to 33KV T2-T3 Bus Coupler Sky Wire | [7 empty] | 25.0MW load
|  |  | depart or fall on work. | [7 empty] | interrup.
| 18:28 | 19:29 | Sirajganj 132/33kV S/S T2-(425) LT Forced S/D Due to 33KV T2-T3 Bus Coupler Sky Wire | [7 empty] | 25.0MW load
|  |  | depart or fall on work. | [7 empty] | interrup.
| 19:00 |  | Day peak generation 14218 MW
| 20:13 | 21:28 | Kallyanpur-Lalbag 132kV Ckt-2 Tripped from Kallyanpur 132/33kV end showing Distance
A Aided Trip Main Protection Trip Trip Circuit Supervision Trip-1 Trip Circuit
Supervision Trip-2 relays Due to প্রচন্ড ঝড় বৃষ্ট্রি
| 20:19 |  | Keranigonj 230/132/33kV S/S 132 kV Hasnabad Ckt. 1 Tripped showing 86.1 relays Due to
SOTF trip & Zone -01 trip
| 20:28 | 21:04 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Tripped showing Overcurrent Relay relays Due to | [7 empty] | 31.0MW load
|  |  | O/C | [7 empty] | interrup.
| 20:28 | 21:04 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 LT Tripped showing Overcurrent Relay relays Due to | [7 empty] | 31.0MW load
|  |  | O/C | [7 empty] | interrup.
| 20:28 | 21:20 | Moghbazar-Rampura 132kV Ckt-2 Tripped from Rampura 230/132kV end showing Distance Trip | [7 empty] | 19.0MW load
|  |  | Zone 2 (A & B phase) relays Due to Thunder Storm (Hatirjhil GIS SS) | [7 empty] | interrup. Rampura
230/132kV end
| 20:28 |  | Aggreko-keraniganj 132kV Ckt-1 Tripped from Keranigonj 230/132/33kV end showing 86.1
relays Due to Zone - 3 trip
| 20:54 | 22:27 | Tangail 132/33kV S/S Tr-1 LT Forced S/D Due to 33kv t-1 bus section isolator red hot | [7 empty] | 80.0MW load
interrup.
| 20:55 | 22:26 | Tangail 132/33kV S/S Tr-2 LT Forced S/D Due to 33kv t-1 bus section isolator red hot | [7 empty] | 80.0MW load
interrup.
| 20:55 | 22:26 | Tangail 132/33kV S/S Tr-2 HT Forced S/D Due to 33kv t-1 bus section isolator red hot | [7 empty] | 80.0MW load
interrup.
| 20:56 | 22:26 | Tangail 132/33kV S/S Tr-1 HT Forced S/D Due to 33kv t-1 bus section isolator red hot | [7 empty] | 80.0MW load
interrup.
| 22:50 | 23:37 | Kushtia 132/33kV S/S T-1 LT Forced S/D Due to Red Hot Maintenance of PBS Bus Section | [7 empty] | 60.0MW load
|  |  | Coupler | [7 empty] | interrup.
| 22:51 | 23:36 | Kushtia 132/33kV S/S T-1 HT Forced S/D Due to Red Hot Maintenance of PBS Bus Section | [7 empty] | 60.0MW load
|  |  | Coupler | [7 empty] | interrup.
| 01:19 | 01:33 | Bhaluka 132/33kV S/S 02. Transformer- 02 LT Tripped showing 50/51/50N/51N trip relays Due | [7 empty] | 30.0MW load
|  |  | to Thundering | [7 empty] | interrup.
| 01:19 | 01:33 | Bhaluka 132/33kV S/S 01. Transformer- 01 LT Tripped showing 50/51/50N/51N trip relays Due | [7 empty] | 30.0MW load
|  |  | to Thundering | [7 empty] | interrup.
| 01:40 | 01:58 | Bhaluka 132/33kV S/S 02. Transformer- 02 LT Tripped showing 50/51/50N/51N
trip,df/dt,59(O/V) trip. relays Due to Thundering
| 01:40 | 01:58 | Bhaluka 132/33kV S/S 01. Transformer- 01 LT Tripped showing 50/51/50N/51N
trip,df/dt,59(O/V) trip. relays Due to Thundering
| 05:00 |  | Minimum Generation: 11257 MW.
| 07:12 |  | Baroirhat 132/33kV S/S TR-1, 406T LT Scheduled S/D Due to Maintenance work
| 07:14 |  | Baroirhat 132/33kV S/S TR-1, 406T HT Scheduled S/D Due to Maintenance work
| 07:25 |  | Daudkandi-Sonargaon 132 kV Ckt-1 Scheduled S/D from Sonargaon 132/33kV end Due to OPGW
change purpose Tower No_83 to 85
| 07:57 |  | Dohazari 132/33kV S/S Power Transformer -T-1 LT Tripped showing Siemence Relay relays Due | [7 empty] | 28.0MW load
|  |  | to T-01 Sec. Trip Due to Bashkali 33kv Feeder. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 01-04-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | GBC-3 Under maintenance.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 402 | 9388800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 160 | 4282500 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 896206 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 326 | 5761293 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 25 | 259632 | FGMO
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 122 | 1332000 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 270926 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 251742 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 421800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 395280 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 547402 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 2241622 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 140 | 1496592 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1076774 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 807840 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 201638 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 20 | 250560 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 350 | 8921363.64 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage (BPDB)
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1468800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2239 | 40272770.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 202962.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 104085 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 747360 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1897380 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 5015370 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 102 | 1425163 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 30 | 200894 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 328179 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 518400 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 9 | 342240 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 58 | 283200 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20164 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 49 | 364320 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 20 | 176703 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 79 | 787854 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 534720 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 43 | 536331 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 136 | 647345 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 27845452 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 51840 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 950 | 22887272.73 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 3151.5 | 64917235.33
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 190 | 4839000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 360 | 8342500 | STG Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 345 | 8156000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | FGMO
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 183168 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 140640 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 3000 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1246816 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 127 | 1659345 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 22 | 213488 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 96 | 2253772 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 167 | 2104800 | -
| Import (Tripura) |  | Import | 0 | 160 | 184 | 3709440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 413203 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 486500 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 101 | 167580 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 84840 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 27 | 565440 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 506836 | -
Cumilla Area Total |  |  |  |  | 2872.921 | 1751.2 | 35076368
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 12 | 324480 | Gas shortage
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10300 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 78 | 1495200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1687200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 204720 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 124320 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 330120 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 203 | 4176340
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 69440 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 940000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3641318.18 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 1441500 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 733344 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 899520 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 98 | 2356050 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 23 | 414792 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7389000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 321 | 9133000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1040 | 27017964.18
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 841 | 20715636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 31 | 163200 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 30 | 217600 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 134 | 3935232 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 16 | 161616 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 606960 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1200 | 28043630 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2252 | 53843874
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 132864 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3042000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 900 | 23181090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 180 | 5394720 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1238400 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7047000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3972 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1683 | 40040046.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 392952 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 148214 | 1 unit is under maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 64274 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 154 | 4095018 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 370 | 9566327 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 131520 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 144307 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 67 | 461968 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 1278624 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 80 | 1043712 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 29820 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 755 | 18042292 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 333744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 737160 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1634.2 | 36469932
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 51 | 1204363 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 1320595 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 25348.68 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1403742 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 141542 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 910800 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 265 | 5006390.68
Eastern Grid Total |  |  |  |  | 17419.968 | 8384.7 | 171460678.15
Western Grid Total |  |  |  |  | 11852.195 | 5834.2 | 135360243.59
National Grid Total |  |  |  |  | 29272.163 | 14218.9 | 306820921.74
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 01-04-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9138.87 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4651.34 | MW
i) Dhaka area |  |  | 4662.37 |  | MW | i) Khulna area |  |  |  | 1900.6 | MW
ii) Chattogram area |  |  | 1512.5 |  | MW | ii) Barishal area |  |  |  | 462.34 | MW
iii) Cumilla area |  |  | 1490 |  | MW | iii) Rajshahi area |  |  |  | 1402.4 | MW
iv) Mymensingh area |  |  | 966 |  | MW | iv) Rangpur area |  |  |  | 886 | MW
v) Sylhet area |  |  | 508 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13790.21 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 90 | 20:00 | 133 | Natore | 163 | 19:00
2 | AKSML | 15.6 | 17:00 | 68 | Hathazari | 83 | 15:00 | 134 | Nawabganj | 47.2 | 19:00
3 | Aftabnagar | 36 | 13:00 | 69 | Hatirjheel | 45 | 13:00 | 135 | Netrakona | 117 | 19:00
4 | Agargaon | 124 | 14:00 | 70 | Ishurdi | 73 | 19:30 | 136 | New | 73 | 15:00
5 | Agrabad | 70 | 14:00 | 71 | Jaldhaka | 82 | 23:00 | 137 | Niamatpur | 80 | 19:00
6 | Amnura | 45 | 14:00 | 72 | Jamalpur | 124 | 07:00 | 138 | Noapara | 47 | 19:00
7 | Ashuganj | 93 | 20:00 | 73 | Jashore | 154 | 19:30 | 139 | PHP | 9 | 09:00
8 | BSRM | 200 | 03:00 | 74 | Jhenaidah | 112 | 19:30 | 140 | Pabna | 91 | 20:00
9 | Bagerhat | 87 | 19:00 | 75 | Joydebpur | 158 | 18:30 | 141 | Palashbari | 124 | 19:30
10 | Bajitpur | 78 | 19:00 | 76 | Joypurhat | 73 | 19:00 | 142 | Panchagarh | 47 | 19:30
11 | Bakerganj | 10.84 | 19:00 | 77 | Juldah | 17 | 00:00 | 143 | Patiya | 10.6 | 20:00
12 | Bakulia | 93 | 19:00 | 78 | KSRM | 14 | 00:00 | 144 | Patuakhali | 67 | 22:00
13 | Banani | 41.6 | 13:00 | 79 | Kabirpur | 266 | 15:00 | 145 | Payra | 32 | 22:00
14 | Bangabhaban | 18 | 10:00 | 80 | Kachua | 101 | 20:00 | 146 | Postogola | 48 | 19:00
15 | Barapukuria | 65 | 18:30 | 81 | Kaliganj | 31 | 19:00 | 147 | Pubail | 32 | 18:30
16 | Barguna | 20 | 18:30 | 82 | Kallyanpur | 93 | 18:30 | 148 | Purbachal | 28 | 14:00
17 | Barishal | 105 | 20:00 | 83 | Kalurghat | 49 | 09:00 | 149 | Purbasadipur | 122 | 13:00
18 | Barishal-230 | 100 | 19:00 | 84 | Kamrangirchar | 80 | 13:00 | 150 | Rahanpur | 34 | 21:00
19 | Baroaulia | 69 | 15:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 26 | 12:00
20 | Baroirhat | 66 | 18:30 | 86 | Kasba | 36 | 21:00 | 152 | Rajbari | 86.5 | 19:30
21 | Bashundhara | 168 | 19:00 | 87 | Kazla | 109 | 13:00 | 153 | Rajendrapur | 128 | 18:00
22 | BashundharaCement | 7 | 00:00 | 88 | Keranigonj | 76 | 19:30 | 154 | Rajshahi | 102 | 19:00
23 | Beanibazar | 58 | 18:30 | 89 | Khagrachori | 32 | 19:00 | 155 | Rajshahi-230 | 98 | 13:00
24 | Benapole | 78 | 13:00 | 90 | Khulna | 61 | 16:00 | 156 | Ramganj | 112 | 18:30
25 | Bhaluka | 144 | 18:30 | 91 | Khulshi | 187 | 19:00 | 157 | Rampur | 40 | 18:30
26 | Bhandaria | 53 | 22:00 | 92 | Kishoreganj | 123 | 19:00 | 158 | Rangamati | 20 | 18:30
27 | Bhangura | 38 | 13:00 | 93 | Kodda | 326 | 18:00 | 159 | Rangpur | 136 | 19:00
28 | Bheramara(GK) | 73 | 19:00 | 94 | Kulaura | 32 | 19:30 | 160 | Ruppur | 4.4 | 11:00
29 | Bhulta | 197 | 11:00 | 95 | Kurigram | 52 | 18:30 | 161 | SSM | 11 | 07:00
30 | Bog-Sherpur | 76 | 15:00 | 96 | Kushtia | 130 | 19:00 | 162 | Saidpur | 98 | 19:00
31 | Bogura | 173 | 19:30 | 97 | Laksam | 23 | 22:00 | 163 | Satkhira | 143 | 19:00
32 | Borhanuddin | 93 | 23:00 | 98 | Lakshmipur | 41 | 22:00 | 164 | Satmasjid | 98 | 14:00
33 | Brahmanbaria | 124 | 19:00 | 99 | Lalbag | 67 | 13:00 | 165 | Savar | 202 | 15:00
34 | Cantonment | 152 | 19:00 | 100 | Lalmonirhat | 52 | 18:30 | 166 | SevenRings | 18.07 | 19:00
35 | Chandina | 24 | 14:00 | 101 | MI_Cement | 8.4 | 22:00 | 167 | ShahCement | 41 | 23:00
36 | Chandpur | 84 | 19:00 | 102 | Madanganj | 41 | 19:30 | 168 | Shahjadpur | 66 | 08:00
37 | Chandraghona | 38 | 19:00 | 103 | Madaripur | 118 | 22:00 | 169 | Shahjibazar | 115 | 19:00
38 | Chapai | 70 | 22:00 | 104 | Madartek | 74 | 22:00 | 170 | Shahmirpur | 53 | 18:00
39 | Charsaidpur | 40 | 00:00 | 105 | Madunaghat | 63 | 19:00 | 171 | Shariatpur | 89 | 21:00
40 | Chauddagram | 85 | 18:00 | 106 | Magura | 72 | 18:30 | 172 | Sherpur | 124 | 18:30
41 | Chhatak | 33 | 19:30 | 107 | Mahasthangarh | 78 | 19:00 | 173 | Shikalbaha | 24.5 | 00:00
42 | Chowmuhani | 146 | 19:00 | 108 | Maijdee | 48 | 22:00 | 174 | Shitalakhya | 76.5 | 16:00
43 | Chuadanga | 126 | 19:00 | 109 | Manikganj | 126 | 19:30 | 175 | Sholosohor | 48 | 19:00
44 | Coxsbazar | 143 | 19:30 | 110 | Maniknagar | 71 | 13:00 | 176 | Shyampur | 148 | 11:00
45 | Cumilla(N) | 113 | 21:00 | 111 | Matarbari | 56 | 20:00 | 177 | Siddhirganj | 122 | 12:00
46 | Cumilla(S) | 183 | 18:30 | 112 | Matuail | 58 | 15:00 | 178 | Sirajganj | 98 | 13:00
47 | Daganbhuiyan | 40 | 19:00 | 113 | Metrorail_Motijheel | 20 | 14:00 | 179 | Sonargaon | 149 | 18:30
48 | Daudkandi | 139 | 19:30 | 114 | Metrorail_Uttara | 0 | 23:00 | 180 | Sreemongol | 65 | 19:00
49 | DhakaUniversity | 68 | 13:00 | 115 | Millgate | 95 | 15:00 | 181 | Sreepur | 117 | 18:00
50 | Dhamrai | 126 | 08:00 | 116 | Mirpur | 136 | 19:00 | 182 | Srinagar | 48.6 | 22:00
51 | Dhanmondi | 120.7 | 13:00 | 117 | Mirsorai | 48 | 05:00 | 183 | Sunamganj | 51 | 22:00
52 | Dohazari | 113 | 20:00 | 118 | Mirzapur | 52 | 13:00 | 184 | Sylhet | 49 | 14:00
53 | Faridpur | 169 | 21:00 | 119 | Mithapukur | 59 | 19:00 | 185 | Sylhet-132 | 91 | 14:00
54 | Fatullah | 104 | 16:00 | 120 | Modern | N/A | N/A | 186 | TK | 21 | 18:30
55 | Fenchuganj | 36 | 18:30 | 121 | Mogbazar | 56.4 | 15:00 | 187 | Tangail | 168 | 14:00
56 | Feni | 98 | 18:30 | 122 | Mongla | 49 | 21:00 | 188 | Taraganj | 24 | 18:30
57 | GPH | 19 | 09:00 | 123 | Motijheel | 46 | 13:00 | 189 | Tasnim | 26 | 09:00
58 | Ghatail | 98 | 17:00 | 124 | Muktagacha | 38 | 14:00 | 190 | Thakurgaon | 99 | 19:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 120 | 19:30 | 191 | Tongi | 139 | 11:00
60 | Ghorashal-230 | 106 | 18:30 | 126 | Muradnagar | 48 | 19:00 | 192 | Ullahpara | 38 | 12:00
61 | Goalpara | 39 | 19:00 | 127 | Mymensingh | 188 | 19:00 | 193 | Ullon | 62 | 19:00
62 | Gollamari | 106 | 19:00 | 128 | Nabinagar | 17 | 15:00 | 194 | Uttara | 80 | 16:00
63 | Gopalganj | 112 | 22:00 | 129 | Naogaon | 122 | 13:00 | 195 | UttaraNew | 29 | 13:00
64 | Gulshan | 122 | 13:00 | 130 | Narail | 63 | 19:00 | 196 | Zigatola | 88 | 15:00
65 | Halishahar | 100 | 16:00 | 131 | Narinda | 69 | 13:00
66 | HaripurSBU | 122 | 16:00 | 132 | Narshingdi | 175 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 01-04-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 12589.76 | 0 |  | 12589.76
1:00 | 12032.61 | 0 |  | 12032.61
2:00 | 11628.83 | 0 |  | 11628.83
3:00 | 11311.79 | 0 |  | 11311.79
4:00 | 10994.48 | 0 |  | 10994.48
5:00 | 10823.64 | 0 |  | 10823.64
6:00 | 10771.09 | 0 |  | 10771.09
7:00 | 11409.27 | 0 |  | 11409.27
8:00 | 11778.72 | 0 |  | 11778.72
9:00 | 11892.74 | 0 |  | 11892.74
10:00 | 12368.62 | 0 |  | 12368.62
11:00 | 12742.05 | 0 |  | 12742.05
12:00 | 13353.99 | 0 |  | 13353.99
13:00 | 13888.79 | 0 |  | 13888.79
14:00 | 13970.93 | 0 |  | 13970.93
15:00 | 14123.53 | 0 |  | 14123.53
16:00 | 13913.5 | 0 |  | 13913.5
17:00 | 13426.22 | 45 |  | 13473.22
18:00 | 13359.46 | 0 |  | 13359.46
19:00 | 14218.9 | 0 |  | 14218.9
19:30 | 14036.56 | 0 |  | 14036.56
20:00 | 13859 | 0 |  | 13859
21:00 | 12995 | 0 |  | 12995
22:00 | 13261 | 0 |  | 13261
23:00 | 13468 | 0 |  | 13468
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 01-04-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6920 | 5669.76 | 12589.76 | DAILY GENERATION CURVE
00:30 | 6700 | 5611.185 | 12311.185
01:00 | 6480 | 5552.61 | 12032.61 | 01-04-2026
01:30 | 6302.5 | 5528.22 | 11830.72
02:00 | 6125 | 5503.83 | 11628.83
02:30 | 6104 | 5366.31 | 11470.31
03:00 | 6083 | 5228.79 | 11311.79
03:30 | 6020.5 | 5132.635 | 11153.135
04:00 | 5958 | 5036.48 | 10994.48
04:30 | 5960.5 | 4948.56 | 10909.06
05:00 | 5963 | 4860.64 | 10823.64
05:30 | 5956.5 | 4840.865 | 10797.365
06:00 | 5950 | 4821.09 | 10771.09
06:30 | 6125.31 | 4964.87 | 11090.18
07:00 | 6300.62 | 5108.65 | 11409.27
07:30 | 6389.635 | 5204.36 | 11593.995
08:00 | 6478.65 | 5300.07 | 11778.72
08:30 | 6503.75 | 5331.98 | 11835.73
09:00 | 6528.85 | 5363.89 | 11892.74
09:30 | 6678.725 | 5451.955 | 12130.68
10:00 | 6828.6 | 5540.02 | 12368.62
10:30 | 6933.545 | 5621.79 | 12555.335
11:00 | 7038.49 | 5703.56 | 12742.05
11:30 | 7224.855 | 5823.165 | 13048.02
12:00 | 7411.22 | 5942.77 | 13353.99
12:30 | 7567.37 | 6054.02 | 13621.39
13:00 | 7723.52 | 6165.27 | 13888.79
13:30 | 7754.41 | 6175.45 | 13929.86
14:00 | 7785.3 | 6185.63 | 13970.93
14:30 | 7900.07 | 6147.16 | 14047.23
15:00 | 8014.84 | 6108.69 | 14123.53
15:30 | 8010.06 | 6008.455 | 14018.515
16:00 | 8005.28 | 5908.22 | 13913.5
16:30 | 7901.095 | 5768.765 | 13669.86
17:00 | 7796.91 | 5629.31 | 13426.22
17:30 | 7839.01 | 5553.83 | 13392.84
18:00 | 7881.11 | 5478.35 | 13359.46
18:30 | 8132.905 | 5656.275 | 13789.18
19:00 | 8384.7 | 5834.2 | 14218.9
19:30 | 8148.16 | 5888.4 | 14036.56
20:00 | 8057.8 | 5801.2 | 13859
20:30 | 7736.4 | 5690.6 | 13427 |  | Executive Engineer
21:00 | 7415 | 5580 | 12995 |  | Network Operation Division
21:30 | 7494.5 | 5633.5 | 13128
22:00 | 7574 | 5687 | 13261
22:30 | 7648 | 5716.5 | 13364.5
23:00 | 7722 | 5746 | 13468

## En-Curve
QF-LDC-12
Date | 01-04-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3223 | 1493 | 861 | 0 | 144 | 759.56 | 80 | 4915.2 | 0 | 130 | 984 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3248 | 1479.5 | 864.5 | 0 | 136 | 756.485 | 80 | 4917.2 | 0 | 98.5 | 729.5 | 0 | 0 | 1.5 | 0 | 01-04-2026
01:00 | 3273 | 1466 | 868 | 0 | 128 | 753.41 | 80 | 4919.2 | 0 | 67 | 475 | 0 | 0 | 3 | 0
01:30 | 3259 | 1460.5 | 868.5 | 0 | 127 | 755.02 | 80 | 4917.7 | 0 | 33.5 | 327.5 | 0 | 0 | 2 | 0 | Energy Generated | 306.8209 |  | MKWHr
02:00 | 3245 | 1455 | 869 | 0 | 126 | 756.63 | 80 | 4916.2 | 0 | 0 | 180 | 0 | 0 | 1 | 0 | Energy not Served | 0.045 |  | MKWHr
02:30 | 3260 | 1465 | 869 | 0 | 128 | 756.71 | 80 | 4741.1 | 0 | 0 | 170 | 0 | 0 | 0.5 | 0 | Total Energy Requirement | 306.8659 |  | MKWHr
03:00 | 3275 | 1475 | 869 | 0 | 130 | 756.79 | 80 | 4566 | 0 | 0 | 160 | 0 | 0 | 0 | 0
03:30 | 3269 | 1439.5 | 869 | 0 | 127 | 758.635 | 80 | 4449.5 | 0 | 0 | 160.5 | 0 | 0 | 0 | 0
04:00 | 3263 | 1404 | 869 | 0 | 124 | 760.48 | 80 | 4333 | 0 | 0 | 161 | 0 | 0 | 0 | 0
04:30 | 3312 | 1410.5 | 868.5 | 0 | 124 | 713.06 | 80 | 4262 | 0 | 0 | 139 | 0 | 0 | 0 | 0
05:00 | 3361 | 1417 | 868 | 0 | 124 | 665.64 | 80 | 4191 | 0 | 0 | 117 | 0 | 0 | 0 | 0
05:30 | 3391 | 1380.5 | 868 | 0 | 122 | 664.365 | 80 | 4174.5 | 0 | 0 | 117 | 0 | 0 | 0 | 0
06:00 | 3421 | 1344 | 868 | 0 | 120 | 663.09 | 80 | 4158 | 0 | 0 | 117 | 0 | 0 | 0 | 0
06:30 | 3448 | 1344.5 | 868 | 0 | 118 | 707.78 | 80 | 4312.5 | 21.4 | 41 | 149 | 0 | 0 | 0 | 0
07:00 | 3475 | 1345 | 868 | 0 | 116 | 752.47 | 80 | 4467 | 42.8 | 82 | 181 | 0 | 0 | 0 | 0
07:30 | 3487 | 1342 | 868 | 0 | 125 | 757.545 | 80 | 4532.6 | 88.85 | 88.5 | 224.5 | 0 | 0 | 0 | 0
08:00 | 3499 | 1339 | 868 | 0 | 134 | 762.62 | 80 | 4598.2 | 134.9 | 95 | 268 | 0 | 0 | 0 | 0
08:30 | 3403 | 1313 | 868 | 0 | 136 | 759.31 | 80 | 4589.6 | 194.82 | 115 | 377 | 0 | 0 | 0 | 0
09:00 | 3307 | 1287 | 868 | 0 | 138 | 756 | 80 | 4581 | 254.74 | 135 | 486 | 0 | 0 | 0 | 0
09:30 | 3372 | 1282 | 868.5 | 0 | 143 | 760 | 80 | 4555 | 337.68 | 131 | 601.5 | 0 | 0 | 0 | 0
10:00 | 3437 | 1277 | 869 | 0 | 148 | 764 | 80 | 4529 | 420.62 | 127 | 717 | 0 | 0 | 0 | 0
10:30 | 3466.5 | 1314.5 | 868.5 | 0 | 152 | 759.5 | 77.5 | 4547 | 521.335 | 127 | 721.5 | 0 | 0 | 0 | 0
11:00 | 3496 | 1352 | 868 | 0 | 156 | 755 | 75 | 4565 | 622.05 | 127 | 726 | 0 | 0 | 0 | 0
11:30 | 3474 | 1348 | 868 | 0 | 156 | 759.5 | 75 | 4564 | 645.02 | 152.5 | 1004 | 0 | 0 | 2 | 0
12:00 | 3452 | 1344 | 868 | 0 | 156 | 764 | 75 | 4563 | 667.99 | 178 | 1282 | 0 | 0 | 4 | 0
12:30 | 3373.5 | 1339 | 868 | 0 | 167 | 764.5 | 73 | 4585.1 | 659.29 | 237 | 1548.5 | 0 | 0 | 6.5 | 0
13:00 | 3295 | 1334 | 868 | 0 | 178 | 765 | 71 | 4607.2 | 650.59 | 296 | 1815 | 0 | 0 | 9 | 0
13:30 | 3268.5 | 1364.5 | 868 | 0 | 174 | 763.5 | 73 | 4582.7 | 640.41 | 334 | 1852.25 | 0 | 0 | 9 | 0
14:00 | 3242 | 1395 | 868 | 0 | 170 | 762 | 75 | 4558.2 | 630.23 | 372 | 1889.5 | 0 | 0 | 9 | 0
14:30 | 3242 | 1432.5 | 868 | 0 | 176 | 762 | 75 | 4597.7 | 550.53 | 390 | 1945 | 0 | 0 | 8.5 | 0
15:00 | 3242 | 1470 | 868 | 0 | 182 | 762 | 75 | 4637.2 | 470.83 | 408 | 2000.5 | 0 | 0 | 8 | 0
15:30 | 3254.5 | 1460.5 | 868 | 0 | 179 | 764.5 | 75 | 4641.2 | 364.715 | 418.5 | 1984.6 | 0 | 0 | 8 | 0
16:00 | 3267 | 1451 | 868 | 0 | 176 | 767 | 75 | 4645.2 | 258.6 | 429 | 1968.7 | 0 | 0 | 8 | 0
16:30 | 3256.5 | 1422.5 | 868 | 0 | 171 | 760.5 | 75 | 4545.1 | 185.06 | 457.5 | 1920.2 | 0 | 0 | 8.5 | 22.5
17:00 | 3246 | 1394 | 868 | 0 | 166 | 754 | 75 | 4445 | 111.52 | 486 | 1871.7 | 0 | 0 | 9 | 45
17:30 | 3191.5 | 1379 | 855 | 0 | 169 | 755 | 77.5 | 4400 | 60.14 | 573.5 | 1926.7 | 0 | 0 | 5.5 | 22.5
18:00 | 3137 | 1364 | 842 | 0 | 172 | 756 | 80 | 4355 | 8.76 | 661 | 1981.7 | 0 | 0 | 2 | 0
18:30 | 3183.5 | 1361.5 | 841.5 | 0 | 178 | 755.5 | 80 | 4461.5 | 4.38 | 690.5 | 2231.8 | 0 | 0 | 1 | 0
19:00 | 3230 | 1359 | 841 | 0 | 184 | 755 | 80 | 4568 | 0 | 720 | 2481.9 | 0 | 0 | 0 | 0
19:30 | 3225 | 1331 | 842 | 0 | 178 | 757 | 80 | 4602.2 | 0 | 595 | 2426.36 | 0 | 0 | 0 | 0
20:00 | 3285 | 1388 | 842 | 0 | 176 | 763 | 80 | 4602.2 | 0 | 535 | 2187.8 | 0 | 0 | 0 | 0
20:30 | 3339.5 | 1436.5 | 841.5 | 0 | 175 | 762 | 80 | 4601.6 | 0 | 471.5 | 1719.4 | 0 | 0 | 0 | 0
21:00 | 3394 | 1485 | 841 | 0 | 174 | 761 | 80 | 4601 | 0 | 408 | 1251 | 0 | 0 | 0 | 0
21:30 | 3375 | 1496.5 | 841 | 0 | 174 | 761.5 | 80 | 4630.5 | 0 | 440 | 1329.5 | 0 | 0 | 0 | 0
22:00 | 3356 | 1508 | 841 | 0 | 174 | 762 | 80 | 4660 | 0 | 472 | 1408 | 0 | 0 | 0 | 0
22:30 | 3348.5 | 1480.5 | 841.5 | 0 | 176 | 760.5 | 80 | 4656 | 0 | 477 | 1544.5 | 0 | 0 | 0 | 0
23:00 | 3341 | 1453 | 842 | 0 | 178 | 759 | 80 | 4652 | 0 | 482 | 1681 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 01-04-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 394 | 20:00 | 377 | 11:00 | Madunaghat | 402 | 20:00 | 393 | 12:00
Amtali | 414 | 04:00 | 409 | 11:00 | Meghnaghat | 398 | 05:00 | 383 | 11:00
Ashuganj | 404 | 05:00 | 392 | 11:00 | Payra | 416 | 05:00 | 410 | 11:00
Bhulta | 393 | 05:00 | 371 | 11:00 | Rahanpur | 408 | 05:00 | 397 | 08:00
Bibiana | 407 | 19:00 | 401 | 09:00 | Rampal | 407 | 05:00 | 394 | 13:00
BIPTC | 399 | 03:00 | 389 | 14:00
Bogura | 403 | 05:00 | 391 | 08:00
Gopalganj | 404 | 05:00 | 392 | 11:00
Kaliakoir | 392 | 20:00 | 366 | 11:00
Korerhat | 405 | 19:00 | 392 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 21:00 | 217 | 11:00 | Jhenaidah | 229 | 05:00 | 215 | 19:00
AKSML | 240 | 19:00 | 230 | 11:00 | Kachua | 231 | 18:00 | 224 | 11:00
Aminbazar | 230 | 05:00 | 218 | 11:00 | Kaliakoir | 236 | 20:00 | 220 | 11:00
Ashuganj | 230 | 05:00 | 221 | 11:00 | Keranigonj | 229 | 21:00 | 216 | 11:00
Ashuganj-400 | 230 | 05:00 | 221 | 11:00 | Khulna(S) | 232 | 05:00 | 219 | 19:30
Baghabari | 233 | 05:00 | 226 | 07:00 | Korerhat | 231 | 19:00 | 223 | 11:00
Barapukuria | 228 | 23:00 | 213 | 07:00 | Madunaghat | 241 | 19:30 | 233 | 11:00
Barapukuria-230 | 228 | 23:00 | 213 | 07:00 | Madunaghat-400 | 241 | 20:00 | 234 | 12:00
Barishal | 229 | 18:00 | 224 | 00:00 | Maniknagar | 225 | 06:00 | 213 | 11:00
Bheramara | 230 | 05:00 | 221 | 11:00 | Meghnaghat | 233 | 03:00 | 221 | 11:00
Bhulta | 226 | 05:00 | 214 | 11:00 | Meghnaghat-400 | 227 | 05:00 | 216 | 11:00
Bibiana | 236 | 04:00 | 230 | 12:00 | Mirsorai | 238 | 19:00 | 228 | 11:00
BIPTC | 233 | 18:00 | 222 | 00:00 | Purbasadipur | 228 | 12:00 | 211 | 08:00
Bogura | 232 | 05:00 | 224 | 08:00 | Rajshahi | 229 | 18:00 | 219 | 00:00
Bogura-400 | 232 | 05:00 | 224 | 08:00 | Rampal | 232 | 05:00 | 220 | 13:00
Borhanuddin | 233 | 05:00 | 230 | 00:00 | Rampur | N/A | N/A | N/A | N/A
BSRM | 231 | 19:00 | 224 | 11:00 | Rampura | 226 | 06:00 | 214 | 11:00
Chowmuhani | 230 | 19:00 | 223 | 11:00 | Shikalbaha | 240 | 19:00 | 231 | 11:00
Cumilla(N) | 227 | 05:00 | 219 | 11:00 | Shyampur | 229 | 21:00 | 215 | 11:00
Faridpur | 228 | 14:00 | 218 | 12:00 | Siddhirganj | 226 | 19:30 | 218 | 13:00
Fenchuganj | 238 | 08:00 | 234 | 15:00 | Sirajgonj | 237 | 05:00 | 231 | 11:00
Feni | 230 | 06:00 | 223 | 11:00 | Sreepur | 228 | 23:00 | 219 | 11:00
Ghorashal | 230 | 00:00 | 222 | 14:00 | Tongi | 232 | 18:30 | 218 | 11:00
Ghorashal-230 | 227 | 05:00 | 215 | 11:00
Gopalganj | 225 | 05:00 | 218 | 11:00
GPH | 237 | 19:00 | 229 | 11:00
Haripur | 226 | 05:00 | 212 | 18:00
Hasnabad | 229 | 21:00 | 216 | 12:00
Hathazari | 238 | 19:00 | 230 | 12:00
Ishurdi | 233 | 05:00 | 225 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 04:00 | 125 | 11:00 | Madunaghat | 139 | 18:00 | 135 | 01:00
Agargaon | 136 | 04:00 | 126 | 11:00 | Magura | 130 | 06:00 | 116 | 19:00
Agrabad | 137 | 18:00 | 132 | 01:00 | Mahasthangarh | 132 | 04:00 | 124 | 08:00
AKS | 135 | 18:00 | 130 | 08:00 | Maijdee | 128 | 18:00 | 124 | 11:00
Aminbazar | 132 | 04:00 | 123 | 11:00 | Manikganj | 130 | 04:00 | 120 | 11:00
Amnura | 135 | 18:00 | 126 | 11:00 | Maniknagar | 133 | 06:00 | 123 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 119 | 13:00 | 112 | 02:00
Ashuganj-230 | 137 | 04:00 | 135 | 10:00 | Matuail | 133 | 21:00 | 125 | 11:00
Bagerhat | 127 | 05:00 | 116 | 13:00 | Metrorail_Motijheel | 132 | 04:00 | 123 | 12:00
Bajitpur | 133 | 05:00 | 129 | 11:00 | Metrorail_Uttara | 131 | 04:00 | 120 | 11:00
Bakerganj | 137 | 18:00 | 129 | 11:00 | Millgate | 134 | 05:00 | 124 | 11:00
Bakulia | 138 | 20:00 | 133 | 12:00 | Mirpur | 133 | 21:00 | 121 | 11:00
Banani | 134 | 04:00 | 124 | 11:00 | Mirzapur | 136 | 19:30 | 118 | 15:00
Bangabhaban | 133 | 21:00 | 123 | 13:00 | Mithapukur | 132 | 06:00 | 121 | 08:00
Barapukuria | 159 | 14:00 | 25 | 18:00 | MI_Cement | 132.5 | 21:00 | 120 | 11:00
Barguna | 137 | 18:00 | 129 | 11:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 134 | 18:00 | 128 | 12:00 | Mogbazar | 135 | 03:00 | 125 | 12:00
Barishal-230 | 134 | 18:00 | 129 | 00:00 | Mongla | 128 | 04:00 | 116 | 13:00
Baroaulia | 137 | 20:00 | 132 | 11:00 | Motijheel | 133 | 21:00 | 123 | 13:00
Baroirhat | 132 | 18:00 | 128 | 11:00 | Muktagacha | 133 | 19:30 | 115 | 13:00
Bashundhara | 134 | 05:00 | 123 | 11:00 | Munshiganj | 131 | 21:00 | 124 | 12:00
BashundharaCement | 133 | 20:00 | 126 | 12:00 | Muradnagar | 128 | 05:00 | 122 | 12:00
Beanibazar | 132 | 10:00 | 127 | 13:00 | Mymensingh | 133 | 23:00 | 113 | 13:00
Benapole | 130 | 05:00 | 110 | 22:00 | Nabinagar | 137 | 19:00 | 121 | 11:00
Bhaluka | 136 | 23:00 | 125 | 12:00 | Naogaon | 135 | 05:00 | 122 | 08:00
Bhandaria | 130 | 06:00 | 124 | 12:00 | Narail | 130 | 06:00 | 115 | 19:30
Bhangura | 132 | 05:00 | 127 | 07:00 | Narinda | 0 | 00:00 | N/A | N/A
Bheramara | 134 | 05:00 | 130 | 00:00 | Narshingdi | 128 | 19:30 | 121 | 21:00
Bheramara(GK) | 137 | 02:00 | 129 | 00:00 | Natore | 138 | 12:00 | 126 | 08:00
Bhulta | 127 | 03:00 | 120 | 11:00 | Nawabganj | 134 | 05:00 | 125 | 11:00
Bog-Sherpur | 133 | 05:00 | 127 | 08:00 | Netrakona | 133 | 09:00 | 120 | 18:30
Bogura | 134 | 05:00 | 128 | 08:00 | New | 136 | 20:00 | 125 | 11:00
Bogura-230 | 135 | 23:00 | 128 | 08:00 | Niamatpur | 136 | 02:00 | 132 | 07:00
Brahmanbaria | 130 | 05:00 | 125 | 11:00 | Noapara | 130 | 04:00 | 118 | 13:00
Cantonment | 136 | 21:00 | 125 | 11:00 | Pabna | 133 | 05:00 | 128 | 01:00
Chandina | 132 | 06:00 | 127 | 11:00 | Palashbari | 129 | 23:00 | 119 | 08:00
Chandpur | 133 | 19:00 | 127 | 01:00 | Panchagarh | 137 | 13:00 | 126 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 139 | 19:00 | 134 | 12:00 | Patiya | 137 | 20:00 | 130 | 13:00
Chapai | 135 | 05:00 | 130 | 08:00 | Patuakhali | 135 | 16:00 | 129 | 11:00
Charsaidpur | 133 | 21:00 | 126 | 11:00 | Payra | 137 | 18:00 | 133 | 00:00
Chauddagram | 129 | 05:00 | 124 | 11:00 | PHP | 131 | 06:00 | 126 | 03:00
Chhatak | 133 | 06:00 | 126 | 00:00 | Postogola | 134 | 21:00 | 122 | 12:00
Chowmuhani | 128 | 18:00 | 124 | 11:00 | Pubail | 140 | 19:00 | 127 | 11:00
Chuadanga | 130 | 06:00 | 114 | 19:00 | Purbachal | 134 | 04:00 | 123 | 11:00
Coxsbazar | 118 | 20:00 | 113 | 00:00 | Purbasadipur | 133 | 23:00 | 121 | 08:00
Cumilla(N) | 131 | 06:00 | 126 | 12:00 | Rahanpur | 136 | 03:00 | 133 | 10:00
Cumilla(S) | 131 | 18:00 | 121 | 15:00 | Rahanpur-400 | 137 | 05:00 | 133 | 08:00
Daganbhuiyan | 129 | 05:00 | 125 | 12:00 | Rahim | 132 | 21:00 | 126 | 11:00
Daudkandi | 125 | 05:00 | 119 | 11:00 | Rajbari | 129 | 05:00 | 123 | 13:00
DhakaUniversity | 134 | 05:00 | 125 | 11:00 | Rajendrapur | 135 | 23:00 | 125 | 12:00
Dhamrai | 137 | 20:00 | 121 | 11:00 | Rajshahi | 131 | 02:00 | 125 | 13:00
Dhanmondi | 134.5 | 05:00 | 126.4 | 11:00 | Rajshahi-230 | 132 | 18:00 | 126 | 00:00
Dohazari | 132 | 18:00 | 126 | 04:00 | Ramganj | 128 | 18:00 | 125 | 11:00
Faridpur | 130 | 04:00 | 125 | 12:00 | Rampur | 138 | 20:00 | 132 | 10:00
Fatullah | 132 | 21:00 | 121 | 11:00 | Rampura | 134 | 05:00 | 125 | 11:00
Fenchuganj | 135 | 07:00 | 132 | 15:00 | Rangamati | 137 | 01:00 | 133 | 11:00
Feni | 129 | 19:00 | 125 | 11:00 | Rangpur | 132 | 04:00 | 123 | 08:00
Feni-230 | 129 | 04:00 | 125 | 11:00 | Ruppur | 134 | 04:00 | 130 | 00:00
Ghatail | 132 | 19:30 | 114 | 15:00 | Saidpur | 131 | 23:00 | 123 | 08:00
Ghorashal | 139 | 19:00 | 131 | 10:00 | Satkhira | 129 | 05:00 | 115 | 19:00
Goalpara | 132 | 05:00 | 122 | 13:00 | Satmasjid | 135 | 04:00 | 125 | 11:00
Gollamari | 132 | 05:00 | 123 | 01:00 | Savar | 133 | 20:00 | 120 | 11:00
Gopalganj | 131 | 05:00 | 124 | 13:00 | SevenRings | 139 | 19:00 | 130 | 11:00
Gopalganj-400 | 134 | 06:00 | 128 | 11:00 | ShahCement | 133 | 21:00 | 126 | 11:00
Gulshan | 133 | 04:00 | 125 | 11:00 | Shahjadpur | 137 | 18:00 | 132 | 10:00
Halishahar | 138 | 19:00 | 132 | 12:00 | Shahjibazar | 130 | 09:00 | 126 | 11:00
Haripur | 133 | 21:00 | 126 | 11:00 | Shahmirpur | 139 | 19:30 | 134 | 12:00
HaripurSBU | 132 | 06:00 | 126 | 11:00 | Shariatpur | 132 | 05:00 | 126 | 11:00
Hasnabad | 133 | 03:00 | 122 | 11:00 | Sherpur | 130 | 19:30 | 115 | 13:00
Hathazari | 138 | 03:00 | 134 | 01:00 | Shikalbaha | 128 | 09:00 | 122 | 12:00
Hatirjheel | 134 | 04:00 | 125 | 11:00 | Shikalbaha-230 | 140 | 19:30 | 134 | 02:00
Ishurdi | 135 | 05:00 | 131 | 00:00 | Shitalakhya | 132.5 | 21:00 | 120 | 11:00
Jaldhaka | 130 | 23:00 | 118 | 08:00 | Sholosohor | 138 | 18:00 | 134 | 10:00
Jamalpur | 133 | 19:30 | 117 | 15:00 | Shyampur | 132 | 22:00 | 121 | 11:00
Jashore | 131 | 06:00 | 113 | 22:00 | Shyampur-230 | 133 | 11:00 | 124 | 12:00
Jhenaidah | 132 | 06:00 | 120 | 19:30 | Siddhirganj | 132 | 21:00 | 125 | 11:00
Jhenaidah-230 | 133 | 05:00 | 120 | 19:30 | Sirajganj | 132 | 18:00 | 126 | 11:00
Joydebpur | 139 | 19:00 | 124 | 11:00 | Sonargaon | 129 | 04:00 | 123 | 12:00
Joypurhat | 128 | 05:00 | 119 | 08:00 | Sreemongol | 131 | 06:00 | 127 | 12:00
Juldah | 139 | 19:00 | 133 | 10:00 | Sreepur | 137 | 23:00 | 130 | 10:00
Kabirpur | 140 | 19:30 | 121 | 15:00 | Srinagar | 134 | 21:00 | 125 | 12:00
Kachua | 131 | 18:00 | 127 | 15:00 | SSM | 140 | 00:00 | 138 | 10:00
Kaliakoir | 139 | 19:30 | 124 | 15:00 | Sunamganj | 131 | 12:00 | 124 | 17:00
Kaliganj | 132 | 06:00 | 118 | 19:30 | Sylhet | 132 | 07:00 | 128 | 15:00
Kallyanpur | 132 | 21:00 | 123 | 11:00 | Sylhet-132 | 132 | 07:00 | 128 | 15:00
Kalurghat | 139 | 18:00 | 134 | 11:00 | Tangail | 134 | 19:30 | 114 | 15:00
Kamrangirchar | 135 | 21:00 | 120 | 11:00 | Taraganj | 131 | 23:00 | 119 | 08:00
Kaptai | N/A | N/A | N/A | N/A | Tasnim | 132 | 21:00 | 123 | 12:00
Kasba | 128 | 05:00 | 121 | 11:00 | Thakurgaon | 138 | 23:00 | 123 | 08:00
Kazla | 133 | 21:00 | 123 | 13:00 | TK | 139 | 20:00 | 134 | 11:00
Keranigonj | 135 | 21:00 | 126 | 11:00 | Tongi | 136 | 19:30 | 128 | 11:00
Khagrachori | 137 | 06:00 | 132 | 11:00 | Ullahpara | 133 | 05:00 | 127 | 08:00
Khulna | 132 | 05:00 | 121 | 13:00 | Ullon | 134 | 04:00 | 125 | 11:00
Khulna(S) | 133 | 05:00 | 123 | 13:00 | Uttara | 132 | 21:00 | 122 | 11:00
Khulshi | 136 | 18:00 | 131 | 12:00 | UttaraNew | 133 | 21:00 | 120 | 11:00
Kishoreganj | 133 | 04:00 | 125 | 18:30 | Zigatola | 136 | 21:00 | 125 | 13:00
Kodda | 141 | 19:00 | 119 | 15:00
Korerhat | 134 | 04:00 | 129 | 11:00
KSRM | 138 | 18:00 | 132 | 12:00
Kulaura | 134 | 05:00 | 131 | 15:00
Kurigram | 130 | 02:00 | 118 | 08:00
Kushtia | 131 | 05:00 | 126 | 00:00
Laksam | 131 | 19:00 | 127 | 11:00
Lakshmipur | 127 | 04:00 | 124 | 11:00
Lalbag | 134 | 21:00 | 125 | 11:00
Lalmonirhat | 129 | 04:00 | 121 | 18:00
Madanganj | 134 | 22:00 | 126 | 12:00
Madaripur | 132 | 18:00 | 128 | 11:00
Madartek | 133 | 03:00 | 124 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division