## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 06-04-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-04-2026 | during | 06-04-2026 | during | 06-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 274 | 412 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 180 | 450 | 450 | 226 | 226 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 327 | 300 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 122 | 126 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 22 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 50 | 50 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 260 | 260 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 88 | 105 | 105 | 88 | 88 | Engine Problem
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 35 | 162 | 162 | 35 | 35 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 9 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 320 | 475 | 584 | 584 | 490 | 490 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage (BPDB)
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 142 | 142 | 160 | 160 | 125 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2081 | 2457 | 5940.22 | 5915.22 | 2564.55 | 2630.55
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 26 | 26 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 12 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 46 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 220 | 220 | 225 | 220 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 98 | 97 | 105 | 105 | 95 | 95 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 32 | 55 | 56 | 64 | 56 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 67 | 63 | 68 | 68 | 68 | 68 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 21 | 100 | 100 | 13 | 13 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 23 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 83 | 76 | 108 | 108 | 68 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.28 | 0 | 3.82 | 0 | 3.82 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 15 | 54.36 | 54.36 | 17 | 17 | BPDB event of default
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 95 | 94 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 24 | 25 | 100 | 100 | 25 | 24 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 92 | 17 | 116 | 116 | 105 | 105 | Liquid fuel shortage
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 138 | 154 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 1 | 6 | 1 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 545 | 320 | 315 | 315 | 320 | 320 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2812.78 | 2575.5 | 3222.68 | 3238.86 | 2636.82 | 2652
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 188 | 139 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 360 | 360 | 350.01 | 350.01 | 350.01 | 350.01 | Plant availability less
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 345 | 340 | 342.01 | 342.01 | 342.01 | 342.01 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 10 | 10 | 41.65 | 41.65 | 41.65 | 41.65 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 22 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 127 | 195 | 195 | 9 | 9 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 95 | 46 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 30 | 29 | 32 | 32 | 32 | 32 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 98 | 99 | 163 | 163 | 101 | 101 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 179 | 180 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 164 | 178 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 16 | 52 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 114 | 114 | 17 | 17 | Liquid fuel shortage
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 51 | 115 | 115 | 17 | 51 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 28 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.745 | 1601 | 1678 | 2754.19 | 2688.19 | 1760.67 | 1770.67
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-04-2026 | during | 06-04-2026 | during | 06-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 22 | 18 | 157.5 | 157.5 | 30 | 30 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.3 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 9 | 70 | 70 | 50 | 50 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 69 | 10 | 10 | 50 | 50 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 32 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 0 | 54.5 | 54.5 | 35 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 169.3 | 108 | 358 | 314 | 221 | 177
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 53 | 53 | 0 | 0 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 156 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 99 | 99 | 100 | 100 | 100 | 100 | Plant availability less
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 77 | 80 | 80 | 80 | 80 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 98 | 98 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 22 | 25 | 25 | 22 | 22 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 321 | 370 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1149 | 1192 | 1327 | 1327 | 1173 | 1173
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 897 | 922 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 37 | 35 | 35 | 35 | 35 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 33 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 180 | 121 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 37 | 0 | 88 | 0 | 88 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1214 | 1232 | 1234.2 | 1234.2 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2328 | 2345 | 3593.2 | 3505.2 | 2582.1 | 2494.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 100 | 110 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 880 | 902 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 110 | 110 | 110 | 110 | 110 | 110 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.24 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1544.24 | 1576 | 2052 | 2051 | 1919 | 1918
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 22.76 | 0 | 58.5 | 0 | 58.5 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 40 | 38 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 32 | 32 | 0 | 0 | Two engines are under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 177 | 150 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 183 | 146 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 20 | 21 | 20 | 20 | 20 | 20 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 58 | 80 | 80 | 80 | 80 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 35 | 35 | BPDB event of default
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 35 | 35 | BPDB event of default
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.57 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 759.39 | 755.72 | 748 | 748 | 708 | 708 | U-2 Under Maintenance
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 26.27 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 32 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1676.99 | 1697.72 | 2523.19 | 2297.99 | 1998.99 | 1773.79
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 51 | 0 | 0 | 0 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 92 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 0.6 | 0 | 6.2 | 0 | 6.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 94 | 108 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 22 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 136 | 0 | 175.34 | 0 | 175.34 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 303.6 | 200 | 459.54 | 248 | 489.54 | 278
System Total |  |  |  |  | 28823.2 | 29269.987 | 13665.91 | 13829.22 | 22230.02 | 21585.46 | 15345.67 | 14867.11
Forecast Scenario (06-04-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13000 |  | 0 |  | 13000
|  |  |  | 1:00 | 12910 |  | 0 |  | 12910
|  |  |  | 2:00 | 13020 |  | 0 |  | 13020
|  |  |  | 3:00 | 13050 |  | 0 |  | 13050
|  |  |  | 4:00 | 13070 |  | 0 |  | 13070
|  |  |  | 5:00 | 13030 |  | 0 |  | 13030
|  |  |  | 6:00 | 13140 |  | 0 |  | 13140
|  |  |  | 7:00 | 13420 |  | 0 |  | 13420
|  |  |  | 8:00 | 13620 |  | 0 |  | 13620
|  |  |  | 9:00 | 13840 |  | 0 |  | 13840
|  |  |  | 10:00 | 13810 |  | 0 |  | 13810
|  |  |  | 11:00 | 13770 |  | 0 |  | 13770
|  |  |  | 12:00 | 13900 |  | 0 |  | 13900
|  |  |  | 13:00 | 13320 |  | 0 |  | 13320
|  |  |  | 14:00 | 13240 |  | 0 |  | 13240
|  |  |  | 15:00 | 13400 |  | 0 |  | 13400
|  |  |  | 16:00 | 13700 |  | 0 |  | 13700
|  |  |  | 17:00 | 13590 |  | 0 |  | 13590
|  |  |  | 18:00 | 13830 |  | 0 |  | 13830
|  |  |  | 18:30 | 14250 |  | 0 |  | 14250
|  |  |  | 19:00 | 14730 |  | 0 |  | 14730
|  |  |  | 19:30 | 14870 |  | 0 |  | 14870
|  |  |  | 20:00 | 14860 |  | 0 |  | 14860
|  |  |  | 21:00 | 14900 |  | 0 |  | 14900
|  |  |  | 22:00 | 14600 |  | 0 |  | 14600
|  |  |  | 23:00 | 14100 |  | 0 |  | 14100
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 13900.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14900.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14047.90 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 324.78896 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:18 hrs on 06-04-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 05-04-2026 | [28 empty] | Date: | 05-04-2026 | [28 empty] | Date: | 05-04-2026 | [28 empty] | Date: | 05-04-2026 | [28 empty] | Date: | 05-04-2026 | [17 empty] | Date: | 05-04-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [17 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 17 | 149 | 140 | 260 | 55 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 142 | 25 | 22 | 0 | 400 | 96 | 16 | 92 | 0 | 0 | 67 | 40 | 17 | 12 | 24 | 0 | 80 | 94 | 28 | 650 | 145 | 0 | 50 | 25.5 | 101 | 221 | 0 | 0 | 0 | 1160 | 0 | 117 | 6 | 0 | 359 | 345 | 51 | 0 | 200 | 10 | 17 | 98 | 186 | 0 | 20 | 17 | 174 | 8 | 0 | 31 | 325 | 0 | 337 | 30 | 0 | 157 | 0 | 16 | 0 | 77 | 30 | 101 | 0 | 97 | 17 | 49 | 48 | 32 | 0 | 0 | 12 | 8206.5 | 869 | 192 | 0 | 22 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1214 | 0 | 0 | 0 | 765 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 185 | 0 | 0 | 0 | 189 | 0 | 414 | 0 | 0 | 0 | 53 | 107 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 307 | 126 | 110 | 0 | 0 | 895 | 17 | 5763 | 13969.5 | 83.4
01:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 149 | 139 | 260 | 55 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 142 | 25 | 22 | 0 | 400 | 86 | 16 | 92 | 0 | 0 | 67 | 40 | 17 | 12 | 24 | 0 | 80 | 95 | 28 | 545 | 143 | 0 | 50 | 25.5 | 95 | 221 | 0 | 0 | 0 | 1160 | 0 | 110 | 0 | 0 | 360 | 345 | 51 | 0 | 208 | 10 | 17 | 98 | 176 | 0 | 20 | 17 | 170 | 0 | 0 | 31 | 310 | 0 | 332 | 30 | 0 | 155 | 0 | 16 | 0 | 77 | 30 | 101 | 0 | 97 | 17 | 49 | 48 | 22 | 0 | 0 | 12 | 8006.5 | 868 | 191 | 0 | 23 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1217 | 0 | 0 | 0 | 762 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 183 | 0 | 0 | 0 | 189 | 0 | 405 | 0 | 0 | 0 | 52 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 307 | 130 | 110 | 0 | 0 | 892 | 17 | 5668 | 13674.5 | 83.39
02:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 149 | 122 | 260 | 55 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 142 | 25 | 22 | 0 | 410 | 91 | 16 | 93 | 0 | 0 | 67 | 32 | 17 | 12 | 24 | 0 | 80 | 94 | 28 | 545 | 150 | 0 | 50 | 25.5 | 99 | 220 | 0 | 0 | 0 | 1160 | 0 | 108 | 0 | 0 | 360 | 345 | 51 | 0 | 206 | 10 | 17 | 98 | 180 | 0 | 20 | 17 | 172 | 0 | 0 | 31 | 315 | 0 | 340 | 30 | 0 | 157 | 0 | 16 | 0 | 77 | 30 | 101 | 0 | 97 | 17 | 49 | 48 | 44 | 0 | 0 | 12 | 8045.5 | 869 | 191 | 0 | 23 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 763 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 182 | 0 | 0 | 0 | 189 | 0 | 414 | 0 | 0 | 0 | 51 | 101 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 307 | 130 | 110 | 0 | 0 | 892 | 17 | 5697.2 | 13742.7 | 83.38
03:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 149 | 117 | 260 | 55 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 142 | 25 | 22 | 0 | 400 | 96 | 16 | 96 | 0 | 0 | 67 | 32 | 17 | 12 | 24 | 0 | 80 | 95 | 30 | 545 | 147 | 0 | 50 | 25.5 | 100 | 221 | 0 | 0 | 0 | 1161 | 0 | 108 | 0 | 0 | 359 | 345 | 51 | 0 | 206 | 10 | 16 | 98 | 183 | 0 | 20 | 17 | 168 | 0 | 0 | 31 | 320 | 0 | 340 | 30 | 0 | 159 | 0 | 16 | 0 | 77 | 30 | 101 | 0 | 97 | 17 | 49 | 48 | 40 | 0 | 0 | 12 | 8041.5 | 869 | 191 | 0 | 23 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234 | 0 | 0 | 0 | 762 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 182 | 0 | 0 | 0 | 188 | 0 | 414 | 0 | 0 | 0 | 51 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 307 | 130 | 110 | 0 | 0 | 892 | 17 | 5663 | 13704.5 | 83.37
04:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 149 | 122 | 260 | 55 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 142 | 25 | 22 | 0 | 435 | 95 | 16 | 91 | 0 | 1 | 67 | 32 | 0 | 12 | 24 | 0 | 80 | 96 | 30 | 545 | 155 | 0 | 50 | 25.5 | 100 | 221 | 0 | 0 | 0 | 1171 | 0 | 110 | 0 | 0 | 360 | 345 | 51 | 0 | 206 | 10 | 17 | 98 | 183 | 0 | 20 | 17 | 162 | 0 | 0 | 31 | 320 | 0 | 360 | 30 | 0 | 159 | 0 | 0 | 0 | 78 | 30 | 100 | 0 | 97 | 17 | 49 | 48 | 35 | 0 | 0 | 0 | 8063.5 | 869 | 191 | 0 | 23 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 761 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 182 | 0 | 0 | 0 | 188 | 0 | 414 | 0 | 0 | 0 | 51 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 307 | 130 | 110 | 0 | 0 | 892 | 17 | 5661.2 | 13724.7 | 83.36
05:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 149 | 122 | 260 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 142 | 25 | 22 | 0 | 400 | 92 | 16 | 90 | 0 | 0 | 67 | 32 | 0 | 12 | 24 | 0 | 80 | 95 | 31 | 545 | 143 | 0 | 45 | 25.5 | 98 | 222 | 0 | 0 | 0 | 1161 | 0 | 108 | 0 | 0 | 360 | 345 | 51 | 0 | 209 | 10 | 17 | 98 | 178 | 0 | 20 | 17 | 162 | 0 | 0 | 31 | 320 | 0 | 326 | 30 | 0 | 155 | 0 | 0 | 0 | 77 | 30 | 101 | 0 | 97 | 17 | 49 | 48 | 32 | 0 | 0 | 0 | 7930.5 | 868 | 192 | 0 | 23 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1214 | 0 | 0 | 0 | 765 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 182 | 0 | 0 | 0 | 188 | 0 | 409 | 0 | 0 | 0 | 51 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 307 | 130 | 110 | 0 | 0 | 892 | 17 | 5632 | 13562.5 | 83.35
06:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 149 | 122 | 260 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 0 | 142 | 25 | 22 | 0 | 415 | 92 | 16 | 90 | 0 | 0 | 67 | 32 | 0 | 12 | 24 | 0.05 | 80 | 94 | 31 | 545 | 150 | 0 | 46 | 25.5 | 97 | 222 | 0 | 0 | 0 | 1164 | 0 | 108 | 0 | 0 | 360 | 345 | 51 | 0 | 218 | 10 | 17 | 98 | 181 | 0 | 20 | 17 | 158 | 0 | 1 | 31 | 315 | 0 | 344 | 30 | 0 | 157 | 0 | 0 | 0 | 77 | 30 | 100 | 0 | 97 | 17 | 49 | 48 | 22 | 0 | 0.24 | 0 | 7937.79 | 892 | 191 | 0 | 23 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32 | 1133 | 0 | 0 | 0 | 762 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29 | 0 | 20 | 0 | 0.49 | 182 | 0 | 0 | 0 | 188 | 0 | 382 | 0 | 0.05 | 0 | 51 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.01 | 100 | 277 | 130 | 110 | 0 | 0 | 892 | 17 | 5521.16 | 13458.95 | 83.34
07:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 149 | 122 | 260 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 5 | 142 | 25 | 22 | 0 | 400 | 92 | 16 | 90 | 0 | 5 | 67 | 32 | 0 | 12 | 24 | 0.71 | 80 | 96 | 29 | 545 | 148 | 0 | 46 | 25.5 | 100 | 222 | 0 | 0 | 0 | 1162 | 3 | 102 | 0 | 0 | 359 | 345 | 51 | 0 | 218 | 10 | 17 | 99 | 180 | 0 | 20 | 17 | 150 | 0 | 7 | 31 | 315 | 0 | 344 | 30 | 0 | 158 | 1 | 16 | 0 | 77 | 30 | 101 | 0 | 98 | 17 | 49 | 48 | 22 | 0.2 | 8.13 | 0 | 7937.54 | 892 | 188 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1234.2 | 0 | 0 | 0 | 766 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.41 | 14 | 20 | 0 | 7.16 | 180 | 0 | 0 | 0 | 188 | 0 | 377 | 0 | 0.57 | 0 | 52 | 100 | 3 | 0 | 0 | 0 | 0 | 0.2 | 39 | 0.1 | 100 | 277 | 130 | 110 | 0 | 0 | 892 | 17 | 5665.64 | 13603.18 | 83.33
08:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 149 | 122 | 260 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 13 | 142 | 25 | 22 | 0 | 400 | 89 | 16 | 92 | 0 | 0 | 67 | 32 | 0 | 12 | 24 | 1.53 | 80 | 95 | 3 | 545 | 145 | 0 | 46 | 25.5 | 96 | 221 | 0 | 0 | 0 | 1162 | 10 | 95 | 0 | 0 | 360 | 345 | 51 | 0 | 196 | 10 | 17 | 98 | 177 | 0 | 20 | 17 | 156 | 0 | 31 | 25 | 310 | 0 | 344 | 30 | 0 | 155 | 2 | 16 | 0 | 77 | 30 | 100 | 0 | 98 | 17 | 49 | 48 | 22 | 0.7 | 18.5 | 0 | 7907.23 | 896 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 1234.2 | 0 | 0 | 0 | 762 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.37 | 15 | 20 | 0 | 21.96 | 183 | 0 | 0 | 0 | 186 | 0 | 361 | 0 | 1.95 | 0 | 52 | 96 | 18 | 0 | 0 | 0 | 0 | 0.4 | 92 | 0.2 | 100 | 276 | 130 | 110 | 0 | 0 | 895 | 17 | 5744.08 | 13651.31 | 83.32
09:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 274 | 0 | 0 | 0 | 0 | 149 | 122 | 260 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 9 | 142 | 21 | 22 | 0 | 320 | 92 | 16 | 83 | 0 | 0 | 67 | 32 | 0 | 12 | 24 | 2.28 | 80 | 95 | 2 | 545 | 138 | 0 | 46 | 25.5 | 98 | 219 | 0 | 0 | 0 | 1224 | 12 | 95 | 0 | 0 | 360 | 345 | 51 | 0 | 188 | 10 | 16 | 98 | 179 | 0 | 20 | 17 | 164 | 0 | 28 | 30 | 315 | 0 | 321 | 30 | 0 | 156 | 7 | 16 | 0 | 77 | 30 | 99 | 0 | 98 | 17 | 49 | 48 | 22 | 1.3 | 32 | 0 | 7813.08 | 897 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 1214 | 0 | 0 | 0 | 759.39 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.76 | 32 | 20 | 0 | 26.27 | 177 | 0 | 0 | 0 | 183 | 0 | 414 | 0 | 2.57 | 0 | 51 | 94 | 22 | 0 | 0 | 0 | 0 | 0.6 | 136 | 0.24 | 100 | 307 | 130 | 110 | 0 | 0 | 880 | 17 | 5852.83 | 13665.91 | 83.3
10:00 | 0 | 88 | 38 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 132 | 90 | 260 | 55 | 17 | 17 | 0 | 90 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 15 | 142 | 21 | 22 | 0 | 450 | 60 | 16 | 78 | 0 | 0 | 34 | 32 | 0 | 10 | 24 | 2.65 | 80 | 94 | 2 | 440 | 94 | 0 | 46 | 25.5 | 99 | 219 | 0 | 0 | 0 | 1224 | 14 | 95 | 0 | 0 | 360 | 345 | 51 | 0 | 196 | 10 | 17 | 97 | 155 | 0 | 20 | 0 | 164 | 0 | 59 | 30 | 320 | 0 | 347 | 30 | 0 | 156 | 3 | 16 | 0 | 77 | 30 | 100 | 0 | 98 | 33 | 49 | 48 | 22 | 0.8 | 38.44 | 0 | 7603.39 | 896 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.99 | 1234.2 | 0 | 0 | 0 | 760.58 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.1 | 16 | 20 | 0 | 38.11 | 176 | 0 | 0 | 0 | 177 | 0 | 414 | 0 | 3.61 | 0 | 53 | 96 | 28 | 0 | 0 | 0 | 0 | 3.6 | 49 | 0.29 | 64 | 307 | 130 | 110 | 0 | 0 | 880 | 17 | 5734.48 | 13337.87 | 83.28
11:00 | 0 | 88 | 38 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 17 | 0 | 112 | 75 | 243 | 55 | 0 | 17 | 0 | 90 | 0 | 0 | 0 | 17 | 323 | 0 | 0 | 10 | 142 | 18 | 22 | 0 | 450 | 17 | 16 | 76 | 0 | 12 | 34 | 24 | 0 | 10 | 24 | 2.94 | 80 | 96 | 2 | 370 | 14 | 0 | 50 | 22 | 95 | 220 | 0 | 0 | 0 | 1224 | 18 | 88 | 0 | 0 | 359 | 345 | 45 | 0 | 184 | 10 | 17 | 97 | 143 | 7 | 14 | 0 | 178 | 0 | 31 | 30 | 310 | 0 | 330 | 30 | 0 | 144 | 6 | 16 | 0 | 76 | 30 | 99 | 0 | 98 | 21 | 49 | 48 | 20 | 0 | 41.02 | 0 | 7267.96 | 897 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 1224 | 0 | 0 | 0 | 761.9 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.45 | 13 | 0 | 0 | 6.44 | 173 | 0 | 0 | 0 | 174 | 0 | 380 | 0 | 0.57 | 0 | 53 | 95 | 29 | 0 | 0 | 0 | 0 | 3.9 | 134 | 0.15 | 16 | 307 | 127 | 110 | 0 | 0 | 880 | 17 | 5706.41 | 12974.37 | 83.26
12:00 | 0 | 88 | 39 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 17.5 | 2 | 120 | 45 | 260 | 55 | 0 | 35 | 0 | 90 | 0 | 0 | 0 | 17 | 321 | 0 | 0 | 15 | 108 | 18 | 22 | 0 | 470 | 17 | 16 | 76 | 0 | 7 | 33 | 24 | 0 | 10 | 24 | 2.42 | 80 | 85 | 2 | 370 | 44 | 0 | 50 | 16 | 90 | 216 | 0 | 0 | 0 | 1160 | 17 | 53 | 0 | 0 | 354 | 335 | 51 | 0 | 194 | 10 | 17 | 97 | 155 | 8 | 14 | 0 | 196 | 0 | 62 | 30 | 305 | 0 | 354 | 30 | 0 | 143 | 10 | 16 | 0 | 76 | 30 | 101 | 0 | 98 | 17 | 49 | 48 | 17 | 0.8 | 21.68 | 0 | 7230.4 | 896 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.65 | 1218 | 0 | 0 | 0 | 762.21 | 0 | 41 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 22.72 | 26 | 0 | 0 | 20.02 | 159 | 0 | 0 | 0 | 155 | 0 | 414 | 0 | 1.7 | 0 | 53 | 96 | 22 | 0 | 0 | 0 | 0 | 5.3 | 126 | 0.4 | 16 | 274 | 128 | 110 | 0 | 0 | 880 | 17 | 5669 | 12899.4 | 83.24
13:00 | 0 | 88 | 28 | 0 | 0 | 0 | 0 | 0 | 279 | 0 | 0 | 17.5 | 17 | 149 | 30 | 145 | 55 | 0 | 35 | 1 | 90 | 0 | 0 | 0 | 17 | 324 | 0 | 0 | 5 | 90 | 18 | 22 | 0 | 420 | 17 | 16 | 75 | 0 | 4 | 33 | 24 | 0 | 10 | 24 | 1.3 | 80 | 82 | 5 | 370 | 14 | 0 | 50 | 16 | 90 | 216 | 0 | 0 | 0 | 1122 | 17 | 15 | 0 | 0 | 356 | 270 | 51 | 0 | 188 | 0 | 17 | 95 | 173 | 9 | 8 | 0 | 192 | 0 | 21 | 30 | 310 | 0 | 330 | 30 | 0 | 140 | 8 | 17 | 0 | 77 | 30 | 100 | 0 | 98 | 0 | 49 | 48 | 16 | 1 | 13.68 | 0 | 6789.48 | 896 | 159 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.85 | 1212 | 0 | 0 | 0 | 763.65 | 0 | 41 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 3.18 | 16 | 0 | 0 | 6.58 | 164 | 0 | 0 | 0 | 147 | 0 | 350 | 0 | 0.72 | 0 | 53 | 50 | 30 | 0 | 0 | 0 | 0 | 0 | 152 | 0.54 | 48 | 273 | 126 | 110 | 0 | 0 | 880 | 17 | 5630.52 | 12420 | 83.22
14:00 | 0 | 35 | 41 | 0 | 0 | 0 | 0 | 0 | 269 | 0 | 0 | 17.5 | 17 | 149 | 15 | 95 | 55 | 0 | 35 | 15 | 90 | 0 | 0 | 0 | 17 | 326 | 0 | 0 | 3 | 52 | 12 | 21 | 0 | 420 | 17 | 16 | 53 | 0 | 16 | 33 | 24 | 0 | 21 | 27 | 0.64 | 80 | 34 | 2 | 370 | 0 | 0 | 50 | 0 | 51 | 217 | 0 | 0 | 0 | 1160 | 16 | 13 | 0 | 0 | 355 | 343 | 51 | 0 | 190 | 0 | 17 | 94 | 85 | 8 | 20 | 0 | 176 | 0 | 39 | 30 | 310 | 0 | 346 | 30 | 0 | 147 | 10 | 0 | 0 | 75 | 30 | 100 | 0 | 98 | 0 | 49 | 48 | 9 | 1 | 20.4 | 0 | 6566.54 | 896 | 148 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.36 | 1215 | 0 | 0 | 0 | 762.36 | 0 | 41 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 9.15 | 109 | 0 | 0 | 19.94 | 163 | 0 | 0 | 0 | 165 | 0 | 414 | 0 | 1.48 | 0 | 52 | 52 | 30 | 0 | 0 | 0 | 0 | 0 | 133 | 0.51 | 16 | 272 | 126 | 110 | 0 | 0 | 890 | 17 | 5766.8 | 12333.34 | 83.2
15:00 | 0 | 35 | 41 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 17.5 | 17 | 149 | 15 | 95 | 55 | 12 | 35 | 15 | 140 | 0 | 0 | 0 | 17 | 325 | 0 | 0 | 14 | 52 | 12 | 20 | 0 | 520 | 17 | 16 | 44 | 0 | 13 | 34 | 24 | 0 | 21 | 26 | 0.47 | 80 | 30 | 2 | 370 | 0 | 0 | 50 | 0 | 47 | 217 | 0 | 0 | 0 | 1165 | 12 | 13 | 0 | 0 | 354 | 340 | 51 | 0 | 211 | 0 | 16 | 97 | 83 | 0 | 20 | 0 | 184 | 0 | 11 | 30 | 315 | 0 | 340 | 30 | 0 | 156 | 5 | 0 | 0 | 76 | 30 | 100 | 0 | 98 | 0 | 49 | 48 | 10 | 1.5 | 36.12 | 0 | 6713.59 | 897 | 142 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.12 | 1236 | 0 | 0 | 0 | 756.65 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 10 | 0 | 13.88 | 80 | 0 | 0 | 45.92 | 158 | 0 | 0 | 0 | 160 | 0 | 414 | 0 | 4.09 | 0 | 53 | 50 | 25 | 34 | 0 | 0 | 0 | 5.5 | 162 | 0.24 | 16 | 285 | 126 | 110 | 0 | 0 | 880 | 17 | 5833.4 | 12546.99 | 83.18
16:00 | 0 | 50 | 41 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 17.5 | 17 | 149 | 35 | 145 | 55 | 28 | 35 | 15 | 225 | 0 | 0 | 0 | 17 | 321 | 0 | 0 | 17 | 70 | 0 | 20 | 0 | 480 | 17 | 16 | 43 | 0 | 7 | 34 | 24 | 0 | 21 | 30 | 0.29 | 80 | 34 | 2 | 370 | 68 | 0 | 50 | 1 | 59 | 217 | 0 | 0 | 0 | 1165 | 8 | 13 | 0 | 0 | 359 | 340 | 51 | 0 | 195 | 0 | 29 | 98 | 102 | 0 | 20 | 4 | 182 | 0 | 26 | 30 | 315 | 0 | 328 | 30 | 0 | 156 | 1 | 16 | 0 | 77 | 30 | 101 | 0 | 98 | 0 | 49 | 48 | 10 | 1.1 | 21.5 | 1 | 6855.39 | 896 | 130 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.68 | 1215 | 0 | 0 | 0 | 755.89 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 21 | 0 | 24.05 | 55 | 0 | 0 | 29.58 | 151 | 0 | 0 | 0 | 153 | 0 | 414 | 0 | 2.85 | 0 | 54 | 59 | 17 | 47 | 0 | 0 | 0 | 3.6 | 103 | 0.11 | 16 | 275 | 126 | 110 | 0 | 0 | 880 | 17 | 5698.76 | 12554.15 | 83.17
17:00 | 0 | 70 | 47 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 17.5 | 17 | 149 | 46 | 195 | 55 | 35 | 35 | 15 | 225 | 0 | 0 | 0 | 17 | 324 | 0 | 0 | 7 | 70 | 20 | 21 | 0 | 480 | 17 | 16 | 43 | 0 | 0 | 34 | 38 | 0 | 21 | 32 | 0 | 80 | 58 | 3 | 370 | 94 | 0 | 50 | 15 | 104 | 217 | 0 | 0 | 0 | 1165 | 2 | 13 | 0 | 0 | 360 | 345 | 51 | 0 | 200 | 0 | 34 | 98 | 147 | 0 | 20 | 17 | 178 | 0 | 5 | 29 | 310 | 0 | 340 | 30 | 0 | 155 | 3 | 16 | 0 | 77 | 30 | 100 | 0 | 98 | 0 | 67 | 9 | 17 | 0.4 | 9.45 | 12 | 7069.35 | 911 | 128 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.65 | 1234 | 0 | 0 | 0 | 753.68 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 25 | 0 | 12.37 | 22 | 0 | 0 | 12.08 | 146 | 0 | 0 | 0 | 146 | 0 | 414 | 0 | 1.12 | 0 | 54 | 89 | 7 | 98 | 0 | 0 | 0 | 2 | 44 | 0.05 | 58 | 277 | 126 | 110 | 0 | 0 | 880 | 17 | 5699.95 | 12769.3 | 83.16
18:00 | 0 | 88 | 47 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 17.5 | 17 | 149 | 126 | 245 | 55 | 35 | 35 | 0 | 180 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 1 | 142 | 20 | 22 | 0 | 310 | 17 | 16 | 53 | 0 | 0 | 67 | 54 | 0 | 21 | 25 | 0 | 80 | 83 | 7 | 370 | 146 | 0 | 50 | 25.5 | 98 | 219 | 0 | 0 | 0 | 1170 | 0 | 15 | 0 | 0 | 360 | 345 | 51 | 0 | 202 | 0 | 34 | 98 | 177 | 8 | 20 | 17 | 172 | 0 | 0 | 29 | 310 | 0 | 341 | 30 | 0 | 150 | 0 | 20 | 0 | 77 | 30 | 101 | 0 | 98 | 0 | 68 | 9 | 17 | 0 | 0.78 | 12 | 7433.78 | 916 | 127 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1233 | 0 | 0 | 0 | 754.66 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 24 | 0 | 1.55 | 0 | 0 | 0 | 0.65 | 145 | 0 | 0 | 0 | 144 | 0 | 414 | 0 | 0.06 | 0 | 56 | 95 | 1 | 99 | 0 | 0 | 0 | 0 | 4 | 0 | 110 | 277 | 127 | 110 | 0 | 0 | 880 | 17 | 5673.92 | 13107.7 | 83.15
19:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 17 | 149 | 128 | 260 | 55 | 35 | 35 | 0 | 180 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 400 | 17 | 16 | 73 | 0 | 0 | 67 | 54 | 0 | 21 | 25 | 0 | 80 | 92 | 14 | 370 | 150 | 0 | 50 | 25.5 | 97 | 220 | 0 | 0 | 0 | 1224 | 0 | 97 | 33 | 0 | 360 | 340 | 51 | 0 | 187 | 12 | 34 | 99 | 179 | 9 | 20 | 17 | 180 | 0 | 0 | 29 | 320 | 0 | 307 | 30 | 0 | 147 | 0 | 22 | 0 | 77 | 30 | 100 | 0 | 98 | 0 | 68 | 9 | 18 | 0 | 0 | 12 | 7844.5 | 921 | 125 | 0 | 32 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1208 | 0 | 0 | 0 | 754.83 | 0 | 38 | 0 | 35 | 35 | 0 | 33 | 28 | 0 | 0 | 0 | 9 | 0 | 0 | 145 | 0 | 0 | 0 | 143 | 0 | 350 | 0 | 0 | 0 | 54 | 94 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 127 | 110 | 0 | 0 | 900 | 17 | 5696.83 | 13541.33 | 83.14
19:30 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 54 | 35 | 149 | 126 | 260 | 55 | 35 | 35 | 0 | 180 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 142 | 22 | 22 | 0 | 400 | 17 | 16 | 73 | 0 | 0 | 67 | 55 | 0 | 21 | 25 | 0 | 80 | 92 | 10 | 340 | 155 | 0 | 50 | 25.5 | 94 | 221 | 0 | 0 | 0 | 1224 | 0 | 150 | 45 | 0 | 360 | 345 | 51 | 10 | 197 | 25 | 51 | 99 | 178 | 9 | 20 | 17 | 160 | 0 | 0 | 29 | 315 | 0 | 340 | 30 | 0 | 154 | 0 | 22 | 0 | 77 | 30 | 100 | 0 | 98 | 0 | 68 | 9 | 18 | 0 | 0 | 12 | 7962.5 | 923 | 121 | 0 | 41 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1230 | 0 | 0 | 0 | 755.18 | 0 | 38 | 0 | 35 | 40 | 0 | 38 | 28 | 0 | 0 | 0 | 20 | 0 | 0 | 144 | 0 | 0 | 0 | 145 | 0 | 350 | 0 | 0 | 0 | 54 | 100 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 127 | 110 | 0 | 0 | 900 | 17 | 5760.18 | 13722.68
20:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 35 | 149 | 126 | 260 | 55 | 35 | 35 | 0 | 180 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 142 | 22 | 22 | 0 | 400 | 17 | 16 | 74 | 0 | 0 | 67 | 55 | 0 | 21 | 25 | 0 | 80 | 93 | 16 | 320 | 154 | 0 | 50 | 25.5 | 94 | 221 | 0 | 0 | 0 | 1224 | 0 | 150 | 107 | 0 | 360 | 345 | 51 | 10 | 194 | 25 | 48 | 99 | 180 | 8 | 20 | 17 | 160 | 0 | 0 | 29 | 315 | 0 | 318 | 30 | 0 | 154 | 0 | 22 | 0 | 77 | 30 | 100 | 0 | 98 | 0 | 69 | 9 | 18 | 0 | 0 | 12 | 7989.5 | 922 | 121 | 0 | 38 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1225 | 0 | 0 | 0 | 756.83 | 0 | 38 | 0 | 35 | 44 | 0 | 58 | 30 | 0 | 0 | 0 | 21 | 0 | 0 | 145 | 0 | 0 | 0 | 145 | 0 | 350 | 0 | 0 | 0 | 0 | 103 | 0 | 99 | 0 | 0 | 10 | 0 | 0 | 0 | 110 | 307 | 130 | 110 | 0 | 0 | 902 | 17 | 5747.83 | 13737.33 | 83.13
21:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 35 | 149 | 126 | 260 | 55 | 35 | 35 | 0 | 180 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 142 | 22 | 22 | 0 | 475 | 17 | 16 | 76 | 0 | 0 | 63 | 55 | 15 | 21 | 25 | 0 | 80 | 94 | 23 | 320 | 154 | 0 | 50 | 25.5 | 97 | 220 | 0 | 0 | 0 | 1224 | 0 | 46 | 127 | 0 | 360 | 340 | 51 | 22 | 139 | 10 | 51 | 99 | 180 | 9 | 20 | 17 | 178 | 0 | 0 | 29 | 310 | 0 | 370 | 30 | 0 | 156 | 0 | 22 | 0 | 77 | 30 | 99 | 0 | 98 | 0 | 69 | 9 | 18 | 0 | 0 | 12 | 8010.5 | 922 | 121 | 0 | 37 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1232 | 0 | 0 | 0 | 755.72 | 0 | 38 | 0 | 35 | 50 | 0 | 58 | 30 | 0 | 0 | 0 | 21 | 0 | 0 | 150 | 0 | 0 | 0 | 146 | 0 | 414 | 0 | 0 | 0 | 0 | 108 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 130 | 110 | 0 | 0 | 902 | 17 | 5818.72 | 13829.22 | 83.12
22:00 | 0 | 70 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 35 | 149 | 129 | 260 | 55 | 35 | 35 | 0 | 200 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 142 | 22 | 22 | 0 | 450 | 17 | 16 | 74 | 0 | 1 | 50 | 55 | 17 | 21 | 25 | 0 | 80 | 93 | 21 | 315 | 140 | 0 | 50 | 25.5 | 98 | 222 | 0 | 0 | 0 | 1224 | 0 | 13 | 45 | 0 | 359 | 345 | 51 | 5 | 174 | 10 | 33 | 100 | 180 | 3 | 20 | 17 | 174 | 0 | 0 | 0 | 310 | 0 | 320 | 30 | 0 | 158 | 0 | 22 | 0 | 77 | 30 | 100 | 0 | 98 | 0 | 59 | 9 | 16 | 0 | 0 | 12 | 7732.5 | 922 | 121 | 0 | 36 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1231 | 0 | 0 | 0 | 754.92 | 0 | 38 | 0 | 35 | 50 | 0 | 58 | 30 | 0 | 0 | 0 | 21 | 0 | 0 | 149 | 0 | 0 | 0 | 144 | 0 | 414 | 0 | 0 | 0 | 0 | 102 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 130 | 110 | 0 | 0 | 902 | 17 | 5807.92 | 13540.42 | 83.11
23:00 | 0 | 70 | 50 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 35 | 149 | 129 | 260 | 55 | 0 | 35 | 0 | 200 | 0 | 0 | 0 | 17 | 331 | 0 | 0 | 0 | 142 | 22 | 22 | 0 | 450 | 17 | 16 | 76 | 0 | 6 | 50 | 55 | 17 | 21 | 25 | 0 | 80 | 94 | 29 | 315 | 145 | 0 | 50 | 25.5 | 96 | 221 | 0 | 0 | 0 | 1224 | 0 | 13 | 45 | 0 | 359 | 345 | 51 | 5 | 181 | 10 | 17 | 100 | 175 | 9 | 20 | 17 | 178 | 0 | 0 | 0 | 305 | 0 | 329 | 30 | 0 | 155 | 0 | 22 | 0 | 77 | 30 | 99 | 0 | 98 | 0 | 59 | 9 | 16 | 0 | 0 | 12 | 7708.5 | 923 | 123 | 0 | 36 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1223 | 0 | 0 | 0 | 762 | 0 | 38 | 0 | 35 | 50 | 0 | 58 | 30 | 0 | 0 | 0 | 21 | 0 | 0 | 149 | 0 | 0 | 0 | 143 | 0 | 414 | 0 | 0 | 0 | 0 | 95 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 130 | 110 | 0 | 0 | 902 | 17 | 5760 | 13468.5 | 83.1
Total KWH | 0 | 1935360 | 1105920 | 0 | 0 | 0 | 0 | 0 | 8359200 | 0 | 0 | 261720 | 297720 | 3529296 | 2314080 | 5669542 | 1323372 | 265000 | 809280 | 53760 | 4198200 | 0 | 0 | 0 | 266070 | 7242912 | 0 | 0 | 118520 | 3012000 | 499800 | 418400 | 0 | 9990454.55 | 1160455 | 386400 | 1816320 | 0 | 73440 | 1279238 | 857280 | 141283 | 379200 | 578880 | 15723 | 1923840 | 2076681 | 384000 | 10560000 | 2696436 | 0 | 1141920 | 511137 | 2247309 | 5031243 | 0 | 0 | 0 | 28445452 | 127035 | 1604145 | 334545 | 0 | 8973400 | 8196000 | 1231408 | 49440 | 4927000 | 220752 | 558720 | 2354726 | 3946080 | 82320 | 470720 | 300960 | 4107840 | 811 | 333082 | 645776 | 7610000 | 0 | 8401000 | 717000 | 0 | 3695890.91 | 48176 | 355296 | 0 | 1857600 | 718176 | 2363900 | 0 | 2357730 | 239040 | 1294800 | 852000 | 464640 | 8000 | 235630 | 138720 | 183199202.46 | 21709091 | 3925152 | 0 | 411840 | 361344 | 0 | 0 | 0 | 0 | 0 | 0 | 438480 | 29447270 | 0 | 0 | 0 | 18097455 | 0 | 954806 | 0 | 403776 | 534048 | 0 | 261376 | 205500 | 0 | 182296 | 400480 | 310931 | 0 | 242256 | 4002000 | 0 | 0 | 0 | 4227273 | 0 | 9593091 | 0 | 21060 | 0 | 923345 | 2253604 | 185792 | 788812 | 0 | 0 | 7000 | 28230.24 | 1130400 | 3031 | 1978656 | 7113000 | 3090000 | 2663860 | 0 | 0 | 21680000 | 430800 | 138006055.24 | 321205257.7

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 05-04-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13665.91 | MW | 09:00 Hr. | Energy Generated |  |  | 321.2053 |  | MKWHr.
| Day Peak Demand |  |  | 14083.91 | MW | 09:00 Hr. | Energy Unserverd |  |  | 15.374 |  | MKWHr.
| Evening Peak Generation |  |  | 13829.22 | MW | 21:00 Hr. | Energy Demand |  |  | 336.5793 |  | MKWHr.
| Evening Peak Demand |  |  | 14599.22 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.4 |  | °C
| Minimum Generation of the Day |  |  | 12333.34 | MW | 14:00 Hr. | Total Gas Supplied |  |  | 888.08 |  | MMCFD
| Maximum Generation of the Day |  |  | 13969.5 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 7.316 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 30.709 | 0 | 20.8431 | 0 | 0 | 0.11852 | 0 | 0 | 51.6706 | Gas | 118.9248 | Gas | 416600710.7107
| Chattogram Zone |  |  | 5.4152 | 39.0055 | 15.2725 | 0 | 1.9238 | 0.14276 | 0 | 0.07344 | 61.8333 | Coal | 98.1691 | Coal | 668154333
| Cumilla Zone |  |  | 26.758 | 0 | 7.1388 | 0 | 0 | 0.33308 | 4.1078 | 0 | 38.3377 | HFO | 54.6745 | HFO | 963282998.9
| Mymensingh Zone |  |  | 0.46464 | 0 | 2.5246 | 0 | 0 | 0.24363 | 0 | 0 | 3.2328 | HSD | 0.007 | HSD | 304990
| Sylhet Zone |  |  | 28.0766 | 0 | 0 | 0 | 0 | 0.048176 | 0 | 0 | 28.1248 | Hydro | 1.9238 | Hydro | 192384
| Khulna Zone |  |  | 3.9252 | 29.4473 | 0.77318 | 0 | 0 | 0.43848 | 21.7091 | 0 | 56.2932 | Solar | 3.5182 | Solar | 57714807.988
| Barishal Zone |  |  | 5.7539 | 28.793 | 2.4095 | 0 | 0 | 0.003031 | 0 | 0 | 36.9593 | Import | 43.9144 | Import | 242608415.9
| Rajshahi Zone |  |  | 17.8224 | 0 | 2.6704 | 0 | 0 | 0.84609 | 18.0975 | 0 | 39.4363 | Wind | 0.07344 | Wind | 1080302.4
| Rangpur Zone |  |  | 0 | 0.92334 | 3.0424 | 0.007 | 0 | 1.3444 | 0 | 0 | 5.3172
| Total |  |  | 118.9248 | 98.1691 | 54.6745 | 0.007 | 1.9238 | 3.5182 | 43.9144 | 0.07344 | 321.2053
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 416600710.7107 |  | Hydro | 192384
|  |  |  | Coal | 668154333 |  | Solar | 57714807.988
|  |  |  | HFO | 963282998.9 |  | Import | 242608415.9
|  |  |  | HSD | 304990 |  | Wind | 1080302.4
[5 empty] | Total: | 234,99,38,942 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7091 | Peak Hr Flow | 922.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 34291981.85 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 18.0975 | Peak Hr Flow | 755.72 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1398 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 4.1078 | Peak Hr Flow | 178.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2317 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 43.9144 | Peak Hr Flow | 1855.72 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 137 |  | 5140
|  |  |  | Chattogram |  | 50 |  | 1429
|  |  |  | Cumilla |  | 90 |  | 1429
|  |  |  | Mymensingh |  | 170 |  | 1108
|  |  |  | Sylhet |  | 60 |  | 468
|  |  |  | Khulna |  | 80 |  | 1691
|  |  |  | Barishal |  | 40 |  | 402
|  |  |  | Rajshahi |  | 70 |  | 1493
|  |  |  | Rangpur |  | 40 |  | 869
|  |  |  | Total |  | 737 |  | 14029
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:37 |  | Haripur EGCB 412 MW CCPP ST tripped.
| 08:48 | 09:00 | Sirajganj 132/33kV S/S T1-(415) LT Tripped showing O/C E/F relays Due to 33kV Kamarkhand | [7 empty] | 30.0MW load
|  |  | Feeder SPBS-2 tripped at this time due to E/F>,E/F>>,O/C>,O/C>>. | [7 empty] | interrup.
| 08:48 | 09:00 | Sirajganj 132/33kV S/S T2-(425) LT Tripped showing O/C E/F relays Due to 33kV Kamarkhand | [7 empty] | 30.0MW load
|  |  | Feeder SPBS-2 tripped at this time due to E/F>,E/F>>,O/C>,O/C>>. | [7 empty] | interrup.
|  | 08:52 | Narail 132/33kV S/S TR1 (403-T) HT is restored.
|  | 08:53 | Narail 132/33kV S/S TR1 (403-T) LT is restored.
| 09:00 |  | Day Peak Generation: 13662 MW.
| 09:21 |  | Rangpur-Saidpur 132kV Ckt-2 Scheduled S/D from Rangpur 132/33kV end.
| 09:21 |  | Meghnaghat 450 MW CCPP (MPL) Tripped with remarks:- ST
| 09:24 |  | Taraganj 132/33kV S/S Taraganj-Rangpur CKT-02 Scheduled S/D
| 09:25 |  | Meghnaghat 450 MW CCPP (MPL) Ready with remarks:- GT Running
| 09:25 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- GT Running
| 10:00 | 15:35 | Ishurdi-Pabna 132kV ckt Project Work S/D from Ishurdi 132/33kV end.
| 10:46 |  | BIPTC S/S 10CF16 Scheduled S/D Due to For Maintenance work
| 11:27 |  | Aftabnagar-Rampura 132kV Ckt-1 Project Work S/D from Ghorashal 230kV end Due to Old
Ghorasha-Ishwardi Tower dismantle work.
| 11:30 | 15:05 | Aminbazar-Keraniganj 230kV Ckt-2 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Aminbazar end BUS DS redhot maintenance work.
| 11:31 | 17:28 | Kachua 230/132/33kV S/S TR-1 LT Project Work S/D | [7 empty] | 8.0MW load
interrup.
| 11:31 | 17:24 | Kachua 230/132/33kV S/S TR-1 HT Project Work S/D | [7 empty] | 8.0MW load
interrup.
| 11:55 | 15:06 | Aminbazar-Keraniganj 230kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Due to redhot maintenance of Bus-1 DS841S
| 12:10 | 12:33 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing 33 kv OC/EF Protection relay relays Due
to Chunarughat and Shayestaganj Feeder Trip
| 12:10 | 14:33 | Aminbazar 400/230/132kV S/S 230 kv Bus 01 Scheduled S/D Due to Due to Redhot maintenance
of Bus DS841S
| 12:14 |  | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Tripped showing 7UT61 Differential relay relays
Due to Differential trip R&Y phase
| 12:14 |  | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Tripped showing 86.1,86.2 relays Due to | [7 empty] | 63.0MW load
|  |  | Differential at 33kV side | [7 empty] | interrup.
| 12:38 | 12:50 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing 33 kv OC/EF protection Relay relays Due
to Shayestaganj Feeder Earth fault
| 14:41 |  | Meghnaghat 450 MW STG Sync
| 14:41 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- ST
| 15:30 | 15:40 | Haripur 230/132kV S/S 132KV Bhulta-2 Forced S/D Due to Transformer Load management.
|  | 16:19 | Rangpur-Saidpur 132kV Ckt-1 is restored.
|  | 16:20 | Taraganj 132/33kV S/S Taraganj-Rangpur CKT-01 is restored.
| 16:47 |  | Haripur 412 MW CCPP Synchronized with remarks:- ST
|  | 18:27 | Naogaon 132/33kV S/S T-3 HT is restored.
|  | 19:44 | Bibiyana-Kaliakoir 400 kV Ckt-2 is restored.
| 21:00 |  | Evening Peak Generation: 13828 MW.
| 06:55 |  | Feni 132/33kV S/S Feni-Lanka HFO PS Scheduled S/D Due to For T2 132KV breaker replacement
work
| 07:20 |  | Feni 132/33kV S/S T-1(405T) LT Scheduled S/D Due to For T2 132KV breaker replacement work
| 07:20 |  | Feni 132/33kV S/S T-1(405T) HT Scheduled S/D Due to For T2 132KV breaker replacement work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 05-04-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 412 | 8359200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 180 | 4198200 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1323372 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7242912 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 261720 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 126 | 2314080 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 265000 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 266070 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 499800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 418400 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 1105920 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 260 | 5669542 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3529296 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1935360 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 53760 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 809280 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 118520 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 297720 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 475 | 9990454.55 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage (BPDB)
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3012000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2457 | 51670606.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 511137 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 127035 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1141920 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1923840 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5031243 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 97 | 2247309 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 55 | 857280 | -
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 63 | 1279238 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 21 | 379200 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 23 | 384000 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 76 | 1816320 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 15723 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 386400 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 15 | 141283 | BPDB event of default
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 94 | 2076681 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 578880 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 1160455 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 154 | 2696436 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28445452 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 73440 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 320 | 10560000 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 2575.5 | 61833272
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 139 | 4927000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 360 | 8973400 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 340 | 8196000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 10 | 220752 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 22 | 49440 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 127 | 334545 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1231408 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 46 | 1604145 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 29 | 645776 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 99 | 2354726 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 180 | 3946080 | -
| Import (Tripura) |  | Import | 0 | 160 | 178 | 4107840 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 811 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 470720 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 300960 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 82320 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 51 | 558720 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 333082 | -
Cumilla Area Total |  |  |  |  | 2870.745 | 1678 | 38337725
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 18 | 464640 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 852000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 69 | 1294800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 235630 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 138720 | From12:00 hrs to24:00 hrs will be dispatching12MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 239040 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 108 | 3232830
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 48176 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 717000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3695890.91 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 99 | 2363900 | plant availability zero
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 718176 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 1857600 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 98 | 2357730 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 355296 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7610000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 370 | 8401000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Shutdown due to HGPI maintanance
Sylhet Area Total |  |  |  |  | 2325 | 1192 | 28124768.91
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 922 | 21709091 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 37 | 411840 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 33 | 361344 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 121 | 3925152 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 438480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1232 | 29447270 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2345 | 56293177
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 0 | 0 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 1978656 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3090000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 902 | 21680000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 110 | 2663860 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 430800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7113000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3031 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1576 | 36959347
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 182296 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Machine Problem
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 38 | 954806 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 205500 | Shutdown for 132kv Breaker Maintenance.
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 150 | 4002000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 146 | 4227273 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9593091 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 310931 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 58 | 261376 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 534048 | BPDB event of default
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 403776 | BPDB event of default
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 21060 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 755.72 | 18097455 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 242256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 400480 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1697.72 | 39436348
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 923345 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 7000 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 92 | 788812 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 28230.24 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 108 | 2253604 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 185792 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1130400 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 200 | 5317183.24
Eastern Grid Total |  |  |  |  | 17417.792 | 8010.5 | 183199202.46
Western Grid Total |  |  |  |  | 11852.195 | 5818.72 | 138006055.24
National Grid Total |  |  |  |  | 29269.987 | 13829.22 | 321205257.7
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 05-04-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9067.62 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4224.8 | MW
i) Dhaka area |  |  | 5003.32 |  | MW | i) Khulna area |  |  |  | 1611 | MW
ii) Chattogram area |  |  | 1379.3 |  | MW | ii) Barishal area |  |  |  | 361.8 | MW
iii) Cumilla area |  |  | 1339 |  | MW | iii) Rajshahi area |  |  |  | 1423 | MW
iv) Mymensingh area |  |  | 938 |  | MW | iv) Rangpur area |  |  |  | 829 | MW
v) Sylhet area |  |  | 408 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13292.42 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 89 | 09:00 | 133 | Natore | 145 | 18:30
2 | AKSML | 12 | 01:00 | 68 | Hathazari | 81 | 23:00 | 134 | Nawabganj | 58 | 20:00
3 | Aftabnagar | 40 | 00:00 | 69 | Hatirjheel | 47 | 12:00 | 135 | Netrakona | 120 | 09:00
4 | Agargaon | 117 | 10:00 | 70 | Ishurdi | 68 | 04:00 | 136 | New | 76 | 09:00
5 | Agrabad | 74 | 12:00 | 71 | Jaldhaka | 63 | 07:00 | 137 | Niamatpur | 110 | 22:00
6 | Amnura | 47 | 22:00 | 72 | Jamalpur | 106 | 06:00 | 138 | Noapara | 43 | 07:00
7 | Ashuganj | 91 | 11:00 | 73 | Jashore | 155 | 08:00 | 139 | PHP | 8 | 23:00
8 | BSRM | 190 | 04:00 | 74 | Jhenaidah | 99 | 04:00 | 140 | Pabna | 102 | 19:00
9 | Bagerhat | 83 | 04:00 | 75 | Joydebpur | 158 | 19:30 | 141 | Palashbari | 122 | 19:30
10 | Bajitpur | 76 | 06:00 | 76 | Joypurhat | 70 | 19:00 | 142 | Panchagarh | 49 | 20:00
11 | Bakerganj | 11.18 | 00:00 | 77 | Juldah | 24 | 12:00 | 143 | Patiya | 11 | 00:00
12 | Bakulia | 96 | 13:00 | 78 | KSRM | 12 | 00:00 | 144 | Patuakhali | 56 | 18:30
13 | Banani | 44 | 10:00 | 79 | Kabirpur | 265 | 09:00 | 145 | Payra | 34 | 00:00
14 | Bangabhaban | 22 | 10:00 | 80 | Kachua | 83 | 05:00 | 146 | Postogola | 54 | 00:00
15 | Barapukuria | 60 | 18:30 | 81 | Kaliganj | 26 | 00:00 | 147 | Pubail | 30 | 18:30
16 | Barguna | 20 | 04:00 | 82 | Kallyanpur | 108 | 01:00 | 148 | Purbachal | 30 | 11:00
17 | Barishal | 95 | 00:00 | 83 | Kalurghat | 45 | 12:00 | 149 | Purbasadipur | 115 | 00:00
18 | Barishal-230 | 92 | 02:00 | 84 | Kamrangirchar | 78 | 19:00 | 150 | Rahanpur | 36 | 19:00
19 | Baroaulia | 68 | 11:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 40 | 12:00
20 | Baroirhat | 55 | 19:00 | 86 | Kasba | 33 | 04:00 | 152 | Rajbari | 75 | 00:00
21 | Bashundhara | 183 | 12:00 | 87 | Kazla | 106 | 00:00 | 153 | Rajendrapur | 132 | 09:00
22 | BashundharaCement | 7 | 00:00 | 88 | Keranigonj | 79 | 20:00 | 154 | Rajshahi | 120 | 19:00
23 | Beanibazar | 52 | 00:00 | 89 | Khagrachori | 28 | 01:00 | 155 | Rajshahi-230 | 82 | 03:00
24 | Benapole | 75 | 07:00 | 90 | Khulna | 55 | 21:00 | 156 | Ramganj | 108 | 18:00
25 | Bhaluka | 142 | 09:00 | 91 | Khulshi | 186 | 13:00 | 157 | Rampur | 40 | 00:00
26 | Bhandaria | 47 | 19:30 | 92 | Kishoreganj | 118 | 10:00 | 158 | Rangamati | 17 | 18:30
27 | Bhangura | 40 | 02:00 | 93 | Kodda | 318 | 09:00 | 159 | Rangpur | 128 | 19:30
28 | Bheramara(GK) | 66 | 07:00 | 94 | Kulaura | 36 | 01:00 | 160 | Ruppur | 3.8 | 10:00
29 | Bhulta | 211 | 06:00 | 95 | Kurigram | 64 | 18:00 | 161 | SSM | 3 | 08:00
30 | Bog-Sherpur | 66 | 05:00 | 96 | Kushtia | 116 | 07:00 | 162 | Saidpur | 92 | 07:00
31 | Bogura | 166 | 08:00 | 97 | Laksam | 30 | 01:00 | 163 | Satkhira | 138 | 07:00
32 | Borhanuddin | 86 | 00:00 | 98 | Lakshmipur | 40 | 22:00 | 164 | Satmasjid | 99 | 12:00
33 | Brahmanbaria | 110 | 07:00 | 99 | Lalbag | 70 | 13:00 | 165 | Savar | 202 | 19:30
34 | Cantonment | 152 | 10:00 | 100 | Lalmonirhat | 57 | 18:30 | 166 | SevenRings | 17.85 | 17:00
35 | Chandina | 19 | 10:00 | 101 | MI_Cement | 17.3 | 02:00 | 167 | ShahCement | 42 | 20:00
36 | Chandpur | 70 | 23:00 | 102 | Madanganj | 45 | 02:00 | 168 | Shahjadpur | 74 | 07:00
37 | Chandraghona | 35 | 01:00 | 103 | Madaripur | 96 | 05:00 | 169 | Shahjibazar | 100 | 00:00
38 | Chapai | 72 | 06:00 | 104 | Madartek | 81 | 00:00 | 170 | Shahmirpur | 50 | 14:00
39 | Charsaidpur | 44 | 13:00 | 105 | Madunaghat | 51 | 14:00 | 171 | Shariatpur | 76 | 01:00
40 | Chauddagram | 70 | 18:00 | 106 | Magura | 63 | 07:00 | 172 | Sherpur | 114 | 21:00
41 | Chhatak | 25 | 01:00 | 107 | Mahasthangarh | 73 | 05:00 | 173 | Shikalbaha | 22 | 00:00
42 | Chowmuhani | 140 | 22:00 | 108 | Maijdee | 38 | 09:00 | 174 | Shitalakhya | 84.5 | 11:00
43 | Chuadanga | 122 | 07:00 | 109 | Manikganj | 123 | 05:00 | 175 | Sholosohor | 47 | 15:00
44 | Coxsbazar | 147 | 13:00 | 110 | Maniknagar | 75 | 13:00 | 176 | Shyampur | 186 | 12:00
45 | Cumilla(N) | 113 | 18:00 | 111 | Matarbari | 50 | 04:00 | 177 | Siddhirganj | 125 | 10:00
46 | Cumilla(S) | 192 | 13:00 | 112 | Matuail | 80 | 12:00 | 178 | Sirajganj | 112 | 00:00
47 | Daganbhuiyan | 35 | 05:00 | 113 | Metrorail_Motijheel | 36 | 18:30 | 179 | Sonargaon | 129 | 08:00
48 | Daudkandi | 132 | 18:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreemongol | 62 | 00:00
49 | DhakaUniversity | 78 | 12:00 | 115 | Millgate | 100 | 12:00 | 181 | Sreepur | 113 | 07:00
50 | Dhamrai | 124 | 07:00 | 116 | Mirpur | 134 | 19:00 | 182 | Srinagar | 48 | 01:00
51 | Dhanmondi | 125 | 13:00 | 117 | Mirsorai | 48 | 11:00 | 183 | Sunamganj | 46 | 22:00
52 | Dohazari | 100 | 13:00 | 118 | Mirzapur | 44 | 03:00 | 184 | Sylhet | 50 | 18:30
53 | Faridpur | 154 | 03:00 | 119 | Mithapukur | 56 | 17:00 | 185 | Sylhet-132 | 88 | 18:00
54 | Fatullah | 93 | 11:00 | 120 | Modern | N/A | N/A | 186 | TK | 24 | 18:30
55 | Fenchuganj | 35 | 02:00 | 121 | Mogbazar | 100.2 | 11:00 | 187 | Tangail | 154 | 00:00
56 | Feni | 100 | 19:30 | 122 | Mongla | 55 | 17:00 | 188 | Taraganj | 24 | 18:30
57 | GPH | 87 | 04:00 | 123 | Motijheel | 50 | 11:00 | 189 | Tasnim | 33 | 14:00
58 | Ghatail | 76 | 00:00 | 124 | Muktagacha | 39 | 00:00 | 190 | Thakurgaon | 88 | 19:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 106 | 01:00 | 191 | Tongi | 138 | 15:00
60 | Ghorashal-230 | 115 | 02:00 | 126 | Muradnagar | 42 | 20:00 | 192 | Ullahpara | 40 | 08:00
61 | Goalpara | 39 | 04:00 | 127 | Mymensingh | 202 | 00:00 | 193 | Ullon | 59 | 00:00
62 | Gollamari | 96 | 09:00 | 128 | Nabinagar | 16 | 09:00 | 194 | Uttara | 84 | 11:00
63 | Gopalganj | 92 | 00:00 | 129 | Naogaon | 130 | 07:00 | 195 | UttaraNew | 34 | 00:00
64 | Gulshan | 124 | 11:00 | 130 | Narail | 63 | 21:00 | 196 | Zigatola | 96 | 00:00
65 | Halishahar | 101.5 | 12:00 | 131 | Narinda | 69 | 13:00
66 | HaripurSBU | 120 | 11:00 | 132 | Narshingdi | 170 | 06:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 05-04-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13969.5 | 1080 |  | 15098.5
1:00 | 13674.5 | 1075 |  | 14797.5
2:00 | 13742.7 | 915 |  | 14698.7
3:00 | 13704.5 | 789 |  | 14529.5
4:00 | 13724.7 | 588 |  | 14338.7
5:00 | 13562.5 | 514 |  | 14099.5
6:00 | 13458.95 | 519 |  | 14000.95
7:00 | 13603.18 | 449 |  | 14072.18
8:00 | 13651.31 | 405 |  | 14074.31
9:00 | 13665.91 | 400 |  | 14083.91
10:00 | 13337.87 | 495 |  | 13855.15
11:00 | 12974.37 | 602 |  | 13603.37
12:00 | 12899.4 | 607 |  | 13533.4
13:00 | 12420 | 511 |  | 12954
14:00 | 12333.34 | 526 |  | 12883.34
15:00 | 12546.99 | 485 |  | 13053.99
16:00 | 12554.15 | 765 |  | 13353.15
17:00 | 12769.3 | 462 |  | 13252.3
18:00 | 13107.7 | 378 |  | 13502.7
19:00 | 13541.33 | 821 |  | 14399.33
19:30 | 13722.68 | 791 |  | 14549.68
20:00 | 13737.33 | 777 |  | 14549.33
21:00 | 13829.22 | 737 |  | 14599.22
22:00 | 13540.42 | 775 |  | 14350.42
23:00 | 13468.5 | 699 |  | 14198.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 05-04-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8206.5 | 5763 | 13969.5 | DAILY GENERATION CURVE
00:30 | 8106.5 | 5715.5 | 13822
01:00 | 8006.5 | 5668 | 13674.5 | 05-04-2026
01:30 | 8026 | 5682.6 | 13708.6
02:00 | 8045.5 | 5697.2 | 13742.7
02:30 | 8043.5 | 5680.1 | 13723.6
03:00 | 8041.5 | 5663 | 13704.5
03:30 | 8052.5 | 5662.1 | 13714.6
04:00 | 8063.5 | 5661.2 | 13724.7
04:30 | 7997 | 5646.6 | 13643.6
05:00 | 7930.5 | 5632 | 13562.5
05:30 | 7934.145 | 5576.58 | 13510.725
06:00 | 7937.79 | 5521.16 | 13458.95
06:30 | 7937.665 | 5593.4 | 13531.065
07:00 | 7937.54 | 5665.64 | 13603.18
07:30 | 7922.385 | 5704.86 | 13627.245
08:00 | 7907.23 | 5744.08 | 13651.31
08:30 | 7860.155 | 5798.455 | 13658.61
09:00 | 7813.08 | 5852.83 | 13665.91
09:30 | 7708.235 | 5793.655 | 13501.89
10:00 | 7603.39 | 5734.48 | 13337.87
10:30 | 7435.675 | 5720.445 | 13156.12
11:00 | 7267.96 | 5706.41 | 12974.37
11:30 | 7249.18 | 5687.705 | 12936.885
12:00 | 7230.4 | 5669 | 12899.4
12:30 | 7009.94 | 5649.76 | 12659.7
13:00 | 6789.48 | 5630.52 | 12420
13:30 | 6678.01 | 5698.66 | 12376.67
14:00 | 6566.54 | 5766.8 | 12333.34
14:30 | 6640.065 | 5800.1 | 12440.165
15:00 | 6713.59 | 5833.4 | 12546.99
15:30 | 6784.49 | 5766.08 | 12550.57
16:00 | 6855.39 | 5698.76 | 12554.15
16:30 | 6962.37 | 5699.355 | 12661.725
17:00 | 7069.35 | 5699.95 | 12769.3
17:30 | 7251.565 | 5686.935 | 12938.5
18:00 | 7433.78 | 5673.92 | 13107.7
18:30 | 7639.14 | 5685.375 | 13324.515
19:00 | 7844.5 | 5696.83 | 13541.33
19:30 | 7962.5 | 5760.18 | 13722.68
20:00 | 7989.5 | 5747.83 | 13737.33
20:30 | 8000 | 5783.275 | 13783.275 |  | Executive Engineer
21:00 | 8010.5 | 5818.72 | 13829.22 |  | Network Operation Division
21:30 | 7871.5 | 5813.32 | 13684.82
22:00 | 7732.5 | 5807.92 | 13540.42
22:30 | 7720.5 | 5783.96 | 13504.46
23:00 | 7708.5 | 5760 | 13468.5

## En-Curve
QF-LDC-12
Date | 05-04-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3660 | 1462 | 869 | 0 | 174 | 765 | 80 | 4279 | 0 | 674 | 2006.5 | 0 | 0 | 0 | 1080 | DAILY ENERGY CURVE
00:30 | 3652 | 1450.5 | 868.5 | 0 | 172 | 763.5 | 80 | 4226 | 0 | 673.5 | 1936 | 0 | 0 | 0 | 1077.5 | 05-04-2026
01:00 | 3644 | 1439 | 868 | 0 | 170 | 762 | 80 | 4173 | 0 | 673 | 1865.5 | 0 | 0 | 0 | 1075
01:30 | 3661.5 | 1447.5 | 868.5 | 0 | 171 | 762.5 | 80 | 4181.1 | 0 | 659 | 1877.5 | 0 | 0 | 0 | 995 | Energy Generated | 321.2053 |  | MKWHr
02:00 | 3679 | 1456 | 869 | 0 | 172 | 763 | 80 | 4189.2 | 0 | 645 | 1889.5 | 0 | 0 | 0 | 915 | Energy not Served | 15.374 |  | MKWHr
02:30 | 3676.5 | 1455.5 | 869 | 0 | 170 | 762.5 | 80 | 4189.6 | 0 | 641.5 | 1879 | 0 | 0 | 0 | 852 | Total Energy Requirement | 336.5793 |  | MKWHr
03:00 | 3674 | 1455 | 869 | 0 | 168 | 762 | 80 | 4190 | 0 | 638 | 1868.5 | 0 | 0 | 0 | 789
03:30 | 3681.5 | 1465 | 869 | 0 | 165 | 761.5 | 80 | 4195.1 | 0 | 640.5 | 1856.5 | 0 | 0 | 0.5 | 688.5
04:00 | 3689 | 1475 | 869 | 0 | 162 | 761 | 80 | 4200.2 | 0 | 643 | 1844.5 | 0 | 0 | 1 | 588
04:30 | 3671 | 1455.5 | 868.5 | 0 | 162 | 763 | 80 | 4185.1 | 0 | 641.5 | 1816.5 | 0 | 0 | 0.5 | 551
05:00 | 3653 | 1436 | 868 | 0 | 162 | 765 | 80 | 4170 | 0 | 640 | 1788.5 | 0 | 0 | 0 | 514
05:30 | 3632 | 1442 | 880 | 0 | 160 | 763.5 | 80 | 4116 | 1.725 | 641 | 1794.5 | 0 | 0 | 0 | 516.5
06:00 | 3611 | 1448 | 892 | 0 | 158 | 762 | 80 | 4062 | 3.45 | 642 | 1800.5 | 0 | 0 | 0 | 519
06:30 | 3607 | 1448 | 892 | 0 | 154 | 764 | 80 | 4112.1 | 55.965 | 626.5 | 1789 | 0 | 0 | 2.5 | 484
07:00 | 3603 | 1448 | 892 | 0 | 150 | 766 | 80 | 4162.2 | 108.48 | 611 | 1777.5 | 0 | 0 | 5 | 449
07:30 | 3582 | 1431 | 894 | 0 | 153 | 764 | 80 | 4163.2 | 193.045 | 598.5 | 1766 | 0 | 0 | 2.5 | 427
08:00 | 3561 | 1414 | 896 | 0 | 156 | 762 | 80 | 4164.2 | 277.61 | 586 | 1754.5 | 0 | 0 | 0 | 405
08:30 | 3533 | 1374.5 | 896.5 | 0 | 160 | 760.695 | 80 | 4192.6 | 324.315 | 588.5 | 1748.5 | 0 | 0 | 0 | 402.5
09:00 | 3505 | 1335 | 897 | 0 | 164 | 759.39 | 80 | 4221 | 371.02 | 591 | 1742.5 | 0 | 0 | 0 | 400
09:30 | 3518 | 1335 | 896.5 | 0 | 164 | 759.985 | 80 | 4179.6 | 343.805 | 553 | 1672 | 0 | 0 | 0 | 447.5
10:00 | 3531 | 1335 | 896 | 0 | 164 | 760.58 | 80 | 4138.2 | 316.59 | 515 | 1601.5 | 0 | 0 | 0 | 495
10:30 | 3486.5 | 1316 | 896.5 | 0 | 171 | 761.24 | 80 | 4098.1 | 355.53 | 493.5 | 1491.75 | 0 | 0 | 6 | 548.5
11:00 | 3442 | 1297 | 897 | 0 | 178 | 761.9 | 80 | 4058 | 394.47 | 472 | 1382 | 0 | 0 | 12 | 602
11:30 | 3445 | 1307 | 896.5 | 0 | 187 | 762.055 | 80 | 4006.5 | 399.58 | 440 | 1403.75 | 0 | 0 | 9.5 | 604.5
12:00 | 3448 | 1317 | 896 | 0 | 196 | 762.21 | 80 | 3955 | 404.69 | 408 | 1425.5 | 0 | 0 | 7 | 607
12:30 | 3363 | 1292.5 | 896 | 0 | 194 | 762.93 | 80 | 3932.5 | 387.27 | 387.5 | 1358.5 | 0 | 0 | 5.5 | 559
13:00 | 3278 | 1268 | 896 | 0 | 192 | 763.65 | 80 | 3910 | 369.85 | 367 | 1291.5 | 0 | 0 | 4 | 511
13:30 | 3350.5 | 1263 | 896 | 0 | 184 | 763.005 | 80 | 3934.5 | 403.665 | 324 | 1168 | 0 | 0 | 10 | 518.5
14:00 | 3423 | 1258 | 896 | 0 | 176 | 762.36 | 80 | 3959 | 437.48 | 281 | 1044.5 | 0 | 0 | 16 | 526
14:30 | 3414.5 | 1340 | 896.5 | 0 | 180 | 759.505 | 80 | 3974 | 443.66 | 285.5 | 1052 | 0 | 0 | 14.5 | 505.5
15:00 | 3406 | 1422 | 897 | 0 | 184 | 756.65 | 80 | 3989 | 449.84 | 290 | 1059.5 | 0 | 0 | 13 | 485
15:30 | 3323.5 | 1447 | 896.5 | 0 | 183 | 756.27 | 80 | 3974 | 389.8 | 324.5 | 1166 | 0 | 0 | 10 | 625
16:00 | 3241 | 1472 | 896 | 0 | 182 | 755.89 | 80 | 3959 | 329.76 | 359 | 1272.5 | 0 | 0 | 7 | 765
16:30 | 3227 | 1480 | 903.5 | 0 | 180 | 754.785 | 80 | 3969.5 | 230.44 | 388.5 | 1444.5 | 0 | 0 | 3.5 | 613.5
17:00 | 3213 | 1488 | 911 | 0 | 178 | 753.68 | 80 | 3980 | 131.12 | 418 | 1616.5 | 0 | 0 | 0 | 462
17:30 | 3322.5 | 1382.5 | 913.5 | 0 | 175 | 754.17 | 80 | 3983 | 70.08 | 531.5 | 1726.25 | 0 | 0 | 0 | 420
18:00 | 3432 | 1277 | 916 | 0 | 172 | 754.66 | 80 | 3986 | 9.04 | 645 | 1836 | 0 | 0 | 0 | 378
18:30 | 3417.5 | 1346.5 | 918.5 | 0 | 176 | 754.745 | 80 | 4024.5 | 4.52 | 682.5 | 1919.75 | 0 | 0 | 0 | 599.5
19:00 | 3403 | 1416 | 921 | 0 | 180 | 754.83 | 80 | 4063 | 0 | 720 | 2003.5 | 0 | 0 | 0 | 821
19:30 | 3458 | 1438 | 923 | 0 | 160 | 755.18 | 80 | 4055 | 0 | 750 | 2103.5 | 0 | 0 | 0 | 791
20:00 | 3441 | 1506 | 922 | 0 | 160 | 756.83 | 80 | 3978 | 0 | 773 | 2110.5 | 10 | 0 | 0 | 777
20:30 | 3463.5 | 1561.5 | 922 | 0 | 169 | 756.275 | 80 | 3981.5 | 0 | 771.5 | 2073 | 5 | 0 | 0 | 757
21:00 | 3486 | 1617 | 922 | 0 | 178 | 755.72 | 80 | 3985 | 0 | 770 | 2035.5 | 0 | 0 | 0 | 737
21:30 | 3497.5 | 1565 | 922 | 0 | 176 | 755.32 | 80 | 3982 | 0 | 741.5 | 1965 | 0 | 0 | 0.5 | 756
22:00 | 3509 | 1513 | 922 | 0 | 174 | 754.92 | 80 | 3979 | 0 | 713 | 1894.5 | 0 | 0 | 1 | 775
22:30 | 3515 | 1513 | 922.5 | 0 | 176 | 758.46 | 80 | 3975 | 0 | 713.5 | 1847.5 | 0 | 0 | 3.5 | 737
23:00 | 3521 | 1513 | 923 | 0 | 178 | 762 | 80 | 3971 | 0 | 714 | 1800.5 | 0 | 0 | 6 | 699
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 05-04-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 397 | 22:00 | 385 | 11:00 | Madunaghat | 406 | 01:00 | 399 | 13:00
Amtali | 415 | 00:00 | 412 | 10:00 | Meghnaghat | 401 | 03:00 | 384 | 11:00
Ashuganj | 410 | 20:00 | 389 | 10:00 | Payra | 417 | 19:00 | 414 | 09:00
Bhulta | 404 | 19:00 | 382 | 09:00 | Rahanpur | 416 | 12:00 | 405 | 07:00
Bibiana | 412 | 19:00 | 404 | 02:00 | Rampal | 404 | 00:00 | 398 | 07:00
BIPTC | 402 | 08:00 | 390 | 00:00
Bogura | 410 | 12:00 | 397 | 07:00
Gopalganj | 406 | 20:00 | 398 | 08:00
Kaliakoir | 394 | 20:00 | 376 | 17:00
Korerhat | 410 | 19:00 | 401 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 234 | 20:00 | 222 | 10:00 | Jhenaidah | 230 | 11:00 | 215 | 07:00
AKSML | 242 | 18:30 | 235 | 12:00 | Kachua | 235 | 20:00 | 229 | 12:00
Aminbazar | 235 | 22:00 | 224 | 09:00 | Kaliakoir | 239 | 20:00 | 227 | 09:00
Ashuganj | 239 | 21:00 | 226 | 08:00 | Keranigonj | 232 | 20:00 | 221 | 09:00
Ashuganj-400 | 239 | 20:00 | 220 | 10:00 | Khulna(S) | 233 | 12:00 | 220 | 07:00
Baghabari | 234 | 02:00 | 230 | 06:00 | Korerhat | 235 | 19:00 | 229 | 09:00
Barapukuria | 226 | 12:00 | 212 | 07:00 | Madunaghat | 243 | 18:00 | 238 | 09:00
Barapukuria-230 | 226 | 12:00 | 210 | 8:00 | Madunaghat-400 | 243 | 01:00 | 238 | 13:00
Barishal | 234 | 13:00 | 227 | 15:00 | Maniknagar | 231 | 19:00 | 218 | 10:00
Bheramara | 233 | 11:00 | 222 | 07:00 | Meghnaghat | 240 | 23:00 | 225 | 10:00
Bhulta | 233 | 19:00 | 219 | 09:00 | Meghnaghat-400 | 235 | 20:00 | 220 | 10:00
Bibiana | 238 | 19:00 | 234 | 00:00 | Mirsorai | 234 | 20:00 | 224 | 15:00
BIPTC | 235 | 11:00 | 222 | 07:00 | Purbasadipur | 226 | 10:00 | 211 | 07:00
Bogura | 235 | 12:00 | 225 | 07:00 | Rajshahi | 232 | 11:00 | 220 | 08:00
Bogura-400 | 235 | 12:00 | 226 | 07:00 | Rampal | 232 | 11:00 | 221 | 07:00
Borhanuddin | 233 | 13:00 | 230 | 04:00 | Rampur | N/A | N/A | N/A | N/A
BSRM | 235 | 19:00 | 230 | 12:00 | Rampura | 232 | 19:00 | 218 | 10:00
Chowmuhani | 233 | 18:00 | 229 | 10:00 | Shikalbaha | 242 | 21:00 | 236 | 13:00
Cumilla(N) | 233 | 19:00 | 224 | 09:00 | Shyampur | 233 | 22:00 | 220 | 09:00
Faridpur | 227 | 19:00 | 222 | 07:00 | Siddhirganj | 234 | 20:00 | 223 | 08:00
Fenchuganj | 240 | 16:00 | 235 | 03:00 | Sirajgonj | 240 | 19:00 | 233 | 09:00
Feni | 235 | 20:00 | 229 | 09:00 | Sreepur | 231 | 19:00 | 222 | 08:00
Ghorashal | 235 | 18:30 | 230 | 00:00 | Tongi | 236 | 19:30 | 225 | 11:00
Ghorashal-230 | 232 | 20:00 | 220 | 09:00
Gopalganj | 227 | 19:00 | 223 | 07:00
GPH | 240 | 20:00 | 235 | 12:00
Haripur | 233 | 19:00 | 220 | 10:00
Hasnabad | 232 | 19:00 | 219 | 09:00
Hathazari | 241 | 20:00 | 235 | 17:00
Ishurdi | 236 | 11:00 | 224 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 19:00 | 128 | 10:00 | Madunaghat | 141 | 19:00 | 137 | 11:00
Agargaon | 137 | 20:00 | 129 | 10:00 | Magura | 138 | 12:00 | 127 | 07:00
Agrabad | 139 | 18:30 | 133 | 14:00 | Mahasthangarh | 132 | 10:00 | 124 | 07:00
AKS | 136 | 17:00 | 133 | 10:00 | Maijdee | 130 | 19:00 | 127 | 10:00
Aminbazar | 134 | 22:00 | 126 | 09:00 | Manikganj | 132 | 21:00 | 122 | 09:00
Amnura | 136 | 12:00 | 128 | 03:00 | Maniknagar | 136 | 20:00 | 127 | 10:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 126 | 18:00 | 113 | 05:00
Ashuganj-230 | 140 | 13:00 | 135 | 08:00 | Matuail | 135 | 21:00 | 126 | 10:00
Bagerhat | 133 | 13:00 | 118 | 07:00 | Metrorail_Motijheel | 136 | 20:00 | 127 | 10:00
Bajitpur | 135 | 19:00 | 126 | 09:00 | Metrorail_Uttara | 133 | 19:00 | 124 | 09:00
Bakerganj | 135 | 03:00 | 132 | 15:00 | Millgate | 137 | 09:00 | 127 | 09:00
Bakulia | 139 | 00:00 | 134 | 13:00 | Mirpur | 132 | 04:00 | 124 | 09:00
Banani | 138 | 19:00 | 129 | 09:00 | Mirzapur | 133 | 20:00 | 124 | 17:00
Bangabhaban | 135 | 19:00 | 126 | 10:00 | Mithapukur | 132 | 10:00 | 122 | 07:00
Barapukuria | 135 | 12:00 | 123 | 07:00 | MI_Cement | 132 | 20:00 | 122.1 | 10:00
Barguna | 135 | 13:00 | 132 | 01:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 137 | 18:30 | 133 | 09:00 | Mogbazar | 140 | 19:00 | 129 | 10:00
Barishal-230 | 135 | 14:00 | 132 | 10:00 | Mongla | 132 | 13:00 | 119 | 07:00
Baroaulia | 139 | 18:00 | 136 | 09:00 | Motijheel | 135 | 19:00 | 126 | 10:00
Baroirhat | 134 | 19:00 | 130 | 12:00 | Muktagacha | 129 | 10:00 | 117 | 15:00
Bashundhara | 137 | 19:00 | 127 | 09:00 | Munshiganj | 134 | 20:00 | 124 | 09:00
BashundharaCement | 135 | 19:00 | 127 | 08:00 | Muradnagar | 131 | 19:00 | 125 | 09:00
Beanibazar | 134 | 07:00 | 127 | 00:00 | Mymensingh | 131 | 13:00 | 115 | 17:00
Benapole | 137 | 11:00 | 120 | 06:00 | Nabinagar | 134 | 22:00 | 126 | 09:00
Bhaluka | 137 | 19:00 | 126 | 08:00 | Naogaon | 138 | 19:00 | 119 | 07:00
Bhandaria | 133 | 22:00 | 129 | 16:00 | Narail | 138 | 12:00 | 127 | 06:00
Bhangura | 133 | 12:00 | 128 | 07:00 | Narinda | 136 | 20:00 | 127 | 10:00
Bheramara | 136 | 11:00 | 131 | 07:00 | Narshingdi | 134 | 19:00 | 127 | 18:30
Bheramara(GK) | 136 | 11:00 | 131 | 07:00 | Natore | 133 | 12:00 | 126 | 07:00
Bhulta | 129 | 18:30 | 121 | 09:00 | Nawabganj | 140 | 19:00 | 133 | 09:00
Bog-Sherpur | 133 | 09:00 | 127 | 07:00 | Netrakona | 131 | 19:00 | 115 | 08:00
Bogura | 134 | 10:00 | 130 | 05:00 | New | 137 | 22:00 | 128 | 09:00
Bogura-230 | 135 | 16:00 | 128 | 07:00 | Niamatpur | 139 | 12:00 | 134 | 22:00
Brahmanbaria | 134 | 13:00 | 123 | 17:00 | Noapara | 136 | 11:00 | 124 | 07:00
Cantonment | 136 | 20:00 | 129 | 09:00 | Pabna | 135 | 10:00 | 125 | 14:00
Chandina | 134 | 19:00 | 129 | 09:00 | Palashbari | 131 | 11:00 | 119 | 07:00
Chandpur | 138 | 18:30 | 132 | 12:00 | Panchagarh | 138 | 04:00 | 131 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 141 | 19:00 | 137 | 11:00 | Patiya | 138 | 18:00 | 133 | 07:00
Chapai | 136 | 10:00 | 134 | 04:00 | Patuakhali | 135 | 18:30 | 132 | 10:00
Charsaidpur | 134 | 19:00 | 126 | 09:00 | Payra | 137 | 00:00 | 135 | 15:00
Chauddagram | 132 | 19:30 | 127 | 15:00 | PHP | 133 | 19:00 | 129 | 12:00
Chhatak | 133 | 07:00 | 127 | 11:00 | Postogola | 134 | 19:00 | 125 | 10:00
Chowmuhani | 132 | 22:00 | 126 | 10:00 | Pubail | 140 | 19:00 | 130 | 08:00
Chuadanga | 136 | 11:00 | 122 | 07:00 | Purbachal | 136 | 18:00 | 127 | 09:00
Coxsbazar | 127 | 18:00 | 113 | 13:00 | Purbasadipur | 132 | 10:00 | 121 | 07:00
Cumilla(N) | 134 | 19:00 | 130 | 08:00 | Rahanpur | 139 | 00:00 | 136 | 06:00
Cumilla(S) | 134 | 19:00 | 120 | 12:00 | Rahanpur-400 | 140 | 12:00 | 135 | 07:00
Daganbhuiyan | 131 | 19:00 | 128 | 09:00 | Rahim | 134 | 18:30 | 126 | 10:00
Daudkandi | 129 | 18:30 | 123 | 08:00 | Rajbari | 130 | 14:00 | 126 | 07:00
DhakaUniversity | 137 | 20:00 | 129 | 09:00 | Rajendrapur | 136 | 19:00 | 125 | 09:00
Dhamrai | 134 | 22:00 | 125 | 09:00 | Rajshahi | 132 | 11:00 | 125 | 07:00
Dhanmondi | 139 | 19:00 | 129.5 | 09:00 | Rajshahi-230 | 136 | 08:00 | 125 | 07:00
Dohazari | 134 | 18:30 | 127 | 13:00 | Ramganj | 132 | 20:00 | 129 | 02:00
Faridpur | 131 | 18:30 | 128 | 01:00 | Rampur | 138 | 00:00 | 133 | 13:00
Fatullah | 134 | 19:00 | 123 | 09:00 | Rampura | 138 | 19:00 | 128 | 10:00
Fenchuganj | 136 | 14:00 | 133 | 03:00 | Rangamati | 140 | 18:00 | 136 | 11:00
Feni | 131 | 19:00 | 128 | 00:00 | Rangpur | 132 | 10:00 | 123 | 07:00
Feni-230 | 132 | 20:00 | 128 | 10:00 | Ruppur | 136 | 11:00 | 131 | 07:00
Ghatail | 127 | 10:00 | 118 | 06:00 | Saidpur | 133 | 10:00 | 124 | 07:00
Ghorashal | 140 | 20:00 | 133 | 15:00 | Satkhira | 135 | 11:00 | 119 | 07:00
Goalpara | 137 | 11:00 | 125 | 07:00 | Satmasjid | 137 | 22:00 | 129 | 10:00
Gollamari | 136 | 11:00 | 127 | 07:00 | Savar | 139 | 05:00 | 124 | 09:00
Gopalganj | 134 | 11:00 | 128 | 07:00 | SevenRings | 141 | 19:00 | 133 | 09:00
Gopalganj-400 | 135 | 19:00 | 132 | 07:00 | ShahCement | 134 | 19:00 | 126 | 09:00
Gulshan | 138 | 19:00 | 128 | 10:00 | Shahjadpur | 136 | 12:00 | 132 | 08:00
Halishahar | 139 | 00:00 | 134 | 13:00 | Shahjibazar | 136 | 13:00 | 129 | 08:00
Haripur | 135 | 19:30 | 127 | 09:00 | Shahmirpur | 140 | 19:30 | 135 | 13:00
HaripurSBU | 135 | 19:00 | 127 | 09:00 | Shariatpur | 133 | 13:00 | 130 | 03:00
Hasnabad | 134 | 19:00 | 125 | 09:00 | Sherpur | 125 | 10:00 | 112 | 15:00
Hathazari | 141 | 20:00 | 136 | 11:00 | Shikalbaha | 129 | 19:00 | 123 | 13:00
Hatirjheel | 138 | 19:00 | 128 | 10:00 | Shikalbaha-230 | 140 | 00:00 | 137 | 11:00
Ishurdi | 138 | 11:00 | 132 | 07:00 | Shitalakhya | 132 | 20:00 | 122.2 | 10:00
Jaldhaka | 131 | 10:00 | 123 | 07:00 | Sholosohor | 140 | 20:00 | 136 | 12:00
Jamalpur | 128 | 10:00 | 114 | 17:00 | Shyampur | 133 | 18:30 | 124 | 11:00
Jashore | 135 | 11:00 | 123 | 06:00 | Shyampur-230 | 136 | 22:00 | 126 | 10:00
Jhenaidah | 141 | 11:00 | 125 | 04:00 | Siddhirganj | 135 | 18:30 | 127 | 09:00
Jhenaidah-230 | 141 | 11:00 | 128 | 07:00 | Sirajganj | 132 | 09:00 | 126 | 07:00
Joydebpur | 137 | 00:00 | 128 | 15:00 | Sonargaon | 135 | 15:00 | 125 | 09:00
Joypurhat | 125 | 10:00 | 115 | 07:00 | Sreemongol | 136 | 13:00 | 129 | 03:00
Juldah | 140 | 18:00 | 134 | 13:00 | Sreepur | 138 | 11:00 | 130 | 08:00
Kabirpur | 138 | 00:00 | 123 | 09:00 | Srinagar | 141 | 19:00 | 134 | 09:00
Kachua | 135 | 20:00 | 130 | 10:00 | SSM | 142 | 00:00 | 140 | 07:00
Kaliakoir | 138 | 20:00 | 128 | 09:00 | Sunamganj | 130 | 07:00 | 126 | 00:00
Kaliganj | 139 | 11:00 | 128 | 06:00 | Sylhet | 133 | 07:00 | 129 | 00:00
Kallyanpur | 132 | 18:00 | 125 | 09:00 | Sylhet-132 | 132 | 05:00 | 130 | 00:00
Kalurghat | 140 | 03:00 | 136 | 13:00 | Tangail | 129 | 10:00 | 120 | 13:00
Kamrangirchar | 141 | 19:00 | 124 | 10:00 | Taraganj | 132 | 12:00 | 120 | 07:00
Kaptai | N/A | N/A | N/A | N/A | Tasnim | 135 | 15:00 | 126 | 10:00
Kasba | 130 | 13:00 | 124 | 08:00 | Thakurgaon | 137 | 04:00 | 130 | 08:00
Kazla | 135 | 20:00 | 127 | 10:00 | TK | 140 | 18:00 | 136 | 13:00
Keranigonj | 141 | 19:00 | 134 | 09:00 | Tongi | 138 | 19:30 | 131 | 09:00
Khagrachori | 139 | 18:00 | 135 | 10:00 | Ullahpara | 133 | 09:00 | 128 | 08:00
Khulna | 136 | 11:00 | 126 | 07:00 | Ullon | 138 | 18:30 | 127 | 10:00
Khulna(S) | 137 | 11:00 | 127 | 07:00 | Uttara | 133 | 22:00 | 124 | 09:00
Khulshi | 137 | 00:00 | 132 | 13:00 | UttaraNew | 133 | 19:00 | 124 | 09:00
Kishoreganj | 133 | 19:00 | 124 | 08:00 | Zigatola | 141 | 20:00 | 133 | 09:00
Kodda | 139 | 00:00 | 126 | 11:00
Korerhat | 136 | 03:00 | 133 | 09:00
KSRM | 140 | 00:00 | 135 | 11:00
Kulaura | 136 | 13:00 | 132 | 18:00
Kurigram | 131 | 10:00 | 119 | 07:00
Kushtia | 137 | 11:00 | 127 | 07:00
Laksam | 134 | 20:00 | 131 | 04:00
Lakshmipur | 130 | 19:00 | 127 | 10:00
Lalbag | 141 | 22:00 | 134 | 10:00
Lalmonirhat | 127 | 22:00 | 121 | 07:00
Madanganj | 135 | 19:00 | 127 | 08:00
Madaripur | 135 | 14:00 | 130 | 00:00
Madartek | 136 | 21:00 | 127 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division