## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-01-04 | Friday
|  | Date (day): | 2019-01-04 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10339 | MW |  |  | (b) At Evening Peak Hour : |  | 12385 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-01-03 | 2019-01-04 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit #1 Under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 155 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 320 | 350 | 320 | 330
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 20 | 35 | 40 | 40 | 38 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 101 | 104 | 100 | 100
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 345 | 350 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 285 | 365 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 |  |  | Reserve
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 20 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 40 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 0 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 97 | 150 | 80 | 200 |  |  | FGMO
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 180 | 120 | 200 | 200
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
21 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 32 | 102 | 102
22 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 47 | 47 | 47 |  | 4 | Engoine problem
23 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 18 | 54 | 54 | 54
24 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
25 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 54 | 55 | 55
26 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 36 | 36 |  | 19 | Engine problem
27 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 24 | 47 | 8 | 47 |  | 61 | Engine problem
28 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 57 | 58 | 58 |  | 22 | Engine problem
29 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
30 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 38 | 43 | 43 | 43 |  | 9 | Engine problem
32 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
33 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 12 | 0 | 300
34 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 0 | 60 | 130 | 130 |  | 19 | Engine problem
| Dhaka area Total |  |  |  |  | 6034 | 5798 | 2038 | 2302 | 3732 | 4401 | 298 | 534
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 150 | 120 | 120 | 60 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 25 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.5 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 37 | 50 | 50
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 42 | 42 | 67 | 67 |  | 163 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 120 | 150 | 150 |  |  | FGMO
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 50 | 50 | 50 | 50 |  | 11
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 70
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 0 | 68
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 90 | 90 |  | 10 | Engine problem
50 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 80 | 92 | 100 | 100
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 27 | 20 | 20
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 13 | 13 | 90 | 100 |  | 8 | Engine problem
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 494.5 | 656 | 804 | 932 | 240 | 457
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 100 | 100 | 100 | 29 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 100 | 100 | 100 | 34 |  | Gas shortage
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 193 | 184 | 221 | 221 |  |  | FGMO
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 260 | 260 |  | 100 | ST Under maint.
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 261 | 360 | 360 |  |  | FGMO
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 40 | 40 | 40 |  | 5 | Engine problem
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 30 | 55 | 0 |  | Gas shortage
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas Shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 0
62 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 88 | 150 | 150
63 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 40 | 85 | 85 | 85
64 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 40
65 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 95 | 100 | 100 |  | 63 | FGMO & STG under maint.
66 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 0 | 155 | 180 | 180
67 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
68 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 0 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 90 | 120 | 85 | 109
69 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 8 | 25 | 0 | 33
70 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
71 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 15 | 22 | 22
72 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1062 | 1367 | 1871 | 2204 | 433 | 168
73 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 170 | 147 | 176 | 176 | 55 |  | Gas shortage
74 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
75 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 80 | 80 | 80 |  | 15 | Engine problem.
76 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.1 | 0 | 2 | 0
77 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 7 | 115 | 100 | 200
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 201.1 | 364 | 380 | 478 | 55 | 15
78 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 26 | 56 | 26 | 26
79 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 63 | 63 | 63 | 63
80 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 163 | 163 | 163
81 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 231 | 220 | 230 | 230 |  |  | FGMO
82 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 22 | 53 | 51 | 51
83 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 21 | 0 | 21 | 21 |  | 23 | Engine problem
84 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
85 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 65 | 56 | 66 | 66 |  |  | FGMO
86 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 86 | 86 | 86
87 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 47 | 48 | 50 | 50
88 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 78 | 78 | 78 | 140
89 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 19 | 20 | 20
90 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 25 | 25 | 50 | 50
91 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 25 | 0 | 25
92 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 210 | 280 | 341 | 341 |  |  | FGMO
| Bibiyana-3 285MW |  | Gas | PDB | 285 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
93 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 9 | 0 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 943 | 1192 | 1256 | 1353 | 0 | 23
94 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 522 | 668 | 330 | 676
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
95 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 99 | 115 | 115
96 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 30 | 0 | 40
97 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
98 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 36 | 0 | 80
99 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 340 | 340 | 410 | 410
100 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
102 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 105 | 105 | 105
| Khulna Area Total |  |  |  |  | 2223 | 2209 | 955 | 1318 | 1100 | 1612 | 0 | 0
103 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 110 | 110
104 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
105 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 26 | 25 | 25 |  | 8 | Engine problem
106 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 195 | 171 | 194 | 194
107 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 51 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 266 | 342 | 424 | 454 | 0 | 8
108 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage.
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 80 | 80 | 80 | 80 |  | 20
109 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50
110 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
111 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
112 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
113 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
114 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
115 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 167 | 159 | 220 | 220 |  |  | FGMO
116 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 141 | 141 | 0 | 0 | 0 | 0 | 141 |  | Gas shortage.
117 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 0 | 0 | 0 | 0 | 282 |  | Gas shortage.
118 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 39 | 0 | 35
119 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
120 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 7 | 10 |  | 0
121 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
122 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 43 | 43 | 52
123 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 90 | 100
| Rajshahi Area Total |  |  |  |  | 1556 | 1546 | 310 | 515 | 623 | 770 | 704 | 20
124 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint.
125 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 149 | 149 | 149 | 125 |  | Coal shortage
126 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 17
127 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15
| Rangpur Area Total |  |  |  |  | 564 | 484 | 149 | 166 | 149 | 181 | 210 | 85
| Total |  |  |  |  | 17685 | 17142 | 6418.6 | 8222 | 10339 | 12385 | 1940 | 1310
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5993.9201 | 7678 | 9654.9309 | 11565.5595
A. |  | 2019-01-03 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 8222 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 4754 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8222 | MW
3 | Day peak Generation : |  |  | 6418.6 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7678 | MW
4 | Evening peak Generation : |  |  | 8222 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 151.5543 | MKWHr | By Solar | 0.1448 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 121.7013 | MKWHr |  | By Oil: | 10.5161 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.6527 | MKWHr |  | By Hydro: | 0.94619 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1940 | MW | Dhaka | 2750 | 2750 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1310 | MW | Chittagong | 819 | 819 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3250 | MW | Khulna | 992 | 992 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1044.57 | MMCFD |  |  | Rajshahi | 794 | 794 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 90507637.032 | ii) Oil : | Taka | 70410463.03 | Comilla | 686 | 686 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14099422 | Total | Taka | 175017522.062 | Mymensingh | 587 | 587 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 3.885 | MKWHr. | Sylhet | 310 | 310 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -460 | MW at | 19:00 | hrs | Barisal | 203 | 203 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -520 | MW at | 19:30 | hrs | Rangpur | 537 | 537 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 27.6° C |  |  | Total | 7678 | 7678 |  | 0
B. |  | 2019-01-04 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 27.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 7500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12385 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 5500 | MW
4 | Reserve(Generation end) |  |  |  | 4885 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 138.2458 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4711 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 12.4582 | MKWHr. | ii) HVDC Flow at Peak Time |  | 668 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.135 | MKWHr. | iii) Maximum HVDC Flow : |  | 668 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.32 |  | (b) Today: | 98.25 |  | (c) Rule Curve: |  | 102.62
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-01-03
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 94 | 0 | 0 | 250 | 42 | 35 | 305 | 260 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 150 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 33 | 33 | 0 | 0 | 35 | 0 | 0 | 120 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 100 | 100 | 0 | 309 | 192 | 8 | 100 | 40 | 24 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 76 | 164 | 0 | 0 | 0 | 10 | 63 | 5 | 5 | 100 | 220 | 57 | 5 | 5 | 78 | 0 | 8 | 0 | 275 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 337 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 19 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 34 | 0 | 5 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 179 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 4065 | 1282 | 5347 | 3461 | 337 | 1224 | 65 | 149 | 35 | 0 | 76 | 0 | 0 | 98.33
2:00 | 35 | 93 | 0 | 0 | 250 | 12 | 20 | 300 | 255 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 150 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 33 | 33 | 0 | 0 | 35 | 0 | 0 | 120 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 100 | 100 | 0 | 301 | 185 | 8 | 100 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 76 | 168 | 0 | 0 | 0 | 10 | 63 | 5 | 5 | 100 | 223 | 40 | 5 | 5 | 78 | 0 | 8 | 0 | 280 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 337 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 18 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 171 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3885 | 1193 | 5078 | 3327 | 337 | 1147 | 7 | 149 | 35 | 0 | 76 | 0 | 0 | 98.33
3:00 | 35 | 93 | 0 | 0 | 240 | 0 | 0 | 300 | 255 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 120 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 33 | 33 | 0 | 0 | 36 | 0 | 0 | 120 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 80 | 100 | 0 | 301 | 184 | 8 | 100 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 72 | 169 | 0 | 0 | 0 | 10 | 63 | 5 | 5 | 100 | 216 | 40 | 5 | 5 | 79 | 0 | 8 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 337 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 18 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 157 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3758 | 1204 | 4962 | 3271 | 337 | 1090 | 7 | 149 | 36 | 0 | 72 | 0 | 0 | 98.33
4:00 | 35 | 94 | 0 | 0 | 240 | 0 | 0 | 285 | 236 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 120 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 22 | 33 | 33 | 0 | 0 | 36 | 0 | 0 | 120 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 80 | 100 | 0 | 301 | 187 | 8 | 100 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 70 | 175 | 0 | 0 | 0 | 10 | 63 | 5 | 5 | 100 | 221 | 40 | 5 | 5 | 78 | 0 | 8 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 337 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 16 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 147 | 0 | 10 | 0 | 0 | 0 | 0 | 0 |  | 3711 | 1164 | 4875 | 3228 | 337 | 1048 | 7 | 149 | 36 | 0 | 70 | 0 | 0 | 98.33
5:00 | 35 | 0 | 0 | 0 | 240 | 0 | 0 | 280 | 235 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 120 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 22 | 33 | 33 | 0 | 0 | 36 | 0 | 0 | 120 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 80 | 80 | 0 | 334 | 182 | 8 | 100 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 68 | 155 | 0 | 0 | 0 | 10 | 40 | 5 | 5 | 100 | 230 | 54 | 5 | 5 | 78 | 0 | 8 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 337 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 16 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 149 | 0 | 10 | 0 | 0 | 0 | 0 | 0 |  | 3620 | 1134 | 4754 | 3100 | 337 | 1057 | 7 | 149 | 36 | 0 | 68 | 0 | 0 | 98.32
6:00 | 35 | 0 | 0 | 0 | 240 | 0 | 0 | 315 | 307 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 130 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 22 | 33 | 33 | 0 | 0 | 37 | 0 | 0 | 120 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 80 | 80 | 0 | 334 | 204 | 8 | 100 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 70 | 153 | 0 | 0 | 0 | 10 | 40 | 5 | 5 | 100 | 238 | 70 | 5 | 5 | 79 | 0 | 8 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 337 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 17 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 161 | 0 | 10 | 0 | 0 | 0 | 0 | 0 |  | 3845 | 1217 | 5062 | 3272 | 337 | 1190 | 7 | 149 | 37 | 0 | 70 | 0 | 0 | 98.32
7:00 | 35 | 0 | 0 | 0 | 280 | 0 | 0 | 365 | 305 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 180 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 22 | 33 | 33 | 0 | 0 | 37 | 0 | 0 | 120 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 80 | 80 | 0 | 334 | 205 | 8 | 100 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 72 | 156 | 0 | 0 | 0 | 10 | 40 | 5 | 5 | 100 | 240 | 70 | 5 | 5 | 79 | 0 | 8 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1.48 | 0 | 0 | 0 | 0 |  | 337 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 153 | 17 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 166 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 4074.48 | 1271 | 5345.48 | 3540 | 337 | 1194 | 15 | 149 | 37 | 0 | 72 | 1.48 | 0 | 98.32
8:00 | 35 | 0 | 0 | 0 | 320 | 12 | 0 | 390 | 336 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 200 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 22 | 33 | 33 | 2 | 0 | 37 | 0 | 0 | 120 | 0 | 0 | 0 | 122 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 0 | 80 | 80 | 0 | 334 | 200 | 8 | 100 | 40 | 5 | 5 | 5 | 5 | 0 | 0 | 19 | 8 | 0 | 15 | 80 | 176 | 0 | 14 | 0.4 | 26 | 63 | 5 | 5 | 100 | 234 | 69 | 5 | 5 | 78 | 0 | 6 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7.5 | 25 | 0 | 0 | 0 |  | 522 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 206 | 18 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 18 | 6 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 178 | 0 | 11 | 0 | 0 | 0 | 0 | 17 |  | 4407.9 | 1601 | 6008.9 | 3802 | 522 | 1305 | 106 | 149 | 37 | 0 | 80 | 7.9 | 0 | 98.38
9:00 | 35 | 20 | 0 | 0 | 320 | 52 | 0 | 360 | 370 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 200 | 0 | 97 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 33 | 33 | 30 | 0 | 37 | 0 | 0 | 120 | 8 | 0 | 0 | 120 | 0 | 0 | 37 | 0 | 0 | 9 | 12 | 1 | 22 | 5 | 0 | 80 | 80 | 0 | 305 | 226 | 8 | 100 | 40 | 5 | 5 | 5 | 5 | 0 | 0 | 19 | 8 | 0 | 15 | 86 | 175 | 0 | 22 | 1.2 | 26 | 63 | 5 | 12 | 100 | 218 | 59 | 5 | 48 | 78 | 0 | 24 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 13 | 80 | 0 | 0 | 0 |  | 523 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 200 | 18 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 18 | 6 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 176 | 0 | 11 | 0 | 0 | 0 | 0 | 53 |  | 4622.2 | 1644 | 6266.2 | 3726 | 523 | 1422 | 309 | 149 | 37 | 0 | 86 | 14.2 | 0 | 98.38
10:00 | 35 | 140 | 0 | 0 | 320 | 52 | 0 | 345 | 290 | 0 | 0 | 400 | 0 | 0 | 0 | 14 | 160 | 0 | 92 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 26 | 33 | 33 | 0 | 0 | 37 | 0 | 0 | 120 | 8 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 10 | 13 | 6 | 22 | 4 | 0 | 80 | 80 | 0 | 305 | 224 | 8 | 100 | 37 | 5 | 5 | 5 | 5 | 0 | 0 | 19 | 8 | 8 | 15 | 92 | 173 | 0 | 22 | 1.6 | 25 | 63 | 5 | 18 | 100 | 217 | 53 | 5 | 48 | 78 | 0 | 25 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 17.4 | 80 | 0 | 0 | 0 |  | 523 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 182 | 19 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 18 | 8 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 170 | 0 | 11 | 0 | 0 | 0 | 0 | 53 |  | 4640 | 1653 | 6293 | 3804 | 523 | 1331 | 338 | 149 | 37 | 0 | 92 | 19 | 0 | 98.38
11:00 | 35 | 155 | 0 | 0 | 320 | 52 | 0 | 348 | 285 | 0 | 0 | 225 | 0 | 0 | 0 | 30 | 198 | 0 | 97 | 0 | 0 | 32 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 27 | 33 | 7 | 0 | 37 | 0 | 0 | 120 | 8 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 10 | 13 | 6 | 22 | 4 | 0 | 80 | 80 | 0 | 305 | 184 | 8 | 100 | 40 | 5 | 5 | 25 | 40 | 0 | 0 | 19 | 8 | 8 | 15 | 90 | 172 | 0 | 22 | 2 | 25 | 63 | 16 | 18 | 100 | 217 | 51 | 50 | 47 | 80 | 0 | 25 | 0 | 200 | 0 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 19.2 | 80 | 0 | 0 | 0 |  | 522 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 196 | 19 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 165 | 0 | 30 | 0 | 0 | 0 | 0 | 53 |  | 4536.2 | 1687 | 6223.2 | 3841 | 522 | 1187 | 376 | 149 | 37 | 0 | 90 | 21.2 | 0 | 98.38
12:00 | 35 | 155 | 0 | 0 | 320 | 101 | 20 | 345 | 285 | 0 | 0 | 225 | 0 | 0 | 0 | 30 | 180 | 0 | 97 | 0 | 0 | 32 | 0 | 10 | 24 | 0 | 0 | 18 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 38 | 0 | 42 | 0 | 0 | 120 | 8 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 10 | 13 | 6 | 22 | 4 | 0 | 80 | 80 | 0 | 320 | 193 | 8 | 100 | 40 | 5 | 5 | 51 | 40 | 0 | 0 | 19 | 8 | 8 | 15 | 90 | 170 | 0 | 22 | 2.1 | 26 | 63 | 22 | 21 | 100 | 231 | 65 | 50 | 47 | 78 | 0 | 25 | 0 | 210 | 0 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 19.5 | 80 | 0 | 0 | 0 |  | 522 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 195 | 20 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 167 | 0 | 51 | 0 | 0 | 0 | 0 | 53 |  | 4738.6 | 1680 | 6418.6 | 3827 | 522 | 1323 | 444 | 149 | 42 | 0 | 90 | 21.6 | 0 | 98.38
13:00 | 35 | 85 | 0 | 0 | 380 | 104 | 35 | 350 | 285 | 0 | 0 | 225 | 0 | 0 | 0 | 30 | 180 | 0 | 115 | 0 | 0 | 7 | 0 | 10 | 24 | 0 | 0 | 18 | 0 | 0 | 19 | 25 | 32 | 33 | 33 | 43 | 0 | 42 | 0 | 0 | 120 | 8 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 10 | 19 | 6 | 22 | 10 | 0 | 80 | 80 | 0 | 305 | 186 | 8 | 100 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 8 | 8 | 15 | 92 | 146 | 0 | 22 | 2 | 53 | 63 | 22 | 21 | 163 | 220 | 53 | 50 | 47 | 97 | 0 | 24 | 0 | 310 | 0 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 18.7 | 80 | 0 | 0 | 0 |  | 523 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 188 | 19 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 173 | 0 | 52 | 0 | 0 | 0 | 0 | 53 |  | 4965.7 | 1680 | 6645.7 | 3835 | 523 | 1554 | 430 | 149 | 42 | 0 | 92 | 20.7 | 0 | 98.38
14:00 | 35 | 0 | 0 | 0 | 320 | 104 | 35 | 349 | 290 | 0 | 0 | 225 | 0 | 0 | 0 | 15 | 180 | 0 | 100 | 0 | 0 | 7 | 0 | 0 | 24 | 0 | 0 | 18 | 0 | 0 | 16 | 25 | 32 | 33 | 33 | 43 | 0 | 41 | 0 | 0 | 120 | 8 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 10 | 13 | 6 | 22 | 7 | 0 | 80 | 80 | 0 | 305 | 186 | 8 | 102 | 40 | 5 | 5 | 51 | 10 | 0 | 0 | 19 | 8 | 8 | 0 | 92 | 148 | 0 | 22 | 1.8 | 56 | 62 | 22 | 21 | 100 | 231 | 46 | 10 | 46 | 98 | 0 | 25 | 0 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 16 | 92 | 0 | 0 | 0 |  | 523 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 191 | 18 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 162 | 0 | 22 | 0 | 0 | 0 | 0 | 53 |  | 4591.8 | 1601 | 6192.8 | 3622 | 523 | 1337 | 411 | 149 | 41 | 0 | 92 | 17.8 | 0 | 98.38
15:00 | 35 | 0 | 0 | 0 | 320 | 104 | 35 | 365 | 300 | 0 | 0 | 225 | 0 | 0 | 0 | 15 | 180 | 0 | 100 | 0 | 0 | 7 | 0 | 0 | 24 | 0 | 0 | 18 | 0 | 0 | 16 | 25 | 32 | 33 | 33 | 43 | 0 | 41 | 0 | 0 | 120 | 8 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 10 | 13 | 6 | 22 | 2 | 0 | 80 | 80 | 0 | 324 | 205 | 8 | 100 | 40 | 5 | 5 | 51 | 10 | 0 | 0 | 19 | 8 | 8 | 15 | 92 | 148 | 0 | 22 | 1 | 56 | 62 | 22 | 21 | 100 | 234 | 64 | 10 | 47 | 78 | 0 | 25 | 0 | 330 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 12.5 | 92 | 0 | 0 | 0 |  | 522 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 195 | 17 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 168 | 0 | 22 | 0 | 0 | 0 | 0 | 53 |  | 4691.5 | 1609 | 6300.5 | 3700 | 522 | 1372 | 411 | 149 | 41 | 0 | 92 | 13.5 | 0 | 98.38
16:00 | 35 | 0 | 0 | 0 | 320 | 104 | 35 | 352 | 300 | 0 | 0 | 225 | 0 | 0 | 0 | 15 | 180 | 0 | 160 | 0 | 0 | 7 | 0 | 0 | 8 | 0 | 0 | 18 | 0 | 0 | 16 | 25 | 32 | 33 | 33 | 43 | 0 | 41 | 0 | 0 | 120 | 8 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 10 | 13 | 6 | 22 | 2 | 0 | 80 | 80 | 0 | 331 | 202 | 8 | 100 | 40 | 5 | 5 | 51 | 10 | 0 | 0 | 19 | 11 | 8 | 15 | 92 | 148 | 0 | 22 | 0.5 | 56 | 62 | 22 | 21 | 100 | 228 | 65 | 10 | 47 | 78 | 0 | 25 | 0 | 295 | 0 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 6.5 | 30 | 0 | 0 | 0 |  | 523 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 40 | 196 | 17 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 159 | 0 | 22 | 0 | 0 | 0 | 0 | 17 |  | 4618 | 1556 | 6174 | 3738 | 523 | 1337 | 280 | 149 | 41 | 7 | 92 | 7 | 0 | 98.38
17:00 | 35 | 0 | 0 | 0 | 300 | 104 | 35 | 360 | 365 | 0 | 0 | 225 | 0 | 0 | 0 | 15 | 150 | 0 | 135 | 0 | 0 | 7 | 0 | 0 | 8 | 0 | 0 | 18 | 18 | 17 | 19 | 25 | 32 | 33 | 33 | 43 | 0 | 41 | 0 | 0 | 120 | 8 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 10 | 13 | 6 | 22 | 2 | 0 | 80 | 80 | 0 | 257 | 191 | 8 | 100 | 37 | 5 | 5 | 51 | 10 | 0 | 0 | 19 | 11 | 25 | 15 | 94 | 148 | 3 | 22 | 0 | 56 | 62 | 41 | 21 | 100 | 231 | 67 | 10 | 46 | 78 | 0 | 25 | 0 | 310 | 0 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 0 | 30 | 0 | 0 | 0 |  | 544 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 7 | 25 | 40 | 196 | 18 | 16 | 0 | 80 | 0 | 0 | 0 | 35 | 12 | 0 | 0 | 8 | 0 | 22 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 164 | 0 | 22 | 0 | 0 | 0 | 0 | 17 |  | 4620 | 1687 | 6307 | 3613 | 544 | 1436 | 363 | 149 | 41 | 67 | 94 | 0 | 0 | 0
18:00 | 35 | 0 | 0 | 0 | 350 | 104 | 35 | 360 | 364 | 0 | 0 | 225 | 0 | 0 | 5 | 17 | 162 | 0 | 140 | 0 | 0 | 27 | 0 | 0 | 47 | 0 | 6 | 54 | 54 | 17 | 19 | 25 | 32 | 33 | 33 | 43 | 0 | 41 | 0 | 0 | 150 | 25 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 34 | 10 | 13 | 6 | 22 | 17 | 0 | 100 | 100 | 0 | 283 | 200 | 8 | 100 | 37 | 5 | 5 | 51 | 85 | 8 | 0 | 19 | 11 | 25 | 15 | 118 | 148 | 40 | 22 | 0 | 56 | 63 | 53 | 0 | 125 | 228 | 67 | 86 | 48 | 96 | 0 | 25 | 9 | 305 | 25 | 11 | 0 | 2 | 0 | 0 | 77 | 0 | 27 | 0 | 92 | 47 | 43 | 0 |  | 667 | 0 | 340 | 0 | 49 | 0 | 0 | 0 | 26 | 40 | 40 | 200 | 25 | 48 | 0 | 80 | 0 | 0 | 0 | 65 | 50 | 0 | 0 | 43 | 37 | 22 | 11 | 11 | 0 | 0 | 149 | 17 | 0 | 0 | 0 | 161 | 0 | 92 | 0 | 0 | 0 | 0 | 105 |  | 5540 | 2278 | 7818 | 3879 | 667 | 1700 | 1037 | 149 | 41 | 227 | 118 | 0 | 0 | 98.38
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 0 | 0 | 350 | 104 | 35 | 350 | 365 | 0 | 0 | 225 | 0 | 0 | 20 | 40 | 120 | 0 | 150 | 0 | 0 | 32 | 0 | 0 | 47 | 0 | 47 | 54 | 54 | 17 | 19 | 25 | 32 | 33 | 33 | 43 | 0 | 42 | 0 | 0 | 150 | 25 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 68 | 10 | 13 | 37 | 22 | 27 | 0 | 100 | 100 | 0 | 261 | 184 | 8 | 95 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 25 | 15 | 120 | 147 | 80 | 22 | 0 | 56 | 63 | 53 | 0 | 163 | 220 | 56 | 86 | 48 | 78 | 19 | 25 | 9 | 280 | 25 | 11 | 0 | 12 | 0 | 0 | 115 | 0 | 60 | 0 | 92 | 155 | 88 | 0 |  | 668 | 0 | 340 | 0 | 99 | 0 | 0 | 0 | 30 | 36 | 40 | 171 | 26 | 48 | 0 | 80 | 0 | 0 | 0 | 100 | 50 | 0 | 0 | 43 | 39 | 22 | 11 | 11 | 0 | 0 | 149 | 17 | 0 | 0 | 0 | 159 | 0 | 97 | 0 | 0 | 0 | 0 | 105 |  | 5881 | 2341 | 8222 | 3747 | 668 | 1730 | 1476 | 149 | 42 | 290 | 120 | 0 | 0 | 98.43
19:30 | 35 | 0 | 0 | 0 | 350 | 104 | 35 | 350 | 365 | 0 | 0 | 225 | 0 | 0 | 50 | 40 | 120 | 0 | 150 | 0 | 0 | 32 | 0 | 0 | 47 | 0 | 47 | 54 | 55 | 17 | 19 | 25 | 32 | 33 | 33 | 43 | 0 | 42 | 0 | 0 | 150 | 25 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 34 | 10 | 13 | 50 | 22 | 32 | 0 | 100 | 100 | 0 | 261 | 184 | 8 | 95 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 25 | 15 | 120 | 147 | 81 | 22 | 0 | 56 | 63 | 53 | 0 | 163 | 220 | 66 | 86 | 49 | 78 | 19 | 25 | 9 | 315 | 25 | 11 | 0 | 12 | 0 | 0 | 72 | 0 | 15 | 0 | 92 | 160 | 100 | 0 |  | 667 | 0 | 340 | 0 | 49 | 0 | 0 | 0 | 30 | 35 | 40 | 200 | 26 | 48 | 0 | 80 | 0 | 0 | 0 | 51 | 50 | 0 | 0 | 43 | 39 | 22 | 11 | 11 | 0 | 0 | 149 | 17 | 0 | 0 | 0 | 165 | 0 | 96 | 0 | 0 | 0 | 0 | 105 |  | 5872 | 2274 | 8146 | 3792 | 667 | 1770 | 1400 | 149 | 42 | 206 | 120 | 0 | 0 | 0
20:00 | 35 | 0 | 0 | 0 | 350 | 104 | 35 | 345 | 365 | 0 | 0 | 225 | 0 | 0 | 64 | 40 | 120 | 0 | 150 | 0 | 0 | 32 | 0 | 0 | 47 | 0 | 47 | 54 | 55 | 0 | 19 | 25 | 32 | 33 | 33 | 43 | 0 | 42 | 0 | 0 | 150 | 25 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 34 | 10 | 13 | 50 | 22 | 35 | 0 | 100 | 100 | 0 | 261 | 184 | 8 | 95 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 25 | 15 | 118 | 146 | 81 | 22 | 0 | 56 | 62 | 51 | 21 | 163 | 221 | 60 | 86 | 49 | 80 | 20 | 25 | 9 | 290 | 25 | 11 | 0 | 0 | 0 | 0 | 48 | 0 | 15 | 0 | 92 | 100 | 100 | 0 |  | 668 | 0 | 340 | 0 | 49 | 0 | 0 | 0 | 30 | 25 | 40 | 194 | 26 | 48 | 0 | 80 | 0 | 0 | 0 | 51 | 50 | 0 | 0 | 43 | 39 | 22 | 11 | 11 | 0 | 0 | 149 | 17 | 0 | 0 | 0 | 165 | 0 | 97 | 0 | 0 | 0 | 0 | 105 |  | 5759 | 2260 | 8019 | 3777 | 668 | 1768 | 1301 | 149 | 42 | 196 | 118 | 0 | 0 | 98.43
21:00 | 35 | 0 | 0 | 0 | 350 | 104 | 35 | 355 | 364 | 0 | 0 | 225 | 0 | 0 | 20 | 40 | 120 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 47 | 54 | 18 | 0 | 19 | 25 | 32 | 33 | 33 | 43 | 0 | 42 | 0 | 0 | 150 | 25 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 52 | 22 | 38 | 0 | 100 | 100 | 0 | 272 | 193 | 8 | 100 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 25 | 15 | 110 | 142 | 81 | 22 | 0 | 56 | 62 | 51 | 21 | 163 | 228 | 68 | 86 | 49 | 80 | 20 | 25 | 9 | 305 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 92 | 100 | 50 | 0 |  | 668 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 40 | 202 | 25 | 48 | 0 | 80 | 0 | 0 | 0 | 26 | 50 | 0 | 0 | 43 | 39 | 22 | 11 | 11 | 0 | 0 | 149 | 17 | 0 | 0 | 0 | 168 | 0 | 97 | 0 | 0 | 0 | 0 | 105 |  | 5549 | 2171 | 7720 | 3843 | 668 | 1784 | 1012 | 149 | 42 | 112 | 110 | 0 | 0 | 98.42
22:00 | 35 | 0 | 0 | 0 | 350 | 104 | 35 | 351 | 368 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 120 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 19 | 25 | 32 | 33 | 33 | 24 | 0 | 42 | 0 | 0 | 150 | 25 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 37 | 22 | 39 | 0 | 100 | 100 | 0 | 260 | 185 | 8 | 100 | 40 | 5 | 5 | 32 | 85 | 0 | 0 | 19 | 11 | 25 | 15 | 100 | 140 | 0 | 22 | 0 | 56 | 62 | 51 | 21 | 163 | 222 | 66 | 86 | 49 | 80 | 20 | 25 | 9 | 310 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 92 | 60 | 0 | 0 |  | 668 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 201 | 24 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 43 | 0 | 22 | 11 | 8 | 0 | 0 | 149 | 17 | 0 | 0 | 0 | 157 | 0 | 97 | 0 | 0 | 0 | 0 | 53 |  | 5079 | 1934 | 7013 | 3790 | 668 | 1774 | 473 | 149 | 42 | 17 | 100 | 0 | 0 | 98.42
23:00 | 35 | 0 | 0 | 0 | 300 | 104 | 35 | 346 | 329 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 120 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 32 | 33 | 33 | 0 | 0 | 45 | 0 | 0 | 150 | 0 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 22 | 37 | 0 | 100 | 100 | 0 | 260 | 184 | 8 | 95 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 25 | 15 | 92 | 141 | 0 | 22 | 0 | 56 | 63 | 51 | 21 | 163 | 220 | 64 | 86 | 49 | 79 | 20 | 25 | 9 | 295 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 92 | 0 | 0 | 0 |  | 668 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 16 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 151 | 0 | 96 | 0 | 0 | 0 | 0 | 0 |  | 4804 | 1766 | 6570 | 3714 | 668 | 1728 | 174 | 149 | 45 | 0 | 92 | 0 | 0 | 98.41
24:00 | 35 | 0 | 0 | 0 | 300 | 104 | 35 | 346 | 327 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 120 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 0 | 0 | 45 | 0 | 0 | 150 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 33 | 0 | 100 | 100 | 0 | 261 | 184 | 8 | 100 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 0 | 8 | 15 | 84 | 141 | 0 | 0 | 0 | 56 | 63 | 51 | 22 | 163 | 232 | 53 | 50 | 49 | 78 | 20 | 25 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 468 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 21 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 3 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 151 | 0 | 97 | 0 | 0 | 0 | 0 | 0 |  | 4501 | 1483 | 5984 | 3580 | 468 | 1650 | 8 | 149 | 45 | 0 | 84 | 0 | 0 | 98.41
KWH | 740000 | 0 | 0 | 0 | 7351236 | 1578636 | 572320 | 8313860 | 7406000 | 0 | 0 | 6671500 | 0 | 0 | 130416 | 339125 | 3864838 | 0 | 2957000 | 0 | 0 | 239760 | 0 | 44807 | 295680 | 0 | 199872 | 365040 | 190171 | 58000 | 223632 | 600000 | 701100 | 805353 | 820200 | 533796 | 0 | 946189 | 0 | 0 | 3200000 | 205200 | 0 | 0 | 2941779 | 0 | 0 | 780480 | 0 | 112133 | 130416 | 156480 | 247200 | 412512 | 472320 | 0 | 2097740 | 2163888 | 0 | 7278000 | 4678000 | 217454 | 2344680 | 699480 | 202080 | 12000 | 760111 | 815530 | 5968 | 0 | 313308 | 137160 | 231000 | 365680 | 2135040 | 3674680 | 319680 | 346392 | 12500 | 836000 | 1427492 | 559800 | 322000 | 3165970 | 5133000 | 1417000 | 832320 | 796320 | 1992160 | 120000 | 443040 | 50220 | 7567800 | 173664 | 146448 | 0 | 27600 | 0 | 0 | 468000 | 0 | 122400 | 132300 | 1191360 | 556800 | 352940 | 0 |  | 12458181 | 0 | 7947360 | 0 | 219840 | 0 | 0 | 0 | 113760 | 117504 | 618375 | 4582418 | 457800 | 199600 | 0 | 1933000 | 0 | 0 | 0 | 226900 | 291420 | 0 | 0 | 500640 | 151897 | 399600 | 181260 | 158706 | 0 | 0 | 3652700 | 86000 | 0 | 0 | 0 | 4121982 | 0 | 966477 | 0 | 0 | 0 | 0 | 916800 |  | 111252056 | 40302220 | 151554276 | 87250748 | 12458181 | 34450558 | 9701898 | 3652700 | 946189 | 814162 | 2135040 | 144800 | 0
Fuel Cost | 636400 | 0 | 0 | 0 | 4704791.04 | 1278695.16 | 537980.8 | 5071454.6 | 4517660 | 0 | 0 | 4469905 | 0 | 0 | 871178.88 | 2072053.75 | 2512144.7 | 0 | 3282270 | 0 | 0 | 1580018.4 | 0 | 285420.59 | 1771123.2 | 0 | 1333146.24 | 2602735.2 | 1188568.75 | 363660 | 167724 | 450000 | 0 | 0 | 0 | 5049710.16 | 0 | 0 | 0 | 0 | 3520000 | 1943244 | 0 | 0 | 3383045.85 | 0 | 0 | 6860419.2 | 0 | 1091054.09 | 807275.04 | 1010860.8 | 1616688 | 350635.2 | 0 | 0 | 1908943.4 | 1969138.08 | 0 | 5021820 | 3274600 | 150043.26 | 2250892.8 | 468651.6 | 173788.8 | 11040 | 623291.02 | 774753.5 | 64693.12 | 0 | 241247.16 | 102870 | 177870 | 274260 | 14603673.6 | 2756010 | 2937859.2 | 266721.84 | 0 | 869440 | 1484591.68 | 537408 | 289800 | 2469456.6 | 3593100 | 1615380 | 890582.4 | 875952 | 2271062.4 | 153600 | 412027.2 | 46704.6 | 4843392 | 130248 | 111300.48 | 0 | 200376 | 0 | 0 | 3346200 | 0 | 0 | 0 | 0 | 5200512 | 3296459.6 | 0 |  | 63536723.1 | 0 | 5324731.2 | 0 | 1822473.6 | 0 | 0 | 0 | 1280937.6 | 1384197.12 | 4872795 | 3161868.42 | 453222 | 1477040 | 0 | 2029650 | 0 | 0 | 0 | 2033024 | 2520783 | 0 | 0 | 4966348.8 | 1787827.69 | 439560 | 170384.4 | 120140.442 | 0 | 0 | 14099422 | 2771780 | 0 | 0 | 0 | 2885387.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 136019622.99 | 117138295.772 | 253157918.762 | 66541990.292 | 63536723.1 | 23965646.74 | 59996949.41 | 14099422 | 0 | 10413513.62 | 14603673.6 | 0 | 0
Yesterday Day Peak | 35 | 155 | 0 | 0 | 320 | 101 | 20 | 345 | 285 | 0 | 0 | 225 | 0 | 0 | 0 | 30 | 180 | 0 | 97 | 0 | 0 | 32 | 0 | 10 | 24 | 0 | 0 | 18 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 38 | 0 | 42 | 0 | 0 | 120 | 8 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 10 | 13 | 6 | 22 | 4 | 0 | 80 | 80 | 0 | 320 | 193 | 8 | 100 | 40 | 5 | 5 | 51 | 40 | 0 | 0 | 19 | 8 | 8 | 15 | 90 | 170 | 0 | 22 | 2.1 | 26 | 63 | 22 | 21 | 100 | 231 | 65 | 50 | 47 | 78 | 0 | 25 | 0 | 210 | 0 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 19.5 | 80 | 0 | 0 | 0 |  | 522 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 195 | 20 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 11 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 167 | 0 | 51 | 0 | 0 | 0 | 0 | 53 |  | 6418.6 | DayPeak
Yesterday Evening Peak | 35 | 0 | 0 | 0 | 350 | 104 | 35 | 350 | 365 | 0 | 0 | 225 | 0 | 0 | 20 | 40 | 120 | 0 | 150 | 0 | 0 | 32 | 0 | 0 | 47 | 0 | 47 | 54 | 54 | 17 | 19 | 25 | 32 | 33 | 33 | 43 | 0 | 42 | 0 | 0 | 150 | 25 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 68 | 10 | 13 | 37 | 22 | 27 | 0 | 100 | 100 | 0 | 261 | 184 | 8 | 95 | 40 | 5 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 25 | 15 | 120 | 147 | 80 | 22 | 0 | 56 | 63 | 53 | 0 | 163 | 220 | 56 | 86 | 48 | 78 | 19 | 25 | 9 | 280 | 25 | 11 | 0 | 12 | 0 | 0 | 115 | 0 | 60 | 0 | 92 | 155 | 88 | 0 |  | 668 | 0 | 340 | 0 | 99 | 0 | 0 | 0 | 30 | 36 | 40 | 171 | 26 | 48 | 0 | 80 | 0 | 0 | 0 | 100 | 50 | 0 | 0 | 43 | 39 | 22 | 11 | 11 | 0 | 0 | 149 | 17 | 0 | 0 | 0 | 159 | 0 | 97 | 0 | 0 | 0 | 0 | 105 |  | 8222 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 0 | 330 | 100 | 40 | 412 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 200 | 0 | 200 | 100 | 100 | 102 | 149 | 100 | 47 | 0 | 47 | 54 | 55 | 36 | 22 | 25 | 33 | 33 | 33 | 43 | 0 | 37 | 30 | 0 | 120 | 25 | 0 | 0 | 150 | 0 | 0 | 50 | 70 | 68 | 90 | 100 | 50 | 22 | 20 | 0 | 100 | 100 | 260 | 360 | 221 | 8 | 100 | 40 | 55 | 5 | 51 | 85 | 40 | 52 | 22 | 11 | 33 | 22 | 109 | 176 | 80 | 22 | 0 | 26 | 63 | 51 | 21 | 163 | 230 | 66 | 86 | 50 | 140 | 20 | 50 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 130 | 0 | 100 | 180 | 150 | 0 |  | 676 | 46 | 410 | 0 | 115 | 0 | 0 | 0 | 40 | 80 | 40 | 194 | 25 | 110 | 30 | 80 | 0 | 50 | 40 | 100 | 50 | 50 | 50 | 52 | 35 | 22 | 10 | 11 | 0 | 0 | 149 | 17 | 15 | 0 | 0 | 220 | 0 | 95 | 100 | 0 | 0 | 0 | 105
Forecast for Day | 35 | 0 | 0 | 0 | 320 | 100 | 40 | 412 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 200 | 0 | 80 | 100 | 100 | 102 | 149 | 100 | 8 | 0 | 47 | 54 | 55 | 36 | 22 | 25 | 33 | 33 | 33 | 43 | 0 | 37 | 30 | 0 | 120 | 25 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 90 | 90 | 50 | 22 | 20 | 0 | 100 | 100 | 260 | 360 | 221 | 8 | 100 | 40 | 30 | 5 | 51 | 85 | 0 | 52 | 22 | 0 | 0 | 22 | 85 | 176 | 80 | 22 | 2 | 26 | 63 | 51 | 21 | 163 | 230 | 66 | 86 | 50 | 78 | 20 | 50 | 0 | 341 | 0 | 11 | 0 | 0 | 300 | 0 | 100 | 0 | 130 | 20 | 100 | 180 | 150 | 0 |  | 330 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 194 | 25 | 110 | 0 | 80 | 0 | 0 | 0 | 90 | 50 | 50 | 50 | 43 | 0 | 22 | 7 | 11 | 0 | 0 | 149 |  | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 0 | 0 | 0 | 105
Generation at 08:00(Today) | 35 | 0 | 0 | 0 | 250 | 62 | 0 | 280 | 246 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 120 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 33 | 33 | 0 | 0 | 43 | 0 | 0 | 150 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 0 | 80 | 80 | 0 | 294 | 201 | 8 | 100 | 40 | 5 | 5 | 6 | 5 | 0 | 0 | 19 | 0 | 0 | 15 | 68 | 154 | 0 | 22 | 0.3 | 20 | 30 | 5 | 21 | 100 | 221 | 40 | 5 | 1 | 76 | 0 | 2 | 0 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7.3 | 4 | 0 | 0 | 0 | 0 | 328 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207 | 17 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 163 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 4754 | 5:00
| Highest Generation |  | 8222 | 19:00
| Day Peak Generation |  | 6418.6 | 12:00
| Evening Peak Generation |  | 8222 | 19:00
| HVDC Max Flow |  | 668 | 19:00
| HVDC EvPeak Flow |  | 668 | 19:00
| Load factor L.F |  | 76.8%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-01-04
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2019-01-03 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6418.6 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 4711 | MW
Evening Peak Generation : |  | 8222 | MW Hour : | 19:00 | Available Max Generation : |  | 12385 | MW
E.P. Demand (at gen end) : |  | 8222 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 7500 | MW
Maximum Generation : |  | 8222 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4885 | MW
Total Gen. (MKWH) : |  | 151.5543 | System Load Factor : | 76.8% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -520 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-01-04
Actual : | 98.25 | Ft.(MSL) , | Rule curve : | 102.62 | Ft.( MSL )
Gas Consumed : | Total = | 1044.57 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 90507637.032
|  | Coal : | 14099422 | Oil : | 70410463.03 | Total : | 175017522.062
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2627.4124 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 883.8917 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 790.2317 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 713.4354 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 645.0552 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 520.5126 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 303.3651 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 134.344 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 401.3862 |  |  | 0 | 0%
Total | 0 |  | 7019.6343 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 8) Raozan # 01
| Nil |  |  | 2) Khulna ST 110 MW |  | 9) Sirajganj Unit-1,3,4
|  |  |  | 3) Ghorasal Unit-1,3,5 |  | 10) Ashuganj #3
4) Tongi GT
5) Haripur GT-1,2
6) Siddhirganj ST 210 MW
7) Bhagabari 71 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Hathazari-AKSML 230 kV bay was under shut down from 09:20 to 17:40 for A/M.
b) Chandraghona-Madunaghat 132 kV Ckt-2 was under shut from 08:43 to 15:41 for A/M.
c) Siddhirganj-Haripur 230 kV CKt-2 was under shut down from 09:50 to 15:38 for A/M.
d) Tongi 230/132 kV T03 was under shut down from 08:40 to 15:12 for A/M.
e) Tangail-Mymensingh RPCL 132 kV Ckt-2 was under shut down from 09:04 to 13:52 for A/M.
f) Comilla (N)-Ashuganj 230 kV Ckt-2 was under shut down from 08:51 to 15:50 for A/M.
g) Sreemongal-Fenchuganj 132 kV Ckt-2 was under shut down from 09:04 to 17:07 for A/M.
h) Baghabari-Sirajganj 230 kV Ckt-1 was shut down at 08:23 for development work.
i) Ishurdi 230/132 kV T1 transformer was under shut down from 08:27 to 17:26 for A/M.
j) Ghorasal Unit-3 was synchronized at 08:40 and again shut down at 13:10.
k) Meghnaghat 450 MW CCPP GT-2 was shut down at 10:22 due to feed water line problem.
l) Hasnabad 230/132 kV T02 transformer was switched on at 10:04.
m) Netrokona 132/33 kV T2 transformer was under shut down from 09:30 to 13:45 for TSCR work.
n) Rajshahi 132/33 kV T3 transformer was shut down at 10:30 for C/W.
o) Jamalpur 132/33 kV T4 transformer was under shut down from 08:15 to 17:26 for A/M.
p) Tongi-Kabirpur 132 kV Ckt-2 tripped at 10:34 from both ends showing dist.relay and was switched on
at 10:53.
q) Bhulta 400/230 kV T2 transformer was under shut down from 10:37 to 11:58 for C/M.
r) Bhandaria-Bagherhat 132 kV Ckt was under shut down from 08:33 to 17:23 for A/M.
s) Bibiyana 400/230 kV ICT-1 was under shut down from 08:38 to 17:01 for A/M.
t) Old Tongi-New Tongi 132 kV Ckt-1 was under shut down from 13:17 to 16:56 for protection work.
u) Rampura 230/132 kV T02 transformer was shut down at 08:46 for A/M.
v) Meghnaghat 450 MW CCPP GT-2 was synchronized at 00:17 (04/01/2019)
w) Saidpur 132 kV Bus-1 & 2 were shut down at 06:33 (04/01/2019) for development work. |  |  |  | About 150 MW Power interruption occurred under Saidpur, Purbasadipur,
x) Kallyanpur-Lalbag 132 kv Ckt-1 & 2 were switched on at 23:11. |  |  |  | Thakurgaon & Panchagar S/S areas from 06:33(04/01/2019) to till now.
y) Lalbag-Kamrangirchar 132 kV Ckt was switched on at 23:11.
z) Sikalbaha-Bakulia 132 kV Ckt-1 was shut down at 07:43 (04/01/2019) for C/M.
aa) Madunaghat-Chandraghona 132 kV CKt-2 was shut down at 08:01(04/01/2019) for A/M.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-01-03 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 35 | 740000 | #2 under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 350 | 7351236
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 35 | 572320 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 104 | 1578636
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 350 | 8313860 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 0 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 365 | 7406000
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 225 | 6671500 | GT-2 under maint.
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 20 | 130416 | Low demand
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 339125 | Low demand
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 0 | 44807 | Reserve
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 223632
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 150 | 2957000 | FGMO
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 120 | 3864838 | Frequency control
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 32 | 239760 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 47 | 199872
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 365040
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 54 | 190171
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 17 | 58000 | Low demand
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 47 | 295680 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1301100 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 805353
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 820200
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 43 | 533796 | Engine problem
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 12 | 27600 | Low demand
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 60 | 122400 | Low demand
| Dhaka area Total |  |  |  | 5798 | 2302 | 45152342
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 150 | 3200000 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 205200
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 132300
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 37 | 247200 | Engine problem
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 42 | 946189 | Low water lavel
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 120 | 2941779 | FGMO
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 50 | 780480
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 68 | 112133
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 130416 | Low demand
| Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 92 | 1191360 | Engine problem
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 412512
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 27 | 472320
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 13 | 156480 | Low demand
| Chattogram area Total |  |  |  | 1681 | 656 | 10928369
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2097740 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2163888 | Gas shortage
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 184 | 4678000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Reserve
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 261 | 7278000 | FGMO
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 40 | 699480 | Engine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 5 | 202080 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 12000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 51 | 760111
| Midland 150MW |  | IPP | 23*7.015 | 150 | 88 | 352940 | Low demand
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 815530
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 5968 | Reserve
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 95 | 2344680 | ST Under maint.
| Chandpur Desh 200MW |  | IPP | 0 | 200 | 155 | 556800 | Low demand
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 313308
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 137160
** | Tripura |  | Imported power | 0 | 160 | 120 | 2135040
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 25 | 231000 | Engine problem
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 15 | 365680
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1367 | 25366859
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 147 | 3674680 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 346392
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 80 | 319680 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 12500
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 115 | 468000 | Low demand
| Mymensingh Area Total |  |  |  | 522 | 364 | 4821252
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 56 | 836000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 63 | 1427492
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 3165970
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 220 | 5133000 | FGMO
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 559800
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 0 | 322000 | Engine problem
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 146448
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 56 | 1417000 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 832320
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 48 | 796320
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 78 | 1992160 | Frequency control
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 19 | 120000
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 25 | 443040 | High voltage
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 25 | 173664
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 280 | 7567800 | FGMO
| Bibiyana-3 285MW |  | PDB | 285 MW | 0 | 0 | 0 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 9 | 50220
| Sylhet Area Total |  |  |  | 1549 | 1192 | 24983234
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 668 | 12458181
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 219840 | Low demand
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 30 | 113760 | Low demand
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 36 | 117504 | Low demand
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 340 | 7947360 | Frequency control
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 618375
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 916800
| Khulna Area Total |  |  |  | 2209 | 1318 | 22391820
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 48 | 199600 | Low demand
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 26 | 457800 | Engine problem
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 171 | 4582418 | FGMO
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 966477
| Barisal Area Total |  |  |  | 462 | 342 | 6206295
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 80 | 1933000 | Gas shortage
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 291420
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 159 | 4121982 | FGMO
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 141 | 0 | 0 | Gas shortage
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 0 | 0 | Gas shortage
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 39 | 151897
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 399600
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 11 | 181260 | Engine problem
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 158706
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 43 | 500640 | Engine problem
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 100 | 226900
| Rajshahi Area Total |  |  |  | 1546 | 515 | 7965405
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 149 | 3652700
122 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 86000
123 | Saidpur GT |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
| Rangpur Area Total |  |  |  | 484 | 166 | 3738700
| Total |  |  |  | 17142 | 8222 | 151554276
| Eastern Grid Total |  |  |  | 12441 | 5881 | 111252056
| Western Grid Total |  |  |  | 4701 | 2341 | 40302220
| National Grid Total |  |  |  | 17142 | 8222 | 151554276
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-01-03 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 5152 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2526 | MW
i) Dhaka area |  |  | 2750 | MW | i) Khulna area |  |  | 992 | MW
ii) Chittagong area |  |  | 819 | MW | ii) Rajshahi area |  |  | 794 | MW
iii) Comilla area |  |  | 686 | MW | iii) Barisal area |  |  | 203 | MW
iv) Mymensingh area |  |  | 587 | MW | iv) Rangpur area |  |  | 537 | MW
v) Sylhet area |  |  | 310 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 7678 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 88 | 1300 | Netrokona | 63 | 1900 | Goalpara | 27 | 1830
Munsiganj | 72 | 2000 | Jamalpur | 83 | 1900 | Central s/s | 60 | 1830
Sonargaon | 44 | 1930 | Sherpur | 68 | 1830 | Noapara | 78 | 1830
Shyampur | 130 | 1500 | Srimongal | 22 | 1800 | Jessore | 106 | 1830
Bhulta | 137 | 2200 | Shahjibazar | 77 | 1930 | Jhenida | 76 | 1800
Madanganj | 50 | 1930 | Fenchuganj | 27 | 1800 | Bottail | 92 | 1830
Shitalakhya | 77 | 1200 | Kulawara | 27 | 1800 | G.K Project | 34 | 1830
Rahim steel | 6 | 1100 | Sylhet | 89 | 1800 | Faridpur | 120 | 1830
Matuail | 74 | 1000 | Chatak | 19 | 1830 | Madaripur | 89 | 1930
Ghorasal | 61 | 1930 | Sunamganj | 25 | 1800 | Gopalganj | 62 | 1830
Narsingdi | 97 | 1930 | Biani Bazar | 28 | 1900 | Bagerhat | 66 | 1900
Haripur (SBU) | 77 | 1930 | Comilla (S) | 120 | 1830 | Mongla | 32 | 800
Ullon | 51 | 1800 | Comilla(N) | 73 | 1830 | Satkhira | 66 | 1830
Hasnabad | 127 | 1830 | Chandpur | 75 | 1930 | Gallamari | 37 | 1300
Magbazar | 86 | 1200 | Feni | 87 | 1900 | Magura | 37 | 1830
Maniknagar | 64 | 1300 | Chowmuhani | 122 | 1900 | Chuadanga | 58 | 1930
Bangabhaban | 20 | 1300 | Ashuganj | 37 | 1930 | Barisal | 84 | 1930
Narinda | 58 | 1100 | Daudkandi | 78 | 1930 | Patuakhali | 62 | 1900
Dhanmondi | 72 | 1400 | B.Baria | 85 | 1930 | Bhandaria | 38 | 1900
Lalbag | 75 | 1200 | Ramganj | 24 | 1800 | Ishurdi | 40 | 1900
Madartek | 31 | 2000 | Madunaghat | 51 | 1800 | Ruppur Paromanobik | 1 | 2000
Mirpur | 80 | 1800 | Hathazari | 66 | 1800 | Natore | 79 | 1930
Kalyanpur | 60 | 1800 | Khulshi | 158 | 1300 | Bogra | 168 | 1800
Gulshan | 76 | 1800 | Halishahar | 94 | 1800 | Noagaon | 86 | 1830
Uttara | 34 | 1800 | Baraulia | 129 | 1100 | Rajshahi | 85 | 2000
Uttara(New) | 4 | 1800 | Sikalbaha | 29 | 1800 | C.Nawabganj | 55 | 1200
Kamrangirchar | 60 | 1100 | Dohazari | 24 | 1930 | Amnura | 24 | 1900
Savar | 94 | 1800 | Cox'sbazar | 65 | 1800 | Pabna | 72 | 1830
Bhasantec | 81 | 1800 | Chandraghona | 19 | 1800 | Shahjadpur | 63 | 1830
Agargaon | 34 | 1800 | Kaptai | 3.5 | 1800 | Serajganj | 59 | 1830
Satmosjid | 53 | 1800 | A. Khaer Stl. | 14 | 300 | Niyamatpur | 62 | 1900
Tongi | 121 | 1100 | Bakulia | 69 | 1830 | Joypurhat | 38 | 1930
Kabirpur | 125 | 1830 | Julda | 19 | 100 | Rangpur | 95 | 1900
Basundhara | 74 | 1800 | TK chemical | 4.4 | 800 | Lalmonirhat | 70 | 1800
Manikganj | 60 | 1900 | Modern Steel | 15 | 800 | Saidpur | 93 | 1830
Joydevpur | 188 | 1830 | Shahmirpur | 21.5 | 1830 | Purbasadipur | 82 | 2000
New Tongi | 83 | 1800 | Khagrachhari | 15 | 1930 | Thakurgaon | 55 | 1800
Korda | 193 | 1830 | Matarbari | 19 | 1830 | Palashbari | 80 | 1900
Dhamrai | 28 | 1800 | Baroiar Hat | 18 | 1800 | Barapukuria | 43 | 2000
Tangail | 126 | 1830 | Rangamati | 8 | 1800 | Panchagar | 36 | 1900
Mymensing | 180 | 1830 | Abul Khair 230 | 163 | 200
Kishorganj | 68 | 1830 | BSRM | 100 | 2000
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-01-03
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 418 | 3:00 | 406 | 12:00 | Kaliakoir | 413 | 4:00 | 400 | 12:00
Bheramara | 408 | 23:00 | 397 | 10:00 | Bhulta | 405 | 5:00 | 393 | 12:00
Ashuganj(N) | 403 | 2:00 | 394 | 14:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 240 | 1:00 | 240 | 1:00 | Hathazari | 226 | 22:00 | 216 | 12:00
Ishurdi | 239 | 3:00 | 232 | 12:00 | Megnaghat | 237 | 1:00 | 230 | 12:00
Ashuganj | 242 | 2:00 | 238 | 17:00 | Fenchuganj | 245 | 1:00 | 239 | 13:00
Serajganj | 235 | 3:00 | 230 | 8:00 | Siddhirganj | 236 | 3:00 | 228 | 12:00
Baghabari | 231 | 1:00 | 228 | 13:00 | Maniknagar | 233 | 1:00 | 227 | 15:00
Barapukuria | 235 | 3:00 | 225 | 18:00 | Old Airport | 235 | 2:00 | 227 | 12:00
Bogra | 232 | 3:00 | 221 | 18:00 | Barisal | 234 | 4:00 | 228 | 21:00
Khulna South | 238 | 14:00 | 226 | 12:00 | AKSML | 223 | 18:30 | 215 | 2:00
Rampura | 230 | 1:00 | 226 | 12:00 | BSRM | 227 | 19:00 | 218 | 11:00
Haripur | 232 | 1:00 | 227 | 12:00 | Bibiyana | 247 | 2:00 | 237 | 11:00
Hasnabad | 236 | 1:00 | 229 | 15:00 | Bhulta | 235 | 1:00 | 227 | 11:00
Aminbazar | 236 | 2:00 | 229 | 12:00 | Ashuganj (S) | 241 | 2:00 | 236 | 10:00
Tongi | 233 | 5:00 | 221 | 12:00 | Kaliakoir | 238 | 3:00 | 228 | 11:00
Comilla (N) | 239 | 4:00 | 233 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 137 | 400 | 133 | 1100 | Ramganj | 138 | 1830 | 132 | 900
Munsiganj | 140 | 1930 | 132 | 1100 | Madanhat | 134 | 1900 | 129 | 700
Megnaghat | 137 | 1900 | 133 | 1000 | Hathazari | 134 | 1900 | 129 | 700
Shyampur | 135 | 200 | 129 | 1300 | Khulshi | 131 | 2000 | 125 | 700
Bhulta | 136 | 100 | 133 | 1200 | Halishahar | 134 | 1900 | 128 | 700
Madanganj | 139 | 1930 | 132 | 900 | Baraulia | 132 | 1900 | 127 | 700
Shitalakhya | 141 | 1900 | 132 | 900 | Sikalbaha | 132 | 1830 | 126 | 700
Rahim steal | 137 | 1930 | 134 | 1000 | Dohazari | 132 | 1830 | 127 | 1100
Matuail | 137 | 600 | 132 | 1400 | Cox'sbazar | 129 | 2200 | 120 | 1800
Ghorasal | 142 | 100 | 140 | 700 | Chandraghona | 133 | 1830 | 128 | 800
Narsinghdi | 139 | 1800 | 134 | 900 | Kaptai | 135 | 1830 | 130 | 300
Haripur (SBU) | 137 | 400 | 133 | 1000 | A. Khaer Stl. | 131 | 1900 | 126 | 800
Ullon | 134 | 600 | 127 | 1200 | Bakulia | 131 | 1900 | 125 | 800
Hasnabad | 140 | 2000 | 132 | 700 | Julda | 133 | 1900 | 127 | 500
Magbazar | 135 | 600 | 128 | 1200 | TK Chemical | 135 | 2000 | 130 | 300
Maniknagar | 137 | 600 | 133 | 1200 | Modern Steel | 131 | 1830 | 126 | 700
Bangabhaban | 138 | 2000 | 130 | 900 | Shahmirpur | 132 | 2000 | 126 | 700
Narinda | 134 | 500 | 126 | 1200 | Khagrachhari | 133 | 1900 | 127 | 1200
Dhanmondi | 134 | 600 | 127 | 1200 | Matarbari | 129 | 2000 | 122 | 1800
Lalbag | 138 | 2000 | 130 | 900 | Baroiar Hat | 135 | 1900 | 130 | 1600
Madartek | 134 | 500 | 126 | 1200 | Rangamati | 132 | 1800 | 127 | 1700
Mirpur | 134 | 400 | 128 | 1200 | Goalpara | 138 | 2400 | 128 | 1200
Kalyanpur | 136 | 400 | 132 | 1200 | Central s/s | 137 | 1500 | 128 | 700
Gulshan | 133 | 600 | 126 | 1200 | Noapara | 136 | 1400 | 125 | 1200
Uttara | 137 | 600 | 129 | 1200 | Jessore | 134 | 1500 | 122 | 700
Uttara(New) | 134 | 500 | 128 | 1200 | Jhenida | 133 | 1500 | 123 | 1930
Kamrangirchar | 140 | 100 | 130 | 900 | Bottail | 139 | 200 | 134 | 1800
Savar | 133 | 600 | 128 | 1200 | G.K.Project | 142 | 100 | 138 | 1800
Bhasantec | 137 | 600 | 131 | 1200 | Faridpur | 135 | 200 | 130 | 1930
Agargaon | 138 | 600 | 132 | 1200 | Madaripur | 135 | 500 | 130 | 1930
Satmosjid | 137 | 500 | 131 | 1200 | Gopalganj | 136 | 1700 | 125 | 2100
Tongi | 136 | 800 | 130 | 1200 | Bagerhat | 137 | 1500 | 126 | 1200
Kabirpur | 136 | 100 | 129 | 1200 | Mongla | 134 | 1500 | 125 | 1200
Basundhara | 129 | 100 | 123 | 1300 | Satkhira | 137 | 1500 | 128 | 1200
Manikganj | 141 | 500 | 134 | 1200 | Gallamari | 138 | 1500 | 129 | 1200
Joydevpur | 142 | 100 | 136 | 1300 | Magura | 137 | 100 | 125 | 1800
New Tongi | 137 | 100 | 129 | 1500 | Chuadanga | 135 | 100 | 122 | 1800
Kodda | 140 | 100 | 133 | 1000 | Barisal | 138 | 600 | 133 | 800
Dhamrai | 136 | 200 | 130 | 1200 | Patuakhali | 136 | 300 | 131 | 2100
Tangail | 138 | 100 | 132 | 700 | Bhandaria | 135 | 1700 | 130 | 700
Mymensing | 138 | 600 | 133 | 1500 | Ishurdi | 140 | 600 | 135 | 1300
Kishorganj | 137 | 500 | 135 | 900 | Ruppur Paromanobik | 142 | 500 | 137 | 1200
Netrokona | 139 | 600 | 134 | 1600 | Natore | 137 | 500 | 130 | 1200
Jamalpur | 139 | 1830 | 126 | 2200 | Bogra | 137 | 600 | 131 | 2000
Sherpur | 138 | 1830 | 127 | 2300 | Noagaon | 135 | 600 | 128 | 1800
Srimongal | 142 | 100 | 140 | 1200 | Rajshahi | 135 | 1900 | 125 | 1200
Shahjibazar | 141 | 2200 | 139 | 1500 | C.Nawabganj | 133 | 1900 | 121 | 1300
Fenchuganj | 141 | 200 | 137 | 1100 | Amnura | 138 | 1900 | 122 | 1200
Khulawara | 140 | 100 | 137 | 1500 | Pabna | 137 | 400 | 130 | 1300
Sylhet | 138 | 100 | 136 | 1200 | Shahjadpur | 143 | 300 | 140 | 2000
Chatak | 139 | 300 | 137 | 1100 | Serajganj | 137 | 600 | 131 | 1200
Sunamganj | 137 | 100 | 135 | 1200 | Niyamatpur | 135 | 400 | 123 | 1800
Biani Bazar | 139 | 300 | 136 | 1200 | Joypurhat | 139 | 100 | 128 | 1800
Cumilla(s) | 131 | 100 | 127 | 1000 | Rangpur | 133 | 600 | 118 | 1800
Cumilla(n) | 141 | 700 | 138 | 1200 | Lalmonirhat | 130 | 600 | 112 | 1800
Chandpur | 143 | 1900 | 137 | 1500 | Saidpur | 133 | 600 | 123 | 1800
Feni | 135 | 2200 | 131 | 1200 | Purbasadipur | 132 | 600 | 113 | 1800
Chowmuhani | 135 | 1830 | 130 | 1700 | Thakurgaon | 128 | 500 | 102 | 1800
Ashuganj | 143 | 600 | 141 | 1600 | Palashbari | 134 | 100 | 121 | 1800
Daudkandi | 137 | 700 | 134 | 1600 | Barapukuria | 135 | 600 | 125 | 1800
B.Baria | 141 | 1900 | 138 | 700 | Panchagar | 124 | 600 | 101 | 1800

## L-Curve
Date | 2019-01-03
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 440 | 4501 | 1483 | 5984 |  |  |  | QF-LDC-12
0:30 | 410 | 4283 | 1382.5 | 5665.5 | Date: | 2019-01-03
1:00 | 380 | 4065 | 1282 | 5347
1:30 | 400 | 3975 | 1237.5 | 5212.5
2:00 | 420 | 3885 | 1193 | 5078
2:30 | 410 | 3821.5 | 1198.5 | 5020 | [5 empty] | Gen. at Eve. Peak | 8222 | 8222 MW (19:00 )
3:00 | 400 | 3758 | 1204 | 4962 | [6 empty] | 19:00
3:30 | 400 | 3734.5 | 1184 | 4918.5 | [5 empty] | Gen. at Day Peak | 6418.6 | 6418.6 MW (12:00 )
4:00 | 400 | 3711 | 1164 | 4875 | [6 empty] | 12:00
4:30 | 390 | 3665.5 | 1149 | 4814.5 | [5 empty] | Highest Generation | 8222
5:00 | 380 | 3620 | 1134 | 4754 | [6 empty] | 19:00
5:30 | 380 | 3732.5 | 1175.5 | 4908
6:00 | 380 | 3845 | 1217 | 5062
6:30 | 420 | 3959.74 | 1244 | 5203.74
7:00 | 460 | 4074.48 | 1271 | 5345.48
7:30 | 430 | 4241.19 | 1436 | 5677.19
8:00 | 400 | 4407.9 | 1601 | 6008.9
8:30 | 350 | 4515.05 | 1622.5 | 6137.55
9:00 | 300 | 4622.2 | 1644 | 6266.2
9:30 | 280 | 4631.1 | 1648.5 | 6279.6
10:00 | 260 | 4640 | 1653 | 6293
10:30 | 140 | 4588.1 | 1670 | 6258.1
11:00 | 20 | 4536.2 | 1687 | 6223.2
11:30 | 125 | 4637.4 | 1683.5 | 6320.9
12:00 | 230 | 4738.6 | 1680 | 6418.6
12:30 | 285 | 4852.15 | 1680 | 6532.15
13:00 | 340 | 4965.7 | 1680 | 6645.7
13:30 | 275 | 4778.75 | 1640.5 | 6419.25
14:00 | 210 | 4591.8 | 1601 | 6192.8
14:30 | 105 | 4641.65 | 1605 | 6246.65
15:00 | 0 | 4691.5 | 1609 | 6300.5
15:30 | 18 | 4654.75 | 1582.5 | 6237.25
16:00 | 36 | 4618 | 1556 | 6174
16:30 | 23 | 4619 | 1621.5 | 6240.5
17:00 | 10 | 4620 | 1687 | 6307
17:30 | 205 | 5080 | 1982.5 | 7062.5
18:00 | 400 | 5540 | 2278 | 7818
18:30 | 430 | 5710.5 | 2309.5 | 8020
19:00 | 460 | 5881 | 2341 | 8222
19:30 | 520 | 5872 | 2274 | 8146
20:00 | 520 | 5759 | 2260 | 8019 |  |  |  | Executive Engineer
20:30 | 475 | 5654 | 2215.5 | 7869.5 |  |  |  | Network Operation Division
21:00 | 430 | 5549 | 2171 | 7720
21:30 | 380 | 5314 | 2052.5 | 7366.5
22:00 | 330 | 5079 | 1934 | 7013 |  |  |  |  | Page 6 of 7
22:30 | 305 | 4941.5 | 1850 | 6791.5
23:00 | 280 | 4804 | 1766 | 6570
23:30 | 360 | 4652.5 | 1624.5 | 6277
24:00 | 440 | 4501 | 1483 | 5984
8222 MW (19:00 )
6418.6 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-01-03 |  | Energy | 151554276
[10 empty] | 2019-01-03 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3580 | 468 | 1650 | 8 | 149 | 45 | 0 | 0 | 84
0:30 | 3520.5 | 402.5 | 1437 | 36.5 | 149 | 40 | 0 | 0 | 80 | Date: | 2019-01-03
1:00 | 3461 | 337 | 1224 | 65 | 149 | 35 | 0 | 0 | 76
1:30 | 3394 | 337 | 1185.5 | 36 | 149 | 35 | 0 | 0 | 76 | [7 empty] | Total Energy | 151.5543 | Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
2:00 | 3327 | 337 | 1147 | 7 | 149 | 35 | 0 | 0 | 76 | [7 empty] | Energy not Served | 0
2:30 | 3299 | 337 | 1118.5 | 7 | 149 | 35.5 | 0 | 0 | 74 | [7 empty] | Energy Requirement | 151.5543
3:00 | 3271 | 337 | 1090 | 7 | 149 | 36 | 0 | 0 | 72
3:30 | 3249.5 | 337 | 1069 | 7 | 149 | 36 | 0 | 0 | 71 | [6 empty] | Shortage
4:00 | 3228 | 337 | 1048 | 7 | 149 | 36 | 0 | 0 | 70
4:30 | 3164 | 337 | 1052.5 | 7 | 149 | 36 | 0 | 0 | 69
5:00 | 3100 | 337 | 1057 | 7 | 149 | 36 | 0 | 0 | 68
5:30 | 3186 | 337 | 1123.5 | 7 | 149 | 36.5 | 0 | 0 | 69
6:00 | 3272 | 337 | 1190 | 7 | 149 | 37 | 0 | 0 | 70
6:30 | 3406 | 337 | 1192 | 11 | 149 | 37 | 0 | 0 | 71 |  |  |  |  | Coal
7:00 | 3540 | 337 | 1194 | 15 | 149 | 37 | 0 | 0 | 72
7:30 | 3671 | 429.5 | 1249.5 | 60.5 | 149 | 37 | 0 | 0 | 76 |  |  |  | Oil |  |  |  | ,
8:00 | 3802 | 522 | 1305 | 106 | 149 | 37 | 0 | 0 | 80
8:30 | 3764 | 522.5 | 1363.5 | 207.5 | 149 | 37 | 0 | 0 | 83
9:00 | 3726 | 523 | 1422 | 309 | 149 | 37 | 0 | 0 | 86
9:30 | 3765 | 523 | 1376.5 | 323.5 | 149 | 37 | 0 | 0 | 89
10:00 | 3804 | 523 | 1331 | 338 | 149 | 37 | 0 | 0 | 92
10:30 | 3822.5 | 522.5 | 1259 | 357 | 149 | 37 | 0 | 0 | 91
11:00 | 3841 | 522 | 1187 | 376 | 149 | 37 | 0 | 0 | 90
11:30 | 3834 | 522 | 1255 | 410 | 149 | 39.5 | 0 | 0 | 90
12:00 | 3827 | 522 | 1323 | 444 | 149 | 42 | 0 | 0 | 90
12:30 | 3831 | 522.5 | 1438.5 | 437 | 149 | 42 | 0 | 0 | 91
13:00 | 3835 | 523 | 1554 | 430 | 149 | 42 | 0 | 0 | 92
13:30 | 3835 | 523 | 1554 | 430 | 149 | 42 | 0 | 0 | 92
14:00 | 3835 | 523 | 1554 | 430 | 149 | 42 | 0 | 0 | 92
14:30 | 3767.5 | 522.5 | 1463 | 420.5 | 149 | 41.5 | 0 | 0 | 92
15:00 | 3700 | 522 | 1372 | 411 | 149 | 41 | 0 | 0 | 92
15:30 | 3719 | 522.5 | 1354.5 | 345.5 | 149 | 41 | 3.5 | 0 | 92
16:00 | 3738 | 523 | 1337 | 280 | 149 | 41 | 7 | 0 | 92
16:30 | 3675.5 | 533.5 | 1386.5 | 321.5 | 149 | 41 | 37 | 0 | 93
17:00 | 3613 | 544 | 1436 | 363 | 149 | 41 | 67 | 0 | 94
17:30 | 3746 | 605.5 | 1568 | 700 | 149 | 41 | 147 | 0 | 106
18:00 | 3879 | 667 | 1700 | 1037 | 149 | 41 | 227 | 0 | 118
18:30 | 3813 | 667.5 | 1715 | 1256.5 | 149 | 41.5 | 258.5 | 0 | 119
19:00 | 3747 | 668 | 1730 | 1476 | 149 | 42 | 290 | 0 | 120
19:30 | 3792 | 667 | 1770 | 1400 | 149 | 42 | 206 | 0 | 120
20:00 | 3777 | 668 | 1768 | 1301 | 149 | 42 | 196 | 0 | 118
20:30 | 3810 | 668 | 1776 | 1156.5 | 149 | 42 | 154 | 0 | 114
21:00 | 3843 | 668 | 1784 | 1012 | 149 | 42 | 112 | 0 | 110
21:30 | 3816.5 | 668 | 1779 | 742.5 | 149 | 42 | 64.5 | 0 | 105
22:00 | 3790 | 668 | 1774 | 473 | 149 | 42 | 17 | 0 | 100
22:30 | 3752 | 668 | 1751 | 323.5 | 149 | 43.5 | 8.5 | 0 | 96
23:00 | 3714 | 668 | 1728 | 174 | 149 | 45 | 0 | 0 | 92
23:30 | 3647 | 568 | 1689 | 91 | 149 | 45 | 0 | 0 | 88 | Max Temp. in Dhaka |  | 27.6° C
24:00 | 3580 | 468 | 1650 | 8 | 149 | 45 | 0 | 0 | 84
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
Note on W13: Author:

## Generation
2019-01-03
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 35 | 35 | 36 | 36 | 36 | 37 | 37 | 37 | 37 | 37 | 37 | 42 | 42 | 41 | 41 | 41 | 41 | 41 |  | 42 | 42 | 42 | 42 | 42 | 45 | 45 | 946189
2 | Kaptai Unit-4 & 5
3 | Chattogram ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3200000
5 | Raozan 25 MW (RPCL) | [7 empty] | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 |  | 25 | 25 | 25 | 25 | 25 | 0 |  | 205200
| Teknaf Solartech 20MW | [5 empty] | 0 | 1.48 | 7.5 | 13 | 17.4 | 19.2 | 19.5 | 18.7 | 16 | 12.5 | 6.5 | 0 | 0 | [8 empty] | 132300
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 120 | 120 | 120 | 120 | 130 | 130 | 130 | 122 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2941779
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | [17 empty] | 34 |  | 68 | 34 | 34 | 0 | 0 |  |  | 112133
12 | Hathazari peaking
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [17 empty] | 8 |  | 0 | 0 | [5 empty] | 5968
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 82 | 66 | 73 | 79 | 82 | 82 | 159 | 135 | 97 | 92 | 97 | 97 | 115 | 100 | 100 | 160 | 135 | 140 |  | 150 | 150 | 150 | 159 | 155 | 150 | 150 | 2957000
17 | Siddhirganj CCPP-335 MW | 150 | 150 | 120 | 120 | 120 | 130 | 180 | 200 | 200 | 160 | 198 | 180 | 180 | 180 | 180 | 180 | 150 | 162 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3864838
18 | Summit Gazipur -2 | [17 empty] | 2 |  | 12 | 12 | 0 | 0 |  |  |  | 27600
19 | Ashuganj 195MW Modular | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal ST: Unit-1,2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 740000
21 | Ghorasal GT: Unit-3 | 94 | 93 | 93 | 94 | 0 |  |  | 0 | 20 | 140 | 155 | 155 | 85
22 | Ghorasal GT: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 250 | 250 | 240 | 240 | 240 | 240 | 280 | 320 | 320 | 320 | 320 | 320 | 380 | 320 | 320 | 320 | 300 | 350 |  | 350 | 350 | 350 | 350 | 350 | 300 | 300 | 7351236
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2097740
30 | Ashuganj ST: Unit- 5 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2163888
32 | Ashuganj Engines TSK | 40 | 5 | 5 | 5 | 5 | 5 | 5 | 40 | 40 | 37 | 40 | 40 | 40 | 40 | 40 | 40 | 37 | 37 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 699480
33 | Ashuganj CCPP 225 MW | 192 | 185 | 184 | 187 | 182 | 204 | 205 | 200 | 226 | 224 | 184 | 193 | 186 | 186 | 205 | 202 | 191 | 200 |  | 184 | 184 | 184 | 193 | 185 | 184 | 184 | 4678000
34 | Ashuganj CCPP(South) | 309 | 301 | 301 | 301 | 334 | 334 | 334 | 334 | 305 | 305 | 305 | 320 | 305 | 305 | 324 | 331 | 257 | 283 |  | 261 | 261 | 261 | 272 | 260 | 260 | 261 | 7278000
Ashuganj CCPP(North)
35 | Ashuganj (Precision) 55MW | 24 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 202080
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 102 | 100 | 100 | 100 | 100 |  | 95 | 95 | 95 | 100 | 100 | 95 | 100 | 2344680
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 305 | 300 | 300 | 285 | 280 | 315 | 365 | 390 | 360 | 345 | 348 | 345 | 350 | 349 | 365 | 352 | 360 | 360 |  | 350 | 350 | 345 | 355 | 351 | 346 | 346 | 8313860
40 | Meghnaghat CCPP 450MW | 360 | 360 | 350 | 330 | 330 | 360 | 360 | 400 | 400 | 400 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 6671500
41 | Haripur Power CCPP 360MW | 260 | 255 | 255 | 236 | 235 | 307 | 305 | 336 | 370 | 290 | 285 | 285 | 285 | 290 | 300 | 300 | 365 | 364 |  | 365 | 365 | 365 | 364 | 368 | 329 | 327 | 7406000
42 | Mymensingh RPCL 210MW | 164 | 168 | 169 | 175 | 155 | 153 | 156 | 176 | 175 | 173 | 172 | 170 | 146 | 148 | 148 | 148 | 148 | 148 |  | 147 | 147 | 146 | 142 | 140 | 141 | 141 | 3674680
43 | Haripur NEPC 110MW
44 | Fenchugonj CCPP-1 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 26 | 26 | 25 | 25 | 26 | 53 | 56 | 56 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 836000
45 | Fenchugonj CCPP-2 | 63 | 63 | 63 | 63 | 40 | 40 | 40 | 63 | 63 | 63 | 63 | 63 | 63 | 62 | 62 | 62 | 62 | 63 |  | 63 | 63 | 62 | 62 | 62 | 63 | 63 | 1427492
46 | Shajibazar 330 MW | 220 | 223 | 216 | 221 | 230 | 238 | 240 | 234 | 218 | 217 | 217 | 231 | 220 | 231 | 234 | 228 | 231 | 228 |  | 220 | 220 | 221 | 228 | 222 | 220 | 232 | 5133000
47 | Shahjibazar GT: Unit- 8, 9 | 57 | 40 | 40 | 40 | 54 | 70 | 70 | 69 | 59 | 53 | 51 | 65 | 53 | 46 | 64 | 65 | 67 | 67 |  | 56 | 66 | 60 | 68 | 66 | 64 | 53 | 1417000
48 | Shahjibazar 86MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 50 | 832320
49 | Shahjibazar (EPL) 50MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 48 | 48 | 47 | 47 | 47 | 46 | 47 | 47 | 46 | 48 |  | 48 | 49 | 49 | 49 | 49 | 49 | 49 | 796320
50 | Sylhet GT 150 MW | 78 | 78 | 79 | 78 | 78 | 79 | 79 | 78 | 78 | 78 | 80 | 78 | 97 | 98 | 78 | 78 | 78 | 96 |  | 78 | 78 | 80 | 80 | 80 | 79 | 78 | 1992160
51 | Sylhet GT 20 MW | [17 empty] | 0 |  | 19 | 19 | 20 | 20 | 20 | 20 | 20 | 120000
52 | Sylhet (EPL) 50MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 24 | 25 | 25 | 25 | 24 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 443040
53 | Sylhet (Desh) 10MW | [17 empty] | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 0 | 50220
54 | Hobiganj 11MW | 8 | 8 | 0 | [7 empty] | 5 | 5 | 5 | 8 | 8 | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 146448
55 | Fenchugonj (Barakatullah) 51MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 16 | 22 | 22 | 22 | 22 | 22 | 41 | 53 |  | 53 | 53 | 51 | 51 | 51 | 51 | 51 | 559800
56 | Shahjahanulla 25 MW | [16 empty] | 0 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 173664
57 | Summit Bibiana- 2 | 275 | 280 | 285 | 285 | 295 | 325 | 330 | 340 | 320 | 300 | 200 | 210 | 310 | 300 | 330 | 295 | 310 | 305 |  | 280 | 315 | 290 | 305 | 310 | 295 | 280 | 7567800
58 | Southern 55MW | [7 empty] | 0 | [8 empty] | 17 | 17 |  | 17 | 17 | 0 | 0 |  |  |  | 58000
59 | Sikalbaha (Energis) | [7 empty] | 4 | 37 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 0 | 780480
60 | Barabkunda (Regent) | 22 | 0 | [5 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 412512
61 | Narshingdi (Doreen) | [8 empty] | 0 | 19 | 19 | 0 | 19 | 16 | 16 | 16 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 223632
62 | Tangail (Doreen) 22MW | [7 empty] | 14 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 346392
63 | Tripura | 76 | 76 | 72 | 70 | 68 | 70 | 72 | 80 | 86 | 92 | 90 | 90 | 92 | 92 | 92 | 92 | 94 | 118 |  | 120 | 120 | 118 | 110 | 100 | 92 | 84 | 2135040
64 | Malancha, Ctg. EPZ (United) | 42 | 30 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 4 | 4 | 4 | 10 | 7 | 2 | 2 | 2 | 17 |  | 27 | 32 | 35 | 38 | 39 | 37 | 33 | 472320
65 | Feni (Doreen) 22MW | [7 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 313308
66 | Feni, Mohipal (Doreen) | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 137160
67 | Jangalia (Summit) 33MW | [8 empty] | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 231000
68 | Summit Cumilla 25MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 365680
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 33 | 33 | 33 | 22 | 22 | 22 | 22 | 22 | 26 | 26 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 701100
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 27 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 805353
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 820200
73 | Ghorashal (Regent) | 42 | 12 | 0 |  |  |  |  | 12 | 52 | 52 | 52 | 101 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 1578636
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla)
78 | Gazipur (RPCL) | [7 empty] | 2 | 30 | 0 | 7 | 38 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 24 | 0 |  | 533796
79 | Kodda 149MW
80 | Jamalpur 95MW | [16 empty] | 3 | 40 |  | 80 | 81 | 81 | 81 | 0 | 0 |  | 319680
81 | Lakdhanvi 52 MW
82 | Madanganj 102MW | [17 empty] | 5 |  | 20 | 50 | 64 | 20 | 0 | 0 |  | 130416
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 40 | 40 | 85 | 10 | 10 | 10 | 10 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 815530
85 | Keraniganj (Powerpac) 100MW | [9 empty] | 0 | 10 | 10 | 10 | 0 | 0 | [11 empty] | 44807
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL)
88 | Ghorashal 78MW (MAX) | 35 | 20 | 0 | [7 empty] | 0 | 20 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 572320
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 12000
91 | Juldah (Acorn) | [7 empty] | 0 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 0 | 0 |  |  | 130416
92 | Fenchuganj (EPL) 44MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 12 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 0 |  | 0 | 0 | 21 | 21 | 21 | 21 | 22 | 322000
93 | Ashuganj (Midland) 51MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 32 | 51 | 51 | 760111
94 | Gagnagar (Orion) | [7 empty] | 0 | 7 | 32 | 32 | 32 | 7 | 7 | 7 | 7 | 7 | 27 |  | 32 | 32 | 32 | 0 | 0 |  |  | 239760
95 | Patenga 50MW | [7 empty] | 0 | 1 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 37 | 50 | 50 | 52 | 37 | 0 |  | 247200
96 | Chattogram ECPV 108 MW | [7 empty] | 0 | 12 | 13 | 13 | 13 | 19 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 0 |  |  |  | 156480
97 | Katpotti 51 MW | [16 empty] | 0 | 6 |  | 47 | 47 | 47 | 47 | 0 | 0 |  | 199872
98 | Bosila 108MW | [10 empty] | 5 | 24 | 24 | 24 | 24 | 8 | 8 | 47 |  | 47 | 47 | 47 | 47 | 0 |  |  | 295680
99 | Madanganj-55 MW | [8 empty] | 0 | 14 | 30 | 30 | 30 | 15 | 15 | 15 | 15 | 17 |  | 40 | 40 | 40 | 40 | 0 | 0 |  | 339125
100 | Northern 55 MW | [16 empty] | 18 | 54 |  | 54 | 55 | 55 | 18 | 0 |  |  | 190171
101 | Kushiara 163 MW CCPP GT | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 163 | 100 | 100 | 100 | 100 | 125 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3165970
102 | Sarishabari (Solar) | [7 empty] | 0.4 | 1.2 | 1.6 | 2 | 2.1 | 2 | 1.8 | 1 | 0.5 | 0 | 0 | [8 empty] | 12500
103 | Banco Energy 54MW | [10 empty] | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 54 |  | 54 | 54 | 54 | 54 | 18 | 0 |  | 365040
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 77 |  | 115 | 72 | 48 | 7 | 7 | 7 | 7 | 468000
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | [16 empty] | 1 | 27 |  | 60 | 15 | 15 | 0 |  |  |  | 122400
115 | Juldah 100 MW Unit-3 | [7 empty] | 25 | 80 | 80 | 80 | 80 | 80 | 92 | 92 | 30 | 30 | 92 |  | 92 | 92 | 92 | 92 | 92 | 92 | 0 | 1191360
116 | Chandpur Desh 200MW | [16 empty] | 0 | 47 |  | 155 | 160 | 100 | 100 | 60 | 0 |  | 556800
117 | Midland 150MW | [17 empty] | 43 |  | 88 | 100 | 100 | 50 | 0 |  |  | 352940
118 | Bibiyana-3 285MW
120 | Eastern Zone Total | 4065 | 3885 | 3758 | 3711 | 3620 | 3845 | 4074.48 | 4407.9 | 4622.2 | 4640 | 4536.2 | 4738.6 | 4965.7 | 4591.8 | 4691.5 | 4618 | 4620 | 5540 |  | 5881 | 5872 | 5759 | 5549 | 5079 | 4804 | 4501 | 111252056
121
122 | o
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | [16 empty] | 16 | 49 |  | 99 | 49 | 49 |  |  |  |  | 219840
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | [16 empty] | 7 | 26 |  | 30 | 30 | 30 | 30 | 0 |  |  | 113760
Khulna CCPP 225MW
129 | Labon Chora 105 MW | [7 empty] | 17 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 17 | 17 | 105 |  | 105 | 105 | 105 | 105 | 53 | 0 |  | 916800
130
131
132
133
| Summit Barisal 110 MW | [16 empty] | 16 | 48 |  | 48 | 48 | 48 | 48 | 0 |  |  | 199600
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 11 | 11 | 11 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 30 | 51 | 52 | 22 | 22 | 22 | 22 | 92 |  | 97 | 96 | 97 | 97 | 97 | 96 | 97 | 966477
| Bhola CCPP 194MW | 189 | 167 | 192 | 185 | 153 | 153 | 153 | 206 | 200 | 182 | 196 | 195 | 188 | 191 | 195 | 196 | 196 | 200 |  | 171 | 200 | 194 | 202 | 201 | 203 | 197 | 4582418
140 | Bhola (Venture) 33MW | 19 | 18 | 18 | 16 | 16 | 17 | 17 | 18 | 18 | 19 | 19 | 20 | 19 | 18 | 17 | 17 | 18 | 25 |  | 26 | 26 | 26 | 25 | 24 | 16 | 21 | 457800
141 | Bangla Trak Noapara
142 | Noapara (KZA) 40MW | [5 empty] | 0 | 8 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 0 |  | 618375
143 | Gopalganj Peaking | [14 empty] | 0 | 7 | 25 | 40 |  | 36 | 35 | 25 |  |  |  |  | 117504
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 522 | 523 | 523 | 522 | 522 | 523 | 523 | 522 | 523 | 544 | 667 |  | 668 | 667 | 668 | 668 | 668 | 668 | 468 | 12458181
147 | Bheramara 360 MW | 250 | 250 | 250 | 230 | 230 | 300 | 340 | 340 | 340 | 370 | 370 | 340 | 340 | 300 | 300 | 300 | 300 | 340 |  | 340 | 340 | 340 | 340 | 340 | 340 | 300 | 7947360
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3652700
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1933000
Baghabari Peaking 50MW
157 | Sirajgonj Unit-1 225MW (Gas)
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 179 | 171 | 157 | 147 | 149 | 161 | 166 | 178 | 176 | 170 | 165 | 167 | 173 | 162 | 168 | 159 | 164 | 161 |  | 159 | 165 | 165 | 168 | 157 | 151 | 151 | 4121982
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas)
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking
162 | Bogra (GBB) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 18 | 18 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 3 | 399600
163 | Bogra (EPL) | [7 empty] | 6 | 6 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 181260
164 | Ullapara (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 8 | 5 | 5 | 158706
165 | Amnura 50MW | 24 | 0 | [14 empty] | 12 | 50 |  | 50 | 50 | 50 | 50 | 24 | 0 |  | 291420
166 | Katakhali (Northern)
167 | Katakhali Peaking
168 | Santahar Peaking | [16 empty] | 0 | 37 |  | 39 | 39 | 39 | 39 | 0 |  |  | 151897
169 | Rajlanka 52 MW | 34 | 0 | [5 empty] | 11 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 43 |  | 43 | 43 | 43 | 43 | 43 | 25 | 1 | 500640
170 | Chapainawabganj-100 MW | [16 empty] | 35 | 65 |  | 100 | 51 | 51 | 26 | 0 |  |  | 226900
171
172
173 | Rangpur GT | [16 empty] | 0 | 17 |  | 17 | 17 | 17 | 17 | 17 | 0 |  | 86000
175 | Saidpur GT | [19 empty] | 0 | 0 | 0 | 0
176
177
178
178 | Western Zone Total | 1282 | 1193 | 1204 | 1164 | 1134 | 1217 | 1271 | 1601 | 1644 | 1653 | 1687 | 1680 | 1680 | 1601 | 1609 | 1556 | 1687 | 2278 | 0 | 2341 | 2274 | 2260 | 2171 | 1934 | 1766 | 1483 | 40302220