## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 09-04-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-04-2026 | during | 09-04-2026 | during | 09-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 413 | 414 | 412 | 412 | 412 | 412 | FGMO not available
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 180 | 180 | 450 | 450 | 226 | 226 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 32 | 49 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 300 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 45 | 125 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 12 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 18.5 | 19 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 17 | 15 | 15 | 15 | 15 | Partial Shutdown due to maintenance
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 34 | 24 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 138 | 260 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 60 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 70 | 105 | 105 | 88 | 88 | Engine Problem
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 72 | 162 | 162 | 35 | 35 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 2 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 480 | 540 | 584 | 584 | 526 | 526 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 60 | 142 | 160 | 160 | 143 | 143 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1991.5 | 2502 | 5933.22 | 5908.22 | 2601.55 | 2630.55
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 31 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 220 | 215 | 225 | 215 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 46 | 92 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 45 | 56 | 64 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 67 | 68 | 68 | 68 | 68 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 13 | 13 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 15 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 62 | 108 | 108 | 38 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.16 | 0 | 2.15 | 0 | 2.15 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 18 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 51 | 106 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 0 | 0 | Liquid fuel shortage
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 51 | 155 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 2 | 0 | 7 | 4 | 7 | 4 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 150 | 150 | 160 | 160 | 150 | 150 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1831.16 | 2349.5 | 3067.01 | 3080.86 | 2350.65 | 2364.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 166 | 185 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 361 | 360 | 350.01 | 350.01 | 350.01 | 350.01 | FGMO not available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 240 | 220 | 342.01 | 342.01 | 320 | 320 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 215 | 215 | 393 | 393 | 250 | 250 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 60 | 142 | 150 | 150 | 60 | 140 | Partial Shutdown due to maintenance
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 12 | 31 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 99 | 99 | 163 | 163 | 101 | 101 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 29 | 198 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 174 | 180 | 84 | 76 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 4 | 9 | 113 | 113 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 39 | 65 | 115 | 115 | 17 | 51 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 33 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.745 | 1491 | 1775 | 2764.19 | 2686.19 | 1825.01 | 1869.01
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-04-2026 | during | 09-04-2026 | during | 09-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 20 | 20 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.1 | 0 | 1.6 | 0 | 1.6 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 68 | 68 | 10 | 10 | 10 | 10 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 70 | 70 | 70 | 70 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 48.62 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 2 | 17 | 17 | 17 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 129.72 | 106 | 320.1 | 276.5 | 172.6 | 129
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 40 | 40 | 0 | 0 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 154 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 111 | 111 | 110 | 110 | 110 | 110 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 52 | 53 | 82 | 82 | 60 | 60 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 99 | 98 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 13 | 25 | 25 | 17 | 17 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 349 | 0 | 385 | 385 | 357 | 357 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1196 | 829 | 1326 | 1326 | 1158 | 1158
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 923 | 923 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 18 | 34 | 34 | 34 | 34 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 65 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 116 | 92 | 410 | 410 | 161 | 161 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 40 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 607 | 597 | 617.1 | 617.1 | 617.1 | 617.1 | U-2 Under Maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1686 | 1695 | 2962.1 | 2887.1 | 1952.2 | 1877.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 0 | 106 | 300 | 300 | 300 | 300 | Unit1 Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 110 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 130 | 130 | 130 | 130 | STG Under Maintenance
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1230 | 1244 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.29 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1887.29 | 2152 | 2462 | 2461 | 2289 | 2288
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 58.83 | 0 | 38 | 0 | 38 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 42 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 164 | 141 | 214 | 214 | 170 | 170 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 144 | 142 | 220 | 220 | 170 | 170 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 53 | 92 | 92 | 92 | 92 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 26 | 49 | 113 | 113 | 35 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 35 | 113 | 113 | 35 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 6.09 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 765 | 759 | 748 | 748 | 708 | 708 | U-2 Under Maintenance
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 58.11 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 92 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1763.03 | 1690 | 2518.84 | 2313.99 | 1883.26 | 1678.41
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 54 | 53 | 50 | 50 | 54 | 54 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 39 | 91 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.7 | 0 | 6.2 | 0 | 6.2 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 113 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 37 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 202 | 0 | 170.69 | 0 | 170.69 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 454.7 | 257 | 484.89 | 278 | 488.89 | 282
System Total |  |  |  |  | 28823.2 | 29269.987 | 12430.4 | 13355.5 | 21838.35 | 21217.86 | 14721.16 | 14276.67
Forecast Scenario (09-04-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12500 |  | 0 |  | 12500
|  |  |  | 1:00 | 12570 |  | 0 |  | 12570
|  |  |  | 2:00 | 12540 |  | 0 |  | 12540
|  |  |  | 3:00 | 12150 |  | 0 |  | 12150
|  |  |  | 4:00 | 11840 |  | 0 |  | 11840
|  |  |  | 5:00 | 11510 |  | 0 |  | 11510
|  |  |  | 6:00 | 11500 |  | 0 |  | 11500
|  |  |  | 7:00 | 12210 |  | 0 |  | 12210
|  |  |  | 8:00 | 12440 |  | 0 |  | 12440
|  |  |  | 9:00 | 12710 |  | 0 |  | 12710
|  |  |  | 10:00 | 12870 |  | 0 |  | 12870
|  |  |  | 11:00 | 13441 |  | 0 |  | 13130
|  |  |  | 12:00 | 14721 |  | 0 |  | 13570
|  |  |  | 13:00 | 14728 |  | 0 |  | 13950
|  |  |  | 14:00 | 14624 |  | 0 |  | 13820
|  |  |  | 15:00 | 14514 |  | 0 |  | 14030
|  |  |  | 16:00 | 14334 |  | 0 |  | 13800
|  |  |  | 17:00 | 14193 |  | 0 |  | 13400
|  |  |  | 18:00 | 14255 |  | 0 |  | 13310
|  |  |  | 18:30 | 14248 |  | 0 |  | 13800
|  |  |  | 19:00 | 14251 |  | 170 |  | 14430
|  |  |  | 19:30 | 14261 |  | 113 |  | 14380
|  |  |  | 20:00 | 14276 |  | 213 |  | 14500
|  |  |  | 21:00 | 14278 |  | 0 |  | 13810
|  |  |  | 22:00 | 14267 |  | 0 |  | 13400
|  |  |  | 23:00 | 14272 |  | 0 |  | 13100
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 13570.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 213
Probable Maximum Demand at Evening Peak: |  |  | 14500.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14278.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 306.50272 MKWHr. |  | 30 | 25 | 20 | 30 | 20 | 25 | 13 | 25 | 25 | 213
*** This report is generated digitally from Operation Information System (OIS) at 10:22 hrs on 09-04-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 08-04-2026 | [28 empty] | Date: | 08-04-2026 | [28 empty] | Date: | 08-04-2026 | [28 empty] | Date: | 08-04-2026 | [28 empty] | Date: | 08-04-2026 | [17 empty] | Date: | 08-04-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 14 | 0 | 485 | 0 | 0 | 0 | 0 | 39 | 17 | 0 | 0 | 12 | 0 | 0 | 80 | 0 | 16 | 315 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1060 | 0 | 0 | 0 | 50 | 361 | 260 | 51 | 0 | 201 | 0 | 0 | 104 | 0 | 0 | 14 | 0 | 162 | 0 | 0 | 0 | 300 | 0 | 394 | 30 | 30 | 156 | 0 | 17 | 0 | 53 | 30 | 110 | 0 | 98 | 0 | 59 | 9 | 11 | 0 | 0 | 12 | 5720 | 922 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 509 | 0 | 0 | 0 | 476.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 162 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 130 | 220 | 0 | 0 | 990 | 0 | 4391.32 | 10111.32 | 82.5
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 18 | 160 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1130 | 0 | 0 | 0 | 40 | 360 | 280 | 51 | 0 | 204 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 156 | 0 | 0 | 0 | 305 | 0 | 394 | 30 | 30 | 162 | 0 | 17 | 0 | 53 | 30 | 110 | 0 | 99 | 0 | 9 | 57 | 11 | 0 | 0 | 12 | 5600 | 922 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 0 | 0 | 0 | 563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 161 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 130 | 220 | 0 | 0 | 1114 | 0 | 4724 | 10324 | 82.48
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 20 | 160 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 951 | 0 | 0 | 0 | 140 | 360 | 280 | 51 | 0 | 189 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 154 | 0 | 0 | 0 | 300 | 0 | 394 | 30 | 30 | 155 | 0 | 17 | 0 | 53 | 30 | 110 | 0 | 99 | 0 | 9 | 56 | 11 | 0 | 0 | 12 | 5492 | 922 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 161 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 130 | 220 | 0 | 0 | 1163 | 0 | 4921 | 10413 | 82.46
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 21 | 160 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 816 | 0 | 0 | 0 | 160 | 361 | 280 | 51 | 0 | 179 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 144 | 0 | 0 | 0 | 300 | 0 | 394 | 30 | 30 | 153 | 0 | 17 | 0 | 53 | 30 | 110 | 0 | 99 | 0 | 9 | 56 | 17 | 0 | 0 | 0 | 5330 | 922 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 592 | 0 | 0 | 0 | 721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 161 | 0 | 414 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221 | 130 | 220 | 0 | 0 | 1100 | 0 | 4823 | 10153 | 82.44
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 25 | 160 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 685 | 0 | 0 | 0 | 190 | 361 | 280 | 51 | 0 | 191 | 0 | 0 | 105 | 0 | 0 | 20 | 0 | 146 | 0 | 0 | 0 | 295 | 0 | 394 | 30 | 30 | 150 | 0 | 17 | 0 | 53 | 30 | 111 | 0 | 99 | 0 | 9 | 55 | 17 | 0 | 0 | 0 | 5237 | 922 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 594 | 0 | 0 | 0 | 716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 162 | 0 | 414 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 130 | 180 | 0 | 0 | 1100 | 0 | 4748 | 9985 | 82.42
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 31 | 160 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 620 | 0 | 0 | 0 | 225 | 360 | 280 | 51 | 0 | 192 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 148 | 0 | 0 | 0 | 300 | 0 | 394 | 30 | 30 | 151 | 0 | 17 | 0 | 53 | 30 | 111 | 0 | 99 | 0 | 9 | 58 | 17 | 0 | 0 | 0 | 5222 | 923 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493 | 0 | 0 | 0 | 721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 161 | 0 | 414 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 130 | 180 | 0 | 0 | 1000 | 0 | 4555 | 9777 | 82.4
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 14 | 0 | 495 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 24 | 160 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 641 | 0 | 0 | 0 | 215 | 360 | 280 | 51 | 0 | 187 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 140 | 0 | 1 | 8 | 300 | 0 | 394 | 30 | 30 | 154 | 0 | 17 | 0 | 53 | 30 | 110 | 0 | 100 | 0 | 9 | 58 | 16 | 0 | 0.62 | 0 | 5270.62 | 922 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.15 | 527 | 0 | 0 | 0 | 722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63 | 0 | 0 | 0 | 0.66 | 165 | 0 | 0 | 0 | 160 | 0 | 414 | 0 | 0.07 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 178 | 130 | 180 | 0 | 0 | 1000 | 0 | 4599.51 | 9870.13 | 82.38
07:00 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 19 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0.87 | 80 | 0 | 23 | 160 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 920 | 4 | 0 | 0 | 215 | 360 | 240 | 51 | 0 | 187 | 0 | 0 | 104 | 0 | 0 | 20 | 0 | 128 | 0 | 17 | 8 | 305 | 0 | 394 | 30 | 30 | 160 | 2 | 17 | 0 | 53 | 30 | 110 | 0 | 100 | 0 | 9 | 58 | 11 | 0.3 | 9.5 | 0 | 5473.67 | 923 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 595 | 0 | 0 | 0 | 764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.67 | 22 | 0 | 0 | 9.67 | 164 | 0 | 0 | 0 | 160 | 0 | 414 | 0 | 0.97 | 0 | 55 | 100 | 4 | 0 | 0 | 0 | 0 | 1.1 | 34 | 0.1 | 0 | 267 | 130 | 220 | 0 | 0 | 1110 | 0 | 5147.51 | 10621.18 | 82.36
08:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 16 | 0 | 19 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.03 | 80 | 0 | 2 | 160 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1160 | 10 | 0 | 0 | 215 | 361 | 240 | 51 | 0 | 177 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 144 | 0 | 39 | 8 | 300 | 0 | 393 | 30 | 30 | 137 | 6 | 17 | 0 | 53 | 30 | 109 | 0 | 100 | 0 | 9 | 57 | 8 | 1 | 25.89 | 0 | 5688.92 | 922 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 615 | 0 | 0 | 0 | 759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.66 | 16 | 0 | 0 | 15.65 | 163 | 0 | 0 | 0 | 160 | 0 | 370 | 0 | 1.54 | 0 | 54 | 115 | 14 | 0 | 0 | 0 | 0 | 2.9 | 65 | 0.29 | 0 | 277 | 130 | 220 | 0 | 0 | 1180 | 0 | 5297.04 | 10985.96 | 82.34
09:00 | 0 | 34 | 10 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 0 | 19 | 15 | 0 | 4 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 9 | 0 | 19 | 14 | 0 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.98 | 80 | 0 | 2 | 150 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1180 | 15 | 0 | 0 | 215 | 360 | 240 | 51 | 0 | 174 | 0 | 0 | 102 | 0 | 0 | 20 | 0 | 150 | 0 | 57 | 8 | 300 | 0 | 394 | 30 | 30 | 156 | 9 | 17 | 0 | 53 | 30 | 111 | 0 | 100 | 0 | 9 | 58 | 7 | 1.8 | 37.27 | 0 | 5930.05 | 922 | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 606 | 0 | 0 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.71 | 38 | 0 | 0 | 14.34 | 164 | 0 | 0 | 0 | 157 | 0 | 414 | 0 | 1.41 | 0 | 54 | 115 | 24 | 0 | 0 | 0 | 0 | 4.2 | 143 | 0.47 | 0 | 277 | 130 | 220 | 0 | 0 | 1200 | 0 | 5450.13 | 11380.18 | 82.33
10:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 0 | 0 | 37 | 15 | 45 | 15 | 5 | 25 | 0 | 180 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 13 | 0 | 19 | 14 | 0 | 510 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.59 | 80 | 0 | 5 | 150 | 0 | 0 | 1 | 0 | 0 | 216 | 0 | 0 | 0 | 1175 | 17 | 0 | 0 | 215 | 361 | 240 | 51 | 0 | 174 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 160 | 0 | 68 | 8 | 300 | 0 | 349 | 30 | 30 | 159 | 8 | 17 | 0 | 53 | 30 | 110 | 0 | 99 | 0 | 9 | 68 | 4 | 2 | 39 | 0 | 6038.59 | 922 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 610 | 0 | 0 | 0 | 762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.58 | 56 | 0 | 0 | 57.52 | 164 | 0 | 0 | 0 | 151 | 0 | 414 | 0 | 5.54 | 0 | 54 | 115 | 30 | 0 | 0 | 0 | 0 | 6.3 | 172 | 0.42 | 0 | 278 | 130 | 220 | 0 | 0 | 1200 | 0 | 5509.36 | 11547.95 | 82.32
11:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 0 | 2 | 52 | 15 | 70 | 20 | 17 | 50 | 0 | 180 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 13 | 12 | 19 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.92 | 80 | 8 | 3 | 150 | 0 | 0 | 18 | 0 | 23 | 213 | 0 | 0 | 0 | 1160 | 19 | 25 | 0 | 215 | 360 | 240 | 51 | 0 | 178 | 0 | 10 | 99 | 24 | 0 | 20 | 0 | 162 | 0 | 55 | 8 | 305 | 0 | 349 | 30 | 30 | 157 | 8 | 17 | 0 | 52 | 30 | 109 | 0 | 99 | 0 | 9 | 68 | 0 | 2.3 | 38.53 | 0 | 6201.75 | 922 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 610 | 0 | 0 | 0 | 763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.26 | 112 | 0 | 0 | 50.82 | 164 | 0 | 0 | 0 | 146 | 0 | 414 | 0 | 5.9 | 0 | 54 | 115 | 36 | 34 | 0 | 0 | 0 | 7.1 | 197 | 0.18 | 0 | 307 | 130 | 220 | 0 | 0 | 1200 | 0 | 5693.26 | 11895.01 | 82.31
12:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 17 | 2 | 60 | 45 | 138 | 32 | 17 | 54 | 0 | 180 | 0 | 0 | 0 | 12 | 335 | 0 | 0 | 30 | 60 | 18.5 | 14 | 0 | 480 | 0 | 16 | 0 | 0 | 2 | 0 | 0 | 0 | 12 | 12 | 4.16 | 80 | 51 | 2 | 150 | 51 | 0 | 31 | 0 | 46 | 214 | 0 | 0 | 0 | 1160 | 0 | 60 | 0 | 215 | 361 | 240 | 51 | 0 | 166 | 0 | 39 | 99 | 29 | 4 | 8 | 0 | 174 | 0 | 33 | 12 | 310 | 0 | 349 | 30 | 30 | 156 | 12 | 17 | 0 | 52 | 30 | 111 | 0 | 99 | 2 | 9 | 68 | 0 | 2.1 | 48.62 | 0 | 6639.38 | 923 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 607 | 0 | 0 | 0 | 765 | 0 | 0 | 0 | 35 | 26 | 0 | 0 | 0 | 0 | 58.83 | 92 | 0 | 0 | 58.11 | 164 | 0 | 0 | 0 | 144 | 0 | 414 | 0 | 6.09 | 0 | 54 | 115 | 37 | 39 | 0 | 0 | 0 | 7.7 | 202 | 0.29 | 0 | 307 | 130 | 220 | 0 | 0 | 1230 | 0 | 5791.02 | 12430.4 | 82.31
13:00 | 0 | 50 | 41 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17.5 | 17 | 103 | 78 | 230 | 45 | 35 | 54 | 0 | 180 | 0 | 0 | 0 | 35 | 334 | 0 | 0 | 31 | 108 | 18.5 | 14 | 0 | 450 | 0 | 16 | 17 | 0 | 6 | 17 | 24 | 0 | 12 | 12 | 2.76 | 80 | 94 | 4 | 150 | 93 | 0 | 43 | 0 | 51 | 215 | 0 | 0 | 0 | 1175 | 19 | 61 | 0 | 215 | 361 | 240 | 51 | 0 | 165 | 0 | 51 | 100 | 17 | 9 | 8 | 0 | 174 | 0 | 28 | 16 | 305 | 0 | 349 | 30 | 30 | 156 | 5 | 17 | 0 | 52 | 30 | 111 | 0 | 99 | 17 | 9 | 68 | 0 | 2.2 | 48.8 | 0 | 7108.76 | 923 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 608 | 0 | 0 | 0 | 765 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 58.33 | 110 | 0 | 0 | 55.15 | 152 | 0 | 0 | 0 | 142 | 0 | 414 | 0 | 5.56 | 0 | 54 | 115 | 35 | 35 | 0 | 0 | 0 | 7.8 | 196 | 0.23 | 32 | 277 | 130 | 220 | 0 | 0 | 1244 | 27 | 5834.07 | 12942.83 | 82.29
14:00 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 18 | 17 | 108 | 78 | 245 | 45 | 35 | 72 | 0 | 180 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 28 | 125 | 18.5 | 14 | 0 | 490 | 0 | 16 | 24 | 0 | 13 | 17 | 25 | 0 | 12 | 12 | 1.48 | 80 | 103 | 3 | 150 | 120 | 0 | 47 | 2 | 51 | 218 | 0 | 0 | 0 | 1160 | 0 | 60 | 0 | 215 | 360 | 240 | 51 | 0 | 159 | 0 | 51 | 98 | 17 | 9 | 14 | 0 | 178 | 0 | 29 | 29 | 305 | 0 | 349 | 30 | 30 | 153 | 10 | 20 | 0 | 52 | 30 | 110 | 0 | 98 | 17 | 9 | 68 | 0 | 1.86 | 43.58 | 0 | 7211.42 | 923 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 606 | 0 | 0 | 0 | 763 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 48.46 | 95 | 0 | 0 | 52.93 | 143 | 0 | 0 | 0 | 142 | 0 | 414 | 0 | 4.83 | 0 | 54 | 115 | 23 | 35 | 0 | 0 | 0 | 6.6 | 180 | 0.33 | 85 | 277 | 130 | 220 | 0 | 0 | 1244 | 35 | 5835.15 | 13046.57 | 82.28
15:00 | 0 | 70 | 49 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17.5 | 17 | 149 | 125 | 244 | 45 | 35 | 72 | 0 | 225 | 0 | 0 | 0 | 35 | 330 | 0 | 0 | 21 | 125 | 18 | 14 | 0 | 450 | 0 | 16 | 26 | 0 | 2 | 17 | 29 | 0 | 12 | 12 | 1.78 | 80 | 101 | 3 | 150 | 160 | 0 | 50 | 25.5 | 59 | 216 | 0 | 0 | 0 | 1160 | 0 | 61 | 0 | 215 | 360 | 240 | 51 | 0 | 155 | 0 | 51 | 98 | 16 | 9 | 12 | 0 | 180 | 0 | 37 | 23 | 315 | 0 | 350 | 30 | 30 | 155 | 8 | 20 | 0 | 53 | 30 | 0 | 0 | 99 | 17 | 9 | 68 | 0 | 1.5 | 34.79 | 0 | 7302.07 | 923 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 612 | 0 | 0 | 0 | 761 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 33.14 | 77 | 0 | 0 | 40.72 | 142 | 0 | 0 | 0 | 142 | 0 | 414 | 0 | 3.82 | 0 | 54 | 115 | 16 | 34 | 0 | 0 | 0 | 3.5 | 137 | 0.27 | 110 | 307 | 130 | 220 | 0 | 0 | 1200 | 35 | 5749.45 | 13051.52 | 82.27
16:00 | 0 | 70 | 49 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17.5 | 17 | 149 | 142 | 260 | 49 | 35 | 72 | 0 | 225 | 0 | 0 | 0 | 35 | 333 | 0 | 0 | 14 | 125 | 18 | 14 | 0 | 440 | 0 | 16 | 36 | 0 | 0 | 42 | 30 | 14 | 12 | 12 | 0.63 | 80 | 95 | 3 | 205 | 140 | 0 | 50 | 25.5 | 51 | 217 | 0 | 0 | 0 | 1190 | 2 | 60 | 0 | 215 | 360 | 220 | 51 | 0 | 152 | 0 | 51 | 98 | 17 | 9 | 12 | 0 | 182 | 0 | 19 | 23 | 310 | 0 | 350 | 30 | 30 | 152 | 2 | 20 | 0 | 79 | 30 | 35 | 0 | 98 | 17 | 9 | 68 | 0 | 0.8 | 22.79 | 8 | 7428.22 | 922 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 593 | 0 | 0 | 0 | 757 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 24 | 0 | 23.25 | 50 | 0 | 0 | 25.26 | 142 | 0 | 0 | 0 | 142 | 0 | 414 | 0 | 2.39 | 0 | 54 | 112 | 16 | 34 | 0 | 0 | 0 | 3.1 | 92 | 0.15 | 110 | 307 | 130 | 220 | 0 | 0 | 1200 | 46 | 5635.15 | 13063.37 | 82.26
17:00 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17.5 | 17 | 149 | 141 | 260 | 49 | 0 | 72 | 0 | 225 | 0 | 0 | 0 | 35 | 333 | 0 | 0 | 6 | 142 | 13 | 14 | 0 | 450 | 0 | 16 | 42 | 0 | 0 | 67 | 30 | 18 | 12 | 12 | 0.54 | 80 | 100 | 3 | 205 | 138 | 0 | 50 | 25.5 | 70 | 217 | 0 | 0 | 0 | 1105 | 1 | 63 | 0 | 215 | 360 | 220 | 51 | 0 | 160 | 0 | 51 | 98 | 55 | 9 | 12 | 0 | 180 | 0 | 13 | 30 | 310 | 0 | 350 | 30 | 30 | 152 | 2 | 20 | 0 | 52 | 30 | 72 | 0 | 98 | 17 | 9 | 67 | 0 | 0.3 | 8.62 | 12 | 7394.46 | 923 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 590 | 0 | 0 | 0 | 761 | 0 | 0 | 0 | 35 | 35 | 0 | 15 | 28 | 0 | 9.24 | 17 | 18 | 0 | 11.32 | 142 | 0 | 0 | 0 | 142 | 0 | 414 | 0 | 1.09 | 0 | 54 | 114 | 4 | 58 | 0 | 0 | 0 | 0.8 | 37 | 0.13 | 110 | 306 | 130 | 220 | 0 | 42 | 1200 | 43 | 5578.58 | 12973.04 | 82.25
18:00 | 0 | 50 | 49 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17.5 | 17 | 149 | 140 | 260 | 49 | 0 | 72 | 0 | 180 | 0 | 0 | 0 | 35 | 328 | 0 | 0 | 0 | 142 | 17 | 14 | 0 | 485 | 0 | 16 | 54 | 0 | 0 | 67 | 30 | 18 | 12 | 12 | 0.01 | 80 | 109 | 8 | 150 | 155 | 0 | 50 | 25.5 | 98 | 217 | 0 | 0 | 0 | 1150 | 0 | 102 | 0 | 215 | 360 | 220 | 51 | 0 | 170 | 0 | 51 | 99 | 197 | 9 | 15 | 0 | 174 | 0 | 1 | 30 | 315 | 0 | 0 | 30 | 30 | 153 | 0 | 13 | 0 | 53 | 30 | 90 | 0 | 98 | 17 | 9 | 67 | 0 | 0 | 0.63 | 12 | 7279.64 | 923 | 92 | 0 | 6.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.28 | 553 | 0 | 0 | 0 | 759 | 0 | 0 | 0 | 35 | 35 | 0 | 53 | 28 | 0 | 1.18 | 0 | 23 | 0 | 0.35 | 141 | 0 | 0 | 0 | 143 | 0 | 414 | 0 | 0.06 | 0 | 54 | 111 | 0 | 67 | 0 | 0 | 0 | 0.2 | 3 | 0.01 | 110 | 307 | 130 | 220 | 0 | 87 | 1200 | 35 | 5546.58 | 12826.22 | 82.23
19:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 54 | 20 | 149 | 140 | 260 | 49 | 17 | 72 | 0 | 225 | 0 | 0 | 0 | 17 | 332 | 0 | 0 | 0 | 142 | 17 | 14 | 0 | 500 | 0 | 16 | 59 | 0 | 0 | 67 | 36 | 18 | 12 | 12 | 0 | 80 | 108 | 5 | 150 | 140 | 0 | 50 | 25.5 | 101 | 220 | 0 | 0 | 0 | 1224 | 0 | 133 | 0 | 215 | 360 | 220 | 51 | 0 | 180 | 0 | 61 | 99 | 198 | 9 | 20 | 0 | 184 | 0 | 0 | 26 | 320 | 0 | 0 | 30 | 30 | 154 | 0 | 13 | 0 | 53 | 30 | 110 | 0 | 98 | 17 | 9 | 67 | 0 | 0 | 0 | 12 | 7537.5 | 923 | 92 | 0 | 15 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595 | 0 | 0 | 0 | 759 | 0 | 35 | 0 | 35 | 35 | 0 | 53 | 28 | 0 | 0 | 0 | 25 | 0 | 0 | 141 | 0 | 0 | 0 | 142 | 0 | 414 | 0 | 0 | 0 | 54 | 112 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 130 | 220 | 0 | 85 | 1240 | 35 | 5708 | 13245.5 | 82.21
19:30 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 35 | 149 | 125 | 260 | 49 | 35 | 72 | 0 | 180 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 142 | 17 | 14 | 0 | 450 | 0 | 16 | 59 | 0 | 0 | 67 | 39 | 18 | 12 | 12 | 0 | 80 | 105 | 8 | 150 | 140 | 0 | 50 | 25.5 | 95 | 220 | 0 | 0 | 0 | 1224 | 0 | 143 | 0 | 215 | 360 | 220 | 51 | 0 | 184 | 0 | 68 | 99 | 200 | 9 | 20 | 0 | 178 | 0 | 0 | 31 | 315 | 0 | 0 | 30 | 30 | 153 | 0 | 13 | 0 | 53 | 30 | 110 | 0 | 98 | 17 | 9 | 67 | 0 | 0 | 0 | 12 | 7440.5 | 923 | 92 | 0 | 20 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 593 | 0 | 0 | 0 | 756 | 0 | 35 | 0 | 35 | 44 | 0 | 53 | 28 | 0 | 0 | 0 | 25 | 0 | 0 | 141 | 0 | 0 | 0 | 142 | 0 | 414 | 0 | 0 | 0 | 54 | 112 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 130 | 220 | 0 | 88 | 1244 | 35 | 5737 | 13177.5
20:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 54 | 35 | 149 | 125 | 260 | 49 | 35 | 72 | 0 | 180 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 142 | 19 | 17 | 0 | 540 | 0 | 16 | 62 | 0 | 0 | 67 | 45 | 18 | 12 | 12 | 0 | 80 | 106 | 15 | 150 | 155 | 0 | 50 | 25.5 | 92 | 220 | 0 | 0 | 0 | 1224 | 0 | 142 | 0 | 215 | 360 | 220 | 51 | 0 | 185 | 0 | 65 | 99 | 198 | 9 | 20 | 0 | 180 | 0 | 0 | 31 | 310 | 0 | 0 | 30 | 30 | 154 | 0 | 13 | 0 | 53 | 30 | 111 | 0 | 98 | 17 | 9 | 68 | 0 | 0 | 0 | 12 | 7561.5 | 923 | 92 | 0 | 18 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 597 | 0 | 0 | 0 | 759 | 0 | 42 | 0 | 35 | 49 | 0 | 53 | 30 | 0 | 0 | 0 | 25 | 0 | 0 | 141 | 0 | 0 | 0 | 142 | 0 | 414 | 0 | 0 | 0 | 53 | 113 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 130 | 220 | 0 | 106 | 1244 | 35 | 5794 | 13355.5 | 82.19
21:00 | 0 | 70 | 31 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 20.5 | 35 | 149 | 125 | 245 | 49 | 35 | 35 | 0 | 225 | 0 | 0 | 0 | 17 | 333 | 0 | 0 | 0 | 142 | 18 | 22 | 0 | 540 | 0 | 16 | 63 | 0 | 0 | 67 | 45 | 18 | 12 | 12 | 0 | 80 | 108 | 16 | 150 | 150 | 0 | 50 | 25.5 | 95 | 221 | 0 | 0 | 0 | 1224 | 0 | 143 | 0 | 215 | 361 | 220 | 51 | 0 | 181 | 0 | 25 | 100 | 197 | 9 | 20 | 0 | 182 | 0 | 0 | 31 | 310 | 0 | 0 | 30 | 30 | 153 | 0 | 21 | 0 | 81 | 30 | 110 | 0 | 98 | 17 | 9 | 68 | 0 | 0 | 0 | 12 | 7560 | 923 | 86 | 0 | 8 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590 | 0 | 0 | 0 | 763 | 0 | 42 | 0 | 35 | 50 | 0 | 44 | 28 | 0 | 0 | 0 | 25 | 0 | 0 | 141 | 0 | 0 | 0 | 142 | 0 | 414 | 0 | 0 | 0 | 55 | 112 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 307 | 130 | 220 | 0 | 120 | 1244 | 35 | 5721 | 13281 | 82.17
22:00 | 0 | 70 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 18 | 35 | 149 | 90 | 228 | 49 | 0 | 35 | 0 | 180 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 108 | 18 | 22 | 0 | 430 | 0 | 16 | 63 | 0 | 0 | 67 | 45 | 18 | 12 | 12 | 0 | 80 | 107 | 16 | 150 | 95 | 0 | 50 | 25.5 | 92 | 223 | 0 | 0 | 0 | 1100 | 0 | 108 | 0 | 215 | 361 | 220 | 51 | 0 | 177 | 0 | 17 | 100 | 197 | 9 | 20 | 0 | 174 | 0 | 0 | 30 | 305 | 0 | 15 | 30 | 30 | 154 | 0 | 21 | 0 | 80 | 30 | 111 | 0 | 98 | 17 | 9 | 57 | 0 | 0 | 0 | 12 | 7007.5 | 922 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 596 | 0 | 0 | 0 | 762 | 0 | 42 | 0 | 35 | 50 | 0 | 44 | 24 | 0 | 0 | 0 | 25 | 0 | 0 | 141 | 0 | 0 | 0 | 142 | 0 | 414 | 0 | 0 | 0 | 53 | 112 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 271 | 130 | 220 | 0 | 156 | 1244 | 35 | 5647 | 12654.5 | 82.15
23:00 | 0 | 34 | 50 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 35 | 140 | 15 | 244 | 49 | 0 | 35 | 0 | 180 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 52 | 18 | 22 | 0 | 450 | 0 | 16 | 59 | 0 | 0 | 67 | 46 | 18 | 12 | 12 | 0 | 80 | 103 | 21 | 150 | 12 | 0 | 0 | 8 | 95 | 224 | 0 | 0 | 0 | 1096 | 0 | 56 | 0 | 215 | 361 | 220 | 51 | 0 | 180 | 0 | 17 | 102 | 155 | 0 | 20 | 0 | 182 | 0 | 0 | 30 | 310 | 0 | 75 | 0 | 30 | 151 | 0 | 23 | 0 | 80 | 30 | 110 | 0 | 99 | 17 | 9 | 58 | 0 | 0 | 0 | 12 | 6566 | 922 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 711 | 0 | 42 | 0 | 35 | 50 | 0 | 44 | 25 | 0 | 0 | 0 | 25 | 0 | 0 | 141 | 0 | 0 | 0 | 143 | 0 | 350 | 0 | 0 | 0 | 53 | 70 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 263 | 130 | 220 | 0 | 192 | 1244 | 35 | 5462 | 12028 | 82.13
Total KWH | 0 | 866880 | 547200 | 0 | 0 | 0 | 0 | 0 | 9925200 | 0 | 0 | 259560 | 294840 | 1819728 | 1268640 | 2985818 | 683885 | 275219 | 786240 | 0 | 4731800 | 0 | 0 | 0 | 267014 | 7348921 | 0 | 0 | 185460 | 1473600 | 411600 | 361080 | 0 | 11258636.36 | 0 | 200727 | 513600 | 0 | 96480 | 582208 | 365698 | 154359 | 146880 | 151680 | 24961 | 1905340 | 1307200 | 282720 | 3760000 | 1361600 | 0 | 587040 | 231550.2 | 1035418 | 5193654 | 0 | 0 | 0 | 25570907 | 88695 | 1098981 | 0 | 4852000 | 8997100 | 5972000 | 1259576 | 0 | 4402000 | 0 | 558720 | 2429856 | 1473120 | 98280 | 419450 | 0 | 3912000 | 0 | 444109 | 347648 | 7411000 | 0 | 6787000 | 661000 | 712200 | 3701536.36 | 81377 | 415536 | 0 | 1392000 | 722304 | 2400700 | 0 | 2377140 | 206280 | 248400 | 1473600 | 107520 | 15100 | 352910 | 132240 | 154774721.92 | 22216727 | 2910528 | 0 | 50880 | 118272 | 0 | 0 | 0 | 0 | 0 | 0 | 509040 | 14385450 | 0 | 0 | 0 | 17541818 | 0 | 190151 | 0 | 423840 | 513984 | 0 | 296336 | 167423 | 0 | 322616 | 722340 | 157090 | 0 | 387760 | 3730182 | 0 | 0 | 0 | 3832682 | 0 | 9895854 | 0 | 36720 | 0 | 1174254 | 1952546 | 238648 | 793756 | 0 | 0 | 0 | 52307.52 | 1411920 | 3363 | 1040448 | 6590000 | 3120000 | 5393070 | 0 | 945454 | 28683636.36 | 408000 | 130217095.88 | 284991817.8

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 08-04-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12430.4 | MW | 12:00 Hr. | Energy Generated |  |  | 284.9918 |  | MKWHr.
| Day Peak Demand |  |  | 12663.44 | MW | 12:00 Hr. | Energy Unserverd |  |  | 3.889 |  | MKWHr.
| Evening Peak Generation |  |  | 13355.5 | MW | 20:00 Hr. | Energy Demand |  |  | 288.8808 |  | MKWHr.
| Evening Peak Demand |  |  | 14098.5 | MW | 20:00 Hr. | Maximum Temperature |  |  | 31 |  | °C
| Minimum Generation of the Day |  |  | 9777 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 894.24 |  | MMCFD
| Maximum Generation of the Day |  |  | 13355.5 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 6.3746 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.0372 | 0 | 11.5286 | 0 | 0 | 0.18546 | 0 | 0 | 45.7513 | Gas | 123.4158 | Gas | 430986003.4324
| Chattogram Zone |  |  | 5.4764 | 29.3309 | 6.638 | 0 | 1.9053 | 0.11366 | 0 | 0.09648 | 43.5607 | Coal | 81.1097 | Coal | 545830493.4288
| Cumilla Zone |  |  | 28.332 | 0 | 3.5767 | 0 | 0 | 0.44411 | 3.912 | 0 | 36.2648 | HFO | 29.9166 | HFO | 520228297.21
| Mymensingh Zone |  |  | 0.10752 | 0 | 2.0605 | 0 | 0 | 0.36801 | 0 | 0 | 2.536 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.5804 | 0 | 0 | 0 | 0 | 0.081377 | 0 | 0 | 26.6618 | Hydro | 1.9053 | Hydro | 190534
| Khulna Zone |  |  | 2.9105 | 14.3855 | 0.16915 | 0 | 0 | 0.50904 | 22.2167 | 0 | 40.1909 | Solar | 4.8773 | Solar | 79013960.964
| Barishal Zone |  |  | 8.5131 | 36.2191 | 1.4484 | 0 | 0 | 0.003363 | 0 | 0 | 46.184 | Import | 43.6705 | Import | 239036041.37
| Rajshahi Zone |  |  | 17.4587 | 0 | 1.7488 | 0 | 0 | 1.4694 | 17.5418 | 0 | 38.2188 | Wind | 0.09648 | Wind | 1419220.8
| Rangpur Zone |  |  | 0 | 1.1743 | 2.7463 | 0 | 0 | 1.7029 | 0 | 0 | 5.6234
| Total |  |  | 123.4158 | 81.1097 | 29.9166 | 0 | 1.9053 | 4.8773 | 43.6705 | 0.09648 | 284.9918
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 430986003.4324 |  | Hydro | 190534
|  |  |  | Coal | 545830493.4288 |  | Solar | 79013960.964
|  |  |  | HFO | 520228297.21 |  | Import | 239036041.37
|  |  |  | HSD | 0 |  | Wind | 1419220.8
[5 empty] | Total: | 181,67,04,551 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.2167 | Peak Hr Flow | 923.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 41895218.18 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.5418 | Peak Hr Flow | 759.00 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1566 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.912 | Peak Hr Flow | 180.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2507 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 43.6705 | Peak Hr Flow | 1862.00 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 194 |  | 4989
|  |  |  | Chattogram |  | 120 |  | 1468
|  |  |  | Cumilla |  | 80 |  | 1376
|  |  |  | Mymensingh |  | 120 |  | 1117
|  |  |  | Sylhet |  | 72 |  | 498
|  |  |  | Khulna |  | 35 |  | 1493
|  |  |  | Barishal |  | 18 |  | 414
|  |  |  | Rajshahi |  | 34 |  | 1369
|  |  |  | Rangpur |  | 38 |  | 872
|  |  |  | Total |  | 711 |  | 13596
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 320
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:18 | 17:05 | Gollamari 132/33kV S/S E01 Gollamari-Gopalgonj Line - 1 Project Work S/D Due to Conductor
Stringing SRTL line
| 08:19 | 17:05 | Gollamari 132/33kV S/S E07 Gollamari-Gopalgonj Line - 2 Project Work S/D Due to Conductor
Stringing SRTL line
| 08:19 | 17:05 | Gopalganj 132/33kV S/S Gallamari-1 Scheduled S/D Due to ALDC
| 08:19 | 17:06 | Gopalganj 132/33kV S/S Gallamari-2 Scheduled S/D Due to ALDC
| 08:23 | 10:58 | Khulna (C) S/S TR-1 425T LT Scheduled S/D Due to Hot spot maintenance
| 08:24 | 10:57 | Khulna (C) S/S TR-1 425T HT Scheduled S/D Due to Hot spot maintenance
| 08:38 | 17:08 | Mirpur 132/33kV S/S Main Bus Scheduled S/D Due to Gantry Structure Painting works.
| 09:06 | 11:02 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to PBS Bus DS Redhot maintenance | [7 empty] | 18.0MW load
interrup.
| 09:07 | 11:01 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to PBS Bus DS Redhot maintenance | [7 empty] | 18.0MW load
interrup.
| 09:17 |  | Sylhet 132/33kV S/S Sylhet-90MW P/S Scheduled S/D Due to Project work Purpose.
| 09:29 | 16:45 | Barapukuria 230/132/33kV S/S 230/132 KV T-02, 713T LT Scheduled S/D Due to Oil leakage
maintenance work
| 09:30 | 16:43 | Barapukuria 230/132/33kV S/S 230/132 KV T-02, 713T HT Scheduled S/D Due to Oil leakage
maintenance work
| 09:58 | 14:16 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 LT Scheduled S/D Due to Tan-delta test
| 09:58 | 16:05 | Kabirpur -Tongi 132kV Ckt-2 Project Work S/D from Tongi 230/132/33kV end Due to Project
shutdown
| 10:00 | 14:15 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 HT Scheduled S/D Due to Tan-delta rest
| 10:14 | 17:16 | Amtali 400/132kV S/S BUS-1 Project Work S/D
| 10:46 | 12:20 | Rajbari 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Red hot maintenance
| 10:46 | 12:21 | Rajbari 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Red hot maintenance
| 11:21 | 16:33 | Kachua 230/132/33kV S/S ATR-1 LT Scheduled S/D Due to DC Mixup
| 11:21 | 16:32 | Kachua 230/132/33kV S/S ATR-1 HT Scheduled S/D Due to DC mixup
| 11:26 | 20:14 | Cumilla(N)-Kachua 132 kV Ckt-2 Project Work S/D from Kachua 230/132/33kV end Due to DFDR
test
|  | 11:34 | Keranigonj 230/132/33kV S/S 132 kV Hasnabad Ckt. 1 is restored.
| 12:10 | 13:37 | Dohazari 132/33kV S/S Power Transformer -T-1 LT Scheduled S/D Due to 33KV Bus Isolator | [7 empty] | 5.0MW load
|  |  | Maintenance | [7 empty] | interrup.
| 12:11 | 13:36 | Dohazari 132/33kV S/S Power Transformer -T-1 HT Scheduled S/D Due to 33KV Bus Isolator | [7 empty] | 5.0MW load
|  |  | Maintenance | [7 empty] | interrup.
| 12:26 | 19:51 | Kachua 230/132/33kV S/S Main Bus-2 (132 kV) Project Work S/D Due to DFDR test
| 12:42 | 14:31 | Rajbari 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Rajbari PBS red hot
maintenance.
| 12:42 | 14:31 | Rajbari 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Rajbari PBS red hot
maintenance.
| 14:38 | 16:47 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 HT Scheduled S/D Due to Tan delta test
| 14:49 | 17:16 | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to 33kv Nobogram feeder work | [7 empty] | 29.0MW load
interrup.
| 15:49 | 17:15 | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Nobogram feeder work | [7 empty] | 29.0MW load
interrup.
| 17:23 |  | Bibiyana-III 400 MW CCPP Tripped with remarks:- GT
| 17:40 | 17:54 | Barishal(N)-Madaripur 132 kV Ckt-1 Tripped from Barishal 230/132kV end showing REL650
relays Due to Overcurrent
| 21:36 | 22:30 | Pabna- Shahjadpur 132kV Ckt-1 Tripped from Pabna 132/33kV end showing Distence
Reiay Zone-1 31.7KM relays.
| 21:39 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- GT
| 22:44 |  | Aminbazar-Airport(Old) 230kV Ckt-2 Scheduled S/D from Agargaon 230/132kV end Due to Shut
down due to Titas gas Line Leakage Rectification.
| 22:58 | 23:17 | Khulna (C) S/S Tr-3 405T HT Tripped showing Earth fault ( Inst.) relays Due to 33 kv | [7 empty] | 12.0MW load
|  |  | khalispur feeder fault | [7 empty] | interrup.
| 03:43 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- STG
| 05:27 |  | Cumilla(N) 230/132/33kV S/S 132KV T-03 LT Scheduled S/D Due to Winding & oil temperature
meter maintenance
| 05:28 |  | Cumilla(N) 230/132/33kV S/S 132KV T-03 HT Scheduled S/D Due to Winding & oil temperature
meter maintenance
| 06:00 |  | Minimum Generation: 9890 MW.
| 07:37 |  | Khulna (C) S/S TR-1 425T LT Scheduled S/D Due to Wzpdcl work
| 07:37 |  | Khulna (C) S/S TR-1 425T HT Scheduled S/D Due to Wzpdcl
| 07:45 |  | Khulna (C) S/S Tr-3 405T LT Tripped showing No relay relays Due to Unknown
| 07:45 |  | Khulna (C) S/S Tr-3 405T HT Tripped showing 26W4, 86T relays Due to Winding temperature
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 08-04-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 414 | 9925200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 180 | 4731800 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 49 | 683885 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7348921 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 259560 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 125 | 1268640 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 275219 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 267014 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 411600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 17 | 361080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 547200 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 260 | 2985818 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1819728 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 866880 | Engine Problem
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 786240 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 185460 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 294840 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 540 | 11258636.36 | FGMO
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1473600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2502 | 45751321.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 231550.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 88695 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 587040 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1905340 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5193654 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 92 | 1035418 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 45 | 365698 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 67 | 582208 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 146880 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 15 | 282720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 62 | 513600 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24961 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 200727 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 18 | 154359 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 106 | 1307200 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 151680 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Liquid fuel shortage
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 155 | 1361600 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 25570907 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 96480 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 150 | 3760000 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 2349.5 | 43560717.2
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 185 | 4402000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 360 | 8997100 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 220 | 5972000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 215 | 4852000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1259576 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 142 | 1098981 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 31 | 347648 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 99 | 2429856 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 198 | 1473120 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 180 | 3912000 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 419450 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 98280 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 65 | 558720 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 444109 | -
Cumilla Area Total |  |  |  |  | 2870.745 | 1775 | 36264840
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 107520 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 68 | 1473600 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 248400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 352910 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 132240 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 206280 | plant availability zero
Mymensingh Area Total |  |  |  |  | 654.21 | 106 | 2536050
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 81377 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 661000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 712200 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3701536.36 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 111 | 2400700 | Plant availability less
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 722304 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 53 | 1392000 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 98 | 2377140 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 13 | 415536 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7411000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 6787000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 829 | 26661793.36
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 923 | 22216727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 18 | 50880 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 65 | 118272 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 92 | 2910528 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 509040 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 597 | 14385450 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1695 | 40190897
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 106 | 945454 | Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 1040448 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3120000 | STG Under Maintenance
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 28683636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5393070 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 408000 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6590000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3363 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2152 | 46183971.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 322616 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 42 | 190151 | Partial Shutdown due to maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 167423 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 141 | 3730182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 142 | 3832682 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9895854 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 157090 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 53 | 296336 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 49 | 513984 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 423840 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 36720 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 759 | 17541818 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 387760 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 722340 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1690 | 38218796
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 53 | 1174254 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 91 | 793756 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 52307.52 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 113 | 1952546 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 238648 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1411920 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 257 | 5623431.52
Eastern Grid Total |  |  |  |  | 17417.792 | 7561.5 | 154774721.92
Western Grid Total |  |  |  |  | 11852.195 | 5794 | 130217095.88
National Grid Total |  |  |  |  | 29269.987 | 13355.5 | 284991817.8
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 08-04-2026
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8862.68 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4023.1 | MW
i) Dhaka area |  |  | 4795.38 |  | MW | i) Khulna area |  |  |  | 1458.3 | MW
ii) Chattogram area |  |  | 1348.3 |  | MW | ii) Barishal area |  |  |  | 396.5 | MW
iii) Cumilla area |  |  | 1296 |  | MW | iii) Rajshahi area |  |  |  | 1334.8 | MW
iv) Mymensingh area |  |  | 997 |  | MW | iv) Rangpur area |  |  |  | 833.5 | MW
v) Sylhet area |  |  | 426 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12885.78 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 9 | 19:00 | 67 | Hasnabad | 84 | 23:00 | 133 | Natore | 144 | 19:30
2 | AKSML | 9.7 | 10:00 | 68 | Hathazari | 77 | 21:00 | 134 | Nawabganj | 49.8 | 20:00
3 | Aftabnagar | 36 | 20:00 | 69 | Hatirjheel | 42 | 15:00 | 135 | Netrakona | 125 | 19:00
4 | Agargaon | 104 | 13:00 | 70 | Ishurdi | 62 | 13:00 | 136 | New | 74 | 15:00
5 | Agrabad | 68 | 14:00 | 71 | Jaldhaka | 68 | 08:00 | 137 | Niamatpur | 96 | 17:00
6 | Amnura | 32 | 12:00 | 72 | Jamalpur | 104 | 06:00 | 138 | Noapara | 37 | 20:00
7 | Ashuganj | 83 | 19:00 | 73 | Jashore | 140 | 20:00 | 139 | PHP | 10 | 12:00
8 | BSRM | 201 | 18:30 | 74 | Jhenaidah | 96 | 20:00 | 140 | Pabna | 83 | 19:30
9 | Bagerhat | 80 | 21:00 | 75 | Joydebpur | 140 | 16:00 | 141 | Palashbari | 112 | 19:30
10 | Bajitpur | 82 | 18:30 | 76 | Joypurhat | 66 | 21:00 | 142 | Panchagarh | 42 | 18:00
11 | Bakerganj | 9.5 | 20:00 | 77 | Juldah | 16 | 13:00 | 143 | Patiya | 10 | 21:00
12 | Bakulia | 88 | 19:30 | 78 | KSRM | 34 | 03:00 | 144 | Patuakhali | 58 | 22:00
13 | Banani | 38 | 13:00 | 79 | Kabirpur | 259 | 21:00 | 145 | Payra | 28 | 21:00
14 | Bangabhaban | 16 | 10:00 | 80 | Kachua | 89 | 22:00 | 146 | Postogola | 48 | 19:00
15 | Barapukuria | 62 | 21:00 | 81 | Kaliganj | 25 | 20:00 | 147 | Pubail | 31 | 09:00
16 | Barguna | 20 | 20:00 | 82 | Kallyanpur | 99 | 21:00 | 148 | Purbachal | 28 | 13:00
17 | Barishal | 95 | 13:00 | 83 | Kalurghat | 41 | 15:00 | 149 | Purbasadipur | 123 | 08:00
18 | Barishal-230 | 94 | 18:30 | 84 | Kamrangirchar | 74 | 19:30 | 150 | Rahanpur | 27 | 23:00
19 | Baroaulia | 72 | 11:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 50 | 12:00
20 | Baroirhat | 58 | 21:00 | 86 | Kasba | 37 | 20:00 | 152 | Rajbari | 78 | 20:00
21 | Bashundhara | 148 | 19:00 | 87 | Kazla | 114 | 13:00 | 153 | Rajendrapur | 127 | 21:00
22 | BashundharaCement | 8 | 00:00 | 88 | Keranigonj | 77 | 14:00 | 154 | Rajshahi | 117 | 13:00
23 | Beanibazar | 64 | 22:00 | 89 | Khagrachori | 34 | 18:30 | 155 | Rajshahi-230 | 62 | 22:00
24 | Benapole | 58 | 19:30 | 90 | Khulna | 66 | 13:00 | 156 | Ramganj | 92 | 21:00
25 | Bhaluka | 146 | 19:00 | 91 | Khulshi | 182 | 19:00 | 157 | Rampur | 38 | 20:00
26 | Bhandaria | 48 | 21:00 | 92 | Kishoreganj | 120 | 18:30 | 158 | Rangamati | 18 | 18:30
27 | Bhangura | 36 | 20:00 | 93 | Kodda | 312 | 18:00 | 159 | Rangpur | 123 | 21:00
28 | Bheramara(GK) | 59 | 18:00 | 94 | Kulaura | 43 | 21:00 | 160 | Ruppur | 4 | 15:00
29 | Bhulta | 209 | 17:00 | 95 | Kurigram | 66 | 03:00 | 161 | SSM | 6 | 23:00
30 | Bog-Sherpur | 70 | 14:00 | 96 | Kushtia | 114 | 13:00 | 162 | Saidpur | 100 | 14:00
31 | Bogura | 162 | 19:30 | 97 | Laksam | 20 | 00:00 | 163 | Satkhira | 118 | 20:00
32 | Borhanuddin | 90 | 20:00 | 98 | Lakshmipur | 37 | 14:00 | 164 | Satmasjid | 94 | 13:00
33 | Brahmanbaria | 129 | 21:00 | 99 | Lalbag | 70 | 12:00 | 165 | Savar | 244 | 15:00
34 | Cantonment | 141 | 13:00 | 100 | Lalmonirhat | 48 | 18:00 | 166 | SevenRings | 22.7 | 19:30
35 | Chandina | 24 | 00:00 | 101 | MI_Cement | 16.7 | 04:00 | 167 | ShahCement | 43 | 07:00
36 | Chandpur | 78 | 21:00 | 102 | Madanganj | 38 | 13:00 | 168 | Shahjadpur | 74 | 19:00
37 | Chandraghona | 34 | 22:00 | 103 | Madaripur | 96 | 20:00 | 169 | Shahjibazar | 117 | 21:00
38 | Chapai | 61 | 07:00 | 104 | Madartek | 70 | 22:00 | 170 | Shahmirpur | 48 | 18:30
39 | Charsaidpur | 43 | 10:00 | 105 | Madunaghat | 50 | 21:00 | 171 | Shariatpur | 77 | 22:00
40 | Chauddagram | 69 | 22:00 | 106 | Magura | 60 | 21:00 | 172 | Sherpur | 110 | 18:00
41 | Chhatak | 31 | 21:00 | 107 | Mahasthangarh | 70 | 07:00 | 173 | Shikalbaha | 29 | 21:00
42 | Chowmuhani | 134 | 21:00 | 108 | Maijdee | 43 | 21:00 | 174 | Shitalakhya | 77.2 | 12:00
43 | Chuadanga | 100 | 19:00 | 109 | Manikganj | 117 | 22:00 | 175 | Sholosohor | 47 | 15:00
44 | Coxsbazar | 141 | 22:00 | 110 | Maniknagar | 64 | 13:00 | 176 | Shyampur | 172 | 12:00
45 | Cumilla(N) | 125 | 23:00 | 111 | Matarbari | 50 | 22:00 | 177 | Siddhirganj | 116 | 12:00
46 | Cumilla(S) | 184 | 19:00 | 112 | Matuail | 75 | 15:00 | 178 | Sirajganj | 102 | 20:00
47 | Daganbhuiyan | 29 | 23:00 | 113 | Metrorail_Motijheel | 27 | 11:00 | 179 | Sonargaon | 142 | 13:00
48 | Daudkandi | 140 | 21:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreemongol | 72 | 22:00
49 | DhakaUniversity | 68 | 13:00 | 115 | Millgate | 94 | 12:00 | 181 | Sreepur | 109 | 20:00
50 | Dhamrai | 108 | 21:00 | 116 | Mirpur | 128 | 18:30 | 182 | Srinagar | 44.8 | 20:00
51 | Dhanmondi | 111 | 13:00 | 117 | Mirsorai | 46 | 03:00 | 183 | Sunamganj | 50 | 22:00
52 | Dohazari | 103 | 21:00 | 118 | Mirzapur | 37 | 17:00 | 184 | Sylhet | 49 | 19:00
53 | Faridpur | 153 | 21:00 | 119 | Mithapukur | 56 | 18:30 | 185 | Sylhet-132 | 100 | 18:30
54 | Fatullah | 90 | 16:00 | 120 | Modern | N/A | N/A | 186 | TK | 24 | 22:00
55 | Fenchuganj | 35 | 22:00 | 121 | Mogbazar | 75 | 15:00 | 187 | Tangail | 142 | 19:00
56 | Feni | 92 | 22:00 | 122 | Mongla | 42 | 15:00 | 188 | Taraganj | 23 | 16:00
57 | GPH | 1 | 01:00 | 123 | Motijheel | 43 | 13:00 | 189 | Tasnim | 21 | 19:00
58 | Ghatail | 60 | 08:00 | 124 | Muktagacha | 31 | 07:00 | 190 | Thakurgaon | 95 | 19:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 103 | 22:00 | 191 | Tongi | 127 | 10:00
60 | Ghorashal-230 | 109 | 22:00 | 126 | Muradnagar | 47 | 20:00 | 192 | Ullahpara | 34 | 20:00
61 | Goalpara | 36 | 18:30 | 127 | Mymensingh | 186 | 18:30 | 193 | Ullon | 49 | 18:30
62 | Gollamari | 92 | 20:00 | 128 | Nabinagar | 13 | 21:00 | 194 | Uttara | 75 | 18:30
63 | Gopalganj | 95 | 21:00 | 129 | Naogaon | 135 | 19:30 | 195 | UttaraNew | 29 | 22:00
64 | Gulshan | 110 | 13:00 | 130 | Narail | 51.5 | 21:00 | 196 | Zigatola | 76 | 14:00
65 | Halishahar | 97 | 12:00 | 131 | Narinda | 66 | 13:00
66 | HaripurSBU | 140 | 16:00 | 132 | Narshingdi | 179 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 08-04-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 10111.32 | 39 |  | 10152.08
1:00 | 10324 | 34 |  | 10360
2:00 | 10413 | 31 |  | 10445
3:00 | 10153 | 21 |  | 10175
4:00 | 9985 | 0 |  | 9985
5:00 | 9777 | 0 |  | 9777
6:00 | 9870.13 | 21 |  | 9892.13
7:00 | 10621.18 | 70 |  | 10694.18
8:00 | 10985.96 | 55 |  | 11043.44
9:00 | 11380.18 | 0 |  | 11380.18
10:00 | 11547.95 | 167 |  | 11722.95
11:00 | 11895.01 | 202 |  | 12106.1
12:00 | 12430.4 | 223 |  | 12663.44
13:00 | 12942.83 | 212 |  | 13164.37
14:00 | 13046.57 | 104 |  | 13155.57
15:00 | 13051.52 | 414 |  | 13484.52
16:00 | 13063.37 | 421 |  | 13503.37
17:00 | 12973.04 | 106 |  | 13084.04
18:00 | 12826.22 | 140 |  | 12972.22
19:00 | 13245.5 | 702 |  | 13979.5
19:30 | 13177.5 | 786 |  | 13998.5
20:00 | 13355.5 | 711 |  | 14098.5
21:00 | 13281 | 124 |  | 13411
22:00 | 12654.5 | 92 |  | 12750.5
23:00 | 12028 | 0 |  | 12028
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 08-04-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5720 | 4391.32 | 10111.32 | DAILY GENERATION CURVE
00:30 | 5660 | 4557.66 | 10217.66
01:00 | 5600 | 4724 | 10324 | 08-04-2026
01:30 | 5546 | 4822.5 | 10368.5
02:00 | 5492 | 4921 | 10413
02:30 | 5411 | 4872 | 10283
03:00 | 5330 | 4823 | 10153
03:30 | 5283.5 | 4785.5 | 10069
04:00 | 5237 | 4748 | 9985
04:30 | 5229.5 | 4651.5 | 9881
05:00 | 5222 | 4555 | 9777
05:30 | 5246.31 | 4577.255 | 9823.565
06:00 | 5270.62 | 4599.51 | 9870.13
06:30 | 5372.145 | 4873.51 | 10245.655
07:00 | 5473.67 | 5147.51 | 10621.18
07:30 | 5581.295 | 5222.275 | 10803.57
08:00 | 5688.92 | 5297.04 | 10985.96
08:30 | 5809.485 | 5373.585 | 11183.07
09:00 | 5930.05 | 5450.13 | 11380.18
09:30 | 5984.32 | 5479.745 | 11464.065
10:00 | 6038.59 | 5509.36 | 11547.95
10:30 | 6120.17 | 5601.31 | 11721.48
11:00 | 6201.75 | 5693.26 | 11895.01
11:30 | 6420.565 | 5742.14 | 12162.705
12:00 | 6639.38 | 5791.02 | 12430.4
12:30 | 6874.07 | 5812.545 | 12686.615
13:00 | 7108.76 | 5834.07 | 12942.83
13:30 | 7160.09 | 5834.61 | 12994.7
14:00 | 7211.42 | 5835.15 | 13046.57
14:30 | 7256.745 | 5792.3 | 13049.045
15:00 | 7302.07 | 5749.45 | 13051.52
15:30 | 7365.145 | 5692.3 | 13057.445
16:00 | 7428.22 | 5635.15 | 13063.37
16:30 | 7411.34 | 5606.865 | 13018.205
17:00 | 7394.46 | 5578.58 | 12973.04
17:30 | 7337.05 | 5562.58 | 12899.63
18:00 | 7279.64 | 5546.58 | 12826.22
18:30 | 7408.57 | 5627.29 | 13035.86
19:00 | 7537.5 | 5708 | 13245.5
19:30 | 7440.5 | 5737 | 13177.5
20:00 | 7561.5 | 5794 | 13355.5
20:30 | 7560.75 | 5757.5 | 13318.25 |  | Executive Engineer
21:00 | 7560 | 5721 | 13281 |  | Network Operation Division
21:30 | 7283.75 | 5684 | 12967.75
22:00 | 7007.5 | 5647 | 12654.5
22:30 | 6786.75 | 5554.5 | 12341.25
23:00 | 6566 | 5462 | 12028

## En-Curve
QF-LDC-12
Date | 08-04-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3614 | 1567 | 922 | 0 | 162 | 476.32 | 80 | 3127 | 0 | 17 | 107 | 0 | 0 | 39 | 39 | DAILY ENERGY CURVE
00:30 | 3618 | 1559 | 922 | 0 | 159 | 519.66 | 95 | 3210 | 0 | 8.5 | 100 | 0 | 0 | 26.5 | 36.5 | 08-04-2026
01:00 | 3622 | 1551 | 922 | 0 | 156 | 563 | 110 | 3293 | 0 | 0 | 93 | 0 | 0 | 14 | 34
01:30 | 3666 | 1546 | 922 | 0 | 155 | 642.5 | 110 | 3222 | 0 | 0 | 85 | 0 | 0 | 20 | 32.5 | Energy Generated | 284.9918 |  | MKWHr
02:00 | 3710 | 1541 | 922 | 0 | 154 | 722 | 110 | 3151 | 0 | 0 | 77 | 0 | 0 | 26 | 31 | Energy not Served | 3.889 |  | MKWHr
02:30 | 3718.5 | 1540.5 | 922 | 0 | 149 | 721.5 | 110 | 3035.5 | 0 | 0 | 71 | 0 | 0 | 15 | 26 | Total Energy Requirement | 288.8808 |  | MKWHr
03:00 | 3727 | 1540 | 922 | 0 | 144 | 721 | 110 | 2920 | 0 | 0 | 65 | 0 | 0 | 4 | 21
03:30 | 3750 | 1518 | 922 | 0 | 145 | 718.5 | 110 | 2838.5 | 0 | 0 | 64.5 | 0 | 0 | 2.5 | 10.5
04:00 | 3773 | 1496 | 922 | 0 | 146 | 716 | 110 | 2757 | 0 | 0 | 64 | 0 | 0 | 1 | 0
04:30 | 3789 | 1502 | 922.5 | 0 | 147 | 718.5 | 110 | 2626 | 0 | 0 | 65.5 | 0 | 0 | 0.5 | 0
05:00 | 3805 | 1508 | 923 | 0 | 148 | 721 | 110 | 2495 | 0 | 0 | 67 | 0 | 0 | 0 | 0
05:30 | 3796.5 | 1528.5 | 922.5 | 0 | 144 | 721.5 | 110 | 2525.5 | 3.565 | 4 | 67 | 0 | 0 | 0.5 | 10.5
06:00 | 3788 | 1549 | 922 | 0 | 140 | 722 | 110 | 2556 | 7.13 | 8 | 67 | 0 | 0 | 1 | 21
06:30 | 3765 | 1553 | 922.5 | 0 | 134 | 743 | 95 | 2831.5 | 70.155 | 11.5 | 118.5 | 0 | 0 | 1.5 | 45.5
07:00 | 3742 | 1557 | 923 | 0 | 128 | 764 | 80 | 3107 | 133.18 | 15 | 170 | 0 | 0 | 2 | 70
07:30 | 3700.5 | 1510 | 922.5 | 0 | 136 | 761.5 | 80 | 3276.5 | 211.57 | 20 | 184 | 0 | 0 | 1 | 62.5
08:00 | 3659 | 1463 | 922 | 0 | 144 | 759 | 80 | 3446 | 289.96 | 25 | 198 | 0 | 0 | 0 | 55
08:30 | 3707 | 1505 | 922 | 0 | 147 | 758 | 80 | 3456.5 | 360.07 | 46 | 201.5 | 0 | 0 | 0 | 27.5
09:00 | 3755 | 1547 | 922 | 0 | 150 | 757 | 80 | 3467 | 430.18 | 67 | 205 | 0 | 0 | 0 | 0
09:30 | 3724 | 1547.5 | 922 | 0 | 155 | 759.5 | 80 | 3467 | 472.065 | 74.5 | 262.5 | 0 | 0 | 0 | 83.5
10:00 | 3693 | 1548 | 922 | 0 | 160 | 762 | 80 | 3467 | 513.95 | 82 | 320 | 0 | 0 | 0 | 167
10:30 | 3685 | 1543 | 922 | 0 | 161 | 762.5 | 80 | 3474 | 573.48 | 88 | 432.5 | 0 | 0 | 0 | 184.5
11:00 | 3677 | 1538 | 922 | 0 | 162 | 763 | 80 | 3481 | 633.01 | 94 | 545 | 0 | 0 | 0 | 202
11:30 | 3668.5 | 1523.25 | 922.5 | 0 | 168 | 764 | 80 | 3494.5 | 632.455 | 147.5 | 761 | 0 | 0 | 1 | 212.5
12:00 | 3660 | 1508.5 | 923 | 0 | 174 | 765 | 80 | 3508 | 631.9 | 201 | 977 | 0 | 0 | 2 | 223
12:30 | 3642.5 | 1492 | 923 | 0 | 174 | 765 | 80 | 3508 | 649.365 | 267.5 | 1181.25 | 0 | 0 | 4 | 217.5
13:00 | 3625 | 1475.5 | 923 | 0 | 174 | 765 | 80 | 3508 | 666.83 | 334 | 1385.5 | 0 | 0 | 6 | 212
13:30 | 3600 | 1498 | 923 | 0 | 176 | 764 | 80 | 3499.5 | 631.45 | 354 | 1459.25 | 0 | 0 | 9.5 | 158
14:00 | 3575 | 1520.5 | 923 | 0 | 178 | 763 | 80 | 3491 | 596.07 | 374 | 1533 | 0 | 0 | 13 | 104
14:30 | 3532.5 | 1528.25 | 923 | 0 | 179 | 762 | 80 | 3487 | 541.795 | 406 | 1602 | 0 | 0 | 7.5 | 259
15:00 | 3490 | 1536 | 923 | 0 | 180 | 761 | 80 | 3483 | 487.52 | 438 | 1671 | 0 | 0 | 2 | 414
15:30 | 3497.5 | 1540 | 922.5 | 0 | 181 | 759 | 80 | 3516 | 404.945 | 471.5 | 1684 | 0 | 0 | 1 | 417.5
16:00 | 3505 | 1544 | 922 | 0 | 182 | 757 | 80 | 3549 | 322.37 | 505 | 1697 | 0 | 0 | 0 | 421
16:30 | 3527.5 | 1533 | 922.5 | 0 | 181 | 759 | 80 | 3525.5 | 227.705 | 533 | 1729 | 0 | 0 | 0 | 263.5
17:00 | 3550 | 1522 | 923 | 0 | 180 | 761 | 80 | 3502 | 133.04 | 561 | 1761 | 0 | 0 | 0 | 106
17:30 | 3384.5 | 1523 | 923 | 0 | 177 | 760 | 80 | 3501.5 | 70.38 | 596.75 | 1883.5 | 0 | 0 | 0 | 123
18:00 | 3219 | 1524 | 923 | 0 | 174 | 759 | 80 | 3501 | 7.72 | 632.5 | 2006 | 0 | 0 | 0 | 140
18:30 | 3237.5 | 1558 | 923 | 0 | 179 | 759 | 80 | 3578 | 3.86 | 671.75 | 2045.75 | 0 | 0 | 0 | 421
19:00 | 3256 | 1592 | 923 | 0 | 184 | 759 | 80 | 3655 | 0 | 711 | 2085.5 | 0 | 0 | 0 | 702
19:30 | 3227 | 1494 | 923 | 0 | 178 | 756 | 80 | 3660 | 0 | 704 | 2155.5 | 0 | 0 | 0 | 786
20:00 | 3231 | 1592 | 923 | 0 | 180 | 759 | 80 | 3681 | 0 | 737 | 2172.5 | 0 | 0 | 0 | 711
20:30 | 3242.5 | 1634.5 | 923 | 0 | 181 | 761 | 80 | 3685.5 | 0 | 707 | 2103.75 | 0 | 0 | 0 | 417.5
21:00 | 3254 | 1677 | 923 | 0 | 182 | 763 | 80 | 3690 | 0 | 677 | 2035 | 0 | 0 | 0 | 124
21:30 | 3243 | 1597 | 922.5 | 0 | 178 | 762.5 | 80 | 3630 | 0 | 636 | 1918.75 | 0 | 0 | 0 | 108
22:00 | 3232 | 1517 | 922 | 0 | 174 | 762 | 80 | 3570 | 0 | 595 | 1802.5 | 0 | 0 | 0 | 92
22:30 | 3179.5 | 1531.5 | 922 | 0 | 178 | 736.5 | 80 | 3574 | 0 | 512.5 | 1627.25 | 0 | 0 | 0 | 46
23:00 | 3127 | 1546 | 922 | 0 | 182 | 711 | 80 | 3578 | 0 | 430 | 1452 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 08-04-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 398 | 04:00 | 388 | 11:00 | Madunaghat | 412 | 05:00 | 403 | 10:00
Amtali | 417 | 05:00 | 411 | 09:00 | Meghnaghat | 401 | 05:00 | 389 | 10:00
Ashuganj | 418 | 24:00 | 402 | 9:00 | Payra | 418 | 05:00 | 411 | 12:00
Bhulta | 406 | 04:00 | 393 | 09:00 | Rahanpur | 421 | 05:00 | 411 | 08:00
Bibiana | 410 | 05:00 | 400 | 18:00 | Rampal | 409 | 05:00 | 397 | 17:00
BIPTC | 402 | 03:00 | 392 | 15:00
Bogura | 416 | 22:00 | 404 | 08:00
Gopalganj | 409 | 05:00 | 398 | 12:00
Kaliakoir | 395 | 23:00 | 371 | 11:00
Korerhat | 412 | 05:00 | 402 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 237 | 05:00 | 228 | 09:00 | Jhenaidah | 235 | 22:00 | 219 | 13:00
AKSML | 239.1 | 18:30 | 229.5 | 09:00 | Kachua | 237 | 19:00 | 228 | 10:00
Aminbazar | 237 | 23:00 | 227 | 11:00 | Kaliakoir | 241 | 23:00 | 227 | 11:00
Ashuganj | 235 | 06:00 | 227 | 09:00 | Keranigonj | 235 | 00:00 | 227 | 09:00
Ashuganj-400 | 235 | 06:00 | 227 | 09:00 | Khulna(S) | 237 | 22:00 | 222 | 14:00
Baghabari | 238 | 22:00 | 230 | 17:00 | Korerhat | 235 | 19:30 | 229 | 09:00
Barapukuria | 229 | 22:00 | 217 | 00:00 | Madunaghat | 238 | 18:00 | 230 | 10:00
Barapukuria-230 | 229 | 22:00 | 217 | 00:00 | Madunaghat-400 | 237 | 20:00 | 231 | 10:00
Barishal | 232 | 05:00 | 227 | 09:00 | Maniknagar | 234 | 02:00 | 224 | 11:00
Bheramara | 234 | 22:00 | 223 | 12:00 | Meghnaghat | 244 | 00:00 | 234 | 09:00
Bhulta | 235 | 05:00 | 226 | 11:00 | Meghnaghat-400 | 236 | 04:00 | 229 | 10:00
Bibiana | 239 | 04:00 | 232 | 11:00 | Mirsorai | 234 | 18:00 | 226 | 09:00
BIPTC | 237 | 22:00 | 223 | 12:00 | Naogaon | 230 | 05:00 | 222 | 13:00
Bogura | 239 | 22:00 | 231 | 08:00 | Purbasadipur | 229 | 07:00 | 217 | 08:00
Bogura-400 | 239 | 22:00 | 231 | 08:00 | Rajshahi | 233 | 22:00 | 221 | 14:00
Borhanuddin | 235 | 03:00 | 232 | 08:00 | Rampal | 235 | 05:00 | 224 | 13:00
BSRM | 235 | 05:00 | 229 | 10:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 236 | 19:30 | 228 | 10:00 | Rampura | 234 | 04:00 | 225 | 11:00
Cumilla(N) | 233 | 05:00 | 227 | 11:00 | Shikalbaha | 237 | 18:00 | 230 | 09:00
Faridpur | 230 | 05:00 | 223 | 09:00 | Shyampur | 235 | 05:00 | 227 | 11:00
Fenchuganj | 241 | 00:00 | 235 | 18:00 | Siddhirganj | 235 | 03:00 | 228 | 11:00
Feni | 235 | 19:00 | 229 | 10:00 | Sirajgonj | 242 | 05:00 | 237 | 09:00
Ghorashal | 235 | 02:00 | 230 | 00:00 | Sreepur | 231 | 05:00 | 226 | 09:00
Ghorashal-230 | 232 | 5:00 | 223 | 11:00 | Tongi | 240 | 23:00 | 225 | 11:00
Gopalganj | 229 | 05:00 | 222 | 12:00
GPH | 234 | 06:00 | 229 | 15:00
Haripur | 235 | 05:00 | 227 | 12:00
Hasnabad | 233 | 00:00 | 227 | 09:00
Hathazari | 236 | 18:00 | 229 | 10:00
Ishurdi | 237 | 22:00 | 226 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 04:00 | 129 | 11:00 | Madunaghat | 138 | 18:00 | 133 | 09:00
Agargaon | 140 | 05:00 | 133 | 12:00 | Magura | 139 | 22:00 | 126 | 14:00
Agrabad | 136 | 18:00 | 130 | 11:00 | Mahasthangarh | 136 | 22:00 | 128 | 08:00
AKS | 134 | 17:00 | 129 | 10:00 | Maijdee | 132 | 19:00 | 127 | 12:00
Aminbazar | 137 | 23:00 | 131 | 09:00 | Manikganj | 137 | 23:00 | 126 | 11:00
Amnura | 138 | 04:00 | 129 | 12:00 | Maniknagar | 138 | 07:00 | 131 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 134 | 00:00 | 113 | 22:00
Ashuganj-230 | 140 | 00:00 | 137 | 10:00 | Matuail | 136 | 00:00 | 130 | 10:00
Bagerhat | 137 | 22:00 | 120 | 17:00 | Metrorail_Motijheel | 138 | 07:00 | 131 | 12:00
Bajitpur | 134 | 05:00 | 130 | 08:00 | Metrorail_Uttara | 138 | 04:00 | 130 | 09:00
Bakerganj | 136 | 05:00 | 132 | 11:00 | Millgate | 139 | 23:00 | 130 | 11:00
Bakulia | 138 | 18:30 | 131 | 10:00 | Mirpur | 135 | 02:00 | 129 | 09:00
Banani | 136 | 04:00 | 129 | 11:00 | Mirzapur | 135 | 23:00 | 123 | 11:00
Bangabhaban | 138 | 04:00 | 130 | 12:00 | Mithapukur | 135 | 22:00 | 125 | 08:00
Barapukuria | 136 | 22:00 | 127 | 08:00 | MI_Cement | 136 | 00:00 | 126.8 | 12:00
Barguna | 137 | 03:00 | 132 | 10:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 138 | 17:00 | 131 | 12:00 | Mogbazar | 137 | 00:00 | 130 | 11:00
Barishal-230 | 136 | 05:00 | 132 | 10:00 | Mongla | 136 | 22:00 | 121 | 13:00
Baroaulia | 136 | 04:00 | 132 | 09:00 | Motijheel | 138 | 04:00 | 130 | 12:00
Baroirhat | 134 | 04:00 | 131 | 10:00 | Muktagacha | 124 | 06:00 | 116 | 10:00
Bashundhara | 139 | 23:00 | 128 | 11:00 | Munshiganj | 136 | 02:00 | 129 | 09:00
BashundharaCement | 136 | 00:00 | 131 | 11:00 | Muradnagar | 133 | 00:00 | 127 | 11:00
Beanibazar | 132 | 05:00 | 123 | 13:00 | Mymensingh | 130 | 23:00 | 113 | 19:00
Benapole | 137 | 22:00 | 120 | 13:00 | Nabinagar | 140 | 23:00 | 129 | 10:00
Bhaluka | 136 | 18:00 | 130 | 09:00 | Naogaon | 139 | 22:00 | 127 | 08:00
Bhandaria | 138 | 23:00 | 130 | 10:00 | Narail | 142 | 22:00 | 125 | 14:00
Bhangura | 137 | 01:00 | 130 | 17:00 | Narinda | 138 | 07:00 | 131 | 12:00
Bheramara | 137 | 05:00 | 131 | 17:00 | Narshingdi | 133 | 05:00 | 126 | 09:00
Bheramara(GK) | 137 | 22:00 | 131 | 12:00 | Natore | 135 | 23:00 | 129 | 14:00
Bhulta | 130 | 00:00 | 125 | 15:00 | Nawabganj | 138 | 00:00 | 132 | 11:00
Bog-Sherpur | 138 | 22:00 | 131 | 08:00 | Netrakona | 130 | 18:00 | 121 | 18:30
Bogura | 138 | 22:00 | 132 | 07:00 | New | 140 | 23:00 | 132 | 09:00
Bogura-230 | 139 | 22:00 | 132 | 08:00 | Niamatpur | 139 | 22:00 | 133 | 08:00
Brahmanbaria | 134 | 07:00 | 126 | 12:00 | Noapara | 137 | 22:00 | 123 | 13:00
Cantonment | 139 | 04:00 | 133 | 11:00 | Pabna | 136 | 03:00 | 130 | 17:00
Chandina | 135 | 04:00 | 130 | 12:00 | Palashbari | 132 | 22:00 | 123 | 09:00
Chandpur | 138 | 18:30 | 129 | 09:00 | Panchagarh | 140 | 07:00 | 132 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 138 | 18:00 | 133 | 10:00 | Patiya | 136 | 04:00 | 131 | 09:00
Chapai | 139 | 01:00 | 135 | 07:00 | Patuakhali | 135 | 13:00 | 132 | 11:00
Charsaidpur | 136 | 00:00 | 129 | 10:00 | Payra | 137 | 03:00 | 134 | 09:00
Chauddagram | 132 | 03:00 | 129 | 09:00 | PHP | 133 | 05:00 | 130 | 09:00
Chhatak | 133 | 08:00 | 123 | 12:00 | Postogola | 136 | 05:00 | 129 | 11:00
Chowmuhani | 133 | 19:00 | 128 | 09:00 | Pubail | 138 | 19:00 | 130 | 09:00
Chuadanga | 140 | 05:00 | 125 | 17:00 | Purbachal | 138 | 04:00 | 129 | 12:00
Coxsbazar | 132 | 00:00 | 113 | 23:00 | Purbasadipur | 134 | 18:30 | 126 | 01:00
Cumilla(N) | 135 | 03:00 | 130 | 11:00 | Rahanpur | 141 | 03:00 | 137 | 08:00
Cumilla(S) | 135 | 05:00 | 119 | 16:00 | Rahanpur-400 | 141 | 04:00 | 137 | 08:00
Daganbhuiyan | 132 | 19:00 | 128 | 10:00 | Rahim | 137 | 00:00 | 130 | 10:00
Daudkandi | 133 | 00:00 | 125 | 10:00 | Rajbari | 133 | 23:00 | 127 | 15:00
DhakaUniversity | 136 | 00:00 | 130 | 11:00 | Rajendrapur | 135 | 03:00 | 130 | 11:00
Dhamrai | 141 | 23:00 | 129 | 09:00 | Rajshahi | 134 | 04:00 | 127 | 14:00
Dhanmondi | 137 | 00:00 | 131 | 10:00 | Rajshahi-230 | 135 | 23:00 | 128 | 12:00
Dohazari | 135 | 00:00 | 128 | 10:00 | Ramganj | 134 | 19:00 | 127 | 09:00
Faridpur | 133 | 05:00 | 129 | 16:00 | Rampur | 136 | 18:00 | 130 | 09:00
Fatullah | 136 | 05:00 | 128 | 10:00 | Rampura | 136 | 04:00 | 129 | 12:00
Fenchuganj | 136 | 00:00 | 133 | 18:00 | Rangamati | 138 | 04:00 | 132 | 11:00
Feni | 131 | 02:00 | 128 | 12:00 | Rangpur | 134 | 23:00 | 126 | 09:00
Feni-230 | 132 | 05:00 | 129 | 09:00 | Ruppur | 140 | 05:00 | 131 | 12:00
Ghatail | 125 | 07:00 | 117 | 10:00 | Saidpur | 134 | 22:00 | 125 | 08:00
Ghorashal | 139 | 19:00 | 133 | 09:00 | Satkhira | 137 | 22:00 | 121 | 13:00
Goalpara | 137 | 22:00 | 125 | 14:00 | Satmasjid | 139 | 03:00 | 133 | 11:00
Gollamari | 137 | 22:00 | 126 | 13:00 | Savar | 135 | 19:00 | 127 | 09:00
Gopalganj | 136 | 22:00 | 130 | 12:00 | SevenRings | 139 | 19:30 | 133 | 11:00
Gopalganj-400 | 136 | 05:00 | 132 | 09:00 | ShahCement | 137 | 13:00 | 129 | 10:00
Gulshan | 136 | 05:00 | 129 | 11:00 | Shahjadpur | 141 | 03:00 | 135 | 11:00
Halishahar | 137 | 18:30 | 131 | 09:00 | Shahjibazar | 135 | 05:00 | 128 | 21:00
Haripur | 137 | 05:00 | 131 | 09:00 | Shahmirpur | 138 | 17:00 | 131 | 09:00
HaripurSBU | 137 | 00:00 | 131 | 09:00 | Shariatpur | 135 | 04:00 | 130 | 12:00
Hasnabad | 136 | 07:00 | 129 | 11:00 | Sherpur | 120 | 07:00 | 108 | 19:30
Hathazari | 138 | 18:00 | 132 | 09:00 | Shikalbaha | 127 | 19:30 | 120 | 12:00
Hatirjheel | 136 | 04:00 | 125 | 12:00 | Shikalbaha-230 | 138 | 18:00 | 133 | 09:00
Ishurdi | 139 | 22:00 | 133 | 14:00 | Shitalakhya | 136 | 00:00 | 126.8 | 12:00
Jaldhaka | 133 | 22:00 | 122 | 08:00 | Sholosohor | 137 | 18:00 | 132 | 11:00
Jamalpur | 122 | 07:00 | 112 | 18:00 | Shyampur | 134 | 00:00 | 129 | 12:00
Jashore | 138 | 22:00 | 122 | 13:00 | Shyampur-230 | 135 | 00:00 | 131 | 09:00
Jhenaidah | 141 | 22:00 | 125 | 14:00 | Siddhirganj | 137 | 00:00 | 130 | 11:00
Jhenaidah-230 | 140 | 05:00 | 129 | 14:00 | Sirajganj | 136 | 22:00 | 128 | 18:00
Joydebpur | 136 | 18:30 | 126 | 09:00 | Sonargaon | 136 | 00:00 | 128 | 10:00
Joypurhat | 131 | 22:00 | 122 | 08:00 | Sreemongol | 134 | 00:00 | 129 | 22:00
Juldah | 137 | 18:00 | 131 | 09:00 | Sreepur | 137 | 05:00 | 133 | 11:00
Kabirpur | 138 | 15:00 | 123 | 11:00 | Srinagar | 139 | 23:00 | 131 | 11:00
Kachua | 135 | 18:30 | 129 | 12:00 | SSM | 140 | 01:00 | 134 | 00:00
Kaliakoir | 141 | 23:00 | 128 | 11:00 | Sunamganj | 132 | 08:00 | 122 | 12:00
Kaliganj | 140 | 22:00 | 127 | 14:00 | Sylhet | 133 | 05:00 | 126 | 13:00
Kallyanpur | 135 | 01:00 | 129 | 09:00 | Sylhet-132 | 133 | 06:00 | 127 | 12:00
Kalurghat | 138 | 18:30 | 133 | 10:00 | Tangail | 132 | 22:00 | 118 | 11:00
Kamrangirchar | 138 | 05:00 | 128 | 09:00 | Taraganj | 135 | 22:00 | 123 | 08:00
Kaptai | N/A | N/A | N/A | N/A | Tasnim | 136 | 00:00 | 128 | 10:00
Kasba | 133 | 00:00 | 127 | 12:00 | Thakurgaon | 140 | 18:30 | 127 | 00:00
Kazla | 138 | 00:00 | 130 | 13:00 | TK | 137 | 04:00 | 133 | 09:00
Keranigonj | 139 | 00:00 | 133 | 10:00 | Tongi | 140 | 00:00 | 133 | 11:00
Khagrachori | 136 | 18:00 | 131 | 10:00 | Ullahpara | 139 | 22:00 | 130 | 18:00
Khulna | 137 | 22:00 | 125 | 13:00 | Ullon | 135 | 00:00 | 129 | 10:00
Khulna(S) | 137 | 22:00 | 126 | 14:00 | Uttara | 140 | 23:00 | 131 | 09:00
Khulshi | 135 | 18:00 | 129 | 10:00 | UttaraNew | 138 | 04:00 | 130 | 09:00
Kishoreganj | 133 | 03:00 | 128 | 18:30 | Zigatola | 139 | 06:00 | 132 | 12:00
Kodda | 138 | 16:00 | 123 | 09:00
Korerhat | 136 | 05:00 | 133 | 09:00
KSRM | 137 | 18:30 | 131 | 09:00
Kulaura | 136 | 00:00 | 131 | 21:00
Kurigram | 134 | 22:00 | 121 | 08:00
Kushtia | 136 | 21:00 | 128 | 17:00
Laksam | 134 | 18:00 | 129 | 12:00
Lakshmipur | 131 | 18:00 | 127 | 10:00
Lalbag | 138 | 02:00 | 130 | 12:00
Lalmonirhat | 132 | 21:00 | 120 | 08:00
Madanganj | 136 | 00:00 | 131 | 11:00
Madaripur | 136 | 23:00 | 131 | 12:00
Madartek | 136 | 04:00 | 128 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division