## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 11-04-2026 | [28 empty] | Date: | 11-04-2026 | [28 empty] | Date: | 11-04-2026 | [28 empty] | Date: | 11-04-2026 | [28 empty] | Date: | 11-04-2026 | [17 empty] | Date: | 11-04-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 17 | 70 | 0 | 145 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 515 | 30 | 16 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 12 | 0 | 80 | 34 | 38 | 160 | 0 | 0 | 46 | 0 | 105 | 224 | 0 | 0 | 0 | 300 | 0 | 138 | 0 | 225 | 365 | 220 | 37 | 0 | 216 | 0 | 17 | 102 | 62 | 0 | 19 | 0 | 146 | 0 | 0 | 0 | 310 | 0 | 348 | 30 | 30 | 158 | 0 | 16 | 0 | 83 | 30 | 0 | 0 | 99 | 0 | 59 | 9 | 49 | 0 | 0 | 12 | 5641 | 879 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 611 | 0 | 0 | 0 | 763.95 | 0 | 0 | 0 | 0 | 66 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 220 | 0 | 414 | 0 | 0 | 0 | 55 | 68 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 404 | 1212 | 35 | 5963.95 | 11604.95 | 81.53
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 42 | 0 | 45 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 500 | 31 | 16 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 80 | 34 | 37 | 160 | 0 | 0 | 46 | 0 | 105 | 225 | 0 | 0 | 0 | 301 | 0 | 50 | 0 | 225 | 365 | 220 | 45 | 0 | 195 | 0 | 17 | 103 | 19 | 0 | 19 | 0 | 136 | 0 | 0 | 0 | 305 | 0 | 348 | 30 | 30 | 160 | 0 | 16 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 9 | 56 | 35 | 0 | 0 | 0 | 5254 | 879 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 602 | 0 | 0 | 0 | 762.25 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 214 | 0 | 414 | 0 | 0 | 0 | 53 | 70 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 404 | 1220 | 17 | 5909.25 | 11163.25 | 81.51
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 37 | 160 | 0 | 0 | 34 | 0 | 51 | 225 | 0 | 0 | 0 | 300 | 0 | 20 | 0 | 225 | 365 | 220 | 45 | 0 | 188 | 0 | 17 | 103 | 17 | 0 | 19 | 0 | 130 | 0 | 0 | 0 | 305 | 0 | 348 | 30 | 30 | 156 | 0 | 16 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 9 | 56 | 37 | 0 | 0 | 0 | 4915 | 879 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605 | 0 | 0 | 0 | 762.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 198 | 0 | 407 | 0 | 0 | 0 | 54 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 130 | 220 | 0 | 404 | 1224 | 0 | 5778.11 | 10693.11 | 81.49
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 37 | 160 | 0 | 0 | 6 | 0 | 0 | 225 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 225 | 365 | 220 | 51 | 0 | 194 | 0 | 0 | 103 | 0 | 0 | 19 | 0 | 130 | 0 | 0 | 0 | 305 | 0 | 348 | 30 | 30 | 156 | 0 | 16 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 9 | 8 | 50 | 0 | 0 | 0 | 4709 | 879 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523 | 0 | 0 | 0 | 763.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 198 | 0 | 395 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 130 | 220 | 0 | 402 | 1180 | 0 | 5568.7 | 10277.7 | 81.47
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 31 | 160 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 300 | 365 | 300 | 51 | 0 | 223 | 0 | 0 | 103 | 0 | 0 | 19 | 0 | 130 | 0 | 0 | 0 | 300 | 0 | 348 | 30 | 30 | 156 | 0 | 16 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 9 | 8 | 52 | 0 | 0 | 0 | 4880 | 879 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 0 | 732.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 198 | 0 | 395 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 130 | 220 | 0 | 285 | 1120 | 0 | 5215.34 | 10095.34 | 81.45
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 31 | 160 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 280 | 365 | 280 | 51 | 0 | 204 | 0 | 0 | 103 | 0 | 0 | 19 | 0 | 122 | 0 | 0 | 0 | 305 | 0 | 348 | 30 | 30 | 157 | 0 | 16 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 9 | 8 | 38 | 0 | 0 | 0 | 4779 | 879 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 628.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 203 | 0 | 414 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222 | 130 | 220 | 0 | 256 | 1000 | 0 | 4953.18 | 9732.18 | 81.44
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 21.5 | 22 | 0 | 485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 80 | 0 | 31 | 160 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 250 | 365 | 260 | 51 | 0 | 176 | 0 | 0 | 103 | 0 | 0 | 19 | 0 | 118 | 0 | 2 | 0 | 310 | 0 | 348 | 30 | 30 | 151 | 0 | 16 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 9 | 35 | 38 | 0 | 0.46 | 0 | 4737.05 | 880 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.57 | 468 | 0 | 0 | 0 | 730.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 209 | 0 | 414 | 0 | 0.05 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 272 | 130 | 220 | 0 | 293 | 1005 | 0 | 5215.49 | 9952.54 | 81.43
07:00 | 0 | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 0 | 32 | 30 | 0 | 4 | 0 | 28 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 4 | 35 | 21.5 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76 | 80 | 2 | 28 | 160 | 0 | 0 | 5 | 0 | 5 | 225 | 0 | 0 | 0 | 302 | 4 | 6 | 0 | 250 | 365 | 260 | 51 | 0 | 172 | 0 | 2 | 103 | 9 | 0 | 19 | 0 | 114 | 0 | 14 | 0 | 315 | 0 | 348 | 30 | 30 | 147 | 1 | 16 | 0 | 83 | 30 | 0 | 0 | 100 | 0 | 9 | 56 | 38 | 0.2 | 4.68 | 0 | 4909.14 | 879 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 600 | 0 | 0 | 0 | 756.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.09 | 17 | 0 | 0 | 9.42 | 195 | 0 | 0 | 0 | 212 | 0 | 398 | 0 | 0.53 | 0 | 53 | 30 | 5 | 16 | 0 | 0 | 0 | 1.2 | 25 | 0.11 | 0 | 272 | 130 | 220 | 0 | 402 | 1102 | 0 | 5710.81 | 10619.95 | 81.42
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 70 | 15 | 0 | 30 | 17 | 34 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 15 | 0 | 21 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.84 | 80 | 15 | 6 | 160 | 0 | 0 | 18 | 0 | 47 | 223 | 0 | 0 | 0 | 302 | 9 | 26 | 0 | 215 | 371 | 260 | 51 | 0 | 178 | 0 | 17 | 99 | 17 | 0 | 19 | 0 | 126 | 0 | 31 | 7 | 310 | 0 | 348 | 30 | 30 | 136 | 2 | 16 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 9 | 56 | 37 | 0.8 | 21.19 | 0 | 5070.83 | 879 | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 604 | 0 | 0 | 0 | 754.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.84 | 46 | 0 | 0 | 24 | 187 | 0 | 0 | 0 | 188 | 0 | 369 | 0 | 2.17 | 0 | 53 | 35 | 14 | 33 | 0 | 0 | 0 | 3.5 | 86 | 0.27 | 0 | 277 | 130 | 220 | 0 | 402 | 1180 | 0 | 5922.47 | 10993.3 | 81.41
09:00 | 0 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 0 | 70 | 15 | 15 | 35 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 22 | 35 | 26 | 22 | 0 | 500 | 3 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.77 | 80 | 18 | 4 | 160 | 0 | 0 | 21 | 0 | 51 | 221 | 0 | 0 | 0 | 303 | 14 | 26 | 0 | 215 | 371 | 260 | 51 | 0 | 192 | 0 | 17 | 99 | 17 | 0 | 12 | 0 | 132 | 0 | 51 | 7 | 310 | 0 | 348 | 30 | 30 | 134 | 9 | 16 | 0 | 80 | 30 | 0 | 0 | 100 | 0 | 9 | 56 | 37 | 1.52 | 35.01 | 0 | 5261.3 | 879 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 590 | 0 | 0 | 0 | 748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.96 | 76 | 0 | 0 | 41.21 | 181 | 0 | 0 | 0 | 179 | 0 | 379 | 0 | 3.57 | 0 | 53 | 55 | 23 | 34 | 0 | 0 | 0 | 5.2 | 139 | 0.46 | 0 | 279 | 130 | 220 | 0 | 400 | 1180 | 0 | 5953.4 | 11214.7 | 81.4
10:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 17 | 0 | 98 | 15 | 60 | 55 | 0 | 35 | 0 | 180 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 28 | 35 | 22 | 15 | 0 | 400 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3.44 | 80 | 90 | 4 | 160 | 0 | 0 | 42 | 0 | 51 | 184 | 0 | 0 | 0 | 302 | 18 | 26 | 0 | 215 | 368 | 260 | 26 | 0 | 203 | 0 | 17 | 97 | 17 | 0 | 12 | 0 | 146 | 0 | 64 | 22 | 305 | 0 | 348 | 30 | 30 | 127 | 9 | 16 | 0 | 80 | 30 | 0 | 0 | 100 | 13 | 9 | 67 | 38 | 1.99 | 44.08 | 0 | 5363.51 | 879 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 590 | 0 | 0 | 0 | 745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.01 | 97 | 0 | 0 | 55.13 | 145 | 0 | 0 | 0 | 151 | 0 | 380 | 0 | 4.78 | 0 | 54 | 70 | 30 | 34 | 0 | 0 | 0 | 6.8 | 179 | 0.59 | 14 | 278 | 130 | 180 | 0 | 400 | 1180 | 0 | 5995.31 | 11358.82 | 81.39
11:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 17 | 0 | 105 | 15 | 60 | 55 | 0 | 54 | 0 | 180 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 32 | 35 | 23 | 15 | 0 | 475 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 3.84 | 80 | 100 | 4 | 160 | 0 | 0 | 45 | 0 | 51 | 213 | 0 | 0 | 0 | 300 | 18 | 26 | 0 | 215 | 359 | 260 | 26 | 0 | 208 | 0 | 17 | 96 | 32 | 7 | 12 | 0 | 134 | 0 | 72 | 22 | 315 | 0 | 348 | 30 | 30 | 140 | 12 | 16 | 0 | 80 | 30 | 0 | 0 | 100 | 17 | 9 | 68 | 11 | 2.07 | 48.62 | 0 | 5630.53 | 879 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 590 | 0 | 0 | 0 | 739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.79 | 111 | 0 | 0 | 62.61 | 161 | 0 | 0 | 0 | 163 | 0 | 398 | 0 | 5.42 | 0 | 54 | 69 | 32 | 34 | 0 | 0 | 0 | 7.7 | 204 | 0.66 | 30 | 277 | 130 | 220 | 0 | 402 | 1180 | 14 | 6172.18 | 11802.71 | 81.38
12:00 | 0 | 55 | 32 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 17 | 4 | 120 | 82 | 227 | 55 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 34 | 125 | 22 | 15 | 0 | 530 | 58 | 16 | 1 | 0 | 1 | 0 | 0 | 0 | 12 | 12 | 1.14 | 80 | 105 | 4 | 160 | 148 | 0 | 45 | 0 | 51 | 215 | 0 | 0 | 0 | 300 | 17 | 26 | 0 | 215 | 357 | 260 | 26 | 0 | 212 | 0 | 17 | 96 | 28 | 10 | 15 | 0 | 142 | 0 | 73 | 31 | 315 | 0 | 348 | 30 | 30 | 155 | 12 | 16 | 0 | 80 | 30 | 0 | 0 | 99 | 17 | 9 | 68 | 15 | 1.51 | 49.3 | 0 | 6213.95 | 879 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 588 | 0 | 0 | 0 | 730 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.21 | 119 | 0 | 0 | 65.13 | 164 | 0 | 0 | 0 | 164 | 0 | 373 | 0 | 5.67 | 0 | 54 | 94 | 34 | 34 | 0 | 0 | 0 | 7.9 | 210 | 0.69 | 31 | 307 | 130 | 220 | 0 | 401 | 1190 | 17 | 6205.6 | 12419.55 | 81.37
13:00 | 0 | 88 | 40 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 17 | 17 | 132 | 142 | 260 | 55 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 34 | 142 | 23 | 15 | 0 | 460 | 90 | 16 | 49 | 0 | 3 | 0 | 32 | 0 | 12 | 12 | 3.87 | 80 | 99 | 10 | 160 | 140 | 0 | 45 | 8 | 51 | 215 | 0 | 0 | 0 | 300 | 18 | 26 | 0 | 215 | 357 | 260 | 26 | 0 | 212 | 0 | 17 | 94 | 30 | 14 | 15 | 0 | 146 | 0 | 70 | 27 | 310 | 0 | 348 | 30 | 30 | 158 | 12 | 16 | 0 | 82 | 30 | 0 | 0 | 98 | 17 | 9 | 67 | 34 | 2.16 | 40.28 | 0 | 6379.31 | 879 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 592 | 0 | 0 | 0 | 729 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 60.11 | 114 | 0 | 0 | 60.78 | 158 | 0 | 0 | 0 | 186 | 0 | 338 | 0 | 5.57 | 0 | 54 | 105 | 34 | 34 | 0 | 0 | 0 | 7.7 | 203 | 0.66 | 92 | 307 | 130 | 220 | 0 | 401 | 1207 | 17 | 6314.82 | 12694.13 | 81.35
14:00 | 0 | 88 | 40 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 17 | 17 | 133 | 138 | 260 | 55 | 0 | 54 | 0 | 180 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 30 | 142 | 22 | 21 | 0 | 470 | 92 | 16 | 88 | 0 | 1 | 0 | 37 | 0 | 12 | 12 | 3.38 | 80 | 103 | 6 | 160 | 148 | 0 | 45 | 20 | 51 | 214 | 0 | 0 | 0 | 300 | 17 | 26 | 0 | 215 | 355 | 260 | 25 | 0 | 210 | 0 | 21 | 80 | 28 | 17 | 15 | 0 | 146 | 0 | 65 | 29 | 310 | 0 | 348 | 30 | 30 | 154 | 3 | 16 | 0 | 82 | 30 | 0 | 0 | 98 | 20 | 9 | 67 | 44 | 2 | 43 | 0 | 6395.38 | 879 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 588 | 0 | 0 | 0 | 730 | 0 | 0 | 0 | 35 | 27 | 0 | 0 | 12 | 0 | 31.7 | 98 | 0 | 0 | 51.4 | 161 | 0 | 0 | 0 | 165 | 0 | 362 | 0 | 4.74 | 0 | 55 | 110 | 29 | 34 | 0 | 0 | 0 | 7.1 | 180 | 0.53 | 106 | 275 | 125 | 220 | 0 | 402 | 1202 | 17 | 6234.47 | 12629.85 | 81.33
15:00 | 0 | 88 | 40 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 17.5 | 17 | 133 | 138 | 260 | 55 | 0 | 54 | 0 | 180 | 0 | 0 | 0 | 25 | 150 | 0 | 0 | 24 | 142 | 21.5 | 21 | 0 | 525 | 97 | 16 | 93 | 0 | 5 | 0 | 38 | 0 | 12 | 12 | 2.62 | 80 | 108 | 4 | 160 | 145 | 0 | 45 | 25.5 | 51 | 214 | 0 | 0 | 0 | 300 | 13 | 26 | 0 | 215 | 352 | 230 | 25 | 0 | 200 | 0 | 34 | 93 | 17 | 12 | 19 | 0 | 170 | 0 | 39 | 30 | 315 | 0 | 349 | 30 | 30 | 153 | 3 | 16 | 0 | 82 | 30 | 0 | 0 | 98 | 48 | 9 | 68 | 42 | 1.51 | 35.71 | 0 | 6481.34 | 879 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 594 | 0 | 0 | 0 | 752 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 14 | 0 | 42.37 | 81 | 0 | 0 | 39.88 | 165 | 0 | 0 | 0 | 164 | 0 | 367 | 0 | 3.73 | 0 | 55 | 109 | 24 | 34 | 0 | 0 | 0 | 4.1 | 145 | 0.46 | 109 | 307 | 125 | 220 | 0 | 403 | 1180 | 17 | 6225.54 | 12706.88 | 81.32
16:00 | 0 | 88 | 40 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 18 | 17 | 133 | 137 | 263 | 55 | 17 | 54 | 0 | 180 | 0 | 0 | 0 | 35 | 150 | 0 | 0 | 15 | 142 | 21.5 | 22 | 0 | 540 | 97 | 16 | 88 | 0 | 7 | 22 | 44 | 0 | 12 | 12 | 1.64 | 80 | 107 | 2 | 160 | 154 | 0 | 45 | 25.5 | 51 | 214 | 0 | 0 | 0 | 292 | 8 | 28 | 0 | 230 | 352 | 230 | 25 | 0 | 200 | 0 | 34 | 94 | 23 | 0 | 19 | 0 | 176 | 0 | 29 | 30 | 310 | 0 | 348 | 30 | 30 | 153 | 1 | 16 | 0 | 81 | 30 | 0 | 0 | 97 | 53 | 9 | 66 | 42 | 0.88 | 23.7 | 2 | 6525.22 | 880 | 250 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 610 | 0 | 0 | 0 | 752 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 14 | 0 | 28.13 | 51 | 0 | 0 | 24.2 | 163 | 0 | 0 | 0 | 158 | 0 | 383 | 0 | 2.29 | 0 | 55 | 111 | 15 | 34 | 0 | 0 | 0 | 1.6 | 92 | 0 | 110 | 307 | 125 | 220 | 0 | 401 | 1170 | 17 | 6110.22 | 12635.44 | 81.31
17:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 17.5 | 17 | 133 | 138 | 263 | 55 | 35 | 54 | 0 | 180 | 0 | 0 | 0 | 40 | 150 | 0 | 0 | 7 | 142 | 19 | 22 | 0 | 500 | 96 | 16 | 82 | 0 | 7 | 67 | 52 | 14 | 12 | 12 | 0.71 | 80 | 108 | 0 | 160 | 145 | 0 | 45 | 25.5 | 61 | 214 | 0 | 0 | 0 | 300 | 3 | 65 | 0 | 240 | 357 | 230 | 25 | 0 | 200 | 0 | 34 | 94 | 85 | 0 | 19 | 0 | 166 | 0 | 9 | 30 | 300 | 0 | 348 | 30 | 30 | 154 | 0 | 16 | 0 | 82 | 30 | 0 | 0 | 96 | 54 | 9 | 67 | 42 | 0.34 | 8.99 | 9 | 6653.04 | 879 | 250 | 0 | 17 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 605 | 0 | 0 | 0 | 849 | 0 | 0 | 0 | 35 | 35 | 0 | 50 | 14 | 0 | 11.24 | 21 | 0 | 0 | 9.58 | 160 | 0 | 0 | 0 | 156 | 0 | 354 | 0 | 0.87 | 0 | 55 | 108 | 6 | 34 | 0 | 0 | 0 | 1.7 | 38 | 0 | 109 | 307 | 125 | 220 | 0 | 400 | 1170 | 17 | 6087.39 | 12740.43 | 81.3
18:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 17.5 | 17 | 133 | 138 | 263 | 55 | 35 | 54 | 0 | 180 | 0 | 0 | 0 | 55 | 150 | 0 | 0 | 1 | 142 | 22 | 22 | 0 | 525 | 91 | 16 | 93 | 0 | 2 | 67 | 52 | 18 | 12 | 12 | 0.02 | 80 | 105 | 3 | 300 | 155 | 0 | 45 | 25.5 | 105 | 216 | 0 | 0 | 0 | 292 | 0 | 110 | 0 | 240 | 357 | 230 | 26 | 0 | 200 | 0 | 44 | 96 | 180 | 0 | 19 | 0 | 162 | 0 | 1 | 30 | 305 | 0 | 348 | 30 | 30 | 155 | 0 | 16 | 0 | 83 | 30 | 30 | 0 | 97 | 54.5 | 9 | 67 | 42 | 0 | 0.85 | 12 | 7049.37 | 879 | 250 | 0 | 18 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 604 | 0 | 0 | 0 | 1020 | 0 | 0 | 0 | 35 | 35 | 0 | 50 | 28 | 0 | 1.1 | 3 | 30 | 0 | 1.11 | 151 | 0 | 0 | 0 | 152 | 0 | 365 | 0 | 0.11 | 0 | 56 | 107 | 1 | 34 | 0 | 0 | 0 | 0.2 | 4 | 0 | 105 | 307 | 125 | 220 | 0 | 402 | 1165 | 35 | 6220.52 | 13269.89 | 81.28
19:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 21 | 18 | 133 | 138 | 265 | 55 | 55 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 150 | 0 | 0 | 0 | 142 | 23 | 0 | 0 | 480 | 99 | 16 | 94 | 0 | 5 | 67 | 52 | 18 | 12 | 12 | 0 | 80 | 107 | 2 | 300 | 138 | 0 | 45 | 25.5 | 105 | 216 | 0 | 0 | 0 | 293 | 0 | 117 | 0 | 220 | 360 | 300 | 51 | 0 | 200 | 0 | 58 | 97 | 177 | 0 | 19 | 0 | 174 | 0 | 0 | 30 | 300 | 0 | 348 | 30 | 30 | 154 | 0 | 16 | 0 | 83 | 30 | 70 | 0 | 97 | 35 | 9 | 67 | 42 | 0 | 0 | 12 | 7133.5 | 879 | 250 | 0 | 25 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 594 | 0 | 0 | 0 | 1141 | 0 | 53 | 0 | 35 | 35 | 0 | 51 | 28 | 0 | 0 | 0 | 30 | 0 | 0 | 170 | 0 | 0 | 0 | 176 | 0 | 352 | 0 | 0 | 0 | 56 | 109 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 307 | 125 | 220 | 0 | 488 | 1180 | 54 | 6567 | 13700.5 | 81.26
19:30 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 45 | 35 | 133 | 139 | 265 | 55 | 55 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 32 | 0 | 0 | 0 | 142 | 23 | 22 | 0 | 490 | 99 | 16 | 94 | 0 | 7 | 67 | 52 | 18 | 12 | 12 | 0 | 80 | 107 | 5 | 300 | 140 | 0 | 47 | 25.5 | 105 | 218 | 0 | 0 | 0 | 293 | 0 | 143 | 0 | 220 | 358 | 270 | 51 | 0 | 208 | 0 | 72 | 98 | 181 | 0 | 20 | 0 | 174 | 0 | 0 | 30 | 305 | 0 | 359 | 30 | 30 | 146 | 0 | 16 | 0 | 83 | 30 | 0 | 0 | 97 | 17 | 9 | 67 | 44 | 0 | 0 | 12 | 7060.5 | 879 | 250 | 0 | 20 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609 | 0 | 0 | 0 | 1244 | 0 | 50 | 0 | 35 | 50 | 0 | 51 | 28 | 0 | 0 | 0 | 30 | 0 | 0 | 158 | 0 | 0 | 0 | 159 | 0 | 393 | 0 | 0 | 0 | 56 | 109 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 307 | 125 | 220 | 0 | 503 | 1207 | 54 | 6766 | 13826.5
20:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 46 | 35 | 133 | 140 | 270 | 55 | 55 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 31 | 0 | 0 | 0 | 142 | 23 | 22 | 0 | 530 | 86 | 16 | 94 | 0 | 3 | 67 | 52 | 18 | 12 | 12 | 0 | 80 | 108 | 14 | 300 | 140 | 0 | 48 | 25.5 | 105 | 218 | 0 | 0 | 0 | 291 | 0 | 140 | 0 | 220 | 360 | 270 | 51 | 0 | 198 | 0 | 72 | 99 | 185 | 0 | 20 | 0 | 172 | 0 | 0 | 30 | 300 | 0 | 359 | 30 | 30 | 150 | 0 | 16 | 0 | 83 | 30 | 0 | 0 | 97 | 17 | 9 | 67 | 44 | 0 | 0 | 12 | 7080.5 | 879 | 250 | 0 | 20 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 598 | 0 | 0 | 0 | 1289 | 0 | 50 | 0 | 35 | 50 | 0 | 51 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 156 | 0 | 0 | 0 | 161 | 0 | 354 | 0 | 0 | 0 | 55 | 104 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 307 | 125 | 220 | 0 | 523 | 1205 | 54 | 6763 | 13843.5 | 81.24
21:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 20.8 | 35 | 133 | 140 | 265 | 55 | 35 | 35 | 0 | 225 | 0 | 0 | 0 | 35 | 33 | 0 | 0 | 0 | 142 | 29 | 22 | 0 | 530 | 87 | 16 | 94 | 0 | 0 | 52 | 45 | 18 | 12 | 12 | 0 | 80 | 106 | 10 | 300 | 150 | 0 | 50 | 25.5 | 105 | 220 | 0 | 0 | 0 | 290 | 0 | 143 | 0 | 220 | 360 | 270 | 51 | 0 | 184 | 0 | 65 | 99 | 184 | 0 | 20 | 0 | 170 | 0 | 0 | 22 | 300 | 0 | 378 | 30 | 30 | 155 | 0 | 16 | 0 | 83 | 30 | 0 | 0 | 97 | 17 | 9 | 68 | 30 | 0 | 0 | 12 | 6984.3 | 879 | 250 | 0 | 20 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 0 | 0 | 0 | 1382 | 0 | 50 | 0 | 35 | 50 | 0 | 51 | 28 | 0 | 0 | 0 | 30 | 0 | 0 | 174 | 0 | 0 | 0 | 177 | 0 | 414 | 0 | 0 | 0 | 55 | 106 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 307 | 125 | 220 | 0 | 504 | 1210 | 54 | 6942 | 13926.3 | 81.22
22:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 17.5 | 35 | 133 | 140 | 270 | 55 | 35 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 142 | 29 | 22 | 0 | 530 | 96 | 16 | 95 | 0 | 0 | 67 | 45 | 18 | 12 | 12 | 0 | 80 | 108 | 17 | 210 | 140 | 0 | 50 | 25.5 | 105 | 221 | 0 | 0 | 0 | 292 | 0 | 142 | 0 | 220 | 361 | 270 | 51 | 0 | 172 | 0 | 21 | 99 | 184 | 0 | 20 | 0 | 172 | 0 | 0 | 22 | 305 | 0 | 372 | 30 | 30 | 158 | 0 | 16 | 0 | 53 | 30 | 100 | 0 | 97 | 0 | 9 | 58 | 30 | 0 | 0 | 12 | 7007 | 879 | 250 | 0 | 20 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590 | 0 | 0 | 0 | 1477 | 0 | 50 | 0 | 35 | 50 | 0 | 51 | 28 | 0 | 0 | 0 | 30 | 0 | 0 | 170 | 0 | 0 | 0 | 175 | 0 | 359 | 0 | 0 | 0 | 55 | 105 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 307 | 130 | 220 | 0 | 506 | 1212 | 35 | 6953 | 13960 | 81.2
23:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 35 | 134 | 140 | 270 | 55 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 142 | 25 | 22 | 0 | 400 | 90 | 16 | 96 | 0 | 0 | 67 | 45 | 18 | 12 | 12 | 0 | 80 | 107 | 11 | 160 | 156 | 0 | 50 | 25.5 | 105 | 221 | 0 | 0 | 0 | 292 | 0 | 140 | 0 | 220 | 360 | 270 | 51 | 0 | 170 | 0 | 17 | 99 | 183 | 0 | 20 | 0 | 174 | 0 | 0 | 22 | 300 | 0 | 371 | 30 | 30 | 158 | 0 | 16 | 0 | 50 | 30 | 100 | 0 | 98 | 0 | 9 | 58 | 30 | 0 | 0 | 12 | 6867.5 | 880 | 250 | 0 | 20 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 602 | 0 | 0 | 0 | 1496 | 0 | 50 | 0 | 35 | 50 | 0 | 51 | 28 | 0 | 0 | 0 | 30 | 0 | 0 | 160 | 0 | 0 | 0 | 175 | 0 | 387 | 0 | 0 | 0 | 55 | 108 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 307 | 130 | 220 | 0 | 388 | 1212 | 17 | 6846 | 13713.5 | 81.18
Total KWH | 0 | 1378560 | 653280 | 0 | 0 | 0 | 0 | 0 | 9414000 | 0 | 0 | 259560 | 299880 | 2171088 | 1746720 | 3547604 | 1001314 | 266723 | 803520 | 0 | 4984800 | 0 | 0 | 0 | 268289 | 5174375 | 0 | 0 | 245246 | 1879200 | 552000 | 479880 | 0 | 11888181.82 | 1283400 | 260945 | 1065600 | 0 | 36175 | 569534 | 449616 | 144515 | 172800 | 176640 | 26285 | 1921920 | 1722073 | 385440 | 4189090.91 | 1804872 | 0 | 861120 | 281133 | 1512145 | 4985395 | 0 | 0 | 0 | 7145453 | 138105 | 1321454 | 0 | 5591500 | 9020200 | 6266000 | 985496 | 0 | 4806000 | 0 | 567360 | 2340184 | 1511520 | 73080 | 439970 | 0 | 3542400 | 0 | 528582 | 388576 | 7418000 | 0 | 8780000 | 717000 | 729960 | 3643200 | 63337 | 382416 | 0 | 1896000 | 718944 | 349200 | 0 | 2374230 | 382680 | 229200 | 1303200 | 847680 | 15750 | 347000 | 104880 | 143831476.73 | 21144727 | 7048800 | 0 | 128160 | 281856 | 0 | 0 | 0 | 0 | 0 | 0 | 672480 | 13738177 | 0 | 0 | 0 | 21407669 | 0 | 268573 | 0 | 410688 | 539904 | 0 | 338496 | 205723 | 0 | 432256 | 852030 | 191250 | 0 | 448496 | 4296818 | 0 | 0 | 0 | 4527000 | 0 | 9410763 | 0 | 39420 | 0 | 1264581 | 1808197 | 252881 | 837283 | 0 | 0 | 0 | 53939.04 | 1504800 | 4710 | 1345056 | 6938000 | 3039000 | 5356430 | 0 | 9498182 | 28381090.91 | 430800 | 147098235.95 | 290929712.68

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 12-04-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-04-2026 | during | 12-04-2026 | during | 12-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 398 | 381 | 412 | 412 | 412 | 412 | FGMO not available
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 450 | 450 | 226 | 226 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 210 | 33 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 20.8 | 53.97 | 53.97 | 53.97 | 53.97 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 82 | 140 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 22 | 29 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 32 | 48 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 227 | 265 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 120 | 133 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 55 | 105 | 105 | 105 | 88 | 88 | Engine Problem
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 35 | 162 | 162 | 162 | 162 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 33 | 0 | 33 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 4 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 530 | 530 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 125 | 142 | 160 | 160 | 125 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2205 | 2268.8 | 5948.22 | 5915.22 | 2830.52 | 2832.52
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 45 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 220 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 105 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 45 | 56 | 64 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 52 | 68 | 68 | 68 | 68 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 13 | 13 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 10 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 1 | 94 | 108 | 108 | 38 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.14 | 0 | 4.04 | 0 | 4.04 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 18 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 105 | 106 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 58 | 87 | 116 | 116 | 70 | 70 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 148 | 150 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 300 | 290 | 1224 | 1224 | 310 | 310 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 0 | 2 | 1 | 2 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 160 | 300 | 160 | 160 | 160 | 160 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1226.14 | 1672.5 | 3063.9 | 3063.86 | 1500.54 | 1500.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 212 | 184 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 357 | 360 | 350.01 | 350.01 | 350.01 | 350.01 | FGMO not available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 260 | 270 | 342.01 | 342.01 | 342.01 | 342.01 | machine problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 215 | 220 | 393 | 393 | 310 | 310 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 26 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 26 | 143 | 150 | 150 | 60 | 140 | Partial Shutdown due to maintenance
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 31 | 22 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 99 | 163 | 163 | 105 | 105 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 28 | 184 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 142 | 170 | 0 | 0 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 10 | 0 | 113 | 113 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 65 | 115 | 115 | 115 | 115 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 73 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.745 | 1508 | 1788 | 2680.19 | 2610.19 | 2013.52 | 2023.52
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-04-2026 | during | 12-04-2026 | during | 12-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 15 | 30 | 157.5 | 157.5 | 60 | 60 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.51 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 68 | 68 | 10 | 10 | 10 | 10 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 70 | 70 | 70 | 70 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 49.3 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 159.81 | 136 | 364.1 | 314 | 219.1 | 169
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 155 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 100 | 100 | 100 | 100 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 83 | 83 | 83 | 83 | 83 | Under Maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 99 | 97 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 348 | 378 | 385 | 385 | 350 | 350 | Gas (RMS) problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1115 | 1119 | 1257 | 1257 | 1172 | 1172
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 879 | 879 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 20 | 27 | 27 | 36 | 36 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 42 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 250 | 410 | 410 | 370 | 370 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 75 | 0 | 99 | 0 | 99 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 588 | 607 | 1234.2 | 1234.2 | 597 | 597 | U-2 Under Maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1792 | 1798 | 3260.2 | 3161.2 | 2167.1 | 2068.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 401 | 504 | 300 | 400 | 400 | 400 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 31 | 102 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 125 | 130 | 130 | 130 | 130 | STG Under Maintenance
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1190 | 1210 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 54 | 150 | 150 | 100 | 100 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 287 | 287 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.69 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2296.69 | 2522 | 2462 | 2561 | 2492 | 2491
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 62.21 | 0 | 64 | 0 | 64 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 47 | 47 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 164 | 174 | 214 | 214 | 194 | 194 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 164 | 177 | 220 | 220 | 198 | 198 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 373 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 51 | 92 | 92 | 92 | 92 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 100 | 100 | BPDB event of default
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 100 | 100 | BPDB event of default
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.67 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 730 | 1382 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 65.13 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 119 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1683.01 | 2391 | 3245.72 | 3014.87 | 2823.14 | 2592.29
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 54 | 55 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.9 | 0 | 6.8 | 0 | 6.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 94 | 106 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 210 | 0 | 199.99 | 0 | 199.99 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 433.9 | 231 | 528.79 | 292 | 514.79 | 278
System Total |  |  |  |  | 28823.2 | 29269.987 | 12419.55 | 13926.3 | 22810.12 | 22189.34 | 15732.71 | 15126.93
Forecast Scenario (12-04-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12780 |  | 0 |  | 12780
|  |  |  | 1:00 | 12180 |  | 0 |  | 12180
|  |  |  | 2:00 | 11690 |  | 0 |  | 11690
|  |  |  | 3:00 | 11270 |  | 0 |  | 11270
|  |  |  | 4:00 | 11130 |  | 0 |  | 11130
|  |  |  | 5:00 | 10900 |  | 0 |  | 10900
|  |  |  | 6:00 | 10890 |  | 0 |  | 10890
|  |  |  | 7:00 | 11420 |  | 0 |  | 11420
|  |  |  | 8:00 | 11940 |  | 0 |  | 11940
|  |  |  | 9:00 | 12210 |  | 0 |  | 12210
|  |  |  | 10:00 | 12470 |  | 0 |  | 12470
|  |  |  | 11:00 | 12860 |  | 0 |  | 12860
|  |  |  | 12:00 | 13470 |  | 0 |  | 13470
|  |  |  | 13:00 | 13930 |  | 0 |  | 13930
|  |  |  | 14:00 | 13810 |  | 0 |  | 13810
|  |  |  | 15:00 | 13690 |  | 0 |  | 13690
|  |  |  | 16:00 | 13300 |  | 0 |  | 13300
|  |  |  | 17:00 | 12910 |  | 0 |  | 12910
|  |  |  | 18:00 | 13170 |  | 0 |  | 13170
|  |  |  | 18:30 | 13800 |  | 0 |  | 13800
|  |  |  | 19:00 | 14710 |  | 0 |  | 14710
|  |  |  | 19:30 | 14800 |  | 0 |  | 14800
|  |  |  | 20:00 | 14700 |  | 0 |  | 14700
|  |  |  | 21:00 | 14650 |  | 0 |  | 14650
|  |  |  | 22:00 | 14400 |  | 0 |  | 14400
|  |  |  | 23:00 | 14100 |  | 0 |  | 14100
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 13470.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14800.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13750.37 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 304.64431 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:25 hrs on 12-04-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 11-04-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12419.55 | MW | 12:00 Hr. | Energy Generated |  |  | 290.9297 |  | MKWHr.
| Day Peak Demand |  |  | 12652.55 | MW | 12:00 Hr. | Energy Unserverd |  |  | 4.1 |  | MKWHr.
| Evening Peak Generation |  |  | 13926.3 | MW | 21:00 Hr. | Energy Demand |  |  | 295.0297 |  | MKWHr.
| Evening Peak Demand |  |  | 14350.57 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34.5 |  | °C
| Minimum Generation of the Day |  |  | 9732.18 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 938.9 |  | MMCFD
| Maximum Generation of the Day |  |  | 13960 | MW | 22:00 Hr. | Production Cost per KWHr |  |  | 6.652 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.4932 | 0 | 14.2757 | 0 | 0 | 0.24525 | 0 | 0 | 47.0142 | Gas | 128.8489 | Gas | 449797075.6094
| Chattogram Zone |  |  | 5.3708 | 11.3345 | 10.3044 | 0 | 1.9219 | 0.16439 | 0 | 0.036175 | 29.1323 | Coal | 71.1546 | Coal | 485188113.8026
| Cumilla Zone |  |  | 29.4493 | 0 | 3.862 | 0 | 0 | 0.52858 | 3.5424 | 0 | 37.3823 | HFO | 37.2481 | HFO | 651821955.07
| Mymensingh Zone |  |  | 0.84768 | 0 | 2.02 | 0 | 0 | 0.36275 | 0 | 0 | 3.2304 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.0089 | 0 | 0 | 0 | 0 | 0.063337 | 0 | 0 | 27.0723 | Hydro | 1.9219 | Hydro | 192192
| Khulna Zone |  |  | 7.0488 | 13.7382 | 0.41002 | 0 | 0 | 0.67248 | 21.1447 | 0 | 43.0142 | Solar | 5.6253 | Solar | 90372949.608
| Barishal Zone |  |  | 8.3954 | 44.8173 | 1.7759 | 0 | 0 | 0.00471 | 0 | 0 | 54.9933 | Import | 46.0948 | Import | 257356280.56
| Rajshahi Zone |  |  | 18.2346 | 0 | 1.9546 | 0 | 0 | 1.7722 | 21.4077 | 0 | 43.3691 | Wind | 0.036175 | Wind | 532134.25
| Rangpur Zone |  |  | 0 | 1.2646 | 2.6455 | 0 | 0 | 1.8116 | 0 | 0 | 5.7217
| Total |  |  | 128.8489 | 71.1546 | 37.2481 | 0 | 1.9219 | 5.6253 | 46.0948 | 0.036175 | 290.9297
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 449797075.6094 |  | Hydro | 192192
|  |  |  | Coal | 485188113.8026 |  | Solar | 90372949.608
|  |  |  | HFO | 651821955.07 |  | Import | 257356280.56
|  |  |  | HSD | 0 |  | Wind | 532134.25
[5 empty] | Total: | 193,52,60,700 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.1447 | Peak Hr Flow | 879.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 52716781.82 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 21.4077 | Peak Hr Flow | 1382.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2700 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.5424 | Peak Hr Flow | 170.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2719 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 46.0948 | Peak Hr Flow | 2431.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5117
|  |  |  | Chattogram |  | 0 |  | 1508
|  |  |  | Cumilla |  | 80 |  | 1395
|  |  |  | Mymensingh |  | 50 |  | 1067
|  |  |  | Sylhet |  | 51 |  | 517
|  |  |  | Khulna |  | 100 |  | 1650
|  |  |  | Barishal |  | 35 |  | 431
|  |  |  | Rajshahi |  | 60 |  | 1431
|  |  |  | Rangpur |  | 30 |  | 792
|  |  |  | Total |  | 406 |  | 13908
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 320
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:05 | 17:36 | Pabna- Shahjadpur 132kV Ckt-1 Scheduled S/D from Pabna 132/33kV end Due to CB Pole
Replacement
| 08:09 | 17:54 | Bhangura 132/33kV S/S Tr-1(403T) LT Scheduled S/D Due to Ckt 2 project work shutdown | [7 empty] | 30.0MW load
interrup.
| 08:10 | 17:53 | Bhangura 132/33kV S/S Tr-1(403T) HT Scheduled S/D Due to Project work for bus 2 | [7 empty] | 30.0MW load
interrup.
| 08:10 | 17:54 | Bhangura 132/33kV S/S Tr-2(413T) LT Scheduled S/D Due to Project shutdown for bus 2 Work | [7 empty] | 30.0MW load
interrup.
| 08:11 | 17:53 | Bhangura 132/33kV S/S Tr-2(413T) HT Scheduled S/D Due to Project shutdown for bus 2 work | [7 empty] | 30.0MW load
interrup.
| 08:17 | 17:43 | Baghabari-Bangura 132 kV Ckt-1 Scheduled S/D from Bhangura 132/33kV end Due to Project | [7 empty] | 30.0MW load
|  |  | shutdown for line 2 and bus work | [7 empty] | interrup. Bhangura
132/33kV end
| 08:20 | 10:55 | Satkhira 132/33kV S/S Transformer-1 (T-1) HT Scheduled S/D
| 08:20 | 10:56 | Satkhira 132/33kV S/S Transformer-2 (T-2) HT Scheduled S/D
| 08:23 | 10:56 | Satkhira 132/33kV S/S Transformer-2 (T-2) LT Scheduled S/D | [7 empty] | 38.0MW load
interrup.
| 08:23 | 10:56 | Satkhira 132/33kV S/S Transformer-1 (T-1) LT Scheduled S/D | [7 empty] | 62.0MW load
interrup.
| 08:23 | 10:55 | Khulna (S)-Satkhira 132kV Ckt-2 Scheduled S/D from Satkhira 132/33kV end. and from
Khulna(S) 230/132kVend.
| 08:23 | 10:55 | Khulna (S)-Satkhira 132kV Ckt-1 Scheduled S/D from Satkhira 132/33kV end. and from
Khulna(S) 230/132kVend.
| 08:57 | 16:20 | Noapara 132/33kV S/S T-1 LT Scheduled S/D Due to T-1 Transformer S/D Due to Painting
Work.
| 08:57 | 16:20 | Noapara 132/33kV S/S T-1 HT Scheduled S/D Due to T-1 Transformer S/D Due to Painting
Work.
|  | 09:05 | Narail 132/33kV S/S TR1 (403-T) HT is restored.
|  | 09:07 | Narail 132/33kV S/S TR1 (403-T) LT is restored.
|  | 09:33 | Faridpur 132/33kV S/S Transformer-2 LT is restored.
|  | 09:33 | Faridpur 132/33kV S/S Transformer-2 HT is restored.
| 09:50 | 10:40 | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-1 Forced S/D from Bog-Sherpur 132/33kV end. and
from Bogura 230/132kV end Due to 132kV Line issue at Sherpur(Bogura) 132kV end
| 09:57 | 15:10 | Ghorashal 230kV S/S TARFO-2 HT Project Work S/D Due to CT oil leakage, Loop change, Red | [7 empty] | 70.0MW load
|  |  | hot maintenance. | [7 empty] | interrup.
| 09:59 | 11:40 | BIPTC S/S 20DF11 Scheduled S/D Due to Corrective Maintenance.
|  | 11:02 | Mymensingh 132/33kV S/S Bus B is restored.
|  | 11:18 | Bhaluka-Mymensingh 132 kV Ckt-1 is restored.
| 12:00 |  | Day Peak Generation: 12416 MW.
|  | 14:35 | Jhenaidah 132/33kV S/S Transformer T-2 HT is restored.
|  | 14:36 | Jhenaidah 132/33kV S/S Transformer T-2 LT is restored.
|  | 15:10 | Kishoreganj 132/33kV S/S Tr-3 (424T) HT is restored.
| 15:10 | 18:30 | Nabinagar 132/33kV S/S Bus Section-1 Project Work S/D Due to Red hot maintenance
| 15:10 | 18:30 | Nabinagar 132/33kV S/S T-1 HT Project Work S/D Due to Red hot maintenance
| 15:10 | 18:30 | Nabinagar 132/33kV S/S T-1 LT Project Work S/D Due to Red hot maintenance
|  | 15:11 | Kishoreganj 132/33kV S/S Tr-3 (424T) LT is restored.
| 15:58 | 18:10 | Halishahar-Julda 132kV Ckt-1 Tripped from Halishahar 132/33kV end showing General trip,B
phase trip,SOTF trip, relays Due to Transient fault and from Juldah 132/33kV end showing
Distance relay. relays Due to Due to bad weather.
| 16:02 |  | Adani Power Jharkhand Ltd. unit-2 was synchronized
|  | 16:15 | Daudkandi-Sonargaon 132 kV Ckt-2 is restored.
| 17:47 | 01:17 | BIPTC S/S Baharampur-3 Forced S/D Due to Shutdown is taken from Baharampur end
|  | 18:38 | Aminbazar-Airport(Old) 230kV Ckt-1 is restored.
| 18:50 | 20:35 | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D Due to None | [7 empty] | 60.0MW load
interrup.
| 18:50 | 20:35 | Kabirpur 132/33kV S/S XFR, T-3 LT Scheduled S/D Due to Red hot Maintanence of 33 kV bus | [7 empty] | 60.0MW load
interrup.
| 18:53 | 20:32 | Kabirpur 132/33kV S/S XFR, T-I HT Scheduled S/D Due to Redhot maintenance of 33 kV bus | [7 empty] | 95.0MW load
interrup.
| 18:53 | 20:32 | Kabirpur 132/33kV S/S XFR, T-I LT Scheduled S/D Due to Redhot maintenance of 33 kV bus | [7 empty] | 95.0MW load
interrup.
| 20:52 | 21:32 | Sherpur 132/33kV S/S Transformer- 02 HT Forced S/D Due to 33KV BUS Side, SPBS Bay-03
Feeder Rad Hot Remove Work.
| 20:52 | 21:33 | Sherpur 132/33kV S/S Transformer- 02 LT Forced S/D Due to 33KV BUS Side, SPBS Bay-03
Feeder Rad Hot Remove Work.
| 21:00 |  | Evening peak generation 13925 MW
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 11-04-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 381 | 9414000 | FGMO not available
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4984800 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1001314 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 33 | 5174375 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 20.8 | 259560 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 140 | 1746720 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 266723 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 268289 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 29 | 552000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 479880 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 48 | 653280 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 265 | 3547604 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 2171088 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1378560 | Engine Problem
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 803520 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 245246 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 299880 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 530 | 11888181.82 | FGMO
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1879200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2268.8 | 47014220.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 281133 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 138105 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 861120 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1921920 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 4985395 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1512145 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 45 | 449616 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 52 | 569534 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 172800 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 10 | 385440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 94 | 1065600 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 26285 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 260945 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 18 | 144515 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 106 | 1722073 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 176640 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 87 | 1283400 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 150 | 1804872 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 290 | 7145453 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 36175 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 300 | 4189090.91 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 1672.5 | 29132256.91
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 184 | 4806000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 360 | 9020200 | FGMO not available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 270 | 6266000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 220 | 5591500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 985496 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 143 | 1321454 | Partial Shutdown due to maintenance
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 22 | 388576 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 99 | 2340184 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 184 | 1511520 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 170 | 3542400 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 439970 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 73080 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 65 | 567360 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 528582 | -
Cumilla Area Total |  |  |  |  | 2870.745 | 1788 | 37382322
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 30 | 847680 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15750 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 68 | 1303200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 229200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 347000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 104880 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 382680 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 136 | 3230390
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 63337 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 717000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 729960 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3643200 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 349200 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 718944 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1896000 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 97 | 2374230 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 382416 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7418000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 378 | 8780000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1119 | 27072287
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 879 | 21144727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 20 | 128160 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 42 | 281856 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 7048800 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 672480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 607 | 13738177 | U-2 Under Maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1798 | 43014200
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 504 | 9498182 | U1 under maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 102 | 1345056 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 125 | 3039000 | STG Under Maintenance
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1210 | 28381090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5356430 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 430800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6938000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4710 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2522 | 54993268.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 432256 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 268573 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 205723 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 174 | 4296818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 177 | 4527000 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9410763 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 191250 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 338496 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 539904 | BPDB event of default
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 410688 | BPDB event of default
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 39420 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1382 | 21407669 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 448496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 852030 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2391 | 43369086
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 55 | 1264581 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 837283 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 53939.04 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 106 | 1808197 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 252881 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1504800 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 231 | 5721681.04
Eastern Grid Total |  |  |  |  | 17417.792 | 6984.3 | 143831476.73
Western Grid Total |  |  |  |  | 11852.195 | 6942 | 147098235.95
National Grid Total |  |  |  |  | 29269.987 | 13926.3 | 290929712.68
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 11-04-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9423.88 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4078.8 | MW
i) Dhaka area |  |  | 5117.38 |  | MW | i) Khulna area |  |  |  | 1550.5 | MW
ii) Chattogram area |  |  | 1508.5 |  | MW | ii) Barishal area |  |  |  | 395.5 | MW
iii) Cumilla area |  |  | 1315 |  | MW | iii) Rajshahi area |  |  |  | 1370.8 | MW
iv) Mymensingh area |  |  | 1017 |  | MW | iv) Rangpur area |  |  |  | 762 | MW
v) Sylhet area |  |  | 466 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13502.68 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 21:00 | 67 | Hasnabad | 84 | 22:00 | 133 | Natore | 131 | 18:30
2 | AKSML | 12 | 13:00 | 68 | Hathazari | 80 | 21:00 | 134 | Nawabganj | 50.8 | 21:00
3 | Aftabnagar | 36 | 13:00 | 69 | Hatirjheel | 39 | 12:00 | 135 | Netrakona | 125 | 19:00
4 | Agargaon | 100 | 13:00 | 70 | Ishurdi | 69 | 13:00 | 136 | New | 70 | 15:00
5 | Agrabad | 70 | 12:00 | 71 | Jaldhaka | 61 | 08:00 | 137 | Niamatpur | 110 | 20:00
6 | Amnura | 45 | 11:00 | 72 | Jamalpur | 106 | 18:30 | 138 | Noapara | 42 | 19:30
7 | Ashuganj | 100 | 19:00 | 73 | Jashore | 123 | 21:00 | 139 | PHP | 8 | 11:00
8 | BSRM | 198 | 23:00 | 74 | Jhenaidah | 90 | 19:00 | 140 | Pabna | 96 | 13:00
9 | Bagerhat | 79 | 21:00 | 75 | Joydebpur | 140 | 20:00 | 141 | Palashbari | 114 | 19:00
10 | Bajitpur | 77 | 18:30 | 76 | Joypurhat | 62 | 19:30 | 142 | Panchagarh | 39 | 21:00
11 | Bakerganj | 10.8 | 22:00 | 77 | Juldah | 23 | 16:00 | 143 | Patiya | 10 | 19:30
12 | Bakulia | 92 | 18:30 | 78 | KSRM | 19 | 09:00 | 144 | Patuakhali | 68 | 22:00
13 | Banani | 36 | 13:00 | 79 | Kabirpur | 258 | 16:00 | 145 | Payra | 33 | 22:00
14 | Bangabhaban | 6 | 11:00 | 80 | Kachua | 88 | 22:00 | 146 | Postogola | 50 | 13:00
15 | Barapukuria | 55 | 14:00 | 81 | Kaliganj | 25 | 21:00 | 147 | Pubail | 30 | 18:30
16 | Barguna | 20 | 19:30 | 82 | Kallyanpur | 105 | 18:00 | 148 | Purbachal | 28 | 13:00
17 | Barishal | 94 | 22:00 | 83 | Kalurghat | 40 | 18:30 | 149 | Purbasadipur | 110 | 12:00
18 | Barishal-230 | 102 | 23:00 | 84 | Kamrangirchar | 77 | 13:00 | 150 | Rahanpur | 30 | 11:00
19 | Baroaulia | 67 | 11:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 27 | 09:00
20 | Baroirhat | 57 | 21:00 | 86 | Kasba | 33 | 21:00 | 152 | Rajbari | 73 | 18:30
21 | Bashundhara | 170 | 13:00 | 87 | Kazla | 113 | 13:00 | 153 | Rajendrapur | 124 | 20:00
22 | BashundharaCement | 8 | 09:00 | 88 | Keranigonj | 82 | 19:00 | 154 | Rajshahi | 133 | 13:00
23 | Beanibazar | 60 | 18:30 | 89 | Khagrachori | 30 | 20:00 | 155 | Rajshahi-230 | 52 | 13:00
24 | Benapole | 56 | 12:00 | 90 | Khulna | 69 | 13:00 | 156 | Ramganj | 98 | 22:00
25 | Bhaluka | 146 | 18:30 | 91 | Khulshi | 167 | 19:00 | 157 | Rampur | 40 | 18:30
26 | Bhandaria | 54 | 22:00 | 92 | Kishoreganj | 119 | 19:00 | 158 | Rangamati | 17 | 12:00
27 | Bhangura | 42 | 20:00 | 93 | Kodda | 315 | 16:00 | 159 | Rangpur | 122 | 18:30
28 | Bheramara(GK) | 61 | 14:00 | 94 | Kulaura | 41 | 18:00 | 160 | Ruppur | 2.6 | 11:00
29 | Bhulta | 215 | 22:00 | 95 | Kurigram | 56 | 07:00 | 161 | SSM | 9 | 06:00
30 | Bog-Sherpur | 66 | 19:00 | 96 | Kushtia | 116 | 14:00 | 162 | Saidpur | 99 | 12:00
31 | Bogura | 165 | 21:00 | 97 | Laksam | 27 | 00:00 | 163 | Satkhira | 125 | 22:00
32 | Borhanuddin | 94 | 19:30 | 98 | Lakshmipur | 36 | 15:00 | 164 | Satmasjid | 99 | 13:00
33 | Brahmanbaria | 115 | 19:00 | 99 | Lalbag | 70 | 13:00 | 165 | Savar | 216 | 18:00
34 | Cantonment | 112 | 13:00 | 100 | Lalmonirhat | 52 | 18:30 | 166 | SevenRings | 15.5 | 00:00
35 | Chandina | 20 | 00:00 | 101 | MI_Cement | 18.8 | 10:00 | 167 | ShahCement | 40 | 02:00
36 | Chandpur | 70 | 19:00 | 102 | Madanganj | 47 | 10:00 | 168 | Shahjadpur | 71 | 18:00
37 | Chandraghona | 35 | 21:00 | 103 | Madaripur | 103 | 22:00 | 169 | Shahjibazar | 97 | 21:00
38 | Chapai | 66 | 11:00 | 104 | Madartek | 70 | 13:00 | 170 | Shahmirpur | 59 | 23:00
39 | Charsaidpur | 42 | 21:00 | 105 | Madunaghat | 51 | 16:00 | 171 | Shariatpur | 80 | 22:00
40 | Chauddagram | 73 | 18:30 | 106 | Magura | 54 | 18:30 | 172 | Sherpur | 112 | 19:00
41 | Chhatak | 26 | 18:00 | 107 | Mahasthangarh | 70 | 13:00 | 173 | Shikalbaha | 33.5 | 15:00
42 | Chowmuhani | 124 | 19:00 | 108 | Maijdee | 40 | 00:00 | 174 | Shitalakhya | 80.4 | 13:00
43 | Chuadanga | 106 | 19:00 | 109 | Manikganj | 121 | 19:30 | 175 | Sholosohor | 48 | 18:30
44 | Coxsbazar | 146 | 21:00 | 110 | Maniknagar | 61 | 13:00 | 176 | Shyampur | 172 | 11:00
45 | Cumilla(N) | 118 | 19:00 | 111 | Matarbari | 54 | 19:00 | 177 | Siddhirganj | 125 | 12:00
46 | Cumilla(S) | 178 | 18:30 | 112 | Matuail | 77 | 12:00 | 178 | Sirajganj | 102 | 13:00
47 | Daganbhuiyan | 35 | 22:00 | 113 | Metrorail_Motijheel | 24 | 17:00 | 179 | Sonargaon | 126 | 21:00
48 | Daudkandi | 127 | 19:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreemongol | 60 | 18:00
49 | DhakaUniversity | 60 | 13:00 | 115 | Millgate | 106 | 22:00 | 181 | Sreepur | 113 | 20:00
50 | Dhamrai | 114 | 08:00 | 116 | Mirpur | 126 | 18:30 | 182 | Srinagar | 44 | 19:30
51 | Dhanmondi | 105 | 13:00 | 117 | Mirsorai | 14 | 19:30 | 183 | Sunamganj | 48 | 18:00
52 | Dohazari | 104 | 20:00 | 118 | Mirzapur | 41 | 23:00 | 184 | Sylhet | 40 | 21:00
53 | Faridpur | 138 | 19:00 | 119 | Mithapukur | 48 | 07:00 | 185 | Sylhet-132 | 118 | 18:30
54 | Fatullah | 84 | 16:00 | 120 | Modern | N/A | N/A | 186 | TK | 25 | 18:30
55 | Fenchuganj | 32 | 09:00 | 121 | Mogbazar | 68 | 13:00 | 187 | Tangail | 162 | 07:00
56 | Feni | 99 | 22:00 | 122 | Mongla | 41 | 19:00 | 188 | Taraganj | 19 | 08:00
57 | GPH | 76 | 19:30 | 123 | Motijheel | 41 | 13:00 | 189 | Tasnim | 32 | 06:00
58 | Ghatail | 70 | 18:00 | 124 | Muktagacha | 34 | 19:00 | 190 | Thakurgaon | 78 | 21:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 111 | 22:00 | 191 | Tongi | 146 | 11:00
60 | Ghorashal-230 | 112 | 21:00 | 126 | Muradnagar | 41 | 18:30 | 192 | Ullahpara | 38 | 13:00
61 | Goalpara | 39 | 20:00 | 127 | Mymensingh | 186 | 19:00 | 193 | Ullon | 49 | 18:30
62 | Gollamari | 96 | 23:00 | 128 | Nabinagar | 29 | 20:00 | 194 | Uttara | 78 | 13:00
63 | Gopalganj | 91 | 22:00 | 129 | Naogaon | 139 | 13:00 | 195 | UttaraNew | 53 | 13:00
64 | Gulshan | 98 | 13:00 | 130 | Narail | 53 | 21:00 | 196 | Zigatola | 79 | 13:00
65 | Halishahar | 99 | 09:00 | 131 | Narinda | 62 | 13:00
66 | HaripurSBU | 132 | 09:00 | 132 | Narshingdi | 189 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 11-04-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 11604.95 | 0 |  | 11604.95
1:00 | 11163.25 | 0 |  | 11163.25
2:00 | 10693.11 | 0 |  | 10693.11
3:00 | 10277.7 | 0 |  | 10277.7
4:00 | 10095.34 | 0 |  | 10095.34
5:00 | 9732.18 | 0 |  | 9732.18
6:00 | 9952.54 | 0 |  | 9952.54
7:00 | 10619.95 | 42 |  | 10663.95
8:00 | 10993.3 | 68 |  | 11064.3
9:00 | 11214.7 | 85 |  | 11303.7
10:00 | 11358.82 | 76 |  | 11437.82
11:00 | 11802.71 | 93 |  | 11899.71
12:00 | 12419.55 | 223 |  | 12652.55
13:00 | 12694.13 | 296 |  | 13003.13
14:00 | 12629.85 | 299 |  | 12942.31
15:00 | 12706.88 | 381 |  | 13104.88
16:00 | 12635.44 | 400 |  | 13053.44
17:00 | 12740.43 | 167 |  | 12915.43
18:00 | 13269.89 | 79 |  | 13352.89
19:00 | 13700.5 | 525 |  | 14249.5
19:30 | 13826.5 | 453 |  | 14299.5
20:00 | 13843.5 | 456 |  | 14320.5
21:00 | 13926.3 | 406 |  | 14350.57
22:00 | 13960 | 278 |  | 14251
23:00 | 13713.5 | 226 |  | 13949.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 11-04-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5641 | 5963.95 | 11604.95 | DAILY GENERATION CURVE
00:30 | 5447.5 | 5936.6 | 11384.1
01:00 | 5254 | 5909.25 | 11163.25 | 11-04-2026
01:30 | 5084.5 | 5843.68 | 10928.18
02:00 | 4915 | 5778.11 | 10693.11
02:30 | 4812 | 5673.405 | 10485.405
03:00 | 4709 | 5568.7 | 10277.7
03:30 | 4794.5 | 5392.02 | 10186.52
04:00 | 4880 | 5215.34 | 10095.34
04:30 | 4829.5 | 5084.26 | 9913.76
05:00 | 4779 | 4953.18 | 9732.18
05:30 | 4758.025 | 5084.335 | 9842.36
06:00 | 4737.05 | 5215.49 | 9952.54
06:30 | 4823.095 | 5463.15 | 10286.245
07:00 | 4909.14 | 5710.81 | 10619.95
07:30 | 4989.985 | 5816.64 | 10806.625
08:00 | 5070.83 | 5922.47 | 10993.3
08:30 | 5166.065 | 5937.935 | 11104
09:00 | 5261.3 | 5953.4 | 11214.7
09:30 | 5312.405 | 5974.355 | 11286.76
10:00 | 5363.51 | 5995.31 | 11358.82
10:30 | 5497.02 | 6083.745 | 11580.765
11:00 | 5630.53 | 6172.18 | 11802.71
11:30 | 5922.24 | 6188.89 | 12111.13
12:00 | 6213.95 | 6205.6 | 12419.55
12:30 | 6296.63 | 6260.21 | 12556.84
13:00 | 6379.31 | 6314.82 | 12694.13
13:30 | 6387.345 | 6274.645 | 12661.99
14:00 | 6395.38 | 6234.47 | 12629.85
14:30 | 6438.36 | 6230.005 | 12668.365
15:00 | 6481.34 | 6225.54 | 12706.88
15:30 | 6503.28 | 6167.88 | 12671.16
16:00 | 6525.22 | 6110.22 | 12635.44
16:30 | 6589.13 | 6098.805 | 12687.935
17:00 | 6653.04 | 6087.39 | 12740.43
17:30 | 6851.205 | 6153.955 | 13005.16
18:00 | 7049.37 | 6220.52 | 13269.89
18:30 | 7091.435 | 6393.76 | 13485.195
19:00 | 7133.5 | 6567 | 13700.5
19:30 | 7060.5 | 6766 | 13826.5
20:00 | 7080.5 | 6763 | 13843.5
20:30 | 7032.4 | 6852.5 | 13884.9 |  | Executive Engineer
21:00 | 6984.3 | 6942 | 13926.3 |  | Network Operation Division
21:30 | 6995.65 | 6947.5 | 13943.15
22:00 | 7007 | 6953 | 13960
22:30 | 6937.25 | 6899.5 | 13836.75
23:00 | 6867.5 | 6846 | 13713.5

## En-Curve
QF-LDC-12
Date | 11-04-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3899 | 1663 | 879 | 0 | 146 | 763.95 | 80 | 3049 | 0 | 63 | 1062 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3879 | 1658 | 879 | 0 | 141 | 763.1 | 80 | 3048 | 0 | 48.5 | 887.5 | 0 | 0 | 0 | 0 | 11-04-2026
01:00 | 3859 | 1653 | 879 | 0 | 136 | 762.25 | 80 | 3047 | 0 | 34 | 713 | 0 | 0 | 0 | 0
01:30 | 3850.5 | 1651 | 879 | 0 | 133 | 762.18 | 80 | 3050.5 | 0 | 17 | 505 | 0 | 0 | 0 | 0 | Energy Generated | 290.9297 |  | MKWHr
02:00 | 3842 | 1649 | 879 | 0 | 130 | 762.11 | 80 | 3054 | 0 | 0 | 297 | 0 | 0 | 0 | 0 | Energy not Served | 4.1 |  | MKWHr
02:30 | 3849 | 1652 | 879 | 0 | 130 | 762.905 | 80 | 2972.5 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | Total Energy Requirement | 295.0297 |  | MKWHr
03:00 | 3856 | 1655 | 879 | 0 | 130 | 763.7 | 80 | 2891 | 0 | 0 | 23 | 0 | 0 | 0 | 0
03:30 | 3953 | 1649.5 | 879 | 0 | 130 | 748.02 | 80 | 2727 | 0 | 0 | 20 | 0 | 0 | 0 | 0
04:00 | 4050 | 1644 | 879 | 0 | 130 | 732.34 | 80 | 2563 | 0 | 0 | 17 | 0 | 0 | 0 | 0
04:30 | 4019 | 1634.5 | 879 | 0 | 126 | 680.26 | 80 | 2478 | 0 | 0 | 17 | 0 | 0 | 0 | 0
05:00 | 3988 | 1625 | 879 | 0 | 122 | 628.18 | 80 | 2393 | 0 | 0 | 17 | 0 | 0 | 0 | 0
05:30 | 3948 | 1629.75 | 879.5 | 0 | 120 | 679.14 | 80 | 2471.5 | 3.97 | 0 | 30.5 | 0 | 0 | 0 | 0
06:00 | 3908 | 1634.5 | 880 | 0 | 118 | 730.1 | 80 | 2550 | 7.94 | 0 | 44 | 0 | 0 | 0 | 0
06:30 | 3908.5 | 1616 | 879.5 | 0 | 116 | 743.28 | 80 | 2720.5 | 60.965 | 37.5 | 124 | 0 | 0 | 0 | 21
07:00 | 3909 | 1597.5 | 879 | 0 | 114 | 756.46 | 80 | 2891 | 113.99 | 75 | 204 | 0 | 0 | 0 | 42
07:30 | 3866 | 1576.75 | 879 | 0 | 120 | 755.575 | 80 | 2934.5 | 219.8 | 61 | 314 | 0 | 0 | 0 | 55
08:00 | 3823 | 1556 | 879 | 0 | 126 | 754.69 | 80 | 2978 | 325.61 | 47 | 424 | 0 | 0 | 0 | 68
08:30 | 3769.5 | 1578 | 879 | 0 | 129 | 751.345 | 80 | 2971.5 | 428.655 | 66 | 451 | 0 | 0 | 0 | 76.5
09:00 | 3716 | 1600 | 879 | 0 | 132 | 748 | 80 | 2965 | 531.7 | 85 | 478 | 0 | 0 | 0 | 85
09:30 | 3654.5 | 1483.5 | 879 | 0 | 139 | 746.5 | 80 | 2964.5 | 607.76 | 107.5 | 624.5 | 0 | 0 | 0 | 80.5
10:00 | 3593 | 1367 | 879 | 0 | 146 | 745 | 80 | 2964 | 683.82 | 130 | 771 | 0 | 0 | 0 | 76
10:30 | 3658 | 1436.5 | 879 | 0 | 140 | 742 | 80 | 2963.5 | 727.265 | 130 | 824.5 | 0 | 0 | 0 | 84.5
11:00 | 3723 | 1506 | 879 | 0 | 134 | 739 | 80 | 2963 | 770.71 | 130 | 878 | 0 | 0 | 0 | 93
11:30 | 3659.5 | 1564.5 | 879 | 0 | 138 | 734.5 | 80 | 2981.5 | 769.13 | 227.5 | 1077 | 0 | 0 | 0.5 | 158
12:00 | 3596 | 1623 | 879 | 0 | 142 | 730 | 80 | 3000 | 767.55 | 325 | 1276 | 0 | 0 | 1 | 223
12:30 | 3560 | 1591.5 | 879 | 0 | 144 | 729.5 | 80 | 3010.5 | 764.34 | 398 | 1398 | 0 | 0 | 2 | 259.5
13:00 | 3524 | 1560 | 879 | 0 | 146 | 729 | 80 | 3021 | 761.13 | 471 | 1520 | 0 | 0 | 3 | 296
13:30 | 3523 | 1540.5 | 879 | 0 | 146 | 729.5 | 80 | 3001.5 | 701.99 | 478.5 | 1580 | 0 | 0 | 2 | 297.5
14:00 | 3522 | 1521 | 879 | 0 | 146 | 730 | 80 | 2982 | 642.85 | 486 | 1640 | 0 | 0 | 1 | 299
14:30 | 3511.5 | 1551.25 | 879 | 0 | 158 | 741 | 80 | 2990.5 | 586.615 | 488 | 1679.5 | 0 | 0 | 3 | 340
15:00 | 3501 | 1581.5 | 879 | 0 | 170 | 752 | 80 | 2999 | 530.38 | 490 | 1719 | 0 | 0 | 5 | 381
15:30 | 3512 | 1585.5 | 879.5 | 0 | 173 | 752 | 80 | 2997 | 436.41 | 512 | 1737.75 | 0 | 0 | 6 | 390.5
16:00 | 3523 | 1589.5 | 880 | 0 | 176 | 752 | 80 | 2995 | 342.44 | 534 | 1756.5 | 0 | 0 | 7 | 400
16:30 | 3513 | 1563.25 | 879.5 | 0 | 171 | 800.5 | 80 | 2996 | 239.935 | 613.5 | 1824.25 | 0 | 0 | 7 | 283.5
17:00 | 3503 | 1537 | 879 | 0 | 166 | 849 | 80 | 2997 | 137.43 | 693 | 1892 | 0 | 0 | 7 | 167
17:30 | 3517.5 | 1556.5 | 879 | 0 | 164 | 934.5 | 80 | 3061.5 | 76.41 | 718 | 2013.25 | 0 | 0 | 4.5 | 123
18:00 | 3532 | 1576 | 879 | 0 | 162 | 1020 | 80 | 3126 | 15.39 | 743 | 2134.5 | 0 | 0 | 2 | 79
18:30 | 3584.5 | 1574.5 | 879 | 0 | 168 | 1080.5 | 80 | 3172 | 7.695 | 776 | 2159.5 | 0 | 0 | 3.5 | 302
19:00 | 3637 | 1573 | 879 | 0 | 174 | 1141 | 80 | 3218 | 0 | 809 | 2184.5 | 0 | 0 | 5 | 525
19:30 | 3469 | 1606 | 879 | 0 | 174 | 1244 | 80 | 3275 | 0 | 812 | 2280.5 | 0 | 0 | 7 | 453
20:00 | 3413 | 1654 | 879 | 0 | 172 | 1289 | 80 | 3279 | 0 | 810 | 2264.5 | 0 | 0 | 3 | 456
20:30 | 3457.5 | 1657.5 | 879 | 0 | 171 | 1335.5 | 80 | 3276 | 0 | 792.5 | 2234.4 | 0 | 0 | 1.5 | 431
21:00 | 3502 | 1661 | 879 | 0 | 170 | 1382 | 80 | 3273 | 0 | 775 | 2204.3 | 0 | 0 | 0 | 406
21:30 | 3589 | 1653.5 | 879 | 0 | 171 | 1429.5 | 80 | 3222.5 | 0 | 782.5 | 2136.15 | 0 | 0 | 0 | 342
22:00 | 3676 | 1646 | 879 | 0 | 172 | 1477 | 80 | 3172 | 0 | 790 | 2068 | 0 | 0 | 0 | 278
22:30 | 3760 | 1549.5 | 879.5 | 0 | 173 | 1486.5 | 80 | 3094 | 0 | 786.5 | 2027.75 | 0 | 0 | 0 | 252
23:00 | 3844 | 1453 | 880 | 0 | 174 | 1496 | 80 | 3016 | 0 | 783 | 1987.5 | 0 | 0 | 0 | 226
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 11-04-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 394 | 05:00 | 382 | 11:00 | Madunaghat | 403 | 08:00 | 398 | 12:00
Amtali | 415 | 04:00 | 408 | 22:00 | Meghnaghat | 395 | 04:00 | 387 | 09:00
Ashuganj | 406 | 4:00 | 393 | 11:00 | Payra | 417 | 04:00 | 411 | 12:00
Bhulta | 401 | 05:00 | 384 | 11:00 | Rahanpur | 413 | 04:00 | 400 | 22:00
Bibiana | 409 | 05:00 | 403 | 11:00 | Rampal | 405 | 04:00 | 391 | 21:00
BIPTC | 400 | 05:00 | 385 | 19:30
Bogura | 411 | 05:00 | 395 | 22:00
Gopalganj | 405 | 04:00 | 392 | 22:00
Kaliakoir | 390 | 04:00 | 379 | 11:00
Korerhat | 406 | 18:30 | 399 | 02:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 234 | 04:00 | 225 | 11:00 | Jhenaidah | 232 | 03:00 | 217 | 22:00
AKSML | 232 | 18:00 | 225 | 03:00 | Kachua | 232 | 19:00 | 227 | 11:00
Aminbazar | 235 | 03:00 | 226 | 11:00 | Kaliakoir | 236 | 04:00 | 223 | 01:00
Ashuganj | 232 | 00:00 | 225 | 11:00 | Keranigonj | 233 | 04:00 | 224 | 11:00
Ashuganj-400 | 232 | 00:00 | 225 | 11:00 | Khulna(S) | 235 | 04:00 | 221 | 22:00
Baghabari | 236 | 05:00 | 227 | 22:00 | Korerhat | 231 | 00:00 | 227 | 04:00
Barapukuria | 224 | 03:00 | 214 | 01:00 | Madunaghat | 233 | 18:00 | 227 | 03:00
Barapukuria-230 | 224 | 03:00 | 214 | 01:00 | Madunaghat-400 | 234 | 19:00 | 227 | 03:00
Barishal | 232 | 04:00 | 225 | 22:00 | Maniknagar | 231 | 04:00 | 223 | 11:00
Bheramara | 235 | 04:00 | 223 | 18:30 | Meghnaghat | 240 | 00:00 | 232 | 11:00
Bhulta | 232 | 04:00 | 224 | 11:00 | Meghnaghat-400 | 234 | 05:00 | 227 | 11:00
Bibiana | 239 | 03:00 | 232 | 11:00 | Mirsorai | 231 | 18:00 | 223 | 11:00
BIPTC | 238 | 04:00 | 222 | 23:00 | Naogaon | 225 | 04:00 | 212 | 22:00
Bogura | 231 | 04:00 | 223 | 22:00 | Purbasadipur | 228 | 19:30 | 214 | 08:00
Bogura-400 | 229 | 00:00 | 222 | 18:30 | Rajshahi | 233 | 04:00 | 222 | 22:00
Borhanuddin | 234 | 06:00 | 230 | 22:00 | Rampal | 233 | 04:00 | 220 | 22:00
BSRM | 231 | 18:00 | 226 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 231 | 18:00 | 226 | 11:00 | Rampura | 232 | 06:00 | 223 | 12:00
Cumilla(N) | 230 | 03:00 | 226 | 11:00 | Shikalbaha | 235 | 18:30 | 226 | 02:00
Faridpur | 228 | 04:00 | 219 | 22:00 | Shyampur | 233 | 04:00 | 224 | 09:00
Fenchuganj | 241 | 05:00 | 237 | 11:00 | Siddhirganj | 233 | 04:00 | 225 | 11:00
Feni | 231 | 18:00 | 225 | 11:00 | Sirajgonj | 239 | 05:00 | 233 | 21:00
Ghorashal | 240 | 01:00 | 230 | 09:00 | Sreepur | 230 | 04:00 | 221 | 19:30
Ghorashal-230 | 231 | 10:00 | 222 | 11:00 | Tongi | 233 | 04:00 | 226 | 10:00
Gopalganj | 227 | 04:00 | 220 | 12:00
GPH | 232 | 18:00 | 227 | 03:00
Haripur | 233 | 05:00 | 225 | 11:00
Hasnabad | 234 | 05:00 | 223 | 11:00
Hathazari | 232 | 19:30 | 227 | 05:00
Ishurdi | 238 | 04:00 | 225 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 04:00 | 129 | 10:00 | Madunaghat | 135 | 13:00 | 131 | 03:00
Agargaon | 139 | 04:00 | 132 | 11:00 | Magura | 138 | 05:00 | 125 | 21:00
Agrabad | 135 | 18:30 | 129 | 02:00 | Mahasthangarh | 132 | 00:00 | 126 | 18:30
AKS | 132 | 18:30 | 128 | 04:00 | Maijdee | 129 | 07:00 | 126 | 02:00
Aminbazar | 136 | 03:00 | 129 | 11:00 | Manikganj | 133 | 04:00 | 124 | 23:00
Amnura | 136 | 00:00 | 128 | 12:00 | Maniknagar | 137 | 03:00 | 130 | 12:00
Ashuganj | 140 | 00:00 | 135 | 21:00 | Matarbari | 122 | 18:30 | 110 | 00:00
Ashuganj-230 | 140 | 00:00 | 135 | 21:00 | Matuail | 135 | 03:00 | 131 | 11:00
Bagerhat | 131 | 04:00 | 117 | 23:00 | Metrorail_Motijheel | 137 | 03:00 | 130 | 12:00
Bajitpur | 134 | 04:00 | 128 | 19:00 | Metrorail_Uttara | 135 | 00:00 | 129 | 11:00
Bakerganj | 134 | 03:00 | 131 | 22:00 | Millgate | 137 | 04:00 | 130 | 09:00
Bakulia | 136 | 18:30 | 129 | 02:00 | Mirpur | 135 | 07:00 | 128 | 11:00
Banani | 135 | 04:00 | 128 | 12:00 | Mirzapur | 133 | 00:00 | 128 | 21:00
Bangabhaban | 137 | 04:00 | 130 | 12:00 | Mithapukur | 132 | 00:00 | 124 | 18:00
Barapukuria | 134 | 03:00 | 126 | 01:00 | MI_Cement | 134 | 04:00 | 125 | 11:00
Barguna | 137 | 12:00 | 130 | 22:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 135 | 04:00 | 132 | 22:00 | Mogbazar | 136 | 02:00 | 130 | 11:00
Barishal-230 | 135 | 04:00 | 131 | 22:00 | Mongla | 129 | 01:00 | 118 | 23:00
Baroaulia | 135 | 18:30 | 130 | 06:00 | Motijheel | 137 | 04:00 | 130 | 12:00
Baroirhat | 132 | 07:00 | 130 | 00:00 | Muktagacha | 129 | 00:00 | 119 | 22:00
Bashundhara | 137 | 04:00 | 129 | 11:00 | Munshiganj | 134 | 19:00 | 129 | 23:00
BashundharaCement | 135 | 00:00 | 131 | 11:00 | Muradnagar | 131 | 04:00 | 128 | 11:00
Beanibazar | 132 | 06:00 | 126 | 18:00 | Mymensingh | 133 | 05:00 | 117 | 05:00
Benapole | 133 | 04:00 | 121 | 12:00 | Nabinagar | 132 | 00:00 | 127 | 09:00
Bhaluka | 135 | 02:00 | 128 | 19:00 | Naogaon | 134 | 00:00 | 125 | 08:00
Bhandaria | 133 | 05:00 | 125 | 22:00 | Narail | 137 | 05:00 | 123 | 21:00
Bhangura | 134 | 00:00 | 127 | 22:00 | Narinda | 137 | 03:00 | 130 | 12:00
Bheramara | 138 | 03:00 | 133 | 12:00 | Narshingdi | 133 | 04:00 | 125 | 11:00
Bheramara(GK) | 137 | 00:00 | 132 | 18:30 | Natore | 133 | 00:00 | 128 | 12:00
Bhulta | 130 | 06:00 | 124 | 11:00 | Nawabganj | 137 | 04:00 | 130 | 11:00
Bog-Sherpur | 133 | 00:00 | 129 | 07:00 | Netrakona | 131 | 06:00 | 118 | 19:00
Bogura | 134 | 00:00 | 129 | 07:00 | New | 137 | 00:00 | 131 | 11:00
Bogura-230 | 134 | 00:00 | 130 | 07:00 | Niamatpur | 134 | 00:00 | 129 | 21:00
Brahmanbaria | 135 | 06:00 | 129 | 21:00 | Noapara | 134 | 04:00 | 123 | 22:00
Cantonment | 138 | 04:00 | 132 | 11:00 | Pabna | 136 | 03:00 | 130 | 13:00
Chandina | 133 | 04:00 | 130 | 11:00 | Palashbari | 130 | 04:00 | 122 | 18:00
Chandpur | 136 | 18:30 | 129 | 01:00 | Panchagarh | 137 | 20:00 | 128 | 06:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 135 | 18:00 | 132 | 00:00 | Patiya | 134 | 18:30 | 126 | 01:00
Chapai | 135 | 04:00 | 130 | 23:00 | Patuakhali | 134 | 02:00 | 131 | 08:00
Charsaidpur | 134 | 00:00 | 130 | 23:00 | Payra | 137 | 04:00 | 134 | 13:00
Chauddagram | 131 | 07:00 | 128 | 11:00 | PHP | 132 | 09:00 | 128 | 11:00
Chhatak | 132 | 04:00 | 125 | 18:00 | Postogola | 136 | 05:00 | 128 | 11:00
Chowmuhani | 130 | 19:30 | 126 | 00:00 | Pubail | 136 | 13:00 | 131 | 07:00
Chuadanga | 136 | 04:00 | 122 | 23:00 | Purbachal | 137 | 05:00 | 129 | 11:00
Coxsbazar | 120 | 18:30 | 110 | 00:00 | Purbasadipur | 131 | 00:00 | 124 | 08:00
Cumilla(N) | 134 | 07:00 | 131 | 03:00 | Rahanpur | 137 | 00:00 | 133 | 22:00
Cumilla(S) | 133 | 04:00 | 123 | 16:00 | Rahanpur-400 | 138 | 03:00 | 133 | 22:00
Daganbhuiyan | 130 | 07:00 | 127 | 02:00 | Rahim | 134 | 00:00 | 131 | 11:00
Daudkandi | 130 | 04:00 | 126 | 11:00 | Rajbari | 131 | 04:00 | 125 | 13:00
DhakaUniversity | 134 | 02:00 | 129 | 11:00 | Rajendrapur | 135 | 05:00 | 128 | 18:00
Dhamrai | 132 | 00:00 | 127 | 11:00 | Rajshahi | 134 | 03:00 | 126 | 13:00
Dhanmondi | 136 | 02:00 | 132 | 11:00 | Rajshahi-230 | 135 | 04:00 | 128 | 12:00
Dohazari | 131 | 18:30 | 120 | 06:00 | Ramganj | 131 | 18:30 | 127 | 00:00
Faridpur | 131 | 05:00 | 127 | 14:00 | Rampur | 135 | 18:30 | 128 | 02:00
Fatullah | 135 | 04:00 | 128 | 11:00 | Rampura | 134 | 00:00 | 129 | 12:00
Fenchuganj | 137 | 05:00 | 133 | 22:00 | Rangamati | 135 | 18:30 | 131 | 02:00
Feni | 130 | 02:00 | 126 | 11:00 | Rangpur | 131 | 00:00 | 124 | 18:30
Feni-230 | 130 | 07:00 | 126 | 11:00 | Ruppur | 138 | 03:00 | 132 | 13:00
Ghatail | 130 | 00:00 | 119 | 22:00 | Saidpur | 132 | 03:00 | 124 | 18:00
Ghorashal | 138 | 01:00 | 134 | 09:00 | Satkhira | 134 | 12:00 | 118 | 22:00
Goalpara | 135 | 04:00 | 124 | 22:00 | Satmasjid | 138 | 02:00 | 132 | 11:00
Gollamari | 134 | 04:00 | 125 | 22:00 | Savar | 134 | 07:00 | 126 | 12:00
Gopalganj | 134 | 05:00 | 126 | 21:00 | SevenRings | 138 | 05:00 | 133 | 09:00
Gopalganj-400 | 135 | 04:00 | 130 | 12:00 | ShahCement | 134 | 00:00 | 130 | 23:00
Gulshan | 134 | 03:00 | 129 | 11:00 | Shahjadpur | 138 | 00:00 | 133 | 10:00
Halishahar | 135 | 18:30 | 129 | 02:00 | Shahjibazar | 136 | 04:00 | 129 | 23:00
Haripur | 135 | 03:00 | 132 | 09:00 | Shahmirpur | 134 | 17:00 | 130 | 00:00
HaripurSBU | 135 | 00:00 | 132 | 09:00 | Shariatpur | 134 | 04:00 | 126 | 22:00
Hasnabad | 135 | 00:00 | 127 | 11:00 | Sherpur | 125 | 00:00 | 112 | 23:00
Hathazari | 136 | 19:30 | 132 | 06:00 | Shikalbaha | 125 | 18:30 | 118 | 02:00
Hatirjheel | 135 | 04:00 | 129 | 12:00 | Shikalbaha-230 | 136 | 17:00 | 130 | 02:00
Ishurdi | 139 | 03:00 | 133 | 18:30 | Shitalakhya | 134 | 03:00 | 125 | 11:00
Jaldhaka | 129 | 13:00 | 121 | 08:00 | Sholosohor | 135 | 18:30 | 131 | 02:00
Jamalpur | 127 | 00:00 | 116 | 23:00 | Shyampur | 133 | 00:00 | 127 | 11:00
Jashore | 133 | 04:00 | 122 | 22:00 | Shyampur-230 | 134 | 05:00 | 128 | 11:00
Jhenaidah | 138 | 04:00 | 126 | 17:00 | Siddhirganj | 135 | 02:00 | 131 | 11:00
Jhenaidah-230 | 139 | 04:00 | 128 | 21:00 | Sirajganj | 133 | 00:00 | 126 | 18:00
Joydebpur | 134 | 19:00 | 127 | 11:00 | Sonargaon | 132 | 00:00 | 131 | 11:00
Joypurhat | 129 | 04:00 | 122 | 08:00 | Sreemongol | 136 | 04:00 | 129 | 22:00
Juldah | 135 | 18:30 | 129 | 08:00 | Sreepur | 138 | 05:00 | 130 | 19:30
Kabirpur | 140 | 13:00 | 128 | 09:00 | Srinagar | 137 | 03:00 | 130 | 12:00
Kachua | 132 | 18:00 | 129 | 01:00 | SSM | 140 | 18:30 | 136 | 08:00
Kaliakoir | 139 | 07:00 | 130 | 11:00 | Sunamganj | 130 | 06:00 | 123 | 18:00
Kaliganj | 137 | 02:00 | 127 | 22:00 | Sylhet | 134 | 05:00 | 129 | 18:30
Kallyanpur | 133 | 00:00 | 128 | 23:00 | Sylhet-132 | 133 | 05:00 | 129 | 18:00
Kalurghat | 136 | 18:30 | 131 | 03:00 | Tangail | 129 | 00:00 | 123 | 22:00
Kamrangirchar | 137 | 03:00 | 127 | 11:00 | Taraganj | 130 | 00:00 | 121 | 07:00
Kaptai | N/A | N/A | N/A | N/A | Tasnim | 134 | 05:00 | 130 | 21:00
Kasba | 131 | 07:00 | 126 | 11:00 | Thakurgaon | 136 | 13:00 | 127 | 06:00
Kazla | 137 | 05:00 | 130 | 12:00 | TK | 136 | 18:30 | 131 | 06:00
Keranigonj | 138 | 05:00 | 131 | 11:00 | Tongi | 138 | 04:00 | 132 | 11:00
Khagrachori | 133 | 18:30 | 130 | 02:00 | Ullahpara | 135 | 03:00 | 128 | 18:00
Khulna | 133 | 05:00 | 124 | 22:00 | Ullon | 134 | 04:00 | 129 | 11:00
Khulna(S) | 135 | 04:00 | 125 | 22:00 | Uttara | 135 | 00:00 | 129 | 11:00
Khulshi | 134 | 18:30 | 127 | 08:00 | UttaraNew | 135 | 00:00 | 129 | 11:00
Kishoreganj | 134 | 04:00 | 125 | 19:00 | Zigatola | 137 | 02:00 | 130 | 12:00
Kodda | 138 | 12:00 | 126 | 09:00
Korerhat | 134 | 18:30 | 131 | 03:00
KSRM | 136 | 18:30 | 130 | 07:00
Kulaura | 137 | 06:00 | 132 | 18:00
Kurigram | 128 | 14:00 | 120 | 18:00
Kushtia | 134 | 05:00 | 129 | 18:00
Laksam | 132 | 18:00 | 128 | 02:00
Lakshmipur | 128 | 06:00 | 126 | 00:00
Lalbag | 137 | 04:00 | 130 | 12:00
Lalmonirhat | 130 | 02:00 | 119 | 18:00
Madanganj | 135 | 00:00 | 131 | 11:00
Madaripur | 134 | 04:00 | 130 | 12:00
Madartek | 134 | 04:00 | 128 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division