## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 15-04-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-04-2026 | during | 15-04-2026 | during | 15-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 409 | 412 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 180 | 450 | 450 | 450 | 450 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 300 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 0 | 53.97 | 53.97 | 17 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 121 | 137 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 26 | 22 | 33 | 33 | 29 | 29 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 49 | 50 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 260 | 293 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 88 | 88 | Engine Problem
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 17 | 162 | 162 | 35 | 35 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 33 | 0 | 33 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 400 | 460 | 584 | 584 | 460 | 460 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 142 | 142 | 160 | 160 | 125 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2339 | 2430 | 5948.22 | 5915.22 | 2762.55 | 2800.55
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 25.5 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 217 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 51 | 105 | 105 | 51 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 36 | 54 | 56 | 64 | 30 | 30 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 67 | 68 | 68 | 34 | 68 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 32 | 36 | 5 | 24 | 40 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 33 | 38 | 108 | 108 | 50 | 90 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.99 | 0 | 3.72 | 0 | 3.72 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 0 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 56 | 54 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 86 | 116 | 116 | 17 | 116 | Liquid fuel shortage
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 17 | 163 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 301 | 551 | 1224 | 1224 | 310 | 310 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 4 | 10 | 6 | 0 | 6 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 160 | 200 | 160 | 200 | 160 | 160 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1152.49 | 1704 | 3067.58 | 3111.86 | 1376.22 | 1543.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 181 | 203 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 0 | 0 | 240 | 240 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 335 | 345 | 342.01 | 342.01 | 342.01 | 342.01 | machine problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 380 | 393 | 393 | 393 | 393 | 393 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 39 | 42 | 41.65 | 41.65 | 41.65 | 41.65 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 44 | 5 | 52.82 | 52.82 | 21 | 21 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 172 | 81 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 138 | 150 | 150 | 20 | 140 | Machine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 20 | 36 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 196 | 200 | 200 | 35 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 176 | 178 | 84 | 76 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 9 | 113 | 113 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 34 | 115 | 115 | 17 | 51 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 46 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.745 | 1510 | 1731 | 2654.18 | 2576.18 | 1611.66 | 1840.66
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-04-2026 | during | 15-04-2026 | during | 15-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 33 | 98 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.75 | 0 | 2.3 | 0 | 2.3 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 31 | 48 | 60 | 60 | 10 | 10 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 78 | 69 | 10 | 10 | 70 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 43.49 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 187.24 | 244 | 352.3 | 304 | 157.3 | 109
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 154 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 102 | 100 | 100 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 81 | 86 | 86 | 53 | 53 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 97 | 96 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 16 | 16 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 349 | 325 | 350 | 350 | 357 | 357 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1117 | 1187 | 1287 | 1287 | 1070 | 1070
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 909 | 908 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 20 | 27 | 27 | 27 | 27 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 43 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 171 | 247 | 410 | 410 | 150 | 150 | Gas Restrction
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 25 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 617.1 | 602 | 617.1 | 617.1 | 617.1 | 617.1 | U#1 Under Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1722.1 | 1820 | 2965.1 | 2880.1 | 1944.2 | 1859.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 306 | 404 | 250 | 300 | 300 | 300 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 99 | 96 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 130 | 130 | 130 | 130 | STG Under Maintenance
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1210 | 1197 | 1244 | 1244 | 1244 | 1244 | Machine Problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 277 | 307 | 307 | 287 | 287 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2289 | 2341 | 2412 | 2461 | 2298 | 2297
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 60.49 | 0 | 62 | 0 | 62 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 40 | 38 | 40 | 40 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 14 | 30 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 160 | 160 | 214 | 214 | 161 | 161 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 140 | 220 | 220 | 140 | 140 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 365 | 383 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 51 | 90 | 90 | 0 | 51 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 1 | 50 | 113 | 113 | 35 | 50 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 35 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.51 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1510 | 1478 | 1435.88 | 1435.88 | 1362 | 1362 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 42.96 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 111 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2446.96 | 2365 | 3234.37 | 3005.87 | 2442.91 | 2280.41
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 55 | 52 | 55 | 55 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 92 | 113 | 113 | 35 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.1 | 0 | 6.8 | 0 | 6.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 114 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 157 | 0 | 200 | 0 | 200 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 284.1 | 258 | 533.8 | 297 | 436.8 | 200
System Total |  |  |  |  | 28823.2 | 29269.987 | 13047.89 | 14080 | 22454.55 | 21838.23 | 14099.64 | 14000.32
Forecast Scenario (15-04-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13183 |  | 971 |  | 14200
|  |  |  | 1:00 | 12440 |  | 1203.3 |  | 13700
|  |  |  | 2:00 | 12271 |  | 887.195 |  | 13200
|  |  |  | 3:00 | 12312 |  | 657.04 |  | 13000
|  |  |  | 4:00 | 12227 |  | 594.965 |  | 12850
|  |  |  | 5:00 | 12157 |  | 375.315 |  | 12550
|  |  |  | 6:00 | 12160 |  | 162.35 |  | 12330
|  |  |  | 7:00 | 12262 |  | 275.04 |  | 12550
|  |  |  | 8:00 | 12054 |  | 330.43 |  | 12400
|  |  |  | 9:00 | 12263 |  | 274.085 |  | 12550
|  |  |  | 10:00 | 12621 |  | 218.695 |  | 12850
|  |  |  | 11:00 | 12796 |  | 433.57 |  | 13250
|  |  |  | 12:00 | 13050 |  | 621 |  | 13700
|  |  |  | 13:00 | 13040 |  | 773.55 |  | 13850
|  |  |  | 14:00 | 12904 |  | 951.18 |  | 13900
|  |  |  | 15:00 | 12902 |  | 1000.84 |  | 13950
|  |  |  | 16:00 | 12873 |  | 885.285 |  | 13800
|  |  |  | 17:00 | 12869 |  | 602.605 |  | 13500
|  |  |  | 18:00 | 12863 |  | 465.085 |  | 13350
|  |  |  | 18:30 | 13900 |  | 716 |  | 14650
|  |  |  | 19:00 | 13900 |  | 812 |  | 14750
|  |  |  | 19:30 | 13950 |  | 907 |  | 14900
|  |  |  | 20:00 | 13980 |  | 974 |  | 15000
|  |  |  | 21:00 | 14000 |  | 1146 |  | 15200
|  |  |  | 22:00 | 13964 |  | 1085 |  | 15100
|  |  |  | 23:00 | 13558 |  | 1091 |  | 14700
Probable Maximum Temperature: |  |  | 35.50°C
Probable Maximum Demand at Day Peak: |  |  | 13700.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 1146
Probable Maximum Demand at Evening Peak: |  |  | 15200.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14000.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 297.26019 MKWHr. |  | 230 | 150 | 155 | 117 | 65 | 155 | 60 | 114 | 100 | 1146
*** This report is generated digitally from Operation Information System (OIS) at 10:24 hrs on 15-04-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 14-04-2026 | [28 empty] | Date: | 14-04-2026 | [28 empty] | Date: | 14-04-2026 | [28 empty] | Date: | 14-04-2026 | [28 empty] | Date: | 14-04-2026 | [17 empty] | Date: | 14-04-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 17 | 149 | 139 | 283 | 55 | 0 | 17 | 0 | 200 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 24 | 15 | 0 | 400 | 96 | 16 | 49 | 0 | 2 | 67 | 54 | 18 | 12 | 12 | 0 | 70 | 92 | 24 | 160 | 72 | 0 | 50 | 25.5 | 58 | 221 | 0 | 0 | 0 | 290 | 0 | 20 | 0 | 375 | 0 | 345 | 51 | 0 | 196 | 0 | 17 | 98 | 57 | 0 | 20 | 0 | 190 | 0 | 0 | 22 | 300 | 0 | 372 | 41 | 30 | 158 | 0 | 12 | 0 | 53 | 30 | 101 | 0 | 98 | 0 | 9 | 35 | 11 | 0 | 0 | 12 | 6348.5 | 881 | 140 | 0 | 25 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 597 | 0 | 0 | 0 | 1451.84 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 28 | 0 | 0 | 0 | 23 | 0 | 0 | 160 | 0 | 0 | 0 | 140 | 0 | 390 | 0 | 0 | 0 | 52 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 307 | 130 | 220 | 0 | 390 | 1244 | 17 | 6491.84 | 12840.34 | 80.46
01:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 149 | 140 | 293 | 55 | 0 | 17 | 0 | 200 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 24 | 21 | 0 | 370 | 96 | 16 | 51 | 0 | 1 | 62 | 54 | 18 | 12 | 12 | 0 | 70 | 93 | 26 | 160 | 36 | 0 | 22 | 25.5 | 68 | 221 | 0 | 0 | 0 | 290 | 0 | 20 | 0 | 393 | 0 | 345 | 51 | 0 | 181 | 0 | 17 | 0 | 17 | 0 | 20 | 0 | 192 | 0 | 0 | 22 | 300 | 0 | 372 | 41 | 30 | 156 | 0 | 12 | 0 | 53 | 30 | 101 | 0 | 98 | 0 | 57 | 9 | 20 | 0 | 0 | 12 | 6160.5 | 881 | 141 | 0 | 25 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584 | 0 | 0 | 0 | 1498.57 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 23 | 0 | 0 | 160 | 0 | 0 | 0 | 140 | 0 | 360 | 0 | 0 | 0 | 52 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 293 | 130 | 180 | 0 | 301 | 1244 | 17 | 6280.57 | 12441.07 | 80.44
02:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 0 | 0 | 149 | 140 | 293 | 55 | 0 | 17 | 0 | 200 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 24 | 21 | 0 | 370 | 82 | 16 | 40 | 0 | 1 | 0 | 45 | 18 | 12 | 12 | 0 | 70 | 92 | 27 | 160 | 17 | 0 | 19 | 25.5 | 68 | 222 | 0 | 0 | 0 | 290 | 0 | 20 | 0 | 393 | 0 | 345 | 51 | 0 | 192 | 0 | 17 | 0 | 17 | 0 | 20 | 0 | 184 | 0 | 0 | 22 | 295 | 0 | 372 | 41 | 30 | 132 | 0 | 12 | 0 | 53 | 30 | 100 | 0 | 98 | 0 | 57 | 9 | 20 | 0 | 0 | 12 | 6015.5 | 881 | 140 | 0 | 25 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 589 | 0 | 0 | 0 | 1506.98 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 18 | 0 | 0 | 160 | 0 | 0 | 0 | 140 | 0 | 360 | 0 | 0 | 0 | 52 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 275 | 130 | 180 | 0 | 301 | 1244 | 17 | 6256.98 | 12272.48 | 80.42
03:00 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 149 | 140 | 293 | 55 | 0 | 17 | 0 | 200 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 24 | 21 | 0 | 390 | 92 | 16 | 36 | 0 | 0 | 0 | 45 | 18 | 12 | 12 | 0 | 70 | 75 | 28 | 160 | 17 | 0 | 19 | 25.5 | 58 | 222 | 0 | 0 | 0 | 290 | 0 | 20 | 0 | 393 | 0 | 345 | 51 | 0 | 195 | 0 | 0 | 0 | 17 | 0 | 20 | 0 | 182 | 0 | 0 | 22 | 300 | 0 | 372 | 41 | 30 | 150 | 0 | 12 | 0 | 30 | 30 | 100 | 0 | 98 | 0 | 57 | 9 | 21 | 0 | 0 | 0 | 5989.5 | 881 | 140 | 0 | 25 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 596 | 0 | 0 | 0 | 1513.62 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 140 | 0 | 380 | 0 | 0 | 0 | 52 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 277 | 130 | 220 | 0 | 301 | 1244 | 17 | 6323.62 | 12313.12 | 80.4
04:00 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 0 | 0 | 149 | 140 | 293 | 55 | 0 | 17 | 0 | 200 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 24 | 21 | 0 | 390 | 87 | 16 | 38 | 0 | 2 | 0 | 45 | 0 | 12 | 12 | 0 | 70 | 55 | 28 | 160 | 17 | 0 | 19 | 25.5 | 36 | 223 | 0 | 0 | 0 | 290 | 0 | 20 | 0 | 393 | 0 | 345 | 51 | 0 | 185 | 0 | 0 | 0 | 17 | 0 | 20 | 0 | 184 | 0 | 0 | 23 | 300 | 0 | 372 | 41 | 30 | 157 | 0 | 12 | 0 | 53 | 30 | 99 | 0 | 98 | 0 | 59 | 9 | 21 | 0 | 0 | 0 | 5956.5 | 888 | 145 | 0 | 25 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588 | 0 | 0 | 0 | 1512.71 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 140 | 0 | 380 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 275 | 130 | 220 | 0 | 301 | 1244 | 17 | 6271.71 | 12228.21 | 80.38
05:00 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 0 | 417 | 0 | 0 | 0 | 0 | 149 | 140 | 293 | 55 | 0 | 17 | 0 | 200 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 24 | 21 | 0 | 390 | 84 | 16 | 38 | 0 | 6 | 0 | 45 | 0 | 12 | 12 | 0 | 70 | 55 | 28 | 160 | 17 | 0 | 19 | 25.5 | 34 | 223 | 0 | 0 | 0 | 290 | 0 | 20 | 0 | 330 | 0 | 345 | 51 | 0 | 186 | 10 | 0 | 0 | 17 | 0 | 20 | 0 | 180 | 0 | 0 | 23 | 295 | 0 | 372 | 41 | 30 | 154 | 0 | 12 | 0 | 53 | 30 | 101 | 0 | 98 | 0 | 59 | 9 | 22 | 0 | 0 | 0 | 5896.5 | 888 | 145 | 0 | 25 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595 | 0 | 0 | 0 | 1499.95 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 140 | 0 | 380 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 275 | 130 | 220 | 0 | 301 | 1244 | 17 | 6261.95 | 12158.45 | 80.37
06:00 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 149 | 144 | 293 | 55 | 0 | 17 | 0 | 200 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 142 | 0 | 21 | 0 | 390 | 85 | 16 | 38 | 0 | 6 | 0 | 45 | 0 | 12 | 12 | 0.1 | 72 | 55 | 28 | 160 | 17 | 0 | 19 | 25.5 | 34 | 223 | 0 | 0 | 0 | 290 | 1 | 20 | 8 | 325 | 0 | 345 | 51 | 3 | 190 | 10 | 0 | 0 | 17 | 0 | 20 | 0 | 162 | 0 | 1 | 23 | 290 | 0 | 372 | 42 | 30 | 154 | 0 | 12 | 0 | 53 | 30 | 100 | 0 | 98 | 0 | 59 | 9 | 23 | 0 | 0.84 | 0 | 5883.44 | 892 | 154 | 0 | 25 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49 | 595 | 0 | 0 | 0 | 1496.05 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 3.5 | 0 | 0 | 0 | 0.76 | 160 | 0 | 0 | 0 | 140 | 0 | 380 | 0 | 0.07 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 99 | 277 | 130 | 220 | 0 | 301 | 1244 | 17 | 6279.87 | 12163.31 | 80.36
07:00 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 149 | 144 | 293 | 55 | 0 | 17 | 0 | 200 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 4 | 142 | 26 | 22 | 0 | 390 | 97 | 16 | 37 | 0 | 3 | 0 | 44 | 0 | 12 | 12 | 0.79 | 74 | 55 | 35 | 160 | 17 | 0 | 19 | 25.5 | 34 | 222 | 0 | 0 | 0 | 291 | 4 | 20 | 26 | 393 | 0 | 345 | 51 | 5 | 187 | 20 | 0 | 0 | 17 | 0 | 20 | 0 | 154 | 0 | 14 | 22 | 290 | 0 | 372 | 41 | 30 | 158 | 2 | 12 | 0 | 53 | 30 | 0 | 0 | 98 | 0 | 59 | 9 | 23 | 0.35 | 7.83 | 0 | 5928.47 | 892 | 159 | 0 | 25 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 6.56 | 602 | 0 | 0 | 0 | 1463.42 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 3.5 | 6 | 0 | 0 | 8.46 | 160 | 0 | 0 | 0 | 140 | 0 | 380 | 0 | 0.73 | 0 | 53 | 0 | 6 | 0 | 0 | 0 | 0 | 0.9 | 23 | 0 | 110 | 307 | 130 | 220 | 0 | 301 | 1244 | 17 | 6341.57 | 12270.04 | 80.35
08:00 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 149 | 128 | 293 | 55 | 0 | 17 | 0 | 200 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 13 | 142 | 26 | 21 | 0 | 340 | 85 | 16 | 38 | 0 | 0 | 0 | 44 | 0 | 12 | 12 | 1.83 | 70 | 55 | 35 | 160 | 17 | 0 | 19 | 25.5 | 34 | 221 | 0 | 0 | 0 | 292 | 9 | 20 | 26 | 310 | 0 | 275 | 51 | 5 | 181 | 34 | 0 | 0 | 17 | 0 | 20 | 0 | 156 | 0 | 27 | 22 | 295 | 0 | 372 | 42 | 30 | 151 | 3 | 0 | 0 | 76 | 30 | 0 | 0 | 98 | 0 | 59 | 9 | 17 | 0.87 | 20.04 | 0 | 5736.24 | 905 | 160 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 12.24 | 594 | 0 | 0 | 0 | 1465.47 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 19.98 | 38 | 0 | 0 | 23.33 | 160 | 0 | 0 | 0 | 140 | 0 | 346 | 0 | 1.97 | 0 | 55 | 0 | 6 | 0 | 0 | 0 | 0 | 2.6 | 41 | 0 | 100 | 266 | 130 | 220 | 0 | 305 | 1232 | 17 | 6323.59 | 12059.83 | 80.34
09:00 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 149 | 128 | 293 | 55 | 4 | 17 | 0 | 200 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 14 | 142 | 26 | 21 | 0 | 340 | 91 | 16 | 37 | 0 | 1 | 0 | 37 | 0 | 12 | 12 | 2.69 | 70 | 55 | 37 | 160 | 17 | 0 | 19 | 25.5 | 34 | 217 | 0 | 0 | 0 | 300 | 14 | 20 | 26 | 318 | 0 | 345 | 51 | 5 | 196 | 39 | 0 | 0 | 17 | 0 | 20 | 0 | 156 | 0 | 49 | 21 | 300 | 0 | 374 | 42 | 30 | 140 | 3 | 0 | 0 | 80 | 30 | 0 | 0 | 98 | 0 | 59 | 9 | 23 | 1.46 | 20.49 | 0 | 5830.14 | 909 | 162 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 619 | 0 | 0 | 0 | 1454 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 34.96 | 69 | 0 | 0 | 36.82 | 160 | 0 | 0 | 0 | 140 | 0 | 363 | 0 | 3.49 | 0 | 53 | 0 | 18 | 0 | 0 | 0 | 0 | 4.1 | 76 | 0 | 105 | 275 | 130 | 180 | 0 | 305 | 1210 | 17 | 6437.37 | 12267.51 | 80.33
10:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 1 | 149 | 108 | 277 | 55 | 17 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 28 | 142 | 26 | 14 | 0 | 400 | 94 | 16 | 39 | 0 | 0 | 0 | 37 | 0 | 12 | 12 | 3.52 | 70 | 55 | 37 | 160 | 17 | 0 | 19 | 25.5 | 34 | 216 | 0 | 0 | 0 | 305 | 16 | 20 | 105 | 340 | 0 | 340 | 51 | 6 | 199 | 40 | 0 | 0 | 18 | 0 | 20 | 0 | 162 | 0 | 38 | 21 | 305 | 0 | 348 | 42 | 30 | 143 | 4 | 8 | 0 | 79 | 30 | 0 | 0 | 98 | 0 | 69 | 9 | 23 | 1.06 | 22.89 | 0 | 6054.97 | 909 | 163 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 617.1 | 0 | 0 | 0 | 1477 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 45.5 | 89 | 0 | 0 | 50.47 | 160 | 0 | 0 | 0 | 140 | 0 | 371 | 0 | 4.71 | 0 | 55 | 0 | 29 | 0 | 0 | 0 | 0 | 5 | 92 | 0 | 107 | 276 | 130 | 220 | 0 | 304 | 1200 | 17 | 6569.78 | 12624.75 | 80.31
11:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 17 | 149 | 114 | 260 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 32 | 142 | 26 | 14 | 0 | 400 | 96 | 16 | 33 | 0 | 1 | 0 | 37 | 0 | 12 | 12 | 3.82 | 70 | 55 | 37 | 160 | 17 | 0 | 19 | 25.5 | 34 | 217 | 0 | 0 | 0 | 300 | 15 | 20 | 153 | 322 | 0 | 340 | 51 | 26 | 193 | 40 | 0 | 0 | 17 | 4 | 20 | 0 | 162 | 0 | 54 | 21 | 310 | 0 | 348 | 42 | 30 | 156 | 10 | 17 | 0 | 79 | 30 | 0 | 0 | 97 | 0 | 78 | 9 | 23 | 0.5 | 31.51 | 0 | 6161.33 | 908 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 617.1 | 0 | 0 | 0 | 1490 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 54.7 | 110 | 0 | 0 | 44.35 | 160 | 0 | 0 | 0 | 140 | 0 | 357 | 0 | 5 | 0 | 56 | 35 | 33 | 0 | 0 | 0 | 0 | 6.7 | 112 | 0 | 107 | 275 | 130 | 220 | 0 | 306 | 1200 | 17 | 6638.85 | 12800.18 | 80.29
12:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 17 | 17 | 149 | 121 | 260 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 33 | 142 | 26 | 14 | 0 | 400 | 90 | 16 | 33 | 0 | 4 | 0 | 36 | 0 | 12 | 10 | 3.99 | 70 | 56 | 32 | 160 | 17 | 0 | 19 | 25.5 | 34 | 215 | 0 | 0 | 0 | 301 | 18 | 20 | 172 | 380 | 0 | 335 | 51 | 44 | 181 | 39 | 0 | 0 | 17 | 9 | 20 | 0 | 176 | 0 | 46 | 20 | 310 | 0 | 349 | 42 | 30 | 152 | 12 | 17 | 0 | 78 | 30 | 0 | 0 | 97 | 0 | 78 | 31 | 33 | 1.75 | 43.49 | 0 | 6305.73 | 909 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 617.1 | 0 | 0 | 0 | 1510 | 0 | 40 | 0 | 0 | 1 | 0 | 0 | 14 | 0 | 60.49 | 111 | 0 | 0 | 42.96 | 160 | 0 | 0 | 0 | 140 | 0 | 365 | 0 | 2.51 | 0 | 55 | 35 | 30 | 0 | 0 | 0 | 0 | 7.1 | 157 | 0 | 99 | 307 | 130 | 220 | 0 | 306 | 1210 | 17 | 6742.16 | 13047.89 | 80.27
13:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 17 | 149 | 121 | 277 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 19 | 142 | 26 | 14 | 0 | 450 | 100 | 16 | 37 | 0 | 7 | 0 | 37 | 0 | 12 | 12 | 1.97 | 69 | 55 | 37 | 160 | 17 | 0 | 19 | 25.5 | 34 | 214 | 0 | 0 | 0 | 301 | 18 | 20 | 153 | 270 | 0 | 335 | 51 | 23 | 194 | 39 | 14 | 0 | 18 | 9 | 20 | 0 | 186 | 0 | 27 | 30 | 310 | 0 | 325 | 42 | 30 | 152 | 5 | 17 | 0 | 76 | 30 | 0 | 0 | 97 | 14 | 69 | 46 | 33 | 1.5 | 45.04 | 0 | 6239.01 | 908 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 617.1 | 0 | 0 | 0 | 1505 | 0 | 41 | 0 | 0 | 33 | 0 | 0 | 14 | 0 | 54.16 | 103 | 0 | 0 | 58.76 | 160 | 0 | 0 | 0 | 140 | 0 | 366 | 0 | 4.98 | 0 | 52 | 35 | 32 | 0 | 0 | 0 | 0 | 6.9 | 152 | 0 | 96 | 307 | 130 | 220 | 0 | 306 | 1222 | 17 | 6805.9 | 13044.91 | 80.25
14:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 17 | 149 | 135 | 277 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 19 | 142 | 22 | 14 | 0 | 420 | 87 | 16 | 38 | 0 | 15 | 0 | 44 | 0 | 12 | 12 | 3.31 | 69 | 54 | 35 | 160 | 17 | 0 | 19 | 25.5 | 34 | 214 | 0 | 0 | 0 | 300 | 16 | 20 | 56 | 270 | 0 | 335 | 51 | 17 | 198 | 37 | 17 | 0 | 19 | 9 | 20 | 0 | 180 | 0 | 28 | 35 | 305 | 0 | 325 | 42 | 30 | 151 | 11 | 17 | 0 | 76 | 30 | 0 | 0 | 97 | 17 | 69 | 47 | 33 | 1.73 | 23.67 | 0 | 6123.21 | 908 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 617.1 | 0 | 0 | 0 | 1508 | 0 | 45 | 0 | 35 | 35 | 0 | 0 | 14 | 0 | 51.32 | 99 | 0 | 0 | 51.47 | 160 | 0 | 0 | 0 | 140 | 0 | 351 | 0 | 4.36 | 0 | 52 | 35 | 12 | 0 | 0 | 0 | 0 | 6 | 112 | 0.52 | 89 | 307 | 125 | 220 | 0 | 305 | 1222 | 17 | 6784.77 | 12907.98 | 80.23
15:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 17.5 | 17 | 149 | 135 | 260 | 55 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 24 | 142 | 22 | 21 | 0 | 450 | 91 | 16 | 37 | 0 | 15 | 0 | 45 | 0 | 12 | 12 | 2.37 | 69 | 55 | 35 | 160 | 17 | 0 | 19 | 25.5 | 34 | 211 | 0 | 0 | 0 | 302 | 13 | 18 | 53 | 360 | 0 | 335 | 51 | 5 | 206 | 41 | 17 | 0 | 17 | 0 | 20 | 0 | 182 | 0 | 42 | 35 | 320 | 0 | 325 | 42 | 30 | 152 | 3 | 17 | 0 | 76 | 30 | 0 | 0 | 96 | 17 | 69 | 46 | 43 | 1.4 | 26.15 | 0 | 6204.92 | 908 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 606 | 0 | 0 | 0 | 1520 | 0 | 37 | 0 | 35 | 35 | 0 | 0 | 14 | 0 | 41.22 | 33 | 0 | 0 | 37.27 | 160 | 0 | 0 | 0 | 140 | 0 | 394 | 0 | 3.44 | 0 | 52 | 35 | 23 | 0 | 0 | 0 | 0 | 5 | 77 | 0.19 | 100 | 307 | 125 | 220 | 0 | 306 | 1215 | 17 | 6700.12 | 12905.04 | 80.21
16:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 17.5 | 17 | 149 | 134 | 260 | 55 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 15 | 142 | 22 | 21 | 0 | 500 | 94 | 16 | 38 | 0 | 15 | 0 | 45 | 0 | 12 | 12 | 1.41 | 70 | 54 | 36 | 160 | 17 | 0 | 19 | 20 | 34 | 212 | 0 | 0 | 0 | 302 | 8 | 15 | 53 | 375 | 0 | 338 | 51 | 5 | 193 | 41 | 18 | 0 | 24 | 0 | 19 | 0 | 176 | 0 | 26 | 35 | 320 | 0 | 325 | 42 | 30 | 152 | 3 | 17 | 0 | 78 | 30 | 100 | 0 | 95 | 2 | 69 | 46 | 70 | 0.84 | 20.94 | 3 | 6309.69 | 908 | 200 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 595 | 0 | 0 | 0 | 1513 | 0 | 37 | 0 | 35 | 35 | 0 | 0 | 14 | 0 | 23.58 | 47 | 0 | 0 | 21.95 | 160 | 0 | 0 | 0 | 140 | 0 | 357 | 0 | 2.44 | 0 | 52 | 35 | 14 | 0 | 0 | 0 | 0 | 2.8 | 64 | 0.26 | 101 | 307 | 125 | 220 | 0 | 306 | 1205 | 17 | 6569.03 | 12878.72 | 80.19
17:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 17.5 | 17 | 149 | 135 | 270 | 55 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 6 | 142 | 22 | 21 | 0 | 450 | 89 | 16 | 37 | 0 | 17 | 0 | 45 | 0 | 12 | 12 | 0.53 | 70 | 55 | 36 | 160 | 17 | 0 | 19 | 17 | 34 | 213 | 0 | 0 | 0 | 300 | 2 | 20 | 53 | 393 | 0 | 338 | 51 | 5 | 181 | 41 | 17 | 0 | 73 | 1 | 17 | 0 | 166 | 0 | 11 | 35 | 315 | 0 | 325 | 42 | 30 | 151 | 1 | 17 | 0 | 80 | 30 | 101 | 0 | 95 | 17 | 69 | 48 | 71 | 0.2 | 7.72 | 11 | 6296.95 | 909 | 210 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 585 | 0 | 0 | 0 | 1488 | 0 | 38 | 0 | 35 | 35 | 0 | 0 | 14 | 0 | 10.41 | 21 | 0 | 0 | 9.74 | 160 | 0 | 0 | 0 | 140 | 0 | 343 | 0 | 0.89 | 0 | 52 | 92 | 5 | 81 | 0 | 0 | 0 | 1.1 | 35 | 0.09 | 97 | 300 | 125 | 220 | 0 | 306 | 1205 | 17 | 6566.23 | 12863.18 | 80.17
18:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 17.5 | 17 | 149 | 134 | 293 | 55 | 17 | 17 | 0 | 180 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 1 | 142 | 22 | 21 | 0 | 450 | 85 | 16 | 38 | 0 | 11 | 67 | 49 | 0 | 12 | 12 | 0 | 70 | 54 | 37 | 160 | 17 | 0 | 28 | 17 | 36 | 215 | 0 | 0 | 0 | 312 | 0 | 41 | 53 | 350 | 0 | 342 | 51 | 5 | 190 | 42 | 17 | 0 | 177 | 8 | 17 | 0 | 162 | 0 | 1 | 36 | 305 | 0 | 325 | 42 | 30 | 134 | 0 | 17 | 0 | 79 | 30 | 100 | 0 | 95 | 17 | 69 | 48 | 85 | 0 | 0.8 | 3 | 6474.3 | 909 | 227 | 0 | 15 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 538 | 0 | 0 | 0 | 1480 | 0 | 38 | 0 | 35 | 35 | 0 | 51 | 17 | 0 | 1.02 | 3 | 0 | 0 | 1.9 | 160 | 0 | 0 | 0 | 140 | 0 | 348 | 0 | 0.16 | 0 | 52 | 114 | 1 | 85 | 0 | 0 | 0 | 0.2 | 4 | 0.01 | 94 | 242 | 115 | 180 | 0 | 306 | 1170 | 17 | 6391.29 | 12865.59 | 80.15
19:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 17.5 | 20 | 149 | 138 | 293 | 55 | 35 | 17 | 0 | 180 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 142 | 22 | 21 | 0 | 480 | 95 | 16 | 37 | 0 | 19 | 67 | 54 | 0 | 12 | 12 | 0 | 70 | 55 | 36 | 200 | 163 | 0 | 48 | 17 | 51 | 219 | 0 | 0 | 0 | 448 | 0 | 122 | 80 | 393 | 0 | 342 | 51 | 5 | 204 | 42 | 33 | 0 | 184 | 10 | 20 | 0 | 182 | 0 | 0 | 36 | 320 | 0 | 325 | 42 | 30 | 149 | 0 | 17 | 0 | 78 | 30 | 100 | 0 | 95 | 17 | 69 | 48 | 84 | 0 | 0 | 12 | 7179.5 | 908 | 238 | 0 | 19 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 1481 | 0 | 38 | 0 | 35 | 45 | 0 | 51 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 52 | 114 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 307 | 130 | 220 | 0 | 404 | 1170 | 17 | 6802 | 13981.5 | 80.13
19:30 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 35 | 149 | 138 | 293 | 55 | 35 | 17 | 0 | 180 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 142 | 22 | 21 | 0 | 450 | 90 | 16 | 38 | 0 | 23 | 67 | 54 | 0 | 12 | 12 | 0 | 70 | 55 | 36 | 200 | 163 | 0 | 50 | 17 | 51 | 219 | 0 | 0 | 0 | 484 | 0 | 140 | 80 | 393 | 0 | 345 | 51 | 5 | 189 | 42 | 34 | 0 | 194 | 9 | 20 | 0 | 180 | 0 | 0 | 36 | 310 | 0 | 325 | 42 | 30 | 154 | 0 | 17 | 0 | 78 | 30 | 100 | 0 | 95 | 17 | 69 | 48 | 84 | 0 | 0 | 12 | 7207 | 909 | 247 | 0 | 23 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590 | 0 | 0 | 0 | 1483 | 0 | 38 | 0 | 35 | 50 | 0 | 51 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 140 | 0 | 348 | 0 | 0 | 0 | 52 | 114 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 272 | 130 | 220 | 0 | 404 | 1190 | 17 | 6742 | 13949
20:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 35 | 149 | 137 | 293 | 55 | 35 | 17 | 0 | 180 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 142 | 22 | 21 | 0 | 460 | 86 | 16 | 38 | 0 | 10 | 67 | 54 | 0 | 12 | 12 | 0 | 70 | 54 | 36 | 200 | 163 | 0 | 50 | 17 | 51 | 217 | 0 | 0 | 0 | 551 | 0 | 138 | 81 | 393 | 0 | 345 | 51 | 5 | 203 | 42 | 34 | 0 | 196 | 9 | 20 | 0 | 178 | 0 | 0 | 36 | 310 | 0 | 325 | 42 | 30 | 154 | 0 | 17 | 0 | 81 | 30 | 102 | 0 | 96 | 17 | 69 | 48 | 98 | 0 | 0 | 12 | 7296 | 908 | 247 | 0 | 20 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 602 | 0 | 0 | 0 | 1478 | 0 | 38 | 0 | 35 | 50 | 0 | 51 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 140 | 0 | 383 | 0 | 0 | 0 | 52 | 114 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 277 | 130 | 220 | 0 | 404 | 1197 | 17 | 6784 | 14080 | 80.11
21:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 35 | 149 | 140 | 293 | 55 | 35 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 22 | 21 | 0 | 450 | 91 | 16 | 37 | 0 | 2 | 67 | 54 | 18 | 12 | 12 | 0 | 70 | 55 | 34 | 200 | 72 | 0 | 50 | 22 | 51 | 218 | 0 | 0 | 0 | 606 | 0 | 142 | 45 | 393 | 0 | 345 | 51 | 5 | 201 | 42 | 33 | 0 | 195 | 9 | 20 | 0 | 184 | 0 | 0 | 36 | 320 | 0 | 314 | 41 | 30 | 156 | 0 | 17 | 0 | 81 | 30 | 100 | 0 | 97 | 17 | 49 | 48 | 98 | 0 | 0 | 12 | 7204 | 909 | 260 | 0 | 20 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 0 | 0 | 0 | 1472 | 0 | 39 | 0 | 35 | 50 | 0 | 51 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 140 | 0 | 409 | 0 | 0 | 0 | 52 | 114 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 307 | 130 | 220 | 0 | 403 | 1200 | 17 | 6864 | 14068 | 80.09
22:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 17 | 149 | 140 | 293 | 55 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 21 | 21 | 0 | 450 | 91 | 16 | 38 | 0 | 7 | 67 | 54 | 18 | 12 | 12 | 0 | 70 | 55 | 34 | 200 | 17 | 0 | 50 | 25.5 | 51 | 218 | 0 | 0 | 0 | 612 | 0 | 138 | 45 | 393 | 0 | 345 | 51 | 5 | 198 | 42 | 18 | 0 | 196 | 9 | 20 | 0 | 192 | 0 | 0 | 36 | 315 | 0 | 334 | 41 | 30 | 159 | 0 | 0 | 0 | 82 | 30 | 100 | 0 | 97 | 17 | 49 | 57 | 98 | 0 | 0 | 12 | 7108.5 | 908 | 250 | 0 | 20 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 1467 | 0 | 40 | 0 | 35 | 50 | 0 | 51 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 50 | 114 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 307 | 130 | 220 | 0 | 403 | 1210 | 17 | 6856 | 13964.5 | 80.07
23:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 17 | 149 | 140 | 293 | 55 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 21 | 21 | 0 | 460 | 90 | 16 | 37 | 0 | 5 | 67 | 54 | 18 | 12 | 12 | 0 | 70 | 55 | 34 | 160 | 17 | 0 | 50 | 25.5 | 51 | 217 | 0 | 0 | 0 | 445 | 0 | 56 | 45 | 393 | 0 | 345 | 44 | 5 | 194 | 42 | 17 | 0 | 181 | 9 | 20 | 0 | 190 | 0 | 0 | 37 | 310 | 0 | 372 | 41 | 30 | 145 | 0 | 0 | 0 | 53 | 30 | 100 | 0 | 97 | 0 | 9 | 58 | 99 | 0 | 0 | 12 | 6731.5 | 908 | 250 | 0 | 20 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 603 | 0 | 0 | 0 | 1491 | 0 | 40 | 0 | 35 | 50 | 0 | 51 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 146 | 0 | 381 | 0 | 0 | 0 | 53 | 114 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 307 | 130 | 220 | 0 | 402 | 1205 | 17 | 6827 | 13558.5 | 80.05
Total KWH | 0 | 2530560 | 1188960 | 0 | 0 | 0 | 0 | 0 | 11340000 | 0 | 0 | 129960 | 296640 | 3607344 | 3203520 | 6842040 | 1321003 | 133793 | 424800 | 0 | 4752300 | 0 | 0 | 0 | 136150 | 7228485 | 0 | 0 | 202133 | 3488400 | 554400 | 462240 | 0 | 10253636.36 | 2189182 | 381382 | 918720 | 0 | 153600 | 493922 | 1106220 | 137088 | 274560 | 291840 | 24957 | 1707093 | 1433527 | 806400 | 3781818.18 | 747709 | 0 | 670080 | 562581 | 1039600 | 5336727 | 0 | 0 | 0 | 8339999 | 128385 | 995272 | 1271273 | 8784000 | 0 | 8210000 | 1228288 | 208800 | 4874000 | 694368 | 294720 | 47995 | 1599360 | 89040 | 474060 | 0 | 4247040 | 0 | 391836 | 677920 | 7433000 | 0 | 8737000 | 989000 | 717960 | 3630027.27 | 53467 | 267312 | 0 | 1620480 | 720192 | 1443400 | 0 | 2334820 | 172440 | 1405200 | 712800 | 1080960 | 12100 | 252970 | 119520 | 154412374.81 | 21795636 | 4610592 | 0 | 303360 | 580224 | 0 | 0 | 0 | 0 | 0 | 0 | 398160 | 14640000 | 0 | 0 | 0 | 34973454 | 0 | 915994 | 0 | 394848 | 534624 | 0 | 322256 | 401520 | 0 | 391936 | 759200 | 53799 | 0 | 360752 | 4126082 | 0 | 0 | 0 | 3678864 | 0 | 9263563 | 0 | 34320 | 0 | 1224436 | 1007783 | 195833 | 750912 | 0 | 0 | 0 | 48140.76 | 964080 | 939 | 2445216 | 7025000 | 3011000 | 5322070 | 0 | 7775324 | 29434181.82 | 432000 | 158176099.58 | 312588474.39

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 14-04-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13047.89 | MW | 12:00 Hr. | Energy Generated |  |  | 312.5885 |  | MKWHr.
| Day Peak Demand |  |  | 13653.89 | MW | 12:00 Hr. | Energy Unserverd |  |  | 15.484 |  | MKWHr.
| Evening Peak Generation |  |  | 14080 | MW | 20:00 Hr. | Energy Demand |  |  | 328.0725 |  | MKWHr.
| Evening Peak Demand |  |  | 14799 | MW | 20:00 Hr. | Maximum Temperature |  |  | 35 |  | °C
| Minimum Generation of the Day |  |  | 12059.83 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 921.44 |  | MMCFD
| Maximum Generation of the Day |  |  | 14080 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 7.095 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.5911 | 0 | 23.3032 | 0 | 0 | 0.20213 | 0 | 0 | 58.0964 | Gas | 125.5133 | Gas | 443234235.4996
| Chattogram Zone |  |  | 6.1431 | 12.1218 | 10.2464 | 0 | 1.7071 | 0.15334 | 0 | 0.1536 | 30.5254 | Coal | 72.2208 | Coal | 490756208.666
| Cumilla Zone |  |  | 25.7928 | 0 | 3.6563 | 0 | 0 | 0.39184 | 4.247 | 0 | 34.088 | HFO | 47.7584 | HFO | 857357028.5
| Mymensingh Zone |  |  | 1.081 | 0 | 2.41 | 0 | 0 | 0.26507 | 0 | 0 | 3.756 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.8932 | 0 | 0 | 0 | 0 | 0.053467 | 0 | 0 | 27.9467 | Hydro | 1.7071 | Hydro | 170709.3
| Khulna Zone |  |  | 4.6106 | 14.64 | 0.88358 | 0 | 0 | 0.39816 | 21.7956 | 0 | 42.328 | Solar | 4.2192 | Solar | 66896616.072
| Barishal Zone |  |  | 8.3331 | 44.2345 | 2.8772 | 0 | 0 | 0.000939 | 0 | 0 | 55.4457 | Import | 61.0161 | Import | 357128255.46
| Rajshahi Zone |  |  | 17.0685 | 0 | 2.623 | 0 | 0 | 1.5462 | 34.9735 | 0 | 56.2112 | Wind | 0.1536 | Wind | 2259456
| Rangpur Zone |  |  | 0 | 1.2244 | 1.7587 | 0 | 0 | 1.2081 | 0 | 0 | 4.1912
| Total |  |  | 125.5133 | 72.2208 | 47.7584 | 0 | 1.7071 | 4.2192 | 61.0161 | 0.1536 | 312.5885
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 443234235.4996 |  | Hydro | 170709.3
|  |  |  | Coal | 490756208.666 |  | Solar | 66896616.072
|  |  |  | HFO | 857357028.5 |  | Import | 357128255.46
|  |  |  | HSD | 0 |  | Wind | 2259456
[5 empty] | Total: | 221,78,02,509 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7956 | Peak Hr Flow | 908.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 43555381.88 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 34.9735 | Peak Hr Flow | 1478.00 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2112 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 4.247 | Peak Hr Flow | 178.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2724 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 61.0161 | Peak Hr Flow | 2564.00 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 112 |  | 4918
|  |  |  | Chattogram |  | 75 |  | 1473
|  |  |  | Cumilla |  | 85 |  | 1509
|  |  |  | Mymensingh |  | 40 |  | 1102
|  |  |  | Sylhet |  | 48 |  | 522
|  |  |  | Khulna |  | 124 |  | 1832
|  |  |  | Barishal |  | 55 |  | 454
|  |  |  | Rajshahi |  | 86 |  | 1626
|  |  |  | Rangpur |  | 63 |  | 867
|  |  |  | Total |  | 688 |  | 14303
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 320
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:12 | 09:42 | Jhenaidah 132/33kV S/S Transformer T-2 HT Tripped showing Transformer diff: 1:87 relays. | [7 empty] | 29.0MW load
interrup.
|  | 09:12 | Jhenaidah 132/33kV S/S Transformer T-3 LT is restored.
| 09:43 | 09:43 | Jhenaidah 132/33kV S/S Transformer T-2 LT Tripped showing Transofmer diff: 1:87T relays. | [7 empty] | 29.0MW load
interrup.
| 11:37 | 12:27 | Jashore-Noapara 132kV Ckt-1 Tripped from Noapara 132/33kV end showing ALSTOM (EPAC
3000) Phase-C Zone-Z1 Distance-23.8KM relays Due to Distance Relay Trip and from
Jashore 132/33kV end showing 1. Distance Relay 2. Zone-1 3. D- 14.43 4. R-Y-B Trip
relays Due to Trip
| 12:00 |  | Day Peak Generation: 13043 MW.
| 13:38 | 15:13 | Rampur 230/132/33 S/S Anandabazar-1 Tripped showing REL670 relays Due to Distance Trip
| 14:01 | 14:22 | Taraganj 132/33kV S/S Taraganj-Rangpur CKT-01 Tripped showing Micom P40 Agile relays.
| 14:01 | 14:20 | Rangpur-Saidpur 132kV Ckt-1 Tripped from Rangpur 132/33kV end showing na relays.
| 21:01 | 21:37 | Fenchuganj-Kulaura 132 kV Ckt-2 Tripped from Fenchuganj 230/132/33kV end showing REL670
relays Due to Bad weather
| 21:07 | 22:06 | Bhangura 132/33kV S/S Tr-1(403T) LT Forced S/D Due to Red Hot In 33KV Tr-1 BKR
| 21:09 | 22:04 | Bhangura 132/33kV S/S Tr-1(403T) HT Forced S/D Due to Red Hot In 33KV Tr-1 BKR
| 22:24 | 22:40 | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 Tripped showing Over curent &Earth falt | [7 empty] | 44.0MW load
|  |  | relays Due to Tripped due to severe storm | [7 empty] | interrup.
| 22:26 | 22:41 | Chattak-Sylhet 132 kV Ckt-2 Tripped from Sylhet 132/33kV end showing SOTF relays Due to | [7 empty] | 25.0MW load
|  |  | Distance Relay | [7 empty] | interrup. Sylhet
132/33kV end
| 23:22 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
| 01:07 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- gt
| 03:15 | 03:54 | Fenchuganj-Sreemangal 132kV Ckt-2 Tripped from Sreemongol 132/33kV end showing Distance
relay relays Due to Power swing fault is caught by Distance relay
| 04:44 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
| 06:15 |  | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Beanibazar 132/33kV | [7 empty] | 25.0MW load
|  |  | end Due to Line Rerouting work | [7 empty] | interrup.
Beanibazar 132/33kV
end
| 06:20 |  | Fenchuganj-Sylhet (South) 132KV Ckt-1 Project Work S/D from Sylhet (South) end Due to
Project Work Of OPGW.
| 06:26 |  | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Fenchuganj
230/132/33kV end Due to Biyanibazar End maintenace Work
| 06:26 |  | Haripur 412 MW CCPP Shutdown with remarks:- ST
| 06:27 |  | Haripur 412 MW CCPP Synchronized with remarks:- GT(False Sms)
|  | 06:28 | Rampura-Ullon-2 132kV Ckt-2 is restored.
| 07:00 |  | Minimum generation: 12327 MW
| 07:02 |  | Rajshahi 132/33kV S/S Transformer T-2(415T) HT Forced S/D Due to 33 kV Poba & Mohonpur | [7 empty] | 15.0MW load
|  |  | feeder red hot maintenance work. | [7 empty] | interrup.
| 07:02 |  | Rajshahi 132/33kV S/S Transformer T-2(415T) LT Forced S/D Due to 33 kV Poba & Mohonpur | [7 empty] | 15.0MW load
|  |  | feeder red hot maintenance work. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 14-04-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 412 | 11340000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 180 | 4752300 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1321003 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7228485 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 129960 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 137 | 3203520 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 133793 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 136150 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 554400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 462240 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 1188960 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 293 | 6842040 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3607344 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2530560 | Engine Problem
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 424800 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 202133 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 296640 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 460 | 10253636.36 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3488400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2430 | 58096364.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 562581 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 128385 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 670080 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1707093 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5336727 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 1039600 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 54 | 1106220 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 67 | 493922 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 274560 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 36 | 806400 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 38 | 918720 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24957 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 381382 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 137088 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 54 | 1433527 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 291840 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 86 | 2189182 | Liquid fuel shortage
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 163 | 747709 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 551 | 8339999 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 10 | 153600 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 200 | 3781818.18 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 1704 | 30525390.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 203 | 4874000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 345 | 8210000 | machine problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 8784000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 42 | 694368 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 5 | 208800 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 81 | 1271273 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1228288 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 138 | 995272 | Machine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 677920 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 47995 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 196 | 1599360 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 178 | 4247040 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 474060 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 89040 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 34 | 294720 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 391836 | -
Cumilla Area Total |  |  |  |  | 2870.745 | 1731 | 34087972
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 98 | 1080960 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 48 | 712800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 69 | 1405200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 252970 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 119520 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 172440 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 244 | 3755990
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 53467 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 989000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 717960 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3630027.27 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 102 | 1443400 | Plant availability less
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 720192 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1620480 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 96 | 2334820 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 267312 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7433000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 325 | 8737000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1187 | 27946658.27
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 908 | 21795636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 20 | 303360 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 43 | 580224 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 247 | 4610592 | Gas Restrction
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 398160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 602 | 14640000 | U#1 Under Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1820 | 42327972
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 404 | 7775324 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 96 | 2445216 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3011000 | STG Under Maintenance
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1197 | 29434181.82 | Machine Problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5322070 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 432000 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 277 | 7025000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 939 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2341 | 55445730.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 391936 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 38 | 915994 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 401520 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 160 | 4126082 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 140 | 3678864 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 383 | 9263563 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 53799 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 322256 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 534624 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 394848 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 34320 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1478 | 34973454 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 360752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 759200 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2365 | 56211212
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 52 | 1224436 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 92 | 750912 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 48140.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 1007783 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 195833 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 964080 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 258 | 4191184.76
Eastern Grid Total |  |  |  |  | 17417.792 | 7296 | 154412374.81
Western Grid Total |  |  |  |  | 11852.195 | 6784 | 158176099.58
National Grid Total |  |  |  |  | 29269.987 | 14080 | 312588474.39
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 14-04-2026
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9164.06 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4450.8 | MW
i) Dhaka area |  |  | 4805.86 |  | MW | i) Khulna area |  |  |  | 1708 | MW
ii) Chattogram area |  |  | 1398.2 |  | MW | ii) Barishal area |  |  |  | 399.2 | MW
iii) Cumilla area |  |  | 1424 |  | MW | iii) Rajshahi area |  |  |  | 1539.6 | MW
iv) Mymensingh area |  |  | 1062 |  | MW | iv) Rangpur area |  |  |  | 804 | MW
v) Sylhet area |  |  | 474 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13614.86 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 15 | 13:00 | 67 | Hasnabad | 87 | 18:00 | 133 | Natore | 156 | 07:00
2 | AKSML | 5.7 | 17:00 | 68 | Hathazari | 85 | 20:00 | 134 | Nawabganj | 58.4 | 05:00
3 | Aftabnagar | 40 | 22:00 | 69 | Hatirjheel | 28 | 14:00 | 135 | Netrakona | 115 | 18:00
4 | Agargaon | 105 | 23:00 | 70 | Ishurdi | 69 | 00:00 | 136 | New | 64.5 | 00:00
5 | Agrabad | 54 | 00:00 | 71 | Jaldhaka | 54 | 21:00 | 137 | Niamatpur | 116 | 19:30
6 | Amnura | 48 | 19:00 | 72 | Jamalpur | 127 | 21:00 | 138 | Noapara | 44 | 19:30
7 | Ashuganj | 94 | 22:00 | 73 | Jashore | 143 | 13:00 | 139 | PHP | 7 | 16:00
8 | BSRM | 183 | 19:00 | 74 | Jhenaidah | 100 | 22:00 | 140 | Pabna | 88 | 08:00
9 | Bagerhat | 79 | 23:00 | 75 | Joydebpur | 120 | 02:00 | 141 | Palashbari | 114 | 19:00
10 | Bajitpur | 71 | 23:00 | 76 | Joypurhat | 64 | 08:00 | 142 | Panchagarh | 38 | 10:00
11 | Bakerganj | 14 | 19:00 | 77 | Juldah | 18 | 16:00 | 143 | Patiya | 11 | 22:00
12 | Bakulia | 92 | 19:00 | 78 | KSRM | 24 | 17:00 | 144 | Patuakhali | 64 | 19:00
13 | Banani | 32 | 14:00 | 79 | Kabirpur | 196 | 00:00 | 145 | Payra | 30 | 19:00
14 | Bangabhaban | 4 | 00:00 | 80 | Kachua | 92 | 21:00 | 146 | Postogola | 53 | 13:00
15 | Barapukuria | 64 | 19:00 | 81 | Kaliganj | 28 | 21:00 | 147 | Pubail | 28 | 00:00
16 | Barguna | 20 | 03:00 | 82 | Kallyanpur | 114 | 16:00 | 148 | Purbachal | 31 | 13:00
17 | Barishal | 94 | 22:00 | 83 | Kalurghat | 31 | 00:00 | 149 | Purbasadipur | 120 | 07:00
18 | Barishal-230 | 106 | 19:00 | 84 | Kamrangirchar | 78 | 13:00 | 150 | Rahanpur | 35 | 12:00
19 | Baroaulia | 61 | 07:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 24 | 01:00
20 | Baroirhat | 64 | 19:00 | 86 | Kasba | 36 | 18:30 | 152 | Rajbari | 79 | 22:00
21 | Bashundhara | 186 | 13:00 | 87 | Kazla | 114 | 13:00 | 153 | Rajendrapur | 111 | 11:00
22 | BashundharaCement | 7 | 00:00 | 88 | Keranigonj | 83 | 12:00 | 154 | Rajshahi | 139 | 00:00
23 | Beanibazar | 58 | 18:30 | 89 | Khagrachori | 34 | 19:00 | 155 | Rajshahi-230 | 72 | 21:00
24 | Benapole | 70 | 20:00 | 90 | Khulna | 56 | 15:00 | 156 | Ramganj | 106 | 20:00
25 | Bhaluka | 136 | 00:00 | 91 | Khulshi | 193 | 19:00 | 157 | Rampur | 40 | 02:00
26 | Bhandaria | 54 | 19:00 | 92 | Kishoreganj | 116 | 18:30 | 158 | Rangamati | 17 | 19:00
27 | Bhangura | 46 | 07:00 | 93 | Kodda | 266 | 02:00 | 159 | Rangpur | 126 | 18:30
28 | Bheramara(GK) | 70 | 21:00 | 94 | Kulaura | 38 | 18:30 | 160 | Ruppur | 4.4 | 16:00
29 | Bhulta | 212 | 21:00 | 95 | Kurigram | 57 | 19:30 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 76 | 04:00 | 96 | Kushtia | 124 | 20:00 | 162 | Saidpur | 88 | 19:00
31 | Bogura | 170 | 19:30 | 97 | Laksam | 22 | 00:00 | 163 | Satkhira | 135 | 07:00
32 | Borhanuddin | 92 | 19:00 | 98 | Lakshmipur | 35 | 19:00 | 164 | Satmasjid | 108 | 13:00
33 | Brahmanbaria | 130 | 21:00 | 99 | Lalbag | 70 | 13:00 | 165 | Savar | 178 | 02:00
34 | Cantonment | 123 | 13:00 | 100 | Lalmonirhat | 45 | 19:00 | 166 | SevenRings | 16.79 | 01:00
35 | Chandina | 20 | 19:00 | 101 | MI_Cement | 16.1 | 05:00 | 167 | ShahCement | 36 | 19:30
36 | Chandpur | 76 | 21:00 | 102 | Madanganj | 36 | 19:00 | 168 | Shahjadpur | 93 | 12:00
37 | Chandraghona | 38 | 19:00 | 103 | Madaripur | 102 | 19:30 | 169 | Shahjibazar | 123 | 22:00
38 | Chapai | 84 | 21:00 | 104 | Madartek | 84 | 00:00 | 170 | Shahmirpur | 52 | 23:00
39 | Charsaidpur | 39 | 18:00 | 105 | Madunaghat | 54 | 16:00 | 171 | Shariatpur | 80 | 18:30
40 | Chauddagram | 77 | 18:30 | 106 | Magura | 60 | 21:00 | 172 | Sherpur | 130 | 18:30
41 | Chhatak | 27 | 21:00 | 107 | Mahasthangarh | 75 | 00:00 | 173 | Shikalbaha | 27 | 01:00
42 | Chowmuhani | 142 | 19:30 | 108 | Maijdee | 41 | 21:00 | 174 | Shitalakhya | 79.4 | 13:00
43 | Chuadanga | 136 | 20:00 | 109 | Manikganj | 128 | 05:00 | 175 | Sholosohor | 42 | 21:00
44 | Coxsbazar | 141 | 10:00 | 110 | Maniknagar | 68 | 00:00 | 176 | Shyampur | 176 | 11:00
45 | Cumilla(N) | 121 | 04:00 | 111 | Matarbari | 49 | 18:30 | 177 | Siddhirganj | 104 | 01:00
46 | Cumilla(S) | 191 | 00:00 | 112 | Matuail | 70 | 00:00 | 178 | Sirajganj | 122 | 23:00
47 | Daganbhuiyan | 37 | 22:00 | 113 | Metrorail_Motijheel | 24 | 19:30 | 179 | Sonargaon | 139 | 09:00
48 | Daudkandi | 131 | 18:30 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreemongol | 86 | 22:00
49 | DhakaUniversity | 56 | 13:00 | 115 | Millgate | 84 | 00:00 | 181 | Sreepur | 83 | 01:00
50 | Dhamrai | 98 | 18:00 | 116 | Mirpur | 133 | 13:00 | 182 | Srinagar | 47 | 18:30
51 | Dhanmondi | 84 | 13:00 | 117 | Mirsorai | 40 | 02:00 | 183 | Sunamganj | 44 | 21:00
52 | Dohazari | 90 | 18:30 | 118 | Mirzapur | 51 | 22:00 | 184 | Sylhet | 64 | 19:00
53 | Faridpur | 158 | 21:00 | 119 | Mithapukur | 52 | 21:00 | 185 | Sylhet-132 | 103 | 14:00
54 | Fatullah | 85 | 00:00 | 120 | Modern | N/A | N/A | 186 | TK | 23.5 | 18:30
55 | Fenchuganj | 35 | 20:00 | 121 | Mogbazar | 67.9 | 13:00 | 187 | Tangail | 206 | 19:00
56 | Feni | 106 | 18:30 | 122 | Mongla | 48 | 00:00 | 188 | Taraganj | 21 | 19:00
57 | GPH | 57 | 00:00 | 123 | Motijheel | 39 | 13:00 | 189 | Tasnim | 34 | 21:00
58 | Ghatail | 86 | 13:00 | 124 | Muktagacha | 31 | 20:00 | 190 | Thakurgaon | 85 | 10:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 100 | 05:00 | 191 | Tongi | 131 | 12:00
60 | Ghorashal-230 | 102 | 09:00 | 126 | Muradnagar | 46 | 22:00 | 192 | Ullahpara | 44 | 11:00
61 | Goalpara | 39 | 19:00 | 127 | Mymensingh | 186 | 20:00 | 193 | Ullon | 56 | 23:00
62 | Gollamari | 96 | 12:00 | 128 | Nabinagar | 13 | 18:30 | 194 | Uttara | 84 | 13:00
63 | Gopalganj | 90 | 19:30 | 129 | Naogaon | 153 | 22:00 | 195 | UttaraNew | 61 | 00:00
64 | Gulshan | 96 | 13:00 | 130 | Narail | 58 | 22:00 | 196 | Zigatola | 82 | 14:00
65 | Halishahar | 70 | 19:30 | 131 | Narinda | 62 | 13:00
66 | HaripurSBU | 132 | 09:00 | 132 | Narshingdi | 166 | 23:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 14-04-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 12840.34 | 1252 |  | 14148.68
1:00 | 12441.07 | 1203 |  | 13698.07
2:00 | 12272.48 | 887 |  | 13199.48
3:00 | 12313.12 | 657 |  | 13000.12
4:00 | 12228.21 | 595 |  | 12850.21
5:00 | 12158.45 | 375 |  | 12550.45
6:00 | 12163.31 | 162 |  | 12332.31
7:00 | 12270.04 | 275 |  | 12557.42
8:00 | 12059.83 | 330 |  | 12404.83
9:00 | 12267.51 | 274 |  | 12553.51
10:00 | 12624.75 | 219 |  | 12853.75
11:00 | 12800.18 | 434 |  | 13254.18
12:00 | 13047.89 | 580 |  | 13653.89
13:00 | 13044.91 | 774 |  | 13853.91
14:00 | 12907.98 | 951 |  | 13901.98
15:00 | 12905.04 | 1001 |  | 13951.04
16:00 | 12878.72 | 885 |  | 13803.72
17:00 | 12863.18 | 584 |  | 13473.18
18:00 | 12865.59 | 465 |  | 13351.59
19:00 | 13981.5 | 687 |  | 14699.5
19:30 | 13949 | 765 |  | 14748
20:00 | 14080 | 688 |  | 14799
21:00 | 14068 | 651 |  | 14748.3
22:00 | 13964.5 | 703 |  | 14699.5
23:00 | 13558.5 | 852 |  | 14448.84
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 14-04-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6348.5 | 6491.84 | 12840.34 | DAILY GENERATION CURVE
00:30 | 6254.5 | 6386.205 | 12640.705
01:00 | 6160.5 | 6280.57 | 12441.07 | 14-04-2026
01:30 | 6088 | 6268.775 | 12356.775
02:00 | 6015.5 | 6256.98 | 12272.48
02:30 | 6002.5 | 6290.3 | 12292.8
03:00 | 5989.5 | 6323.62 | 12313.12
03:30 | 5973 | 6297.665 | 12270.665
04:00 | 5956.5 | 6271.71 | 12228.21
04:30 | 5926.5 | 6266.83 | 12193.33
05:00 | 5896.5 | 6261.95 | 12158.45
05:30 | 5889.97 | 6270.91 | 12160.88
06:00 | 5883.44 | 6279.87 | 12163.31
06:30 | 5905.955 | 6310.72 | 12216.675
07:00 | 5928.47 | 6341.57 | 12270.04
07:30 | 5832.355 | 6332.58 | 12164.935
08:00 | 5736.24 | 6323.59 | 12059.83
08:30 | 5783.19 | 6380.48 | 12163.67
09:00 | 5830.14 | 6437.37 | 12267.51
09:30 | 5942.555 | 6503.575 | 12446.13
10:00 | 6054.97 | 6569.78 | 12624.75
10:30 | 6108.15 | 6604.315 | 12712.465
11:00 | 6161.33 | 6638.85 | 12800.18
11:30 | 6233.53 | 6690.505 | 12924.035
12:00 | 6305.73 | 6742.16 | 13047.89
12:30 | 6272.37 | 6774.03 | 13046.4
13:00 | 6239.01 | 6805.9 | 13044.91
13:30 | 6181.11 | 6795.335 | 12976.445
14:00 | 6123.21 | 6784.77 | 12907.98
14:30 | 6164.065 | 6742.445 | 12906.51
15:00 | 6204.92 | 6700.12 | 12905.04
15:30 | 6257.305 | 6634.575 | 12891.88
16:00 | 6309.69 | 6569.03 | 12878.72
16:30 | 6303.32 | 6567.63 | 12870.95
17:00 | 6296.95 | 6566.23 | 12863.18
17:30 | 6385.625 | 6478.76 | 12864.385
18:00 | 6474.3 | 6391.29 | 12865.59
18:30 | 6826.9 | 6596.645 | 13423.545
19:00 | 7179.5 | 6802 | 13981.5
19:30 | 7207 | 6742 | 13949
20:00 | 7296 | 6784 | 14080
20:30 | 7250 | 6824 | 14074 |  | Executive Engineer
21:00 | 7204 | 6864 | 14068 |  | Network Operation Division
21:30 | 7156.25 | 6860 | 14016.25
22:00 | 7108.5 | 6856 | 13964.5
22:30 | 6920 | 6841.5 | 13761.5
23:00 | 6731.5 | 6827 | 13558.5

## En-Curve
QF-LDC-12
Date | 14-04-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3590 | 1477 | 881 | 0 | 190 | 1451.84 | 70 | 3040 | 0 | 737 | 1401.5 | 0 | 0 | 2 | 1252 | DAILY ENERGY CURVE
00:30 | 3532.5 | 1445 | 881 | 0 | 191 | 1475.205 | 70 | 2982 | 0 | 734 | 1328.5 | 0 | 0 | 1.5 | 1227.5 | 14-04-2026
01:00 | 3475 | 1413 | 881 | 0 | 192 | 1498.57 | 70 | 2924 | 0 | 731 | 1255.5 | 0 | 0 | 1 | 1203
01:30 | 3479.5 | 1399 | 881 | 0 | 188 | 1502.775 | 70 | 2917.5 | 0 | 693 | 1225 | 0 | 0 | 1 | 1045 | Energy Generated | 312.5885 |  | MKWHr
02:00 | 3484 | 1385 | 881 | 0 | 184 | 1506.98 | 70 | 2911 | 0 | 655 | 1194.5 | 0 | 0 | 1 | 887 | Energy not Served | 15.484 |  | MKWHr
02:30 | 3496.5 | 1415.5 | 881 | 0 | 183 | 1510.3 | 70 | 2915.5 | 0 | 646.5 | 1174 | 0 | 0 | 0.5 | 772 | Total Energy Requirement | 328.0725 |  | MKWHr
03:00 | 3509 | 1446 | 881 | 0 | 182 | 1513.62 | 70 | 2920 | 0 | 638 | 1153.5 | 0 | 0 | 0 | 657
03:30 | 3508 | 1461 | 884.5 | 0 | 183 | 1513.165 | 70 | 2915.5 | 0 | 629.5 | 1105 | 0 | 0 | 1 | 626
04:00 | 3507 | 1476 | 888 | 0 | 184 | 1512.71 | 70 | 2911 | 0 | 621 | 1056.5 | 0 | 0 | 2 | 595
04:30 | 3483.5 | 1472 | 888 | 0 | 182 | 1506.33 | 70 | 2914.5 | 0 | 621 | 1052 | 0 | 0 | 4 | 485
05:00 | 3460 | 1468 | 888 | 0 | 180 | 1499.95 | 70 | 2918 | 0 | 621 | 1047.5 | 0 | 0 | 6 | 375
05:30 | 3462.5 | 1459 | 890 | 0 | 171 | 1498 | 71 | 2919 | 4.88 | 623 | 1056.5 | 0 | 0 | 6 | 268.5
06:00 | 3465 | 1450 | 892 | 0 | 162 | 1496.05 | 72 | 2920 | 9.76 | 625 | 1065.5 | 0 | 0 | 6 | 162
06:30 | 3454 | 1479 | 892 | 0 | 158 | 1479.735 | 73 | 2939 | 48.94 | 620.5 | 1068 | 0 | 0 | 4.5 | 218.5
07:00 | 3443 | 1508 | 892 | 0 | 154 | 1463.42 | 74 | 2958 | 88.12 | 616 | 1070.5 | 0 | 0 | 3 | 275
07:30 | 3346 | 1487 | 898.5 | 0 | 155 | 1464.445 | 72 | 2931 | 153.99 | 595.5 | 1060 | 0 | 0 | 1.5 | 302.5
08:00 | 3249 | 1466 | 905 | 0 | 156 | 1465.47 | 70 | 2904 | 219.86 | 575 | 1049.5 | 0 | 0 | 0 | 330
08:30 | 3285.5 | 1446 | 907 | 0 | 156 | 1459.735 | 70 | 2913 | 298.435 | 571 | 1056.5 | 0 | 0 | 0.5 | 302
09:00 | 3322 | 1426 | 909 | 0 | 156 | 1454 | 70 | 2922 | 377.01 | 567 | 1063.5 | 0 | 0 | 1 | 274
09:30 | 3347 | 1532.5 | 909 | 0 | 159 | 1465.5 | 70 | 2919.55 | 413.58 | 558 | 1071.5 | 0 | 0 | 0.5 | 246.5
10:00 | 3372 | 1639 | 909 | 0 | 162 | 1477 | 70 | 2917.1 | 450.15 | 549 | 1079.5 | 0 | 0 | 0 | 219
10:30 | 3359.5 | 1686.5 | 908.5 | 0 | 162 | 1483.5 | 70 | 2915.6 | 498.865 | 535.5 | 1092 | 0 | 0 | 0.5 | 326.5
11:00 | 3347 | 1734 | 908 | 0 | 162 | 1490 | 70 | 2914.1 | 547.58 | 522 | 1104.5 | 0 | 0 | 1 | 434
11:30 | 3376.5 | 1747.5 | 908.5 | 0 | 169 | 1500 | 70 | 2935.1 | 570.935 | 524.5 | 1119.5 | 0 | 0 | 2.5 | 507
12:00 | 3406 | 1761 | 909 | 0 | 176 | 1510 | 70 | 2956.1 | 594.29 | 527 | 1134.5 | 0 | 0 | 4 | 580
12:30 | 3345 | 1767.5 | 908.5 | 0 | 181 | 1507.5 | 69.5 | 2960.6 | 585.8 | 533 | 1182.5 | 0 | 0 | 5.5 | 677
13:00 | 3284 | 1774 | 908 | 0 | 186 | 1505 | 69 | 2965.1 | 577.31 | 539 | 1230.5 | 0 | 0 | 7 | 774
13:30 | 3278 | 1701.5 | 908 | 0 | 183 | 1506.5 | 69 | 2964.1 | 549.845 | 554 | 1251.5 | 0 | 0 | 11 | 862.5
14:00 | 3272 | 1629 | 908 | 0 | 180 | 1508 | 69 | 2963.1 | 522.38 | 569 | 1272.5 | 0 | 0 | 15 | 951
14:30 | 3349 | 1625.5 | 908 | 0 | 181 | 1514 | 69 | 2955.55 | 459.21 | 565.5 | 1264.75 | 0 | 0 | 15 | 976
15:00 | 3426 | 1622 | 908 | 0 | 182 | 1520 | 69 | 2948 | 396.04 | 562 | 1257 | 0 | 0 | 15 | 1001
15:30 | 3465 | 1648 | 908 | 0 | 179 | 1516.5 | 69.5 | 2937.5 | 334.63 | 566 | 1252.75 | 0 | 0 | 15 | 943
16:00 | 3504 | 1674 | 908 | 0 | 176 | 1513 | 70 | 2927 | 273.22 | 570 | 1248.5 | 0 | 0 | 15 | 885
16:30 | 3511 | 1646 | 908.5 | 0 | 171 | 1500.5 | 70 | 2917.5 | 202.45 | 572 | 1356 | 0 | 0 | 16 | 734.5
17:00 | 3518 | 1618 | 909 | 0 | 166 | 1488 | 70 | 2908 | 131.68 | 574 | 1463.5 | 0 | 0 | 17 | 584
17:30 | 3517 | 1584.5 | 909 | 0 | 164 | 1484 | 70 | 2844 | 73.885 | 643.5 | 1560.5 | 0 | 0 | 14 | 524.5
18:00 | 3516 | 1551 | 909 | 0 | 162 | 1480 | 70 | 2780 | 16.09 | 713 | 1657.5 | 0 | 0 | 11 | 465
18:30 | 3602 | 1615 | 908.5 | 0 | 172 | 1480.5 | 70 | 2985.5 | 8.045 | 732.5 | 1834.5 | 0 | 0 | 15 | 576
19:00 | 3688 | 1679 | 908 | 0 | 182 | 1481 | 70 | 3191 | 0 | 752 | 2011.5 | 0 | 0 | 19 | 687
19:30 | 3631 | 1644 | 909 | 0 | 180 | 1483 | 70 | 3192 | 0 | 777 | 2040 | 0 | 0 | 23 | 765
20:00 | 3695 | 1658 | 908 | 0 | 178 | 1478 | 70 | 3283 | 0 | 773 | 2027 | 0 | 0 | 10 | 688
20:30 | 3707.5 | 1640 | 908.5 | 0 | 181 | 1475 | 70 | 3329.5 | 0 | 774.5 | 1982 | 0 | 0 | 6 | 669.5
21:00 | 3720 | 1622 | 909 | 0 | 184 | 1472 | 70 | 3376 | 0 | 776 | 1937 | 0 | 0 | 2 | 651
21:30 | 3726 | 1612.5 | 908.5 | 0 | 188 | 1469.5 | 70 | 3379 | 0 | 776 | 1882.25 | 0 | 0 | 4.5 | 677
22:00 | 3732 | 1603 | 908 | 0 | 192 | 1467 | 70 | 3382 | 0 | 776 | 1827.5 | 0 | 0 | 7 | 703
22:30 | 3729 | 1580.5 | 908 | 0 | 191 | 1479 | 70 | 3278.5 | 0 | 773.5 | 1746 | 0 | 0 | 6 | 777.5
23:00 | 3726 | 1558 | 908 | 0 | 190 | 1491 | 70 | 3175 | 0 | 771 | 1664.5 | 0 | 0 | 5 | 852
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 14-04-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 392 | 18:00 | 384 | 12:00 | Madunaghat | 405 | 01:00 | 397 | 11:00
Amtali | 412 | 01:00 | 409 | 21:00 | Meghnaghat | 394 | 18:00 | 386 | 12:00
Ashuganj | 400 | 08:00 | 394 | 12:00 | Payra | 414 | 02:00 | 412 | 00:00
Bhulta | 401 | 19:00 | 389 | 12:00 | Rahanpur | 407 | 18:30 | 398 | 07:00
Bibiana | 408 | 18:00 | 403 | 10:00 | Rampal | 402 | 00:00 | 392 | 22:00
BIPTC | 397 | 06:00 | 387 | 13:00
Bogura | 401 | 18:00 | 387 | 07:00
Gopalganj | 400 | 08:00 | 394 | 12:00
Kaliakoir | 388 | 03:00 | 381 | 12:00
Korerhat | 406 | 19:30 | 397 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 08:00 | 226 | 11:00 | Jhenaidah | 229 | 01:00 | 220 | 07:00
AKSML | 233.6 | 00:00 | 226.9 | 10:00 | Kachua | 231 | 18:00 | 223 | 11:00
Aminbazar | 232 | 04:00 | 226 | 12:00 | Kaliakoir | 237 | 19:30 | 230 | 12:00
Ashuganj | 234 | 19:00 | 228 | 14:00 | Keranigonj | 231 | 19:30 | 224 | 12:00
Ashuganj-400 | 234 | 19:00 | 228 | 14:00 | Khulna(S) | 230 | 00:00 | 222 | 21:00
Baghabari | 234 | 00:00 | 229 | 07:00 | Korerhat | 231 | 19:30 | 224 | 12:00
Barapukuria | 224 | 17:00 | 212 | 07:00 | Madunaghat | 233 | 00:00 | 228 | 10:00
Barapukuria-230 | 224 | 17:00 | 212 | 07:00 | Madunaghat-400 | 234 | 01:00 | 228 | 11:00
Barishal | 230 | 07:00 | 226 | 18:30 | Maniknagar | 229 | 06:00 | 224 | 11:00
Bheramara | 234 | 01:00 | 227 | 07:00 | Meghnaghat | 238 | 19:30 | 231 | 13:00
Bhulta | 231 | 19:00 | 225 | 12:00 | Meghnaghat-400 | 232 | 19:30 | 226 | 12:00
Bibiana | 236 | 18:00 | 232 | 10:00 | Mirsorai | 232 | 19:30 | 223 | 11:00
BIPTC | 236 | 01:00 | 226 | 12:00 | Naogaon | 223 | 01:00 | 132 | 03:00
Bogura | 234 | 18:00 | 226 | 07:00 | Purbasadipur | 227 | 17:00 | 211 | 07:00
Bogura-400 | 233 | 18:00 | 224 | 07:00 | Rajshahi | 232 | 01:00 | 223 | 07:00
Borhanuddin | 233 | 09:00 | 230 | 12:00 | Rampal | 230 | 00:00 | 222 | 22:00
BSRM | 231 | 19:30 | 225 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 232 | 19:30 | 222 | 12:00 | Rampura | 230 | 06:00 | 223 | 13:00
Cumilla(N) | 231 | 19:30 | 224 | 12:00 | Shikalbaha | 234 | 00:00 | 228 | 11:00
Faridpur | 225 | 01:00 | 220 | 11:00 | Shyampur | 231 | 19:30 | 224 | 11:00
Fenchuganj | 240 | 07:00 | 237 | 10:00 | Siddhirganj | 231 | 22:00 | 226 | 11:00
Feni | 232 | 19:30 | 225 | 10:00 | Sirajgonj | 239 | 01:00 | 235 | 12:00
Ghorashal | 232 | 01:00 | 228 | 00:00 | Sreepur | 231 | 19:00 | 223 | 14:00
Ghorashal-230 | 230 | 07:00 | 224 | 12:00 | Tongi | 233 | 04:00 | 227 | 10:00
Gopalganj | 224 | 01:00 | 220 | 13:00
GPH | 233 | 19:30 | 228 | 10:00
Haripur | 231 | 19:30 | 225 | 12:00
Hasnabad | 230 | 04:00 | 223 | 12:00
Hathazari | 231 | 00:00 | 227 | 04:00
Ishurdi | 235 | 01:00 | 228 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 04:00 | 130 | 12:00 | Madunaghat | 135 | 00:00 | 132 | 10:00
Agargaon | 136 | 03:00 | 131 | 13:00 | Magura | 135 | 00:00 | 127 | 20:00
Agrabad | 133 | 00:00 | 129 | 12:00 | Mahasthangarh | 132 | 17:00 | 126 | 07:00
AKS | 131 | 00:00 | 128 | 12:00 | Maijdee | 129 | 19:30 | 124 | 03:00
Aminbazar | 133 | 07:00 | 128 | 12:00 | Manikganj | 130 | 08:00 | 126 | 00:00
Amnura | 136 | 03:00 | 128 | 12:00 | Maniknagar | 135 | 03:00 | 130 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 117 | 00:00 | 111 | 06:00
Ashuganj-230 | 140 | 02:00 | 136 | 00:00 | Matuail | 134 | 18:00 | 130.5 | 12:00
Bagerhat | 127 | 00:00 | 119 | 06:00 | Metrorail_Motijheel | 135 | 03:00 | 130 | 12:00
Bajitpur | 135 | 02:00 | 130 | 14:00 | Metrorail_Uttara | 134 | 03:00 | 130 | 12:00
Bakerganj | 135 | 05:00 | 131 | 19:00 | Millgate | 135 | 03:00 | 132 | 11:00
Bakulia | 134 | 00:00 | 130 | 10:00 | Mirpur | 132 | 05:00 | 127 | 13:00
Banani | 134 | 02:00 | 130 | 11:00 | Mirzapur | 136 | 02:00 | 128 | 11:00
Bangabhaban | 135 | 04:00 | 130 | 12:00 | Mithapukur | 131 | 22:00 | 122 | 07:00
Barapukuria | 133 | 17:00 | 125 | 07:00 | MI_Cement | 132 | 18:00 | 125 | 12:00
Barguna | 134 | 08:00 | 131 | 02:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 136 | 08:00 | 133 | 12:00 | Mogbazar | 135 | 01:00 | 123 | 14:00
Barishal-230 | 135 | 07:00 | 132 | 12:00 | Mongla | 128 | 00:00 | 121 | 21:00
Baroaulia | 134 | 00:00 | 130 | 12:00 | Motijheel | 135 | 04:00 | 130 | 12:00
Baroirhat | 132 | 01:00 | 128 | 10:00 | Muktagacha | 130 | 00:00 | 118 | 07:00
Bashundhara | 135 | 05:00 | 129 | 13:00 | Munshiganj | 135 | 08:00 | 129 | 10:00
BashundharaCement | 135 | 19:30 | 131 | 11:00 | Muradnagar | 131 | 19:30 | 127 | 10:00
Beanibazar | 134 | 23:00 | 126 | 18:30 | Mymensingh | 134 | 00:00 | 120 | 07:00
Benapole | 130 | 00:00 | 120 | 21:00 | Nabinagar | 132 | 04:00 | 128 | 00:00
Bhaluka | 137 | 21:00 | 131 | 14:00 | Naogaon | 136 | 00:00 | 124 | 08:00
Bhandaria | 132 | 07:00 | 125 | 21:00 | Narail | 134 | 00:00 | 126 | 22:00
Bhangura | 133 | 01:00 | 128 | 07:00 | Narinda | 135 | 03:00 | 130 | 12:00
Bheramara | 135 | 00:00 | 132 | 07:00 | Narshingdi | 133 | 04:00 | 121 | 18:30
Bheramara(GK) | 135 | 00:00 | 133 | 02:00 | Natore | 133 | 01:00 | 127 | 12:00
Bhulta | 127 | 18:30 | 124 | 10:00 | Nawabganj | 134 | 08:00 | 129 | 11:00
Bog-Sherpur | 133 | 01:00 | 128 | 07:00 | Netrakona | 130 | 01:00 | 124 | 08:00
Bogura | 135 | 00:00 | 129 | 08:00 | New | 136 | 04:00 | 132 | 10:00
Bogura-230 | 135 | 17:00 | 129 | 07:00 | Niamatpur | 136 | 00:00 | 131 | 08:00
Brahmanbaria | 135 | 03:00 | 129 | 21:00 | Noapara | 132 | 00:00 | 124 | 20:00
Cantonment | 136 | 04:00 | 126 | 06:00 | Pabna | 133 | 00:00 | 129 | 12:00
Chandina | 133 | 18:00 | 130 | 10:00 | Palashbari | 128 | 17:00 | 120 | 10:00
Chandpur | 134 | 19:00 | 124 | 10:00 | Panchagarh | 138 | 17:00 | 126 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 135 | 00:00 | 132 | 11:00 | Patiya | 134 | 00:00 | 128 | 10:00
Chapai | 136 | 00:00 | 131 | 10:00 | Patuakhali | 134 | 08:00 | 131 | 22:00
Charsaidpur | 134 | 19:00 | 131 | 09:00 | Payra | 135 | 00:00 | 134 | 21:00
Chauddagram | 130 | 18:00 | 127 | 02:00 | PHP | 131 | 18:00 | 128 | 07:00
Chhatak | 132 | 23:00 | 127 | 10:00 | Postogola | 133 | 18:00 | 128 | 12:00
Chowmuhani | 128 | 18:00 | 125 | 07:00 | Pubail | 139 | 18:30 | 133 | 06:00
Chuadanga | 132 | 01:00 | 121 | 21:00 | Purbachal | 135 | 06:00 | 129 | 12:00
Coxsbazar | 119 | 00:00 | 110 | 06:00 | Purbasadipur | 132 | 17:00 | 122 | 07:00
Cumilla(N) | 133 | 18:00 | 129 | 12:00 | Rahanpur | 138 | 00:00 | 134 | 07:00
Cumilla(S) | 133 | 19:30 | 120 | 13:00 | Rahanpur-400 | 139 | 00:00 | 135 | 07:00
Daganbhuiyan | 129 | 18:00 | 125 | 12:00 | Rahim | 133 | 01:00 | 129 | 12:00
Daudkandi | 129 | 00:00 | 125 | 05:00 | Rajbari | 128 | 00:00 | 125 | 11:00
DhakaUniversity | 134 | 03:00 | 130 | 12:00 | Rajendrapur | 138 | 02:00 | 130 | 14:00
Dhamrai | 133 | 07:00 | 129 | 10:00 | Rajshahi | 133 | 01:00 | 126 | 10:00
Dhanmondi | 135 | 19:30 | 131.5 | 12:00 | Rajshahi-230 | 134 | 01:00 | 128 | 12:00
Dohazari | 130 | 01:00 | 123 | 10:00 | Ramganj | 130 | 18:00 | 121 | 10:00
Faridpur | 130 | 00:00 | 126 | 22:00 | Rampur | 134 | 00:00 | 129 | 10:00
Fatullah | 133 | 18:00 | 127 | 11:00 | Rampura | 134 | 04:00 | 129 | 13:00
Fenchuganj | 136 | 06:00 | 133 | 15:00 | Rangamati | 134 | 00:00 | 131 | 10:00
Feni | 129 | 00:00 | 126 | 10:00 | Rangpur | 131 | 17:00 | 124 | 10:00
Feni-230 | 130 | 19:30 | 126 | 10:00 | Ruppur | 135 | 00:00 | 130 | 06:00
Ghatail | 130 | 03:00 | 121 | 07:00 | Saidpur | 131 | 00:00 | 123 | 07:00
Ghorashal | 139 | 05:00 | 137 | 00:00 | Satkhira | 129 | 00:00 | 119 | 07:00
Goalpara | 132 | 01:00 | 126 | 21:00 | Satmasjid | 136 | 03:00 | 131 | 13:00
Gollamari | 133 | 00:00 | 127 | 20:00 | Savar | 131 | 06:00 | 126 | 12:00
Gopalganj | 133 | 00:00 | 129 | 04:00 | SevenRings | 139 | 03:00 | 136 | 10:00
Gopalganj-400 | 133 | 00:00 | 131 | 11:00 | ShahCement | 134 | 19:00 | 131 | 09:00
Gulshan | 134 | 05:00 | 129 | 13:00 | Shahjadpur | 136 | 00:00 | 131 | 12:00
Halishahar | 135 | 01:00 | 130 | 12:00 | Shahjibazar | 134 | 02:00 | 128 | 22:00
Haripur | 134 | 04:00 | 131 | 10:00 | Shahmirpur | 134 | 00:00 | 130 | 10:00
HaripurSBU | 134 | 04:00 | 131 | 10:00 | Shariatpur | 133 | 12:00 | 129 | 18:30
Hasnabad | 133 | 19:00 | 128 | 12:00 | Sherpur | 133 | 00:00 | 111 | 07:00
Hathazari | 135 | 00:00 | 132 | 10:00 | Shikalbaha | 123 | 00:00 | 120 | 09:00
Hatirjheel | 135 | 05:00 | 130 | 13:00 | Shikalbaha-230 | 135 | 00:00 | 131 | 11:00
Ishurdi | 137 | 01:00 | 133 | 07:00 | Shitalakhya | 132 | 18:00 | 125 | 12:00
Jaldhaka | 130 | 23:00 | 122 | 10:00 | Sholosohor | 135 | 00:00 | 132 | 04:00
Jamalpur | 130 | 00:00 | 114 | 07:00 | Shyampur | 133 | 19:00 | 126 | 12:00
Jashore | 131 | 00:00 | 121 | 21:00 | Shyampur-230 | 134 | 19:30 | 128 | 11:00
Jhenaidah | 136 | 00:00 | 125 | 06:00 | Siddhirganj | 134 | 07:00 | 131 | 09:00
Jhenaidah-230 | 137 | 01:00 | 127 | 22:00 | Sirajganj | 133 | 05:00 | 125 | 12:00
Joydebpur | 137 | 00:00 | 134 | 16:00 | Sonargaon | 132 | 21:00 | 129 | 10:00
Joypurhat | 127 | 00:00 | 119 | 07:00 | Sreemongol | 134 | 02:00 | 129 | 22:00
Juldah | 135 | 00:00 | 130 | 12:00 | Sreepur | 138 | 02:00 | 133 | 14:00
Kabirpur | 139 | 00:00 | 127 | 01:00 | Srinagar | 134 | 19:00 | 129 | 12:00
Kachua | 133 | 19:30 | 126 | 06:00 | SSM | 140 | 00:00 | 138 | 01:00
Kaliakoir | 140 | 05:00 | 130 | 11:00 | Sunamganj | 130 | 23:00 | 122 | 21:00
Kaliganj | 135 | 00:00 | 127 | 21:00 | Sylhet | 134 | 23:00 | 129 | 22:00
Kallyanpur | 132 | 07:00 | 127 | 12:00 | Sylhet-132 | 133 | 23:00 | 130 | 09:00
Kalurghat | 135 | 00:00 | 132 | 10:00 | Tangail | 132 | 04:00 | 122 | 13:00
Kamrangirchar | 135 | 04:00 | 126 | 12:00 | Taraganj | 131 | 18:00 | 122 | 07:00
Kaptai | N/A | N/A | N/A | N/A | Tasnim | 132 | 21:00 | 129 | 10:00
Kasba | 130 | 19:00 | 126 | 12:00 | Thakurgaon | 137 | 17:00 | 123 | 10:00
Kazla | 137 | 07:00 | 130 | 12:00 | TK | 135 | 00:00 | 132 | 10:00
Keranigonj | 135 | 08:00 | 129 | 12:00 | Tongi | 137 | 04:00 | 133 | 12:00
Khagrachori | 132 | 00:00 | 130 | 10:00 | Ullahpara | 134 | 01:00 | 128 | 10:00
Khulna | 132 | 00:00 | 126 | 21:00 | Ullon | 134 | 08:00 | 130 | 11:00
Khulna(S) | 133 | 00:00 | 127 | 21:00 | Uttara | 135 | 08:00 | 129 | 12:00
Khulshi | 132 | 01:00 | 128 | 14:00 | UttaraNew | 135 | 07:00 | 130 | 12:00
Kishoreganj | 135 | 01:00 | 128 | 14:00 | Zigatola | 135 | 19:30 | 130 | 12:00
Kodda | 140 | 15:00 | 134 | 10:00
Korerhat | 134 | 19:30 | 129 | 10:00
KSRM | 134 | 00:00 | 131 | 01:00
Kulaura | 135 | 06:00 | 133 | 00:00
Kurigram | 129 | 22:00 | 120 | 10:00
Kushtia | 133 | 01:00 | 129 | 05:00
Laksam | 132 | 18:00 | 126 | 10:00
Lakshmipur | 128 | 01:00 | 124 | 03:00
Lalbag | 134 | 06:00 | 129 | 12:00
Lalmonirhat | 128 | 22:00 | 121 | 05:00
Madanganj | 135 | 19:30 | 131 | 11:00
Madaripur | 133 | 00:00 | 130 | 22:00
Madartek | 134 | 05:00 | 129 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division