## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 16-04-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-04-2026 | during | 16-04-2026 | during | 16-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 184 | 404 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 180 | 450 | 450 | 226 | 226 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 320 | 326 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 18 | 18 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 136 | 137 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 24 | 33 | 33 | 29 | 29 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 40 | 50 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 245 | 290 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 133 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 35 | 162 | 162 | 35 | 35 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 33 | 0 | 33 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 565 | 450 | 584 | 584 | 526 | 526 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 142 | 142 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2280 | 2456 | 5948.22 | 5915.22 | 2638.55 | 2659.55
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 16 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50 | 19 | 50 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 | 70 | 70 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 212 | 220 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 51 | 105 | 105 | 34 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 40 | 48 | 56 | 64 | 54 | 54 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 67 | 68 | 68 | 34 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 16 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 37 | 38 | 108 | 108 | 38 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.12 | 0 | 3.99 | 0 | 3.99 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 18 | 54.36 | 54.36 | 0 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 56 | 110 | 110 | 54 | 54 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 99 | 17 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 17 | 163 | 163 | 163 | 17 | 163 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 292 | 612 | 1224 | 1224 | 310 | 310 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 21 | 6 | 10 | 0 | 10 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 160 | 160 | 160 | 160 | 160 | 160 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1135.12 | 1657.5 | 3061.85 | 3061.86 | 1212.49 | 1449.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 206 | 198 | 221 | 221 | 205 | 205 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 0 | 0 | 240 | 240 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 330 | 345 | 342.01 | 342.01 | 342.01 | 342.01 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 372 | 340 | 393 | 393 | 375 | 375 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 41 | 42 | 41.65 | 41.65 | 37 | 37 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 43 | 20 | 52.82 | 52.82 | 45 | 45 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 86 | 86 | 195 | 195 | 87 | 87 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Machine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 140 | 150 | 150 | 20 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 21 | 27 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 190 | 200 | 200 | 35 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 176 | 194 | 84 | 76 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 9 | 113 | 113 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 20 | 51 | 115 | 115 | 0 | 51 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 52 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.745 | 1457 | 1706 | 2654.18 | 2576.18 | 1481.01 | 1727.01
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-04-2026 | during | 16-04-2026 | during | 16-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 67 | 70 | 157.5 | 157.5 | 20 | 20 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.97 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 61 | 60 | 60 | 10 | 50 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 10 | 10 | 60 | 60 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 20.76 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 156.73 | 187 | 352.1 | 304 | 167.1 | 159
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 0 | 0 | 0 | 0 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 153 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 101 | 102 | 100 | 100 | 100 | 100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 52 | 33 | 83 | 83 | 53 | 53 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 97 | 95 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 17 | 17 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 349 | 337 | 350 | 350 | 320 | 320 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1206 | 1144 | 1234 | 1234 | 1104 | 1104
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 908 | 908 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 23.5 | 27 | 27 | 25 | 25 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 23 | 32 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 250 | 410 | 410 | 150 | 150 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 64.29 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 606 | 604 | 617.1 | 617.1 | 597 | 1200
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1851.29 | 1817.5 | 2965.1 | 2880.1 | 1922.1 | 2440.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 255 | 304 | 250 | 300 | 250 | 300 | Plant availability less
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 107 | 101 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 125 | 125 | 130 | 130 | 130 | 130 | STG Under Maintenance
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1195 | 1225 | 1244 | 1244 | 1200 | 1200 | Machine Problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.75 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2226.75 | 2259 | 2412 | 2461 | 2224 | 2273
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 58.07 | 0 | 62 | 0 | 62 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 47 | 43 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 23 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 158 | 195 | 214 | 214 | 200 | 200 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 169 | 172 | 220 | 220 | 175 | 175 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 404 | 359 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 30 | 30 | 0 | 0 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 48 | 92 | 92 | 0 | 51 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 1 | 50 | 113 | 113 | 0 | 50 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.67 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1494.01 | 1481.14 | 1435.88 | 1435.88 | 1362 | 1362 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 60.72 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 107 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2501.47 | 2431.14 | 3243.37 | 3014.87 | 2416.91 | 2324.41
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 51 | 49 | 55 | 55 | 55 | 55 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 92 | 113 | 113 | 35 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.1 | 0 | 6.8 | 0 | 6.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 14 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 128 | 0 | 166.22 | 0 | 166.22 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 235.1 | 191 | 500.02 | 297 | 408.02 | 205
System Total |  |  |  |  | 28823.2 | 29269.987 | 13049.46 | 13849.14 | 22370.84 | 21744.23 | 13574.18 | 14341.57
Forecast Scenario (16-04-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12828 |  | 696 |  | 13550
|  |  |  | 1:00 | 12462 |  | 418 |  | 12900
|  |  |  | 2:00 | 12265 |  | 893 |  | 13200
|  |  |  | 3:00 | 12060 |  | 993 |  | 13100
|  |  |  | 4:00 | 12042 |  | 915 |  | 13000
|  |  |  | 5:00 | 11985 |  | 874 |  | 12900
|  |  |  | 6:00 | 11972 |  | 791 |  | 12800
|  |  |  | 7:00 | 11918 |  | 1033 |  | 13000
|  |  |  | 8:00 | 11944 |  | 1056 |  | 13050
|  |  |  | 9:00 | 12001 |  | 1241 |  | 13300
|  |  |  | 10:00 | 12013 |  | 1420.085 |  | 13500
|  |  |  | 11:00 | 12150 |  | 1480.25 |  | 13700
|  |  |  | 12:00 | 12500 |  | 1432.5 |  | 14000
|  |  |  | 13:00 | 12600 |  | 1384.75 |  | 14050
|  |  |  | 14:00 | 12800 |  | 1337 |  | 14200
|  |  |  | 15:00 | 12900 |  | 1337 |  | 14300
|  |  |  | 16:00 | 12950 |  | 1480.25 |  | 14500
|  |  |  | 17:00 | 13000 |  | 1384.75 |  | 14450
|  |  |  | 18:00 | 13200 |  | 1432.5 |  | 14700
|  |  |  | 18:30 | 13300 |  | 1384.75 |  | 14750
|  |  |  | 19:00 | 14000 |  | 1146 |  | 15200
|  |  |  | 19:30 | 14050 |  | 1193.75 |  | 15300
|  |  |  | 20:00 | 14100 |  | 1193.75 |  | 15350
|  |  |  | 21:00 | 14300 |  | 1146 |  | 15500
|  |  |  | 22:00 | 13800 |  | 1337 |  | 15200
|  |  |  | 23:00 | 13000 |  | 1528 |  | 14600
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 14000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 1146
Probable Maximum Demand at Evening Peak: |  |  | 15500.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14300.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 292.015 MKWHr. |  | 0 | 160 | 190 | 200 | 90 | 170 | 66 | 150 | 120 | 1146
*** This report is generated digitally from Operation Information System (OIS) at 08:56 hrs on 16-04-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 15-04-2026 | [28 empty] | Date: | 15-04-2026 | [28 empty] | Date: | 15-04-2026 | [28 empty] | Date: | 15-04-2026 | [28 empty] | Date: | 15-04-2026 | [17 empty] | Date: | 15-04-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 96 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 17 | 149 | 140 | 293 | 47 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 142 | 21 | 21 | 0 | 450 | 100 | 16 | 38 | 0 | 1 | 67 | 54 | 18 | 12 | 12 | 0 | 70 | 56 | 34 | 160 | 17 | 0 | 50 | 25.5 | 33 | 218 | 0 | 0 | 0 | 320 | 0 | 20 | 63 | 393 | 0 | 345 | 44 | 20 | 196 | 42 | 17 | 0 | 100 | 0 | 20 | 0 | 186 | 0 | 0 | 37 | 310 | 0 | 372 | 41 | 30 | 160 | 0 | 12 | 0 | 53 | 30 | 101 | 0 | 97 | 0 | 9 | 57 | 101 | 0 | 0 | 12 | 6576.5 | 909 | 250 | 0 | 20 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605 | 0 | 0 | 0 | 1481 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 171 | 0 | 414 | 0 | 0 | 0 | 50 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 307 | 130 | 220 | 0 | 311 | 1220 | 17 | 6599 | 13175.5 | 80.03
01:00 | 0 | 92 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 149 | 141 | 293 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 142 | 21 | 21 | 0 | 440 | 96 | 16 | 37 | 0 | 0 | 0 | 54 | 18 | 12 | 12 | 0 | 70 | 51 | 35 | 160 | 17 | 0 | 22 | 25.5 | 34 | 218 | 0 | 0 | 0 | 295 | 0 | 20 | 63 | 393 | 0 | 345 | 44 | 20 | 199 | 42 | 17 | 0 | 22 | 0 | 20 | 0 | 186 | 0 | 0 | 37 | 315 | 0 | 372 | 41 | 30 | 160 | 0 | 12 | 0 | 53 | 30 | 101 | 0 | 97 | 0 | 9 | 58 | 105 | 0 | 0 | 8 | 6353.5 | 909 | 250 | 0 | 14 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604 | 0 | 0 | 0 | 1456 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 170 | 0 | 407 | 0 | 0 | 0 | 50 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 307 | 130 | 220 | 0 | 253 | 1212 | 17 | 6379 | 12732.5 | 80.01
02:00 | 0 | 103 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 149 | 141 | 293 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 142 | 21 | 21 | 0 | 400 | 102 | 16 | 38 | 0 | 0 | 0 | 54 | 18 | 12 | 12 | 0 | 70 | 45 | 35 | 160 | 17 | 0 | 19 | 25.5 | 34 | 218 | 0 | 0 | 0 | 290 | 0 | 20 | 0 | 240 | 170 | 345 | 44 | 0 | 205 | 0 | 16 | 0 | 17 | 0 | 20 | 0 | 180 | 0 | 0 | 28 | 315 | 0 | 372 | 41 | 30 | 160 | 0 | 12 | 0 | 53 | 30 | 100 | 0 | 97 | 0 | 9 | 58 | 105 | 0 | 0 | 12 | 6200.5 | 909 | 250 | 0 | 14 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604 | 0 | 0 | 0 | 1479 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 175 | 0 | 374 | 0 | 0 | 0 | 51 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 307 | 130 | 220 | 0 | 254 | 1212 | 17 | 6384 | 12584.5 | 79.99
03:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 149 | 142 | 293 | 55 | 0 | 17 | 0 | 200 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 21 | 21 | 0 | 400 | 92 | 16 | 37 | 0 | 0 | 0 | 54 | 18 | 12 | 12 | 0 | 70 | 55 | 35 | 160 | 17 | 0 | 19 | 25.5 | 34 | 220 | 0 | 0 | 0 | 295 | 0 | 20 | 0 | 270 | 170 | 345 | 44 | 0 | 193 | 0 | 17 | 0 | 17 | 0 | 20 | 0 | 176 | 0 | 0 | 23 | 320 | 0 | 372 | 41 | 30 | 159 | 0 | 12 | 0 | 30 | 30 | 100 | 0 | 97 | 0 | 9 | 58 | 105 | 0 | 0 | 0 | 6136.5 | 908 | 250 | 0 | 14 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604 | 0 | 0 | 0 | 1484 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 164 | 0 | 379 | 0 | 0 | 0 | 50 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 307 | 130 | 220 | 0 | 255 | 1212 | 17 | 6360 | 12496.5 | 79.97
04:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 149 | 142 | 293 | 55 | 0 | 17 | 0 | 200 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 142 | 21 | 21 | 0 | 400 | 95 | 16 | 38 | 0 | 1 | 0 | 54 | 0 | 12 | 12 | 0 | 70 | 55 | 35 | 160 | 17 | 0 | 19 | 25.5 | 34 | 220 | 0 | 0 | 0 | 290 | 0 | 20 | 0 | 305 | 170 | 345 | 44 | 0 | 189 | 0 | 17 | 0 | 17 | 0 | 20 | 0 | 172 | 0 | 0 | 30 | 315 | 0 | 372 | 41 | 30 | 161 | 0 | 16 | 0 | 50 | 30 | 99 | 0 | 97 | 0 | 9 | 58 | 105 | 0 | 0 | 0 | 6189.5 | 908 | 250 | 0 | 14 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 0 | 0 | 0 | 1481 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 166 | 0 | 373 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 307 | 130 | 220 | 0 | 255 | 1212 | 17 | 6325 | 12514.5 | 79.95
05:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 149 | 141 | 293 | 55 | 0 | 17 | 0 | 200 | 0 | 0 | 0 | 17 | 326 | 0 | 0 | 0 | 142 | 21 | 21 | 0 | 440 | 97 | 16 | 37 | 0 | 5 | 0 | 54 | 0 | 12 | 12 | 0 | 70 | 54 | 35 | 160 | 17 | 0 | 19 | 25.5 | 34 | 220 | 0 | 0 | 0 | 290 | 0 | 20 | 8 | 365 | 0 | 345 | 44 | 0 | 183 | 10 | 17 | 0 | 17 | 0 | 20 | 0 | 172 | 0 | 0 | 30 | 315 | 0 | 372 | 41 | 30 | 161 | 0 | 16 | 0 | 53 | 30 | 101 | 0 | 98 | 0 | 9 | 58 | 105 | 0 | 0 | 0 | 6166.5 | 909 | 250 | 0 | 14 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 0 | 0 | 0 | 1444 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 170 | 0 | 406 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 307 | 130 | 220 | 0 | 253 | 1212 | 17 | 6327 | 12493.5 | 79.93
06:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 0 | 149 | 141 | 293 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 1 | 142 | 21 | 21 | 0 | 544 | 99 | 16 | 38 | 0 | 6 | 0 | 54 | 0 | 12 | 12 | 0.12 | 70 | 55 | 31 | 160 | 17 | 0 | 19 | 25.5 | 34 | 220 | 0 | 0 | 0 | 293 | 0 | 20 | 80 | 375 | 0 | 345 | 44 | 10 | 182 | 42 | 17 | 0 | 17 | 0 | 20 | 0 | 170 | 0 | 2 | 30 | 310 | 0 | 372 | 41 | 30 | 161 | 0 | 0 | 0 | 53 | 30 | 100 | 0 | 98 | 0 | 9 | 58 | 105 | 0.03 | 0.23 | 0 | 6362.88 | 909 | 250 | 0 | 14 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 608 | 0 | 0 | 0 | 1464 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81 | 0 | 0 | 0 | 0.99 | 151 | 0 | 0 | 0 | 172 | 0 | 414 | 0 | 0.09 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 106 | 307 | 130 | 220 | 0 | 255 | 1212 | 17 | 6354.89 | 12717.77 | 79.92
07:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 149 | 141 | 293 | 47 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 6 | 142 | 23 | 21 | 0 | 530 | 97 | 16 | 37 | 0 | 8 | 0 | 54 | 0 | 12 | 12 | 0 | 70 | 55 | 28 | 160 | 17 | 0 | 19 | 25.5 | 34 | 220 | 0 | 0 | 0 | 291 | 3 | 20 | 145 | 307 | 0 | 320 | 44 | 20 | 173 | 42 | 17 | 0 | 17 | 0 | 20 | 0 | 160 | 0 | 14 | 30 | 310 | 0 | 372 | 41 | 30 | 155 | 1 | 8 | 0 | 53 | 30 | 100 | 0 | 98 | 0 | 9 | 58 | 105 | 0.16 | 11.45 | 0 | 6006.11 | 908 | 250 | 0 | 14 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 588 | 0 | 0 | 0 | 1469 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.74 | 17 | 0 | 0 | 5.44 | 146 | 0 | 0 | 0 | 167 | 0 | 355 | 0 | 0.62 | 0 | 51 | 0 | 2 | 0 | 0 | 0 | 0 | 0.9 | 18 | 0.08 | 104 | 307 | 130 | 220 | 0 | 255 | 1212 | 17 | 6324.78 | 12330.89 | 79.91
08:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 0 | 149 | 141 | 293 | 51 | 2 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 13 | 142 | 0 | 21 | 0 | 535 | 89 | 16 | 38 | 0 | 5 | 0 | 54 | 0 | 12 | 12 | 0 | 70 | 55 | 3 | 160 | 17 | 0 | 19 | 18 | 34 | 218 | 0 | 0 | 0 | 293 | 6 | 20 | 150 | 345 | 0 | 345 | 44 | 40 | 191 | 42 | 17 | 0 | 17 | 0 | 20 | 0 | 176 | 0 | 31 | 30 | 310 | 0 | 372 | 41 | 30 | 141 | 4 | 17 | 0 | 53 | 30 | 100 | 0 | 98 | 0 | 9 | 58 | 105 | 0.38 | 10.05 | 0 | 6259.43 | 907 | 250 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 607 | 0 | 0 | 0 | 1460 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.95 | 43 | 0 | 0 | 25.3 | 142 | 0 | 0 | 0 | 162 | 0 | 376 | 0 | 2.06 | 0 | 51 | 0 | 9 | 0 | 0 | 0 | 0 | 2.4 | 69 | 0.28 | 99 | 307 | 130 | 220 | 0 | 255 | 1212 | 17 | 6458.99 | 12718.42 | 79.9
09:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 149 | 139 | 293 | 52 | 17 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 22 | 142 | 28 | 21 | 0 | 530 | 95 | 16 | 38 | 0 | 5 | 0 | 54 | 0 | 12 | 12 | 2.87 | 70 | 55 | 2 | 160 | 17 | 0 | 19 | 17 | 34 | 216 | 0 | 0 | 0 | 290 | 15 | 20 | 140 | 393 | 0 | 345 | 44 | 47 | 189 | 42 | 16 | 0 | 17 | 0 | 20 | 0 | 186 | 0 | 43 | 29 | 315 | 0 | 358 | 42 | 30 | 159 | 6 | 17 | 0 | 53 | 30 | 100 | 0 | 100 | 0 | 9 | 58 | 100 | 0.72 | 10 | 0 | 6353.59 | 907 | 250 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 70.14 | 603 | 0 | 0 | 0 | 1459 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.5 | 72 | 0 | 0 | 33.26 | 153 | 0 | 0 | 0 | 169 | 0 | 358 | 0 | 3.43 | 0 | 51 | 0 | 11 | 0 | 0 | 0 | 0 | 2.3 | 76 | 0.55 | 103 | 307 | 130 | 220 | 0 | 255 | 1205 | 17 | 6565.18 | 12918.77 | 79.89
10:00 | 0 | 88 | 49 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 149 | 139 | 276 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 25 | 142 | 26 | 14 | 0 | 540 | 95 | 16 | 37 | 0 | 19 | 0 | 54 | 0 | 12 | 12 | 3.68 | 70 | 55 | 2 | 160 | 17 | 0 | 19 | 16 | 34 | 214 | 0 | 0 | 0 | 291 | 0 | 20 | 81 | 305 | 0 | 340 | 44 | 46 | 203 | 42 | 17 | 0 | 17 | 0 | 20 | 0 | 178 | 0 | 50 | 22 | 315 | 0 | 361 | 42 | 30 | 159 | 10 | 17 | 0 | 53 | 30 | 100 | 0 | 100 | 0 | 9 | 58 | 95 | 0.98 | 25 | 0 | 6187.66 | 907 | 250 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 80.38 | 607 | 0 | 0 | 0 | 1495.89 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.97 | 94 | 0 | 0 | 51.46 | 156 | 0 | 0 | 0 | 169 | 0 | 385 | 0 | 3.57 | 0 | 51 | 35 | 13 | 0 | 0 | 0 | 0 | 0 | 160 | 0.24 | 105 | 307 | 130 | 220 | 0 | 254 | 1190 | 27 | 6805.51 | 12993.17 | 79.88
11:00 | 0 | 88 | 49 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 18 | 0 | 136 | 138 | 260 | 55 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 32 | 142 | 21 | 22 | 0 | 550 | 100 | 16 | 38 | 0 | 17 | 0 | 32 | 0 | 12 | 12 | 1.87 | 70 | 55 | 2 | 160 | 17 | 0 | 19 | 17 | 34 | 213 | 0 | 0 | 0 | 290 | 17 | 20 | 81 | 315 | 0 | 335 | 44 | 45 | 208 | 42 | 17 | 0 | 17 | 7 | 20 | 0 | 172 | 0 | 32 | 21 | 320 | 0 | 349 | 42 | 30 | 157 | 11 | 17 | 0 | 53 | 30 | 97 | 0 | 100 | 0 | 9 | 58 | 80 | 2.16 | 44.86 | 0 | 6175.89 | 908 | 250 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 85.13 | 606 | 0 | 0 | 0 | 1485.74 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.28 | 105 | 0 | 0 | 50.3 | 161 | 0 | 0 | 0 | 172 | 0 | 403 | 0 | 5.55 | 0 | 51 | 35 | 14 | 0 | 0 | 0 | 0 | 0 | 91 | 0.26 | 109 | 307 | 125 | 220 | 0 | 253 | 1190 | 17 | 6768.26 | 12944.15 | 79.87
12:00 | 0 | 88 | 40 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 18 | 0 | 133 | 136 | 245 | 55 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 32 | 142 | 21 | 22 | 0 | 565 | 99 | 16 | 37 | 0 | 21 | 0 | 40 | 0 | 12 | 12 | 4.12 | 70 | 55 | 2 | 160 | 17 | 0 | 19 | 16 | 34 | 212 | 0 | 0 | 0 | 292 | 17 | 20 | 86 | 372 | 0 | 330 | 44 | 43 | 206 | 41 | 20 | 0 | 17 | 9 | 20 | 0 | 176 | 0 | 52 | 21 | 320 | 0 | 349 | 42 | 30 | 156 | 12 | 17 | 0 | 52 | 30 | 101 | 0 | 97 | 0 | 9 | 58 | 67 | 1.97 | 20.76 | 0 | 6234.85 | 908 | 250 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 64.29 | 606 | 0 | 0 | 0 | 1494.01 | 0 | 47 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 58.07 | 107 | 0 | 0 | 60.72 | 158 | 0 | 0 | 0 | 169 | 0 | 404 | 0 | 2.67 | 0 | 51 | 35 | 14 | 0 | 0 | 0 | 0 | 7.1 | 128 | 0.75 | 107 | 307 | 125 | 220 | 0 | 255 | 1195 | 17 | 6814.61 | 13049.46 | 79.86
13:00 | 0 | 88 | 40 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 18 | 0 | 132 | 134 | 245 | 33 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 17 | 325 | 0 | 0 | 32 | 142 | 23.8 | 22 | 0 | 530 | 91 | 16 | 37 | 0 | 29 | 0 | 40 | 0 | 12 | 12 | 3.09 | 68 | 66 | 0 | 160 | 17 | 0 | 19 | 16 | 34 | 214 | 0 | 0 | 0 | 292 | 17 | 20 | 86 | 372 | 0 | 335 | 44 | 43 | 187 | 37 | 17 | 0 | 25 | 9 | 20 | 0 | 186 | 0 | 71 | 28 | 315 | 0 | 349 | 42 | 30 | 154 | 7 | 17 | 0 | 51 | 30 | 100 | 0 | 97 | 0 | 9 | 57 | 66 | 1.9 | 49.26 | 0 | 6243.05 | 907 | 250 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 74.34 | 605 | 0 | 0 | 0 | 1487.91 | 0 | 47 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 56.07 | 103 | 0 | 0 | 60.99 | 162 | 0 | 0 | 0 | 172 | 0 | 379 | 0 | 5.45 | 0 | 51 | 35 | 21 | 0 | 0 | 0 | 0 | 6.6 | 164 | 0.31 | 109 | 307 | 125 | 220 | 0 | 255 | 1200 | 17 | 6874.67 | 13117.72 | 79.85
14:00 | 0 | 88 | 48 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 18 | 0 | 132 | 133 | 260 | 0 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 17 | 318 | 0 | 0 | 28 | 142 | 25 | 21 | 0 | 530 | 32 | 16 | 35 | 0 | 27 | 0 | 39 | 0 | 12 | 12 | 3.11 | 68 | 55 | 0 | 160 | 17 | 0 | 19 | 16 | 34 | 213 | 0 | 0 | 0 | 300 | 16 | 20 | 86 | 360 | 0 | 330 | 44 | 32 | 204 | 37 | 18 | 0 | 17 | 9 | 20 | 0 | 188 | 0 | 51 | 26 | 310 | 0 | 337 | 42 | 30 | 154 | 7 | 17 | 0 | 32 | 30 | 100 | 0 | 97 | 0 | 9 | 57 | 64 | 1.82 | 31.18 | 0 | 6058.11 | 908 | 250 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 79.85 | 602 | 0 | 0 | 0 | 1487.1 | 0 | 43 | 0 | 35 | 35 | 0 | 0 | 8 | 0 | 48.59 | 94 | 0 | 0 | 52.24 | 170 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 4.96 | 0 | 49 | 35 | 14 | 0 | 0 | 0 | 0 | 5.1 | 168 | 0.46 | 102 | 307 | 125 | 220 | 0 | 254 | 1200 | 17 | 6736.3 | 12794.41 | 79.84
15:00 | 0 | 88 | 48 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 18 | 0 | 149 | 133 | 257 | 0 | 12 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 320 | 0 | 0 | 21 | 142 | 24.5 | 21 | 0 | 530 | 13 | 16 | 32 | 0 | 27 | 0 | 39 | 0 | 12 | 12 | 2.31 | 68 | 55 | 0 | 160 | 17 | 0 | 19 | 16 | 34 | 213 | 0 | 0 | 0 | 300 | 12 | 18 | 97 | 360 | 0 | 327 | 44 | 20 | 202 | 37 | 18 | 0 | 17 | 0 | 20 | 0 | 188 | 0 | 32 | 26 | 315 | 0 | 337 | 42 | 30 | 153 | 7 | 17 | 0 | 32 | 30 | 102 | 0 | 96 | 0 | 9 | 57 | 64 | 1.33 | 33.72 | 0 | 6039.86 | 907 | 250 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 46.53 | 608 | 0 | 0 | 0 | 1493 | 0 | 43 | 0 | 35 | 35 | 0 | 0 | 14 | 0 | 37.06 | 75 | 0 | 0 | 39.6 | 194 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 3.57 | 0 | 48 | 35 | 9 | 0 | 0 | 0 | 0 | 2.3 | 54 | 0.46 | 104 | 307 | 125 | 220 | 0 | 303 | 1210 | 17 | 6634.52 | 12674.38 | 79.83
16:00 | 0 | 88 | 40 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 18 | 4 | 149 | 118 | 244 | 15 | 20 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 320 | 0 | 0 | 14 | 142 | 24.5 | 21 | 0 | 530 | 17 | 16 | 38 | 0 | 24 | 0 | 39 | 0 | 12 | 12 | 1.47 | 68 | 60 | 0 | 160 | 17 | 0 | 19 | 16 | 34 | 216 | 0 | 0 | 0 | 317 | 8 | 20 | 86 | 360 | 0 | 335 | 44 | 20 | 204 | 37 | 17 | 0 | 28 | 0 | 20 | 0 | 180 | 0 | 31 | 20 | 315 | 0 | 337 | 42 | 30 | 153 | 3 | 17 | 0 | 32 | 30 | 101 | 0 | 95 | 1 | 9 | 58 | 64 | 0.84 | 21.04 | 5 | 6034.85 | 907 | 350 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 34.12 | 605 | 0 | 0 | 0 | 1485.87 | 0 | 43 | 0 | 35 | 35 | 0 | 0 | 14 | 0 | 23.87 | 32 | 0 | 0 | 23.42 | 193 | 0 | 0 | 0 | 19 | 0 | 402 | 0 | 2.06 | 0 | 47 | 35 | 6 | 0 | 0 | 0 | 0 | 1.8 | 65 | 0.16 | 102 | 307 | 125 | 220 | 0 | 303 | 1210 | 17 | 6665.3 | 12700.15 | 79.82
17:00 | 0 | 105 | 40 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 0 | 18 | 17 | 141 | 118 | 285 | 30 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 321 | 0 | 0 | 6 | 142 | 18.5 | 21 | 0 | 530 | 17 | 16 | 37 | 0 | 19 | 0 | 39 | 0 | 12 | 12 | 0.6 | 70 | 57 | 2 | 160 | 17 | 0 | 19 | 16 | 34 | 215 | 0 | 0 | 0 | 400 | 3 | 16 | 86 | 365 | 0 | 335 | 44 | 20 | 205 | 37 | 18 | 0 | 70 | 0 | 20 | 0 | 174 | 0 | 12 | 24 | 305 | 0 | 337 | 42 | 30 | 153 | 2 | 17 | 0 | 32 | 30 | 100 | 0 | 95 | 17 | 9 | 61 | 56 | 0.31 | 7.37 | 7 | 6102.78 | 908 | 350 | 0 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19.23 | 607 | 0 | 0 | 0 | 1485.22 | 0 | 43 | 0 | 35 | 35 | 0 | 0 | 14 | 0 | 9.75 | 18 | 0 | 0 | 8.68 | 194 | 0 | 0 | 0 | 50 | 0 | 399 | 0 | 0.79 | 0 | 45 | 35 | 4 | 78 | 0 | 0 | 0 | 1.3 | 26 | 0.12 | 101 | 307 | 125 | 220 | 0 | 302 | 1210 | 17 | 6679.09 | 12781.87 | 79.81
18:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 18 | 30 | 145 | 118 | 290 | 45 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 1 | 142 | 22.5 | 21 | 0 | 450 | 17 | 16 | 37 | 0 | 10 | 0 | 39 | 0 | 12 | 12 | 0 | 70 | 55 | 6 | 160 | 17 | 0 | 37 | 16 | 34 | 214 | 0 | 0 | 0 | 420 | 0 | 15 | 86 | 365 | 0 | 340 | 44 | 20 | 203 | 38 | 24 | 0 | 176 | 3 | 20 | 0 | 170 | 0 | 1 | 27 | 305 | 0 | 337 | 42 | 30 | 153 | 0 | 17 | 0 | 32 | 30 | 100 | 0 | 95 | 17 | 9 | 63 | 68 | 0.04 | 0.76 | 12 | 6149.3 | 907 | 250 | 0 | 20 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25 | 590 | 0 | 0 | 0 | 1490.16 | 0 | 43 | 0 | 35 | 35 | 0 | 38 | 27 | 0 | 1.12 | 1 | 0 | 0 | 0.72 | 186 | 0 | 0 | 0 | 144 | 0 | 350 | 0 | 0.1 | 0 | 47 | 35 | 1 | 99 | 0 | 0 | 0 | 0.2 | 3 | 0.01 | 96 | 307 | 125 | 180 | 0 | 302 | 1212 | 17 | 6569.56 | 12718.86 | 79.8
19:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 54 | 35 | 149 | 120 | 290 | 55 | 55 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 324 | 0 | 0 | 0 | 142 | 23.5 | 21 | 0 | 530 | 17 | 16 | 37 | 0 | 8 | 67 | 48 | 0 | 12 | 12 | 0 | 70 | 56 | 6 | 160 | 17 | 0 | 50 | 16 | 51 | 214 | 0 | 0 | 0 | 612 | 0 | 98 | 86 | 355 | 0 | 342 | 44 | 20 | 201 | 36 | 52 | 0 | 180 | 10 | 20 | 0 | 196 | 0 | 0 | 27 | 300 | 0 | 337 | 42 | 30 | 150 | 0 | 17 | 0 | 32 | 30 | 101 | 0 | 96 | 17 | 9 | 60 | 70 | 0 | 0 | 12 | 6882.5 | 907 | 250 | 0 | 25.5 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 598 | 0 | 0 | 0 | 1488.88 | 0 | 43 | 0 | 35 | 45 | 0 | 48 | 27 | 0 | 0 | 0 | 28 | 0 | 0 | 182 | 0 | 0 | 0 | 183 | 0 | 376 | 0 | 0 | 0 | 48 | 35 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 307 | 125 | 180 | 0 | 303 | 1220 | 17 | 6702.38 | 13584.88 | 79.79
19:30 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 54 | 35 | 149 | 136 | 290 | 55 | 55 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 325 | 0 | 0 | 0 | 142 | 23.5 | 0 | 0 | 450 | 17 | 16 | 37 | 0 | 7 | 67 | 48 | 0 | 12 | 12 | 0 | 70 | 56 | 2 | 160 | 17 | 0 | 50 | 16 | 51 | 216 | 0 | 0 | 0 | 612 | 0 | 140 | 86 | 345 | 0 | 345 | 44 | 20 | 195 | 38 | 52 | 0 | 180 | 9 | 20 | 0 | 190 | 0 | 0 | 27 | 305 | 0 | 337 | 42 | 30 | 148 | 0 | 17 | 0 | 33 | 30 | 100 | 0 | 95 | 18 | 9 | 64 | 68 | 0 | 0 | 12 | 6896.5 | 907 | 250 | 0 | 23.5 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585 | 0 | 0 | 0 | 1479.09 | 0 | 43 | 0 | 35 | 50 | 0 | 48 | 27 | 0 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 0 | 0 | 158 | 0 | 346 | 0 | 0 | 0 | 48 | 44 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 307 | 125 | 180 | 0 | 301 | 1220 | 17 | 6601.59 | 13498.09
20:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 269 | 0 | 0 | 54 | 35 | 149 | 137 | 290 | 55 | 55 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 325 | 0 | 0 | 0 | 142 | 24 | 21 | 0 | 500 | 17 | 16 | 38 | 0 | 9 | 67 | 48 | 0 | 12 | 12 | 0 | 70 | 54 | 6 | 160 | 17 | 0 | 50 | 16 | 51 | 217 | 0 | 0 | 0 | 612 | 0 | 140 | 86 | 345 | 0 | 345 | 44 | 20 | 195 | 41 | 51 | 0 | 178 | 9 | 20 | 0 | 186 | 0 | 0 | 27 | 305 | 0 | 337 | 42 | 30 | 148 | 0 | 17 | 0 | 33 | 30 | 100 | 0 | 95 | 27 | 9 | 65 | 70 | 0 | 0 | 12 | 7002 | 907 | 250 | 0 | 23.5 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 1480.06 | 0 | 43 | 0 | 35 | 50 | 0 | 48 | 30 | 0 | 0 | 0 | 25 | 0 | 0 | 166 | 0 | 0 | 0 | 159 | 0 | 404 | 0 | 0 | 0 | 48 | 50 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 307 | 125 | 180 | 0 | 303 | 1222 | 17 | 6686.56 | 13688.56 | 79.78
21:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 18 | 35 | 149 | 137 | 290 | 55 | 35 | 35 | 0 | 180 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 142 | 24 | 21 | 0 | 450 | 17 | 16 | 38 | 0 | 6 | 67 | 48 | 18 | 12 | 12 | 0 | 70 | 56 | 16 | 160 | 163 | 0 | 50 | 25.5 | 51 | 220 | 0 | 0 | 0 | 612 | 0 | 140 | 86 | 340 | 0 | 345 | 44 | 20 | 198 | 42 | 51 | 0 | 190 | 9 | 20 | 0 | 194 | 0 | 0 | 27 | 305 | 0 | 337 | 42 | 30 | 153 | 0 | 17 | 0 | 33 | 30 | 102 | 0 | 95 | 35 | 9 | 61 | 70 | 0 | 0 | 12 | 7150.5 | 908 | 250 | 0 | 23.5 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604 | 0 | 0 | 0 | 1481.14 | 0 | 43 | 0 | 35 | 50 | 0 | 48 | 23 | 0 | 0 | 0 | 25 | 0 | 0 | 195 | 0 | 0 | 0 | 172 | 0 | 359 | 0 | 0 | 0 | 49 | 50 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 307 | 125 | 180 | 0 | 304 | 1225 | 17 | 6698.64 | 13849.14 | 79.77
22:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 18 | 35 | 149 | 121 | 292 | 55 | 0 | 35 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 22 | 22 | 0 | 400 | 17 | 16 | 37 | 0 | 1 | 67 | 48 | 18 | 12 | 12 | 0 | 70 | 55 | 24 | 160 | 163 | 0 | 50 | 25.5 | 51 | 220 | 0 | 0 | 0 | 612 | 0 | 140 | 86 | 340 | 0 | 345 | 44 | 20 | 197 | 42 | 50 | 0 | 195 | 9 | 20 | 0 | 192 | 0 | 0 | 27 | 300 | 0 | 337 | 42 | 30 | 152 | 0 | 17 | 0 | 33 | 30 | 100 | 0 | 95 | 35 | 9 | 67 | 59 | 0 | 0 | 12 | 7009.5 | 907 | 250 | 0 | 18 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 0 | 0 | 0 | 1460.9 | 0 | 43 | 0 | 35 | 50 | 0 | 48 | 27 | 0 | 0 | 0 | 25 | 0 | 0 | 190 | 0 | 0 | 0 | 167 | 0 | 341 | 0 | 0 | 0 | 49 | 50 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 307 | 125 | 220 | 0 | 304 | 1227 | 17 | 6689.9 | 13699.4 | 79.76
23:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 35 | 149 | 122 | 292 | 55 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 22 | 22 | 0 | 370 | 17 | 16 | 38 | 0 | 0 | 67 | 40 | 18 | 12 | 12 | 0 | 70 | 55 | 28 | 160 | 163 | 0 | 50 | 25.5 | 51 | 220 | 0 | 0 | 0 | 612 | 0 | 46 | 83 | 330 | 0 | 345 | 44 | 20 | 170 | 42 | 17 | 0 | 195 | 9 | 20 | 0 | 192 | 0 | 0 | 28 | 295 | 0 | 348 | 42 | 30 | 151 | 0 | 17 | 0 | 33 | 30 | 103 | 0 | 98 | 35 | 9 | 67 | 61 | 0 | 0 | 12 | 6785.5 | 908 | 250 | 0 | 18 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 0 | 0 | 0 | 1474.64 | 0 | 43 | 0 | 35 | 50 | 0 | 48 | 27 | 0 | 0 | 0 | 26 | 0 | 0 | 180 | 0 | 0 | 0 | 178 | 0 | 358 | 0 | 0 | 0 | 53 | 50 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 286 | 110 | 180 | 0 | 320 | 1227 | 17 | 6666.64 | 13452.14 | 79.75
Total KWH | 0 | 2348160 | 1145760 | 0 | 0 | 0 | 0 | 0 | 6451200 | 0 | 0 | 259560 | 274680 | 3527712 | 3205920 | 6746444 | 1116096 | 266103 | 803520 | 0 | 5027800 | 0 | 0 | 0 | 269245 | 7649594 | 0 | 0 | 223458 | 3452400 | 545400 | 494280 | 0 | 11742272.73 | 1441473 | 386400 | 902400 | 0 | 259200 | 422302 | 1103808 | 136800 | 283200 | 293760 | 23629 | 1646080 | 1345709 | 367680 | 3636363.64 | 864800 | 0 | 659520 | 501136.2 | 952618 | 5121836 | 0 | 0 | 0 | 9027272 | 119610 | 938400 | 1856727 | 8348500 | 556000 | 8198000 | 1048008 | 540000 | 4812000 | 832104 | 564480 | 0 | 1540320 | 87360 | 496130 | 0 | 4344960 | 0 | 403964 | 651984 | 7521000 | 0 | 8800000 | 989000 | 717600 | 3716590.91 | 72630 | 364704 | 0 | 1021440 | 718656 | 2373000 | 0 | 2327050 | 194040 | 220800 | 1428000 | 1852800 | 12750 | 288470 | 120720 | 153003389.48 | 21926545 | 6427584 | 0 | 240960 | 654336 | 0 | 0 | 0 | 0 | 0 | 0 | 622080 | 14545455 | 0 | 0 | 0 | 35530909 | 0 | 1023379 | 0 | 396864 | 530784 | 0 | 246864 | 276000 | 0 | 405272 | 792870 | 133105 | 0 | 397504 | 4045909 | 0 | 0 | 0 | 3694318 | 0 | 9378981 | 0 | 36120 | 0 | 1154181 | 572205 | 133249 | 767001 | 0 | 0 | 0 | 30641.52 | 1013760 | 4105 | 2471520 | 7375000 | 3077000 | 5301090 | 0 | 6698182 | 29317818.18 | 439200 | 159660791.7 | 312664181.18

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 15-04-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13049.46 | MW | 12:00 Hr. | Energy Generated |  |  | 312.6642 |  | MKWHr.
| Day Peak Demand |  |  | 14401.46 | MW | 12:00 Hr. | Energy Unserverd |  |  | 27.285 |  | MKWHr.
| Evening Peak Generation |  |  | 13849.14 | MW | 21:00 Hr. | Energy Demand |  |  | 339.9492 |  | MKWHr.
| Evening Peak Demand |  |  | 15398.14 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.2 |  | °C
| Minimum Generation of the Day |  |  | 12330.89 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 927.57 |  | MMCFD
| Maximum Generation of the Day |  |  | 13849.14 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.0391 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.9105 | 0 | 23.4156 | 0 | 0 | 0.22346 | 0 | 0 | 55.5496 | Gas | 126.4143 | Gas | 445295106.0913
| Chattogram Zone |  |  | 5.4895 | 12.6636 | 9.2939 | 0 | 1.6461 | 0.14324 | 0 | 0.2592 | 29.4956 | Coal | 71.7543 | Coal | 486451820.8786
| Cumilla Zone |  |  | 26.6875 | 0 | 3.7825 | 0 | 0 | 0.40396 | 4.345 | 0 | 35.2189 | HFO | 46.2078 | HFO | 830265541.93
| Mymensingh Zone |  |  | 1.8528 | 0 | 1.9636 | 0 | 0 | 0.30122 | 0 | 0 | 4.1176 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.549 | 0 | 0 | 0 | 0 | 0.07263 | 0 | 0 | 28.6217 | Hydro | 1.6461 | Hydro | 164608
| Khulna Zone |  |  | 6.4276 | 14.5455 | 0.8953 | 0 | 0 | 0.62208 | 21.9265 | 0 | 44.417 | Solar | 4.5801 | Solar | 72625058.714
| Barishal Zone |  |  | 8.3781 | 43.391 | 2.9107 | 0 | 0 | 0.004105 | 0 | 0 | 54.6839 | Import | 61.8024 | Import | 362266409.86
| Rajshahi Zone |  |  | 17.1192 | 0 | 2.607 | 0 | 0 | 1.6318 | 35.5309 | 0 | 56.8889 | Wind | 0.2592 | Wind | 3812832
| Rangpur Zone |  |  | 0 | 1.1542 | 1.3392 | 0 | 0 | 1.1777 | 0 | 0 | 3.671
| Total |  |  | 126.4143 | 71.7543 | 46.2078 | 0 | 1.6461 | 4.5801 | 61.8024 | 0.2592 | 312.6642
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 445295106.0913 |  | Hydro | 164608
|  |  |  | Coal | 486451820.8786 |  | Solar | 72625058.714
|  |  |  | HFO | 830265541.93 |  | Import | 362266409.86
|  |  |  | HSD | 0 |  | Wind | 3812832
[5 empty] | Total: | 220,08,81,377 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9265 | Peak Hr Flow | 908.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 54104872.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 35.5309 | Peak Hr Flow | 1481.14 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2395 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 4.345 | Peak Hr Flow | 194.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2867 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 61.8024 | Peak Hr Flow | 2583.14 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 360 |  | 5646
|  |  |  | Chattogram |  | 120 |  | 1487
|  |  |  | Cumilla |  | 210 |  | 1446
|  |  |  | Mymensingh |  | 80 |  | 1016
|  |  |  | Sylhet |  | 25 |  | 479
|  |  |  | Khulna |  | 319 |  | 1804
|  |  |  | Barishal |  | 95 |  | 436
|  |  |  | Rajshahi |  | 195 |  | 1661
|  |  |  | Rangpur |  | 78 |  | 868
|  |  |  | Total |  | 1482 |  | 14843
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 320
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:14 | Fenchuganj-Sylhet (South) 132KV Ckt-1 is restored.
|  | 08:20 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 is restored.
| 08:30 | 12:00 | Shariatpur 132/33kV S/S T1-406T LT Scheduled S/D Due to Emergency Maintenance Work.
| 08:30 | 09:38 | Kurigram-Lalmonirhat 132kV Ckt-1 Scheduled S/D from Kurigram 132/33kV end Due to Energy
Meter Replacement at Rangpur Grid End.
| 08:31 | 11:59 | Shariatpur 132/33kV S/S T1-406T HT Scheduled S/D Due to Emergency Maintenance Work
| 08:31 | 09:37 | Kurigram-Rangpur 132kV Ckt-1 Scheduled S/D from Rangpur 132/33kV end Due to Energy meter
replace
| 08:40 | 16:51 | Gollamari 132/33kV S/S Tr-1 LT Project Work S/D Due to project work:132kv T-1 painting
work
| 08:41 | 16:50 | Gollamari 132/33kV S/S Tr-1 HT Project Work S/D Due to Project work:132kv T-1 painting
|  | 09:01 | Rajshahi 132/33kV S/S Transformer T-2(415T) HT is restored.
|  | 09:01 | Rajshahi 132/33kV S/S Transformer T-2(415T) LT is restored.
| 09:05 |  | Goalpara- Khulna (C) 132kV Ckt-2 Scheduled S/D from Khulna (C) end Due to Due to
replacement of distance relay by the SPMD Khulna.
| 09:36 |  | Korerhat 400/230/132kV S/S ATR-3(7103T) HT Project Work S/D Due to For project work
| 09:36 |  | Korerhat 400/230/132kV S/S ATR-3(7103T) LT Project Work S/D Due to For project work
| 09:57 | 14:36 | Bogura(New)-Naogaon 132 kV Ckt-1 Forced S/D from Naogaon 132/33kV end Due to Insulator
change work from Joypurhat Grid end.
| 10:44 | 11:08 | Bagerhat-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end.
| 11:45 |  | Jamalpur 132/33kV S/S T-4 LT Project Work S/D Due to Project work for transformer
painting.
| 11:45 |  | Jamalpur 132/33kV S/S T-4 HT Project Work S/D Due to Project work for transformer
painting.
| 12:00 |  | Day Peak Generation: 13045 MW
| 12:15 | 15:30 | Shariatpur 132/33kV S/S T2-416T LT Scheduled S/D Due to Emergency Maintenance work.
| 12:17 | 15:26 | Shariatpur 132/33kV S/S T2-416T HT Scheduled S/D Due to Emergency Maintenance work.
| 12:39 | 13:12 | Jaldhaka-Saidpur 132kV Ckt-1 Forced S/D from Saidpur 132/33kV end Due to For Jaldhaka end
sub-station work
|  | 14:40 | Kushtia 132/33kV S/S T-3 HT is restored.
|  | 14:48 | Kushtia 132/33kV S/S T-3 LT is restored.
| 17:08 | 17:26 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Lockout relay, Over current protection
relay relays Due to Due to 33 kV Agla feeder fault
| 18:28 |  | Haripur 412 MW CCPP Synchronized with remarks:- ST
| 00:10 | 00:39 | Ghorasal- Ishwardi 230 kV Ckt-1 Tripped from Ghorashal 230kV end showing General Trip B
Phase Trip Zone-1 Trip SOTF Distance-28 KM relays Due to Bad weather
|  | 00:14 | Gopalganj 400/132kV S/S 400kV Rooppur is restored.
| 00:50 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- gt
| 03:25 | 03:59 | GPH 230/33kV S/S HATHAZARI Tripped showing Relay Trip, R Phase trip, Zone-1/1B Trip, CR
REC/DT Trip. relays.
| 04:30 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
| 06:14 |  | Sirajganj-Sreepur 230 kV Ckt-1 Forced S/D from Sirajgonj 230 end Due to For D/S
Maintenance
| 06:16 |  | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-1 Forced S/D Due to DS Connector Repair At
sirajganj end.
| 06:39 |  | Bhaluka-Mymensingh 132 kV Ckt-1 Scheduled S/D from Bhaluka 132/33kV end Due to High
temperature maintenance.
| 07:00 |  | Minimum generation: 11918 MW
| 07:02 |  | Bhaluka 132/33kV S/S Bus A Scheduled S/D Due to High temperature maintenance.
| 07:03 |  | Nawabganj 132/33kV S/S TR-2 LT Scheduled S/D Due to BAY 105, 132 kV TR-02, Y Phase PT
replacement.
| 07:04 |  | Nawabganj 132/33kV S/S TR-2 HT Scheduled S/D Due to BAY 105, 132 kV TR-02, Y Phase PT
replacement.
| 07:10 |  | Sylhet 132/33kV S/S T2 LT Scheduled S/D Due to Botteshwar feeder 33 KV Bus side DS
Maintenance purpose.
| 07:11 |  | Sylhet 132/33kV S/S T2 HT Scheduled S/D Due to Botteshwar feeder 33 KV Bus side DS
Maintenance purpose.
| 07:20 |  | Kishoreganj 132/33kV S/S Tr-2 (414T) HT Scheduled S/D Due to 33kv bajitpur incoming loops | [7 empty] | 15.0MW load
|  |  | change | [7 empty] | interrup.
| 07:20 |  | Kishoreganj 132/33kV S/S Tr-2 (414T) LT Scheduled S/D Due to 33 kv bajitpur incoming | [7 empty] | 15.0MW load
|  |  | loops change | [7 empty] | interrup.
| 07:26 |  | Bhaluka 132/33kV S/S Sreepur Ckt- 02 Scheduled S/D Due to High temperature maintenance.
| 07:27 |  | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-2 Scheduled S/D Due to Redhot Maintenancce
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 15-04-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 404 | 6451200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 180 | 5027800 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1116096 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 326 | 7649594 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 18 | 259560 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 137 | 3205920 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 266103 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 269245 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 24 | 545400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 494280 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 1145760 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 290 | 6746444 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3527712 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2348160 | Engine Problem
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 803520 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 223458 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 274680 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 450 | 11742272.73 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3452400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2456 | 55549604.73
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 501136.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 119610 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 659520 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1646080 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5121836 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 952618 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 48 | 1103808 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 67 | 422302 | Engine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 283200 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 16 | 367680 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 38 | 902400 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23629 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 386400 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 18 | 136800 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 56 | 1345709 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 293760 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 1441473 | Liquid fuel shortage
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 163 | 864800 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 9027272 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 6 | 259200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 160 | 3636363.64 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 1657.5 | 29495596.84
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 198 | 4812000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 0 | 556000 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 345 | 8198000 | machine problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 340 | 8348500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 42 | 832104 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 20 | 540000 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 86 | 1856727 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1048008 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 140 | 938400 | Machine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 27 | 651984 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 190 | 1540320 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 194 | 4344960 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 496130 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 87360 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 51 | 564480 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 403964 | -
Cumilla Area Total |  |  |  |  | 2870.745 | 1706 | 35218937
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 70 | 1852800 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12750 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 61 | 1428000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 220800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 288470 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 120720 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 194040 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 187 | 4117580
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 72630 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 989000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 717600 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 153 | 3716590.91 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 102 | 2373000 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 718656 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 33 | 1021440 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 95 | 2327050 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 364704 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7521000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 337 | 8800000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1144 | 28621670.91
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 908 | 21926545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 23.5 | 240960 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 32 | 654336 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 6427584 | Gas Restrction
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 622080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 604 | 14545455 | U#1 Under Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1817.5 | 44416960
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 304 | 6698182 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 101 | 2471520 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 125 | 3077000 | STG Under Maintenance
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1225 | 29317818.18 | Machine Problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 180 | 5301090 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 439200 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7375000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4105 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2259 | 54683915.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 405272 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 1023379 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 23 | 276000 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 195 | 4045909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 172 | 3694318 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 359 | 9378981 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 133105 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 48 | 246864 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 530784 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 396864 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 36120 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1481.14 | 35530909 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 397504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 792870 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2431.14 | 56888879
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1154181 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 92 | 767001 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 30641.52 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 572205 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 133249 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1013760 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 191 | 3671037.52
Eastern Grid Total |  |  |  |  | 17417.792 | 7150.5 | 153003389.48
Western Grid Total |  |  |  |  | 11852.195 | 6698.64 | 159660791.7
National Grid Total |  |  |  |  | 29269.987 | 13849.14 | 312664181.18
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 15-04-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9278.59 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4082.1 | MW
i) Dhaka area |  |  | 5285.89 |  | MW | i) Khulna area |  |  |  | 1485 | MW
ii) Chattogram area |  |  | 1366.7 |  | MW | ii) Barishal area |  |  |  | 340.7 | MW
iii) Cumilla area |  |  | 1236 |  | MW | iii) Rajshahi area |  |  |  | 1466.4 | MW
iv) Mymensingh area |  |  | 936 |  | MW | iv) Rangpur area |  |  |  | 790 | MW
v) Sylhet area |  |  | 454 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13360.69 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 13 | 17:00 | 67 | Hasnabad | 89 | 23:00 | 133 | Natore | 157 | 19:00
2 | AKSML | 6.7 | 21:00 | 68 | Hathazari | 80 | 00:00 | 134 | Nawabganj | 50 | 05:00
3 | Aftabnagar | 42 | 18:30 | 69 | Hatirjheel | 51 | 15:00 | 135 | Netrakona | 77 | 09:00
4 | Agargaon | 123 | 13:00 | 70 | Ishurdi | 71 | 14:00 | 136 | New | 80 | 15:00
5 | Agrabad | 54 | 18:30 | 71 | Jaldhaka | 67 | 10:00 | 137 | Niamatpur | 120 | 19:00
6 | Amnura | 52 | 13:00 | 72 | Jamalpur | 115 | 06:00 | 138 | Noapara | 35 | 06:00
7 | Ashuganj | 97 | 22:00 | 73 | Jashore | 139 | 10:00 | 139 | PHP | 6 | 10:00
8 | BSRM | 187 | 12:00 | 74 | Jhenaidah | 93 | 06:00 | 140 | Pabna | 101 | 12:00
9 | Bagerhat | 80 | 00:00 | 75 | Joydebpur | 170 | 20:00 | 141 | Palashbari | 112 | 20:00
10 | Bajitpur | 86 | 22:00 | 76 | Joypurhat | 62 | 23:00 | 142 | Panchagarh | 41 | 10:00
11 | Bakerganj | 13 | 03:00 | 77 | Juldah | 18 | 16:00 | 143 | Patiya | 10.6 | 03:00
12 | Bakulia | 101 | 21:00 | 78 | KSRM | 30 | 18:00 | 144 | Patuakhali | 56 | 06:00
13 | Banani | 49.2 | 13:00 | 79 | Kabirpur | 265 | 20:00 | 145 | Payra | 30 | 02:00
14 | Bangabhaban | 21 | 11:00 | 80 | Kachua | 77 | 05:00 | 146 | Postogola | 56 | 19:00
15 | Barapukuria | 64 | 15:00 | 81 | Kaliganj | 28 | 05:00 | 147 | Pubail | 26 | 08:00
16 | Barguna | 16 | 01:00 | 82 | Kallyanpur | 120 | 19:00 | 148 | Purbachal | 34 | 13:00
17 | Barishal | 96 | 18:30 | 83 | Kalurghat | 42 | 10:00 | 149 | Purbasadipur | 114 | 12:00
18 | Barishal-230 | 86 | 02:00 | 84 | Kamrangirchar | 81 | 19:00 | 150 | Rahanpur | 37 | 13:00
19 | Baroaulia | 63 | 15:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 30 | 16:00
20 | Baroirhat | 50 | 23:00 | 86 | Kasba | 31 | 06:00 | 152 | Rajbari | 73 | 01:00
21 | Bashundhara | 196 | 15:00 | 87 | Kazla | 121 | 13:00 | 153 | Rajendrapur | 122 | 08:00
22 | BashundharaCement | 7 | 10:00 | 88 | Keranigonj | 71 | 00:00 | 154 | Rajshahi | 136 | 00:00
23 | Beanibazar | 52 | 18:00 | 89 | Khagrachori | 30 | 00:00 | 155 | Rajshahi-230 | 101 | 13:00
24 | Benapole | 74 | 06:00 | 90 | Khulna | 68 | 13:00 | 156 | Ramganj | 96 | 02:00
25 | Bhaluka | 149 | 22:00 | 91 | Khulshi | 195 | 21:00 | 157 | Rampur | 42 | 21:00
26 | Bhandaria | 45 | 06:00 | 92 | Kishoreganj | 124 | 21:00 | 158 | Rangamati | 19 | 21:00
27 | Bhangura | 39 | 00:00 | 93 | Kodda | 316 | 20:00 | 159 | Rangpur | 121 | 20:00
28 | Bheramara(GK) | 67 | 04:00 | 94 | Kulaura | 37 | 21:00 | 160 | Ruppur | 7 | 07:00
29 | Bhulta | 221 | 23:00 | 95 | Kurigram | 55 | 18:00 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 82 | 13:00 | 96 | Kushtia | 138 | 19:00 | 162 | Saidpur | 102 | 14:00
31 | Bogura | 170 | 23:00 | 97 | Laksam | 22 | 00:00 | 163 | Satkhira | 119 | 23:00
32 | Borhanuddin | 71 | 06:00 | 98 | Lakshmipur | 37 | 03:00 | 164 | Satmasjid | 112 | 13:00
33 | Brahmanbaria | 102 | 04:00 | 99 | Lalbag | 74 | 13:00 | 165 | Savar | 217 | 20:00
34 | Cantonment | 142 | 13:00 | 100 | Lalmonirhat | 51 | 07:00 | 166 | SevenRings | 17.84 | 11:00
35 | Chandina | 24 | 12:00 | 101 | MI_Cement | 16.2 | 22:00 | 167 | ShahCement | 36 | 09:00
36 | Chandpur | 70 | 05:00 | 102 | Madanganj | 42 | 18:30 | 168 | Shahjadpur | 85 | 06:00
37 | Chandraghona | 38 | 23:00 | 103 | Madaripur | 88 | 23:00 | 169 | Shahjibazar | 108 | 00:00
38 | Chapai | 73 | 12:00 | 104 | Madartek | 82 | 19:00 | 170 | Shahmirpur | 52 | 00:00
39 | Charsaidpur | 43 | 15:00 | 105 | Madunaghat | 51 | 19:30 | 171 | Shariatpur | 70 | 22:00
40 | Chauddagram | 65 | 01:00 | 106 | Magura | 56 | 06:00 | 172 | Sherpur | 110 | 02:00
41 | Chhatak | 37 | 21:00 | 107 | Mahasthangarh | 76 | 18:30 | 173 | Shikalbaha | 30 | 02:00
42 | Chowmuhani | 126 | 21:00 | 108 | Maijdee | 39 | 05:00 | 174 | Shitalakhya | 87.4 | 12:00
43 | Chuadanga | 116 | 07:00 | 109 | Manikganj | 125 | 08:00 | 175 | Sholosohor | 46 | 23:00
44 | Coxsbazar | 127 | 05:00 | 110 | Maniknagar | 74 | 13:00 | 176 | Shyampur | 178 | 12:00
45 | Cumilla(N) | 110 | 18:30 | 111 | Matarbari | 56 | 22:00 | 177 | Siddhirganj | 132 | 13:00
46 | Cumilla(S) | 195 | 19:00 | 112 | Matuail | 81.2 | 10:00 | 178 | Sirajganj | 124 | 11:00
47 | Daganbhuiyan | 37 | 04:00 | 113 | Metrorail_Motijheel | 23 | 19:30 | 179 | Sonargaon | 117 | 08:00
48 | Daudkandi | 124 | 23:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sreemongol | 56 | 19:30
49 | DhakaUniversity | 84 | 13:00 | 115 | Millgate | 103 | 12:00 | 181 | Sreepur | 97 | 21:00
50 | Dhamrai | 132 | 20:00 | 116 | Mirpur | 151 | 15:00 | 182 | Srinagar | 43.2 | 20:00
51 | Dhanmondi | 139 | 13:00 | 117 | Mirsorai | 52 | 13:00 | 183 | Sunamganj | 35 | 18:00
52 | Dohazari | 81 | 00:00 | 118 | Mirzapur | 53 | 23:00 | 184 | Sylhet | 46 | 01:00
53 | Faridpur | 152 | 01:00 | 119 | Mithapukur | 51 | 17:00 | 185 | Sylhet-132 | 112 | 21:00
54 | Fatullah | 94 | 16:00 | 120 | Modern | N/A | N/A | 186 | TK | 23.5 | 05:00
55 | Fenchuganj | 30 | 18:30 | 121 | Mogbazar | 91.6 | 16:00 | 187 | Tangail | 197 | 23:00
56 | Feni | 96 | 18:30 | 122 | Mongla | 34 | 15:00 | 188 | Taraganj | 21 | 10:00
57 | GPH | 12 | 23:00 | 123 | Motijheel | 52 | 13:00 | 189 | Tasnim | 32 | 06:00
58 | Ghatail | 90 | 23:00 | 124 | Muktagacha | 30 | 00:00 | 190 | Thakurgaon | 85 | 19:00
59 | Ghorashal | 11 | 18:00 | 125 | Munshiganj | 94 | 07:00 | 191 | Tongi | 148 | 10:00
60 | Ghorashal-230 | 100 | 23:00 | 126 | Muradnagar | 42 | 03:00 | 192 | Ullahpara | 47 | 13:00
61 | Goalpara | 36 | 03:00 | 127 | Mymensingh | 177 | 20:00 | 193 | Ullon | 57 | 19:00
62 | Gollamari | 90 | 02:00 | 128 | Nabinagar | 16 | 08:00 | 194 | Uttara | 91 | 13:00
63 | Gopalganj | 82 | 21:00 | 129 | Naogaon | 144 | 00:00 | 195 | UttaraNew | 62 | 19:00
64 | Gulshan | 142 | 13:00 | 130 | Narail | 54 | 06:00 | 196 | Zigatola | 89 | 15:00
65 | Halishahar | 97.5 | 10:00 | 131 | Narinda | 75 | 13:00
66 | HaripurSBU | 120 | 05:00 | 132 | Narshingdi | 197 | 23:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 15-04-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13175.5 | 971 |  | 14190.5
1:00 | 12732.5 | 924 |  | 13698.5
2:00 | 12584.5 | 779 |  | 13398.5
3:00 | 12496.5 | 720 |  | 13248.5
4:00 | 12514.5 | 655 |  | 13198.5
5:00 | 12493.5 | 580 |  | 13099.5
6:00 | 12717.77 | 511 |  | 13251.77
7:00 | 12330.89 | 547 |  | 12902.89
8:00 | 12718.42 | 605 |  | 13350.42
9:00 | 12918.77 | 845 |  | 13801.77
10:00 | 12993.17 | 871 |  | 13903.17
11:00 | 12944.15 | 1060 |  | 14052.15
12:00 | 13049.46 | 1294 |  | 14401.46
13:00 | 13117.72 | 1373 |  | 14552.72
14:00 | 12794.41 | 1700 |  | 14570.41
15:00 | 12674.38 | 1843 |  | 14600.38
16:00 | 12700.15 | 1800 |  | 14581.15
17:00 | 12781.87 | 1693 |  | 14550.87
18:00 | 12718.86 | 1608 |  | 14398.86
19:00 | 13584.88 | 1592 |  | 15248.88
19:30 | 13498.09 | 1722 |  | 15297.09
20:00 | 13688.56 | 1587 |  | 15346.56
21:00 | 13849.14 | 1482 |  | 15398.14
22:00 | 13699.4 | 1339 |  | 15098.4
23:00 | 13452.14 | 906 |  | 14399.14
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 15-04-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6576.5 | 6599 | 13175.5 | DAILY GENERATION CURVE
00:30 | 6465 | 6489 | 12954
01:00 | 6353.5 | 6379 | 12732.5 | 15-04-2026
01:30 | 6277 | 6381.5 | 12658.5
02:00 | 6200.5 | 6384 | 12584.5
02:30 | 6168.5 | 6372 | 12540.5
03:00 | 6136.5 | 6360 | 12496.5
03:30 | 6163 | 6342.5 | 12505.5
04:00 | 6189.5 | 6325 | 12514.5
04:30 | 6178 | 6326 | 12504
05:00 | 6166.5 | 6327 | 12493.5
05:30 | 6264.69 | 6340.945 | 12605.635
06:00 | 6362.88 | 6354.89 | 12717.77
06:30 | 6184.495 | 6339.835 | 12524.33
07:00 | 6006.11 | 6324.78 | 12330.89
07:30 | 6132.77 | 6391.885 | 12524.655
08:00 | 6259.43 | 6458.99 | 12718.42
08:30 | 6306.51 | 6512.085 | 12818.595
09:00 | 6353.59 | 6565.18 | 12918.77
09:30 | 6270.625 | 6685.345 | 12955.97
10:00 | 6187.66 | 6805.51 | 12993.17
10:30 | 6181.775 | 6786.885 | 12968.66
11:00 | 6175.89 | 6768.26 | 12944.15
11:30 | 6205.37 | 6791.435 | 12996.805
12:00 | 6234.85 | 6814.61 | 13049.46
12:30 | 6238.95 | 6844.64 | 13083.59
13:00 | 6243.05 | 6874.67 | 13117.72
13:30 | 6150.58 | 6805.485 | 12956.065
14:00 | 6058.11 | 6736.3 | 12794.41
14:30 | 6048.985 | 6685.41 | 12734.395
15:00 | 6039.86 | 6634.52 | 12674.38
15:30 | 6037.355 | 6649.91 | 12687.265
16:00 | 6034.85 | 6665.3 | 12700.15
16:30 | 6068.815 | 6672.195 | 12741.01
17:00 | 6102.78 | 6679.09 | 12781.87
17:30 | 6126.04 | 6624.325 | 12750.365
18:00 | 6149.3 | 6569.56 | 12718.86
18:30 | 6515.9 | 6635.97 | 13151.87
19:00 | 6882.5 | 6702.38 | 13584.88
19:30 | 6896.5 | 6601.59 | 13498.09
20:00 | 7002 | 6686.56 | 13688.56
20:30 | 7076.25 | 6692.6 | 13768.85 |  | Executive Engineer
21:00 | 7150.5 | 6698.64 | 13849.14 |  | Network Operation Division
21:30 | 7080 | 6694.27 | 13774.27
22:00 | 7009.5 | 6689.9 | 13699.4
22:30 | 6897.5 | 6678.27 | 13575.77
23:00 | 6785.5 | 6666.64 | 13452.14

## En-Curve
QF-LDC-12
Date | 15-04-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3823 | 1653 | 909 | 0 | 186 | 1481 | 70 | 2973 | 0 | 702 | 1377.5 | 0 | 0 | 1 | 971 | DAILY ENERGY CURVE
00:30 | 3820.5 | 1651 | 909 | 0 | 186 | 1468.5 | 70 | 2927 | 0 | 660.5 | 1261 | 0 | 0 | 0.5 | 947.5 | 15-04-2026
01:00 | 3818 | 1649 | 909 | 0 | 186 | 1456 | 70 | 2881 | 0 | 619 | 1144.5 | 0 | 0 | 0 | 924
01:30 | 3798 | 1587.5 | 909 | 0 | 183 | 1467.5 | 70 | 2879.5 | 0 | 619.5 | 1144.5 | 0 | 0 | 0 | 851.5 | Energy Generated | 312.6642 |  | MKWHr
02:00 | 3778 | 1526 | 909 | 0 | 180 | 1479 | 70 | 2878 | 0 | 620 | 1144.5 | 0 | 0 | 0 | 779 | Energy not Served | 27.285 |  | MKWHr
02:30 | 3765 | 1504 | 908.5 | 0 | 178 | 1481.5 | 70 | 2880.5 | 0 | 619 | 1134 | 0 | 0 | 0 | 749.5 | Total Energy Requirement | 339.9492 |  | MKWHr
03:00 | 3752 | 1482 | 908 | 0 | 176 | 1484 | 70 | 2883 | 0 | 618 | 1123.5 | 0 | 0 | 0 | 720
03:30 | 3765.5 | 1492.5 | 908 | 0 | 174 | 1482.5 | 70 | 2882 | 0 | 621.5 | 1109 | 0 | 0 | 0.5 | 687.5
04:00 | 3779 | 1503 | 908 | 0 | 172 | 1481 | 70 | 2881 | 0 | 625 | 1094.5 | 0 | 0 | 1 | 655
04:30 | 3761 | 1528.5 | 908.5 | 0 | 172 | 1462.5 | 70 | 2880 | 0 | 622.5 | 1096 | 0 | 0 | 3 | 617.5
05:00 | 3743 | 1554 | 909 | 0 | 172 | 1444 | 70 | 2879 | 0 | 620 | 1097.5 | 0 | 0 | 5 | 580
05:30 | 3758 | 1647 | 909 | 0 | 171 | 1454 | 70 | 2882.5 | 4.135 | 613 | 1091.5 | 0 | 0 | 5.5 | 545.5
06:00 | 3773 | 1740 | 909 | 0 | 170 | 1464 | 70 | 2886 | 8.27 | 606 | 1085.5 | 0 | 0 | 6 | 511
06:30 | 3523.5 | 1771 | 908.5 | 0 | 165 | 1466.5 | 70 | 2875 | 52.83 | 606 | 1079 | 0 | 0 | 7 | 529
07:00 | 3274 | 1802 | 908 | 0 | 160 | 1469 | 70 | 2864 | 97.39 | 606 | 1072.5 | 0 | 0 | 8 | 547
07:30 | 3400.5 | 1790.5 | 907.5 | 0 | 168 | 1464.5 | 70 | 2874.5 | 177.905 | 599 | 1065.75 | 0 | 0 | 6.5 | 576
08:00 | 3527 | 1779 | 907 | 0 | 176 | 1460 | 70 | 2885 | 258.42 | 592 | 1059 | 0 | 0 | 5 | 605
08:30 | 3532 | 1800 | 907 | 0 | 181 | 1459.5 | 70 | 2878 | 333.095 | 582 | 1071 | 0 | 0 | 5 | 725
09:00 | 3537 | 1821 | 907 | 0 | 186 | 1459 | 70 | 2871 | 407.77 | 572 | 1083 | 0 | 0 | 5 | 845
09:30 | 3507.5 | 1791.5 | 907 | 0 | 182 | 1477.445 | 70 | 2865.5 | 485.525 | 567 | 1090.5 | 0 | 0 | 12 | 858
10:00 | 3478 | 1762 | 907 | 0 | 178 | 1495.89 | 70 | 2860 | 563.28 | 562 | 1098 | 0 | 0 | 19 | 871
10:30 | 3468 | 1769.5 | 907.5 | 0 | 175 | 1490.815 | 70 | 2858.5 | 555.345 | 550.5 | 1105.5 | 0 | 0 | 18 | 965.5
11:00 | 3458 | 1777 | 908 | 0 | 172 | 1485.74 | 70 | 2857 | 547.41 | 539 | 1113 | 0 | 0 | 17 | 1060
11:30 | 3472.5 | 1785 | 908 | 0 | 174 | 1489.875 | 70 | 2861.5 | 564.93 | 538 | 1114 | 0 | 0 | 19 | 1177
12:00 | 3487 | 1793 | 908 | 0 | 176 | 1494.01 | 70 | 2866 | 582.45 | 537 | 1115 | 0 | 0 | 21 | 1294
12:30 | 3471.5 | 1771.9 | 907.5 | 0 | 181 | 1490.96 | 69 | 2868 | 627.73 | 540 | 1131 | 0 | 0 | 25 | 1333.5
13:00 | 3456 | 1750.8 | 907 | 0 | 186 | 1487.91 | 68 | 2870 | 673.01 | 543 | 1147 | 0 | 0 | 29 | 1373
13:30 | 3373.5 | 1733.4 | 907.5 | 0 | 187 | 1487.505 | 68 | 2871 | 639.16 | 546 | 1115 | 0 | 0 | 28 | 1536.5
14:00 | 3291 | 1716 | 908 | 0 | 188 | 1487.1 | 68 | 2872 | 605.31 | 549 | 1083 | 0 | 0 | 27 | 1700
14:30 | 3300 | 1717.25 | 907.5 | 0 | 188 | 1490.05 | 68 | 2904 | 491.095 | 552 | 1089.5 | 0 | 0 | 27 | 1771.5
15:00 | 3309 | 1718.5 | 907 | 0 | 188 | 1493 | 68 | 2936 | 376.88 | 555 | 1096 | 0 | 0 | 27 | 1843
15:30 | 3376 | 1713 | 907 | 0 | 184 | 1489.435 | 68 | 2942.5 | 322.33 | 540.5 | 1119 | 0 | 0 | 25.5 | 1821.5
16:00 | 3443 | 1707.5 | 907 | 0 | 180 | 1485.87 | 68 | 2949 | 267.78 | 526 | 1142 | 0 | 0 | 24 | 1800
16:30 | 3409 | 1700.5 | 907.5 | 0 | 177 | 1485.545 | 69 | 2990 | 193.465 | 541 | 1246.5 | 0 | 0 | 21.5 | 1746.5
17:00 | 3375 | 1693.5 | 908 | 0 | 174 | 1485.22 | 70 | 3031 | 119.15 | 556 | 1351 | 0 | 0 | 19 | 1693
17:30 | 3321 | 1637.5 | 907.5 | 0 | 172 | 1487.69 | 70 | 3034.5 | 65.675 | 594 | 1446 | 0 | 0 | 14.5 | 1650.5
18:00 | 3267 | 1581.5 | 907 | 0 | 170 | 1490.16 | 70 | 3038 | 12.2 | 632 | 1541 | 0 | 0 | 10 | 1608
18:30 | 3369.5 | 1618 | 907 | 0 | 183 | 1489.52 | 70 | 3143 | 6.1 | 695.25 | 1661.5 | 0 | 0 | 9 | 1600
19:00 | 3472 | 1654.5 | 907 | 0 | 196 | 1488.88 | 70 | 3248 | 0 | 758.5 | 1782 | 0 | 0 | 8 | 1592
19:30 | 3455 | 1553.5 | 907 | 0 | 190 | 1479.09 | 70 | 3233 | 0 | 774.5 | 1829 | 0 | 0 | 7 | 1722
20:00 | 3545 | 1629 | 907 | 0 | 186 | 1480.06 | 70 | 3252 | 0 | 774.5 | 1836 | 0 | 0 | 9 | 1587
20:30 | 3613.5 | 1589 | 907.5 | 0 | 190 | 1480.6 | 70 | 3256.5 | 0 | 772.5 | 1881.75 | 0 | 0 | 7.5 | 1534.5
21:00 | 3682 | 1549 | 908 | 0 | 194 | 1481.14 | 70 | 3261 | 0 | 770.5 | 1927.5 | 0 | 0 | 6 | 1482
21:30 | 3646 | 1544.5 | 907.5 | 0 | 193 | 1471.02 | 70 | 3263 | 0 | 762.25 | 1913.5 | 0 | 0 | 3.5 | 1410.5
22:00 | 3610 | 1540 | 907 | 0 | 192 | 1460.9 | 70 | 3265 | 0 | 754 | 1899.5 | 0 | 0 | 1 | 1339
22:30 | 3601.5 | 1502.5 | 907.5 | 0 | 192 | 1467.77 | 70 | 3264.5 | 0 | 751.5 | 1818 | 0 | 0 | 0.5 | 1122.5
23:00 | 3593 | 1465 | 908 | 0 | 192 | 1474.64 | 70 | 3264 | 0 | 749 | 1736.5 | 0 | 0 | 0 | 906
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 15-04-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 393 | 03:00 | 381 | 12:00 | Madunaghat | 402 | 01:00 | 398 | 10:00
Amtali | 413 | 03:00 | 410 | 00:00 | Meghnaghat | 394 | 02:00 | 383 | 12:00
Ashuganj | 411 | 4:00 | 394 | 12:00 | Payra | 415 | 07:00 | 410 | 08:00
Bhulta | 403 | 03:00 | 387 | 13:00 | Rahanpur | 409 | 19:30 | 400 | 06:00
Bibiana | 409 | 07:00 | 403 | 13:00 | Rampal | 404 | 19:30 | 396 | 10:00
BIPTC | 397 | 07:00 | 387 | 15:00
Bogura | 403 | 22:00 | 391 | 13:00
Gopalganj | 401 | 02:00 | 393 | 13:00
Kaliakoir | 390 | 02:00 | 380 | 12:00
Korerhat | 403 | 00:00 | 396 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 02:00 | 222 | 12:00 | Jhenaidah | 230 | 02:00 | 223 | 06:00
AKSML | 235 | 18:30 | 229 | 04:00 | Kachua | 233 | 19:00 | 225 | 02:00
Aminbazar | 234 | 04:00 | 223 | 12:00 | Kaliakoir | 237 | 02:00 | 229 | 23:00
Ashuganj | 240 | 23:00 | 225 | 13:00 | Keranigonj | 231 | 02:00 | 221 | 12:00
Ashuganj-400 | 235 | 4:00 | 220 | 12:00 | Khulna(S) | 232 | 19:00 | 223 | 23:00
Baghabari | 235 | 19:30 | 230 | 06:00 | Korerhat | 233 | 19:00 | 225 | 10:00
Barapukuria | 225 | 22:00 | 213 | 10:00 | Madunaghat | 233 | 18:30 | 228 | 09:00
Barapukuria-230 | 225 | 22:00 | 212 | 11:00 | Madunaghat-400 | 232 | 01:00 | 230 | 03:00
Barishal | 230 | 19:00 | 227 | 12:00 | Maniknagar | 231 | 04:00 | 221 | 12:00
Bheramara | 234 | 19:30 | 228 | 06:00 | Meghnaghat | 239 | 05:00 | 230 | 10:00
Bhulta | 232 | 02:00 | 222 | 13:00 | Meghnaghat-400 | 232 | 02:00 | 224 | 12:00
Bibiana | 237 | 04:00 | 233 | 12:00 | Mirsorai | 231 | 21:00 | 222 | 12:00
BIPTC | 236 | 19:30 | 228 | 06:00 | Naogaon | 228 | 15:00 | 218 | 00:00
Bogura | 235 | 19:30 | 228 | 06:00 | Purbasadipur | 224 | 22:00 | 213 | 10:00
Bogura-400 | 235 | 22:00 | 227 | 12:00 | Rajshahi | 234 | 19:30 | 224 | 13:00
Borhanuddin | 234 | 16:00 | 231 | 01:00 | Rampal | 231 | 02:00 | 225 | 10:00
BSRM | 232 | 18:00 | 225 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 233 | 19:00 | 224 | 12:00 | Rampura | 232 | 04:00 | 220 | 13:00
Cumilla(N) | 231 | 19:00 | 225 | 12:00 | Shikalbaha | 233 | 18:30 | 228 | 20:00
Faridpur | 225 | 19:30 | 221 | 01:00 | Shyampur | 232 | 04:00 | 221 | 12:00
Fenchuganj | 240 | 01:00 | 238 | 13:00 | Siddhirganj | 230 | 00:00 | 223 | 14:00
Feni | 232 | 18:00 | 225 | 12:00 | Sirajgonj | 244 | 23:00 | 236 | 08:00
Ghorashal | 235 | 01:00 | 228 | 11:00 | Sreepur | 230 | 19:30 | 224 | 14:00
Ghorashal-230 | 231 | 04:00 | 221 | 12:00 | Tongi | 232 | 04:00 | 225 | 11:00
Gopalganj | 225 | 19:30 | 220 | 11:00
GPH | 233 | 19:00 | 228 | 12:00
Haripur | 232 | 04:00 | 222 | 12:00
Hasnabad | 232 | 05:00 | 221 | 12:00
Hathazari | 231 | 04:00 | 227 | 09:00
Ishurdi | 236 | 19:30 | 230 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 02:00 | 127 | 12:00 | Madunaghat | 136 | 18:30 | 130 | 07:00
Agargaon | 137 | 02:00 | 129 | 12:00 | Magura | 135 | 02:00 | 130 | 06:00
Agrabad | 134 | 18:30 | 130 | 07:00 | Mahasthangarh | 133 | 18:30 | 127 | 06:00
AKS | 132 | 00:00 | 129 | 10:00 | Maijdee | 130 | 18:00 | 125 | 03:00
Aminbazar | 134 | 03:00 | 127 | 11:00 | Manikganj | 131 | 01:00 | 124 | 11:00
Amnura | 137 | 19:30 | 128 | 06:00 | Maniknagar | 136 | 03:00 | 127 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 126 | 18:30 | 114 | 02:00
Ashuganj-230 | 140 | 07:00 | 136 | 15:00 | Matuail | 134 | 05:00 | 129 | 12:00
Bagerhat | 130 | 03:00 | 124 | 10:00 | Metrorail_Motijheel | 136 | 03:00 | 127 | 12:00
Bajitpur | 137 | 23:00 | 130 | 21:00 | Metrorail_Uttara | 136 | 02:00 | 127 | 12:00
Bakerganj | 135 | 19:00 | 132 | 00:00 | Millgate | 137 | 02:00 | 128 | 12:00
Bakulia | 134 | 00:00 | 131 | 12:00 | Mirpur | 133 | 02:00 | 126 | 10:00
Banani | 135 | 02:00 | 126 | 12:00 | Mirzapur | 134 | 22:00 | 129 | 08:00
Bangabhaban | 135 | 02:00 | 127 | 12:00 | Mithapukur | 132 | 22:00 | 121 | 10:00
Barapukuria | 134 | 22:00 | 124 | 10:00 | MI_Cement | 133 | 03:00 | 123 | 12:00
Barguna | 135 | 18:00 | 133 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 136 | 18:00 | 134 | 07:00 | Mogbazar | 138 | 18:00 | 128 | 12:00
Barishal-230 | 134 | 02:00 | 133 | 00:00 | Mongla | 129 | 15:00 | 124 | 10:00
Baroaulia | 134 | 17:00 | 128 | 18:00 | Motijheel | 135 | 02:00 | 127 | 12:00
Baroirhat | 132 | 18:00 | 129 | 01:00 | Muktagacha | 134 | 22:00 | 121 | 06:00
Bashundhara | 136 | 02:00 | 125 | 12:00 | Munshiganj | 133 | 02:00 | 128 | 14:00
BashundharaCement | 134 | 04:00 | 130 | 10:00 | Muradnagar | 132 | 19:30 | 127 | 12:00
Beanibazar | 133 | 00:00 | 128 | 18:00 | Mymensingh | 135 | 21:00 | 122 | 00:00
Benapole | 131 | 01:00 | 124 | 06:00 | Nabinagar | 133 | 01:00 | 126 | 08:00
Bhaluka | 139 | 23:00 | 132 | 21:00 | Naogaon | 137 | 15:00 | 120 | 10:00
Bhandaria | 134 | 14:00 | 130 | 01:00 | Narail | 136 | 19:00 | 128 | 06:00
Bhangura | 133 | 07:00 | 129 | 11:00 | Narinda | 136 | 3:00 | 127 | 12:00
Bheramara | 136 | 09:00 | 134 | 06:00 | Narshingdi | 133 | 22:00 | 124 | 12:00
Bheramara(GK) | 136 | 09:00 | 133 | 06:00 | Natore | 133 | 19:30 | 127 | 12:00
Bhulta | 127 | 00:00 | 123 | 12:00 | Nawabganj | 135 | 02:00 | 128 | 12:00
Bog-Sherpur | 133 | 18:30 | 128 | 06:00 | Netrakona | 137 | 22:00 | 125 | 21:00
Bogura | 135 | 18:30 | 130 | 06:00 | New | 137 | 01:00 | 130 | 15:00
Bogura-230 | 136 | 19:30 | 124 | 11:00 | Niamatpur | 137 | 15:00 | 132 | 06:00
Brahmanbaria | 137 | 23:00 | 131 | 11:00 | Noapara | 133 | 02:00 | 127 | 10:00
Cantonment | 137 | 02:00 | 128 | 12:00 | Pabna | 134 | 09:00 | 131 | 06:00
Chandina | 134 | 19:30 | 129 | 12:00 | Palashbari | 131 | 22:00 | 120 | 10:00
Chandpur | 138 | 18:00 | 126 | 01:00 | Panchagarh | 136 | 20:00 | 128 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 136 | 18:30 | 133 | 08:00 | Patiya | 135 | 18:30 | 130 | 03:00
Chapai | 137 | 19:30 | 132 | 12:00 | Patuakhali | 134 | 09:00 | 131 | 00:00
Charsaidpur | 134 | 19:30 | 129 | 13:00 | Payra | 136 | 17:00 | 135 | 00:00
Chauddagram | 132 | 19:00 | 124 | 16:00 | PHP | 132 | 19:00 | 128 | 05:00
Chhatak | 132 | 01:00 | 127 | 21:00 | Postogola | 135 | 02:00 | 125 | 12:00
Chowmuhani | 131 | 19:00 | 125 | 00:00 | Pubail | 139 | 00:00 | 133 | 15:00
Chuadanga | 133 | 02:00 | 125 | 10:00 | Purbachal | 136 | 02:00 | 126 | 12:00
Coxsbazar | 126 | 14:00 | 113 | 20:00 | Purbasadipur | 130 | 22:00 | 121 | 10:00
Cumilla(N) | 133 | 18:00 | 130 | 12:00 | Rahanpur | 139 | 18:30 | 136 | 02:00
Cumilla(S) | 133 | 18:00 | 120 | 19:00 | Rahanpur-400 | 140 | 19:30 | 136 | 06:00
Daganbhuiyan | 131 | 18:00 | 126 | 03:00 | Rahim | 134 | 05:00 | 130 | 12:00
Daudkandi | 133 | 19:30 | 125 | 12:00 | Rajbari | 128 | 18:00 | 126 | 00:00
DhakaUniversity | 134 | 01:00 | 126 | 12:00 | Rajendrapur | 136 | 18:00 | 130 | 21:00
Dhamrai | 133 | 04:00 | 128 | 08:00 | Rajshahi | 132 | 19:30 | 125 | 13:00
Dhanmondi | 135.5 | 03:00 | 130 | 12:00 | Rajshahi-230 | 134 | 19:30 | 128 | 12:00
Dohazari | 133 | 18:30 | 125 | 03:00 | Ramganj | 132 | 18:00 | 122 | 01:00
Faridpur | 130 | 02:00 | 127 | 01:00 | Rampur | 134 | 18:30 | 130 | 10:00
Fatullah | 133 | 03:00 | 123 | 12:00 | Rampura | 135 | 04:00 | 127 | 12:00
Fenchuganj | 137 | 07:00 | 134 | 13:00 | Rangamati | 135 | 19:00 | 132 | 03:00
Feni | 130 | 19:00 | 126 | 15:00 | Rangpur | 133 | 23:00 | 121 | 10:00
Feni-230 | 130 | 18:00 | 126 | 12:00 | Ruppur | 138 | 04:00 | 133 | 06:00
Ghatail | 130 | 22:00 | 122 | 06:00 | Saidpur | 132 | 19:30 | 122 | 10:00
Ghorashal | 139 | 01:00 | 135 | 16:00 | Satkhira | 130 | 02:00 | 124 | 11:00
Goalpara | 134 | 02:00 | 127 | 23:00 | Satmasjid | 137 | 03:00 | 124 | 15:00
Gollamari | 134 | 02:00 | 129 | 11:00 | Savar | 132 | 02:00 | 124 | 12:00
Gopalganj | 133 | 02:00 | 129 | 11:00 | SevenRings | 140 | 02:00 | 135 | 11:00
Gopalganj-400 | 134 | 19:00 | 131 | 10:00 | ShahCement | 134 | 19:30 | 129 | 13:00
Gulshan | 134 | 02:00 | 126 | 12:00 | Shahjadpur | 135 | 00:00 | 132 | 12:00
Halishahar | 135 | 18:30 | 131 | 08:00 | Shahjibazar | 135 | 23:00 | 128 | 21:00
Haripur | 135 | 04:00 | 129 | 12:00 | Shahmirpur | 135 | 18:00 | 131 | 23:00
HaripurSBU | 135 | 04:00 | 130 | 15:00 | Shariatpur | 132 | 00:00 | 130 | 11:00
Hasnabad | 133 | 02:00 | 125 | 12:00 | Sherpur | 134 | 22:00 | 114 | 00:00
Hathazari | 136 | 05:00 | 132 | 09:00 | Shikalbaha | 123 | 00:00 | 121 | 07:00
Hatirjheel | 135 | 02:00 | 126 | 12:00 | Shikalbaha-230 | 136 | 19:00 | 132 | 06:00
Ishurdi | 137 | 02:00 | 134 | 06:00 | Shitalakhya | 133 | 03:00 | 123 | 12:00
Jaldhaka | 130 | 22:00 | 120 | 10:00 | Sholosohor | 135 | 18:00 | 132 | 08:00
Jamalpur | 134 | 22:00 | 117 | 06:00 | Shyampur | 132 | 00:00 | 125 | 12:00
Jashore | 132 | 02:00 | 125 | 11:00 | Shyampur-230 | 134 | 04:00 | 127 | 12:00
Jhenaidah | 137 | 19:30 | 126 | 06:00 | Siddhirganj | 134 | 00:00 | 129 | 13:00
Jhenaidah-230 | 137 | 02:00 | 131 | 11:00 | Sirajganj | 131 | 18:30 | 126 | 04:00
Joydebpur | 138 | 00:00 | 131 | 20:00 | Sonargaon | 132 | 00:00 | 125 | 03:00
Joypurhat | 128 | 18:30 | 116 | 13:00 | Sreemongol | 137 | 00:00 | 129 | 21:00
Juldah | 135 | 18:30 | 131 | 08:00 | Sreepur | 137 | 18:00 | 133 | 14:00
Kabirpur | 139 | 00:00 | 125 | 23:00 | Srinagar | 134 | 01:00 | 129 | 11:00
Kachua | 135 | 19:00 | 127 | 12:00 | SSM | 138 | 00:00 | 138 | 00:00
Kaliakoir | 139 | 02:00 | 130 | 23:00 | Sunamganj | 130 | 01:00 | 127 | 17:00
Kaliganj | 135 | 19:30 | 131 | 06:00 | Sylhet | 133 | 00:00 | 131 | 17:00
Kallyanpur | 133 | 01:00 | 120 | 15:00 | Sylhet-132 | 132 | 00:00 | 128 | 21:00
Kalurghat | 136 | 18:30 | 133 | 12:00 | Tangail | 130 | 12:00 | 124 | 08:00
Kamrangirchar | 135 | 03:00 | 124 | 11:00 | Taraganj | 130 | 19:30 | 122 | 10:00
Kaptai | N/A | N/A | N/A | N/A | Tasnim | 133 | 02:00 | 127 | 12:00
Kasba | 131 | 18:00 | 126 | 12:00 | Thakurgaon | 134 | 20:00 | 126 | 01:00
Kazla | 135 | 02:00 | 127 | 13:00 | TK | 136 | 19:00 | 133 | 02:00
Keranigonj | 136 | 02:00 | 129 | 12:00 | Tongi | 137 | 04:00 | 132 | 11:00
Khagrachori | 134 | 17:00 | 131 | 00:00 | Ullahpara | 133 | 19:30 | 129 | 05:00
Khulna | 133 | 19:00 | 128 | 23:00 | Ullon | 135 | 02:00 | 126 | 12:00
Khulna(S) | 134 | 02:00 | 128 | 10:00 | Uttara | 136 | 02:00 | 128 | 12:00
Khulshi | 133 | 18:30 | 129 | 14:00 | UttaraNew | 136 | 02:00 | 127 | 12:00
Kishoreganj | 136 | 22:00 | 129 | 21:00 | Zigatola | 135 | 01:00 | 129 | 12:00
Kodda | 139 | 22:00 | 130 | 11:00
Korerhat | 134 | 21:00 | 130 | 13:00
KSRM | 137 | 18:30 | 131 | 07:00
Kulaura | 136 | 02:00 | 133 | 18:30
Kurigram | 130 | 22:00 | 118 | 10:00
Kushtia | 134 | 15:00 | 131 | 11:00
Laksam | 134 | 19:00 | 127 | 03:00
Lakshmipur | 130 | 18:00 | 125 | 02:00
Lalbag | 135 | 06:00 | 128 | 12:00
Lalmonirhat | 128 | 19:30 | 117 | 11:00
Madanganj | 134 | 04:00 | 130 | 10:00
Madaripur | 134 | 02:00 | 131 | 10:00
Madartek | 135 | 04:00 | 126 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division