## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 17-04-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-04-2026 | during | 17-04-2026 | during | 17-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 381 | 412 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 450 | 450 | 226 | 226 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 326 | 328 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 18 | 18 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 93 | 142 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 24.5 | 23 | 33 | 33 | 29 | 29 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 40 | 50 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 45 | 294 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 113 | 52 | 95 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 35 | 162 | 162 | 35 | 35 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 33 | 0 | 33 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 530 | 570 | 584 | 584 | 526 | 526 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 142 | 142 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2105.5 | 2564 | 5851.22 | 5861.22 | 2638.55 | 2659.55
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 16 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50 | 19 | 50 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 | 70 | 70 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 218 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 51 | 105 | 105 | 34 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 39 | 55 | 56 | 64 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 67 | 68 | 68 | 34 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 12 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 20 | 19 | 108 | 108 | 38 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.7 | 0 | 4.11 | 0 | 4.11 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 18 | 54.36 | 54.36 | 0 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 55 | 110 | 110 | 54 | 54 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 0 | 0 | Liquid fuel shortage
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 17 | 163 | 163 | 163 | 17 | 17 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 353 | 612 | 1224 | 1224 | 612 | 612 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 18 | 0 | 2 | 0 | 2 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 160 | 470 | 470 | 470 | 470 | 470 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1067.7 | 1901.5 | 3363.97 | 3372.86 | 1713.61 | 1821.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 202 | 207 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 0 | 0 | 240 | 240 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 335 | 345 | 342.01 | 342.01 | 342.01 | 342.01 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 365 | 393 | 393 | 375 | 375 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 39 | 10 | 41.65 | 41.65 | 37 | 37 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 11 | 5 | 52.82 | 52.82 | 6 | 6 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 63 | 53 | 195 | 195 | 87 | 87 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Machine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 147 | 150 | 150 | 20 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 22 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 196 | 200 | 200 | 35 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 160 | 164 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 6 | 9 | 113 | 113 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 51 | 115 | 115 | 17 | 51 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 52 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.745 | 1378 | 1638 | 2654.18 | 2578.18 | 1459.01 | 1688.01
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-04-2026 | during | 17-04-2026 | during | 17-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 30 | 35 | 157.5 | 157.5 | 50 | 50 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.13 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 58 | 10 | 10 | 10 | 10 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 60 | 60 | 10 | 10 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.4 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 2 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 147.53 | 131 | 352.1 | 304 | 147.1 | 99
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 154 | 156 | 163 | 163 | 153 | 153 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 101 | 100 | 100 | 110 | 110 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 78 | 83 | 83 | 76 | 76 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 99 | 98 | 98 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 17 | 25 | 25 | 17 | 17 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 349 | 330 | 350 | 350 | 350 | 350 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 998 | 1178 | 1282 | 1282 | 1185 | 1185
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 908 | 908 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 27.5 | 28 | 28 | 25 | 25 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 22 | 42 | 50 | 50 | 30 | 30 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 233 | 182 | 410 | 410 | 250.03 | 250.03 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 42 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 593 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1798 | 2393.7 | 3583.2 | 3498.2 | 2639.33 | 2554.33
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 353 | 432 | 250 | 400 | 250 | 300 | Plant availability less
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 32 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 125 | 125 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1220 | 1200 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 290 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.41 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2258.41 | 2316 | 2412 | 2561 | 2268 | 2317
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 32.75 | 0 | 62 | 0 | 62 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 39 | 40 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 14 | 28 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 178 | 199 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 170 | 190 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 403 | 382 | 413.79 | 413.79 | 408 | 408 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 32 | 32 | 25 | 25 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 85 | 86 | 86 | 0 | 51 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 1 | 50 | 113 | 113 | 0 | 50 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.78 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1474 | 1472 | 1435.88 | 1435.88 | 1512 | 1512 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 52.28 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 67 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2435.81 | 2513 | 3239.37 | 3010.87 | 2665.1 | 2572.6
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 50 | 52 | 52 | 51 | 51 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 92 | 113 | 113 | 35 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.7 | 0 | 6.8 | 0 | 6.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 35 | 50 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 162 | 0 | 170.86 | 0 | 170.86 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 232.7 | 212 | 501.66 | 294 | 328.66 | 136
System Total |  |  |  |  | 28823.2 | 29269.987 | 12421.65 | 14847.2 | 23239.7 | 22762.33 | 15044.36 | 15032.99
Forecast Scenario (17-04-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13015.84 |  | 1417.3728 |  | 14500
|  |  |  | 1:00 | 12891.84 |  | 1067.8428 |  | 14010
|  |  |  | 2:00 | 12891.84 |  | 733.5928 |  | 13660
|  |  |  | 3:00 | 12891.84 |  | 303.8428 |  | 13210
|  |  |  | 4:00 | 12855.84 |  | 3.9728 |  | 12860
|  |  |  | 5:00 | 12680 |  | 0 |  | 12680
|  |  |  | 6:00 | 12180 |  | 0 |  | 12180
|  |  |  | 7:00 | 12070 |  | 0 |  | 12070
|  |  |  | 8:00 | 12260 |  | 0 |  | 12260
|  |  |  | 9:00 | 12210 |  | 0 |  | 12210
|  |  |  | 10:00 | 12390 |  | 0 |  | 12390
|  |  |  | 11:00 | 12730 |  | 0 |  | 12730
|  |  |  | 12:00 | 13430 |  | 0 |  | 13430
|  |  |  | 13:00 | 13598.77 |  | 402.2747 |  | 14020
|  |  |  | 14:00 | 13558.17 |  | 39.9477 |  | 13600
|  |  |  | 15:00 | 13537.23 |  | 40.8454 |  | 13580
|  |  |  | 16:00 | 13353.48 |  | 15.7766 |  | 13370
|  |  |  | 17:00 | 13050 |  | 0 |  | 13050
|  |  |  | 18:00 | 13080 |  | 0 |  | 13080
|  |  |  | 18:30 | 13576.84 |  | 117.6178 |  | 13700
|  |  |  | 19:00 | 14200 |  | 191 |  | 14400
|  |  |  | 19:30 | 14500 |  | 95.5 |  | 14600
|  |  |  | 20:00 | 14800 |  | 38.2 |  | 14840
|  |  |  | 21:00 | 14850 |  | 76.4 |  | 14930
|  |  |  | 22:00 | 14720 |  | 171.9 |  | 14900
|  |  |  | 23:00 | 14600 |  | 286.5 |  | 14900
Probable Maximum Temperature: |  |  | 34.2 °C
Probable Maximum Demand at Day Peak: |  |  | 13430.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 76
Probable Maximum Demand at Evening Peak: |  |  | 14930.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14850.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 317.84485 MKWHr. |  | 21 | 12 | 10 | 9 | 0 | 10 | 0 | 9 | 5 | 76
*** This report is generated digitally from Operation Information System (OIS) at 10:03 hrs on 17-04-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 16-04-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12421.65 | MW | 12:00 Hr. | Energy Generated |  |  | 310.3686 |  | MKWHr.
| Day Peak Demand |  |  | 14251.65 | MW | 12:00 Hr. | Energy Unserverd |  |  | 25.879 |  | MKWHr.
| Evening Peak Generation |  |  | 14847.2 | MW | 21:00 Hr. | Energy Demand |  |  | 336.2476 |  | MKWHr.
| Evening Peak Demand |  |  | 15370 | MW | 20:00 Hr. | Maximum Temperature |  |  | 34.2 |  | °C
| Minimum Generation of the Day |  |  | 11922.52 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 901.02 |  | MMCFD
| Maximum Generation of the Day |  |  | 14892 | MW | 22:00 Hr. | Production Cost per KWHr |  |  | 6.6245 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.7172 | 0 | 15.6511 | 0 | 0 | 0.1531 | 0 | 0 | 50.5214 | Gas | 126.7328 | Gas | 445277014.0603
| Chattogram Zone |  |  | 5.6416 | 16.1873 | 7.4818 | 0 | 1.6699 | 0.14536 | 0 | 0.17184 | 31.2978 | Coal | 80.8822 | Coal | 551324270.5228
| Cumilla Zone |  |  | 25.9567 | 0 | 3.7277 | 0 | 0 | 0.37239 | 4.1107 | 0 | 34.1675 | HFO | 35.4352 | HFO | 633613971.38
| Mymensingh Zone |  |  | 0.86016 | 0 | 1.9528 | 0 | 0 | 0.31617 | 0 | 0 | 3.1291 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.9386 | 0 | 0 | 0 | 0 | 0.07305 | 0 | 0 | 27.0117 | Hydro | 1.6699 | Hydro | 166988
| Khulna Zone |  |  | 5.5414 | 19.2582 | 1.0463 | 0 | 0 | 0.38664 | 21.9418 | 0 | 48.1744 | Solar | 3.8441 | Solar | 62641098.488
| Barishal Zone |  |  | 8.4308 | 44.2124 | 0.95126 | 0 | 0 | 0.003064 | 0 | 0 | 53.5975 | Import | 61.6325 | Import | 360489252.1
| Rajshahi Zone |  |  | 18.6463 | 0 | 3.3016 | 0 | 0 | 1.0054 | 35.58 | 0 | 58.5334 | Wind | 0.17184 | Wind | 2527766.4
| Rangpur Zone |  |  | 0 | 1.2244 | 1.3225 | 0 | 0 | 1.3889 | 0 | 0 | 3.9358
| Total |  |  | 126.7328 | 80.8822 | 35.4352 | 0 | 1.6699 | 3.8441 | 61.6325 | 0.17184 | 310.3686
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 445277014.0603 |  | Hydro | 166988
|  |  |  | Coal | 551324270.5228 |  | Solar | 62641098.488
|  |  |  | HFO | 633613971.38 |  | Import | 360489252.1
|  |  |  | HSD | 0 |  | Wind | 2527766.4
[5 empty] | Total: | 205,60,40,360 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9418 | Peak Hr Flow | 908.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 50637454.54 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 35.58 | Peak Hr Flow | 1472.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2875 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 4.1107 | Peak Hr Flow | 164.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 3154 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 61.6325 | Peak Hr Flow | 2544.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 10 |  | 5564
|  |  |  | Chattogram |  | 35 |  | 1528
|  |  |  | Cumilla |  | 103 |  | 1511
|  |  |  | Mymensingh |  | 98 |  | 1042
|  |  |  | Sylhet |  | 0 |  | 609
|  |  |  | Khulna |  | 0 |  | 1654
|  |  |  | Barishal |  | 0 |  | 411
|  |  |  | Rajshahi |  | 145 |  | 1588
|  |  |  | Rangpur |  | 90 |  | 891
|  |  |  | Total |  | 481 |  | 14798
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 320
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:02 | 15:37 | Gollamari 132/33kV S/S Tr-1 LT Project Work S/D Due to Paint Work
| 08:03 | 15:35 | Gollamari 132/33kV S/S Tr-1 HT Project Work S/D Due to Paint Work
| 08:24 | 15:58 | Bogura(New)-Naogaon 132 kV Ckt-2 Project Work S/D from Bogura 230/132kV end Due to
Project work at Naogaon S/S. and from Naogaon 132/33kV end Due to Project work.
|  | 08:34 | Bhaluka 132/33kV S/S Sreepur Ckt- 02 is restored.
|  | 08:34 | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-2 is restored.
| 08:38 | 09:22 | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Scheduled S/D Due to High temperature
maintenance.
| 09:02 | 09:16 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT Forced S/D | [7 empty] | 4.0MW load
interrup.
| 09:02 | 09:16 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT Forced S/D | [7 empty] | 4.0MW load
interrup.
|  | 09:08 | Sylhet 132/33kV S/S T2 HT is restored.
| 09:08 |  | Sylhet 225 MW CCPP tripped showing generator protection relay.
|  | 09:08 | Sylhet 132/33kV S/S T2 LT is restored.
|  | 09:16 | Kishoreganj 132/33kV S/S Tr-2 (414T) LT is restored.
|  | 09:16 | Bhaluka 132/33kV S/S Bus A is restored.
|  | 09:16 | Kishoreganj 132/33kV S/S Tr-2 (414T) HT is restored.
| 09:40 | 10:32 | Bhaluka 132/33kV S/S Bus B Scheduled S/D Due to High temperature maintenance.
|  | 10:08 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-1 is restored.
|  | 10:10 | Sirajganj-Sreepur 230 kV Ckt-1 is restored.
| 10:10 |  | Gopalganj 400/132kV S/S 400kV Rooppur Scheduled S/D
|  | 10:29 | Bhaluka-Mymensingh 132 kV Ckt-1 is restored.
| 12:00 |  | Day Peak Generation: 12417 MW.
| 12:50 | 13:07 | Jashore 132/33kV S/S JH-2(L1) Tripped showing Distance relays Due to Distance trip
| 13:42 | 13:58 | Khulna (S)-Satkhira 132kV Ckt-1 Tripped from Satkhira 132/33kV end showing Over current,
Earth fault, Distance relays Due to Earth fault and from Khulna(S) 230/132kV end showing
distance relay relays Due to Earth Fault
| 13:52 |  | Kushtia 132/33kV S/S T-1 LT Project Work S/D
| 13:53 |  | Kushtia 132/33kV S/S T-1 HT Project Work S/D
|  | 13:59 | Nawabganj 132/33kV S/S TR-2 HT is restored.
| 14:07 | 15:15 | Khulna(C )-Noapara 132kV Ckt-2 Tripped from Noapara 132/33kV end showing Distance Relay
(21): Siemens SIPROTEC 7SA87 Relay Info: Zone: Z1, Distance: 12.4km, Phase: A Phase
relays Due to Distance Relay Trip
| 14:10 |  | Rampal 1320 MW (BIFPCL) Unit-1 tripped
|  | 14:16 | Nawabganj 132/33kV S/S TR-2 LT is restored.
| 14:47 | 15:03 | Noapara 132/33kV S/S T-2 LT Tripped showing SIEMENS SIPROTEC-7SJ81 Protection: | [7 empty] | 6.0MW load
|  |  | 50N/51N IMDT> Pick up Protection: 50/51 DMT: Operate relays Due to Due REB-1 Feeder | [7 empty] | interrup.
over current & earth fault
| 14:47 | 15:03 | Noapara 132/33kV S/S T-1 LT Tripped showing SIEMENS SIPROTEC-7SJ81 Protection: | [7 empty] | 6.0MW load
|  |  | 50N/51N IMDT> Pick up Protection: 50/51 DMT: Operate relays Due to Due REB-1 Feeder | [7 empty] | interrup.
over current & earth fault
| 14:49 |  | Rampal 1320 MW (BIFPCL) Unit-1 was synchronized
| 14:49 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U-1
| 15:34 |  | Anowara-Sikalbaha 230 kV Ckt-2 Project Work S/D from Shikalbaha 230/132kV end.
|  | 15:58 | Naogaon 132/33kV S/S Naogaon-SPPP Ckt-1 is restored.
|  | 16:27 | Korerhat 400/230/132kV S/S ATR-3(7103T) HT is restored.
|  | 16:33 | Korerhat 400/230/132kV S/S ATR-3(7103T) LT is restored.
| 16:41 |  | Sylhet 225 MW CCPP GT was synchronized
|  | 17:05 | Naogaon 132/33kV S/S T-4 HT is restored.
|  | 18:07 | Naogaon 132/33kV S/S T-4 LT is restored.
| 18:29 | 21:09 | Barishal 230/132kV S/S T-5 LT Tripped showing P142 relays Due to 33kv Rahmatpur feeder | [7 empty] | 40.0MW load
|  |  | trip | [7 empty] | interrup.
| 18:29 | 20:14 | Barishal 230/132kV S/S T-4 LT Tripped showing P142 relays Due to 33 kv Rahmatpur feeder | [7 empty] | 40.0MW load
|  |  | trip | [7 empty] | interrup.
| 21:00 |  | Evening peak generation is 14846 MW.
| 21:06 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- gt
| 22:28 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
| 05:09 |  | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Fenchuganj
230/132/33kV end Due to project work at Sylhet South SS end.
| 06:01 |  | Fenchuganj-Sylhet (South) 132KV Ckt-1 Project Work S/D from Sylhet (South) end Due to
Project Work Of OPGW.
| 06:04 |  | Fenchuganj -Sylhet 132kV Ckt-1 Scheduled S/D from Beanibazar 132/33kV end Due to Line | [7 empty] | 25.0MW load
|  |  | re-routing work | [7 empty] | interrup.
Beanibazar 132/33kV
end
| 06:12 |  | Ashuganj-Brahmanbaria 132kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end.
| 07:31 |  | Goalpara 132/33kV S/S T1 LT Scheduled S/D Due to High temperature rised in both side of
Txr-1. Main works by nut-bolt tighting in the both side clamp
| 07:32 |  | Goalpara 132/33kV S/S T1 HT Scheduled S/D Due to High temperature rised in both side of
Txr-1. Main works by nut-bolt tighting in the both side clamp
| 07:34 |  | Maniknagar 132/33kV S/S Transformer GT-1 HT Scheduled S/D Due to DPDC 33/11 KV
upgradation work
| 07:51 |  | Baroaulia-Hathazari 132 kV Ckt-2 Scheduled S/D from Baroaulia 132/33kV end Due to
Maintenance work at hathazari end
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 16-04-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 412 | 9522000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4747100 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 720394 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 328 | 7618858 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 18 | 261720 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 142 | 2903040 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 266882 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 267344 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 519600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 524160 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 1069440 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 294 | 2510847 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 113 | 1121760 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2184000 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 803520 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 153104 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 301680 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 570 | 11785454.55 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3240480 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2564 | 50521383.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 544892.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 125685 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 637920 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1669880 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5286892 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 979382 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 55 | 933216 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 67 | 362476 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 12 | 354720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 19 | 476160 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19680 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 391418 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 18 | 138339 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1368291 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 211200 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 163 | 1438545 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 10674544 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 171840 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 470 | 5512727.27 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 1901.5 | 31297807.67
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 207 | 4952000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 0 | 724300 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 345 | 8184000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 365 | 8814500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 10 | 567288 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 5 | 140640 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 53 | 1037090 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1052768 | Machine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 147 | 933381 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 22 | 388608 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 196 | 1767360 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 164 | 4110720 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 484100 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 80640 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 51 | 557760 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 372391 | -
Cumilla Area Total |  |  |  |  | 2870.745 | 1638 | 34167546
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 35 | 860160 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1389600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 218400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 303720 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 127680 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 217080 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 131 | 3129090
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 73050 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 981000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 688320 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3720354.54 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 101 | 1503600 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 710688 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1652160 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 99 | 1571950 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 312528 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7141000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 330 | 8657000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1178 | 27011650.54
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 908 | 21941818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 27.5 | 310080 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 42 | 736256 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 182 | 5541408 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 386640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 19258178 | Unit1 Under Maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2393.7 | 48174380
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 432 | 7825455 | Plant availability less
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 512064 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 125 | 3075000 | STG Under Maintenance
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 29186909.09 | Machine Problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5355830 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 439200 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 290 | 7200000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3064 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2316 | 53597522.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 251504 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 996135 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 418671 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 199 | 4612545 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 190 | 4589536 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 382 | 9444218 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 379400 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 85 | 566432 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 537696 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 403296 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24000 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1472 | 35580000 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 293248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 436670 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2513 | 58533351
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1224436 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 92 | 769036 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 30157.44 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 553441 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 156362 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1202400 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 212 | 3935832.44
Eastern Grid Total |  |  |  |  | 17417.792 | 7412.5 | 146127477.76
Western Grid Total |  |  |  |  | 11852.195 | 7434.7 | 164241085.53
National Grid Total |  |  |  |  | 29269.987 | 14847.2 | 310368563.29
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 16-04-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10007.88 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4310 | MW
i) Dhaka area |  |  | 5553.78 |  | MW | i) Khulna area |  |  |  | 1654.5 | MW
ii) Chattogram area |  |  | 1493.1 |  | MW | ii) Barishal area |  |  |  | 411.3 | MW
iii) Cumilla area |  |  | 1408 |  | MW | iii) Rajshahi area |  |  |  | 1443.2 | MW
iv) Mymensingh area |  |  | 944 |  | MW | iv) Rangpur area |  |  |  | 801 | MW
v) Sylhet area |  |  | 609 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14317.88 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 14 | 06:00 | 67 | Hasnabad | 107 | 19:30 | 133 | Natore | 172 | 15:00
2 | AKSML | 6.8 | 03:00 | 68 | Hathazari | 91 | 20:00 | 134 | Nawabganj | 65.6 | 00:00
3 | Aftabnagar | 40 | 00:00 | 69 | Hatirjheel | 48 | 13:00 | 135 | Netrakona | 130 | 19:00
4 | Agargaon | 124 | 13:00 | 70 | Ishurdi | 70 | 18:30 | 136 | New | 76.9 | 12:00
5 | Agrabad | 58 | 19:00 | 71 | Jaldhaka | 66 | 21:00 | 137 | Niamatpur | 109 | 00:00
6 | Amnura | 44 | 05:00 | 72 | Jamalpur | 107 | 01:00 | 138 | Noapara | 40 | 07:00
7 | Ashuganj | 83 | 23:00 | 73 | Jashore | 141 | 00:00 | 139 | PHP | 5 | 02:00
8 | BSRM | 199 | 17:00 | 74 | Jhenaidah | 104 | 19:00 | 140 | Pabna | 94 | 01:00
9 | Bagerhat | 83 | 22:00 | 75 | Joydebpur | 152 | 21:00 | 141 | Palashbari | 126 | 18:00
10 | Bajitpur | 82 | 21:00 | 76 | Joypurhat | 66 | 01:00 | 142 | Panchagarh | 42 | 19:00
11 | Bakerganj | 14.6 | 19:30 | 77 | Juldah | 20 | 08:00 | 143 | Patiya | 12 | 19:30
12 | Bakulia | 97 | 18:30 | 78 | KSRM | 16 | 12:00 | 144 | Patuakhali | 68 | 21:00
13 | Banani | 49 | 14:00 | 79 | Kabirpur | 270 | 18:00 | 145 | Payra | 50 | 13:00
14 | Bangabhaban | 20 | 10:00 | 80 | Kachua | 84 | 23:00 | 146 | Postogola | 55 | 13:00
15 | Barapukuria | 62 | 15:00 | 81 | Kaliganj | 26 | 03:00 | 147 | Pubail | 30 | 18:30
16 | Barguna | 22 | 21:00 | 82 | Kallyanpur | 120 | 00:00 | 148 | Purbachal | 37 | 13:00
17 | Barishal | 109 | 20:00 | 83 | Kalurghat | 38 | 19:00 | 149 | Purbasadipur | 120 | 15:00
18 | Barishal-230 | 98 | 02:00 | 84 | Kamrangirchar | 82 | 13:00 | 150 | Rahanpur | 38 | 01:00
19 | Baroaulia | 65 | 00:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 23 | 08:00
20 | Baroirhat | 57 | 19:30 | 86 | Kasba | 32 | 01:00 | 152 | Rajbari | 88.5 | 19:00
21 | Bashundhara | 204 | 13:00 | 87 | Kazla | 118 | 13:00 | 153 | Rajendrapur | 131 | 17:00
22 | BashundharaCement | 8 | 21:00 | 88 | Keranigonj | 94 | 19:30 | 154 | Rajshahi | 138 | 15:00
23 | Beanibazar | 84 | 19:30 | 89 | Khagrachori | 32 | 20:00 | 155 | Rajshahi-230 | 93 | 01:00
24 | Benapole | 64 | 08:00 | 90 | Khulna | 66 | 13:00 | 156 | Ramganj | 96 | 01:00
25 | Bhaluka | 103 | 21:00 | 91 | Khulshi | 184 | 18:00 | 157 | Rampur | 46 | 23:00
26 | Bhandaria | 56 | 19:00 | 92 | Kishoreganj | 87 | 22:00 | 158 | Rangamati | 18 | 20:00
27 | Bhangura | 40 | 06:00 | 93 | Kodda | 315 | 19:00 | 159 | Rangpur | 128 | 18:00
28 | Bheramara(GK) | 64 | 22:00 | 94 | Kulaura | 47 | 21:00 | 160 | Ruppur | 4.4 | 10:00
29 | Bhulta | 233 | 21:00 | 95 | Kurigram | 68 | 18:30 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 76 | 01:00 | 96 | Kushtia | 158 | 19:00 | 162 | Saidpur | 98 | 15:00
31 | Bogura | 171 | 00:00 | 97 | Laksam | 21 | 23:00 | 163 | Satkhira | 138 | 19:00
32 | Borhanuddin | 94 | 19:00 | 98 | Lakshmipur | 35 | 03:00 | 164 | Satmasjid | 110 | 14:00
33 | Brahmanbaria | 135 | 21:00 | 99 | Lalbag | 77 | 13:00 | 165 | Savar | 236 | 19:00
34 | Cantonment | 144 | 13:00 | 100 | Lalmonirhat | 44 | 19:30 | 166 | SevenRings | 19.33 | 16:00
35 | Chandina | 23 | 13:00 | 101 | MI_Cement | 17 | 00:00 | 167 | ShahCement | 45 | 00:00
36 | Chandpur | 68 | 21:00 | 102 | Madanganj | 41 | 19:00 | 168 | Shahjadpur | 77 | 21:00
37 | Chandraghona | 42 | 19:30 | 103 | Madaripur | 111 | 23:00 | 169 | Shahjibazar | 122 | 22:00
38 | Chapai | 77 | 18:30 | 104 | Madartek | 82 | 00:00 | 170 | Shahmirpur | 65 | 01:00
39 | Charsaidpur | 41 | 00:00 | 105 | Madunaghat | 52 | 00:00 | 171 | Shariatpur | 88 | 21:00
40 | Chauddagram | 69 | 01:00 | 106 | Magura | 65 | 19:00 | 172 | Sherpur | 104 | 23:00
41 | Chhatak | 36 | 19:30 | 107 | Mahasthangarh | 75 | 18:00 | 173 | Shikalbaha | 28 | 01:00
42 | Chowmuhani | 160 | 20:00 | 108 | Maijdee | 39 | 06:00 | 174 | Shitalakhya | 87 | 11:00
43 | Chuadanga | 116 | 01:00 | 109 | Manikganj | 142 | 00:00 | 175 | Sholosohor | 46 | 10:00
44 | Coxsbazar | 151 | 19:30 | 110 | Maniknagar | 77 | 13:00 | 176 | Shyampur | 186 | 11:00
45 | Cumilla(N) | 127 | 21:00 | 111 | Matarbari | 57 | 01:00 | 177 | Siddhirganj | 135 | 11:00
46 | Cumilla(S) | 203 | 18:30 | 112 | Matuail | 76 | 12:00 | 178 | Sirajganj | 116 | 19:00
47 | Daganbhuiyan | 35 | 02:00 | 113 | Metrorail_Motijheel | 45 | 16:00 | 179 | Sonargaon | 134 | 22:00
48 | Daudkandi | 161 | 21:00 | 114 | Metrorail_Uttara | 9 | 11:00 | 180 | Sreemongol | 86 | 20:00
49 | DhakaUniversity | 84 | 12:00 | 115 | Millgate | 102 | 11:00 | 181 | Sreepur | 100 | 22:00
50 | Dhamrai | 134 | 19:00 | 116 | Mirpur | 147 | 18:30 | 182 | Srinagar | 53 | 19:30
51 | Dhanmondi | 137 | 13:00 | 117 | Mirsorai | 57 | 12:00 | 183 | Sunamganj | 58 | 22:00
52 | Dohazari | 105 | 19:30 | 118 | Mirzapur | 42 | 02:00 | 184 | Sylhet | 68 | 19:00
53 | Faridpur | 163 | 19:30 | 119 | Mithapukur | 62 | 18:30 | 185 | Sylhet-132 | 133 | 19:00
54 | Fatullah | 93 | 12:00 | 120 | Modern | N/A | N/A | 186 | TK | 28.5 | 21:00
55 | Fenchuganj | 46 | 19:30 | 121 | Mogbazar | 89.6 | 13:00 | 187 | Tangail | 154 | 21:00
56 | Feni | 97 | 22:00 | 122 | Mongla | 47 | 07:00 | 188 | Taraganj | 21 | 19:00
57 | GPH | 74 | 13:00 | 123 | Motijheel | 50 | 13:00 | 189 | Tasnim | 28 | 00:00
58 | Ghatail | 62 | 18:30 | 124 | Muktagacha | 30 | 23:00 | 190 | Thakurgaon | 82 | 19:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 122 | 19:30 | 191 | Tongi | 153 | 23:00
60 | Ghorashal-230 | 108 | 22:00 | 126 | Muradnagar | 46 | 18:30 | 192 | Ullahpara | 44 | 18:30
61 | Goalpara | 42 | 01:00 | 127 | Mymensingh | 185 | 20:00 | 193 | Ullon | 64 | 23:00
62 | Gollamari | 92 | 00:00 | 128 | Nabinagar | 11 | 00:00 | 194 | Uttara | 95 | 13:00
63 | Gopalganj | 91 | 18:30 | 129 | Naogaon | 142 | 00:00 | 195 | UttaraNew | 61 | 00:00
64 | Gulshan | 136 | 13:00 | 130 | Narail | 54 | 01:00 | 196 | Zigatola | 88 | 13:00
65 | Halishahar | 106 | 15:00 | 131 | Narinda | 78 | 13:00
66 | HaripurSBU | 130 | 19:00 | 132 | Narshingdi | 187 | 22:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 16-04-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 12829.39 | 690 |  | 13550.44
1:00 | 12463.33 | 418 |  | 12900.33
2:00 | 12265.86 | 893 |  | 13198.86
3:00 | 12061.41 | 993 |  | 13099.41
4:00 | 12042.92 | 915 |  | 12998.92
5:00 | 11985.99 | 874 |  | 12898.99
6:00 | 11974.87 | 791 |  | 12801.87
7:00 | 11922.52 | 1033 |  | 13001.52
8:00 | 11947.52 | 1056 |  | 13051.52
9:00 | 12003.95 | 1241 |  | 13300.95
10:00 | 12017.55 | 1516 |  | 13601.55
11:00 | 12223.2 | 1603 |  | 13898.2
12:00 | 12421.65 | 1751 |  | 14251.65
13:00 | 12327.46 | 1935 |  | 14349.46
14:00 | 12381.02 | 1912 |  | 14379.02
15:00 | 12436.12 | 1878 |  | 14399.12
16:00 | 12565.02 | 1681 |  | 14322.02
17:00 | 13151.59 | 986 |  | 14181.59
18:00 | 13582.27 | 687 |  | 14300.27
19:00 | 14495.5 | 721 |  | 15248.5
19:30 | 14776.7 | 510 |  | 15309.7
20:00 | 14817 | 529 |  | 15370
21:00 | 14847.2 | 481 |  | 15350.2
22:00 | 14892 | 419 |  | 15330
23:00 | 14083.5 | 876 |  | 14998.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 16-04-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6298.5 | 6530.89 | 12829.39 | DAILY GENERATION CURVE
00:30 | 6147 | 6499.36 | 12646.36
01:00 | 5995.5 | 6467.83 | 12463.33 | 16-04-2026
01:30 | 5861.5 | 6503.095 | 12364.595
02:00 | 5727.5 | 6538.36 | 12265.86
02:30 | 5691 | 6472.635 | 12163.635
03:00 | 5654.5 | 6406.91 | 12061.41
03:30 | 5651.5 | 6400.665 | 12052.165
04:00 | 5648.5 | 6394.42 | 12042.92
04:30 | 5627 | 6387.455 | 12014.455
05:00 | 5605.5 | 6380.49 | 11985.99
05:30 | 5617.705 | 6362.725 | 11980.43
06:00 | 5629.91 | 6344.96 | 11974.87
06:30 | 5576.68 | 6372.015 | 11948.695
07:00 | 5523.45 | 6399.07 | 11922.52
07:30 | 5507.97 | 6427.05 | 11935.02
08:00 | 5492.49 | 6455.03 | 11947.52
08:30 | 5513.015 | 6462.72 | 11975.735
09:00 | 5533.54 | 6470.41 | 12003.95
09:30 | 5509.25 | 6501.5 | 12010.75
10:00 | 5484.96 | 6532.59 | 12017.55
10:30 | 5569.69 | 6550.685 | 12120.375
11:00 | 5654.42 | 6568.78 | 12223.2
11:30 | 5675.575 | 6646.85 | 12322.425
12:00 | 5696.73 | 6724.92 | 12421.65
12:30 | 5698.755 | 6675.8 | 12374.555
13:00 | 5700.78 | 6626.68 | 12327.46
13:30 | 5714.415 | 6639.825 | 12354.24
14:00 | 5728.05 | 6652.97 | 12381.02
14:30 | 5743.56 | 6665.01 | 12408.57
15:00 | 5759.07 | 6677.05 | 12436.12
15:30 | 5729.96 | 6770.61 | 12500.57
16:00 | 5700.85 | 6864.17 | 12565.02
16:30 | 5869.32 | 6988.985 | 12858.305
17:00 | 6037.79 | 7113.8 | 13151.59
17:30 | 6263.645 | 7103.285 | 13366.93
18:00 | 6489.5 | 7092.77 | 13582.27
18:30 | 6831.5 | 7207.385 | 14038.885
19:00 | 7173.5 | 7322 | 14495.5
19:30 | 7379.5 | 7397.2 | 14776.7
20:00 | 7411.5 | 7405.5 | 14817
20:30 | 7412 | 7420.1 | 14832.1 |  | Executive Engineer
21:00 | 7412.5 | 7434.7 | 14847.2 |  | Network Operation Division
21:30 | 7420 | 7449.6 | 14869.6
22:00 | 7427.5 | 7464.5 | 14892
22:30 | 7061.5 | 7426.25 | 14487.75
23:00 | 6695.5 | 7388 | 14083.5

## En-Curve
QF-LDC-12
Date | 16-04-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3589 | 1439 | 907 | 0 | 184 | 1465.89 | 70 | 3327 | 0 | 651 | 1196.5 | 0 | 0 | 0 | 690 | DAILY ENERGY CURVE
00:30 | 3665 | 1485.5 | 907 | 0 | 183 | 1463.36 | 70 | 3311 | 0 | 597.5 | 964 | 0 | 0 | 0 | 554 | 16-04-2026
01:00 | 3741 | 1532 | 907 | 0 | 182 | 1460.83 | 70 | 3295 | 0 | 544 | 731.5 | 0 | 0 | 0 | 418
01:30 | 3709.5 | 1530 | 907.5 | 0 | 179 | 1461.595 | 70 | 3312 | 0 | 561.5 | 632 | 0 | 0 | 1.5 | 655.5 | Energy Generated | 310.3686 |  | MKWHr
02:00 | 3678 | 1528 | 908 | 0 | 176 | 1462.36 | 70 | 3329 | 0 | 579 | 532.5 | 0 | 0 | 3 | 893 | Energy not Served | 25.879 |  | MKWHr
02:30 | 3721 | 1514.5 | 908 | 0 | 174 | 1460.135 | 70 | 3212 | 0 | 581.5 | 514.5 | 0 | 0 | 8 | 943 | Total Energy Requirement | 336.2476 |  | MKWHr
03:00 | 3764 | 1501 | 908 | 0 | 172 | 1457.91 | 70 | 3095 | 0 | 584 | 496.5 | 0 | 0 | 13 | 993
03:30 | 3804.5 | 1492 | 908 | 0 | 169 | 1462.165 | 70 | 3071 | 0 | 588 | 471 | 0 | 0 | 16.5 | 954
04:00 | 3845 | 1483 | 908 | 0 | 166 | 1466.42 | 70 | 3047 | 0 | 592 | 445.5 | 0 | 0 | 20 | 915
04:30 | 3786.5 | 1521 | 907.5 | 0 | 164 | 1466.455 | 70 | 3044.5 | 0 | 592 | 445.5 | 0 | 0 | 17 | 894.5
05:00 | 3728 | 1559 | 907 | 0 | 162 | 1466.49 | 70 | 3042 | 0 | 592 | 445.5 | 0 | 0 | 14 | 874
05:30 | 3730 | 1583 | 907.5 | 0 | 156 | 1464.61 | 70 | 3011 | 3.32 | 590.5 | 453.5 | 0 | 0 | 11 | 832.5
06:00 | 3732 | 1607 | 908 | 0 | 150 | 1462.73 | 70 | 2980 | 6.64 | 589 | 461.5 | 0 | 0 | 8 | 791
06:30 | 3716 | 1610 | 908 | 0 | 150 | 1462.285 | 70 | 2960.5 | 38.41 | 566 | 460.5 | 0 | 0 | 7 | 912
07:00 | 3700 | 1613 | 908 | 0 | 150 | 1461.84 | 70 | 2941 | 70.18 | 543 | 459.5 | 0 | 0 | 6 | 1033
07:30 | 3692 | 1614.5 | 908 | 0 | 142 | 1462.31 | 70 | 2906 | 130.46 | 534.5 | 471.75 | 0 | 0 | 3.5 | 1044.5
08:00 | 3684 | 1616 | 908 | 0 | 134 | 1462.78 | 70 | 2871 | 190.74 | 526 | 484 | 0 | 0 | 1 | 1056
08:30 | 3645 | 1589.5 | 907.5 | 0 | 137 | 1466.39 | 70 | 2870.5 | 271.845 | 524.5 | 491 | 0 | 0 | 2.5 | 1148.5
09:00 | 3606 | 1563 | 907 | 0 | 140 | 1470 | 70 | 2870 | 352.95 | 523 | 498 | 0 | 0 | 4 | 1241
09:30 | 3528.5 | 1596.5 | 907.5 | 0 | 147 | 1465 | 70 | 2869 | 422.75 | 514 | 488 | 0 | 0 | 2.5 | 1378.5
10:00 | 3451 | 1630 | 908 | 0 | 154 | 1460 | 70 | 2868 | 492.55 | 505 | 478 | 0 | 0 | 1 | 1516
10:30 | 3435 | 1666.75 | 908 | 0 | 157 | 1466 | 70 | 2865 | 536.125 | 502 | 507 | 0 | 0 | 7.5 | 1559.5
11:00 | 3419 | 1703.5 | 908 | 0 | 160 | 1472 | 70 | 2862 | 579.7 | 499 | 536 | 0 | 0 | 14 | 1603
11:30 | 3449.5 | 1701 | 908 | 0 | 160 | 1473 | 70 | 2949 | 561.425 | 488 | 546.5 | 0 | 0 | 16 | 1677
12:00 | 3480 | 1698.5 | 908 | 0 | 160 | 1474 | 70 | 3036 | 543.15 | 477 | 557 | 0 | 0 | 18 | 1751
12:30 | 3449.5 | 1698.75 | 908 | 0 | 165 | 1461 | 70 | 3031.5 | 516.305 | 470.5 | 582.5 | 0 | 0 | 21.5 | 1843
13:00 | 3419 | 1699 | 908 | 0 | 170 | 1448 | 70 | 3027 | 489.46 | 464 | 608 | 0 | 0 | 25 | 1935
13:30 | 3452 | 1697.5 | 908 | 0 | 169 | 1458.5 | 68 | 3027.5 | 448.24 | 473 | 628 | 0 | 0 | 24.5 | 1923.5
14:00 | 3485 | 1696 | 908 | 0 | 168 | 1469 | 66 | 3028 | 407.02 | 482 | 648 | 0 | 0 | 24 | 1912
14:30 | 3499.5 | 1695 | 907.5 | 0 | 170 | 1469 | 66 | 3072 | 359.82 | 484.5 | 661.75 | 0 | 0 | 23.5 | 1895
15:00 | 3514 | 1694 | 907 | 0 | 172 | 1469 | 66 | 3116 | 312.62 | 487 | 675.5 | 0 | 0 | 23 | 1878
15:30 | 3472.5 | 1687.5 | 907 | 0 | 183 | 1472 | 67 | 3229 | 254.12 | 503.45 | 710 | 0 | 0 | 15 | 1779.5
16:00 | 3431 | 1681 | 907 | 0 | 194 | 1475 | 68 | 3342 | 195.62 | 519.9 | 744.5 | 0 | 0 | 7 | 1681
16:30 | 3449.5 | 1631.5 | 907.5 | 0 | 193 | 1477.5 | 68 | 3499.5 | 133.855 | 563.95 | 929 | 0 | 0 | 5 | 1333.5
17:00 | 3468 | 1582 | 908 | 0 | 192 | 1480 | 68 | 3657 | 72.09 | 608 | 1113.5 | 0 | 0 | 3 | 986
17:30 | 3514 | 1598 | 908 | 0 | 183 | 1492.5 | 69 | 3670.5 | 42.93 | 658.5 | 1229 | 0 | 0 | 1.5 | 836.5
18:00 | 3560 | 1614 | 908 | 0 | 174 | 1505 | 70 | 3684 | 13.77 | 709 | 1344.5 | 0 | 0 | 0 | 687
18:30 | 3603 | 1574 | 907.5 | 0 | 182 | 1499.5 | 70 | 3922 | 6.885 | 763.5 | 1510.5 | 0 | 0 | 0 | 704
19:00 | 3646 | 1534 | 907 | 0 | 190 | 1494 | 70 | 4160 | 0 | 818 | 1676.5 | 0 | 0 | 0 | 721
19:30 | 3552 | 1716 | 908 | 0 | 182 | 1489 | 70 | 4254.2 | 0 | 827 | 1778.5 | 0 | 0 | 0 | 510
20:00 | 3575 | 1735 | 907 | 0 | 180 | 1482 | 70 | 4245 | 0 | 840.5 | 1782.5 | 0 | 0 | 0 | 529
20:30 | 3602.5 | 1737.5 | 907.5 | 0 | 172 | 1477 | 70 | 4266.6 | 0 | 839 | 1760 | 0 | 0 | 0 | 505
21:00 | 3630 | 1740 | 908 | 0 | 164 | 1472 | 70 | 4288.2 | 0 | 837.5 | 1737.5 | 0 | 0 | 0 | 481
21:30 | 3717.5 | 1641.5 | 908 | 0 | 182 | 1476.5 | 70 | 4317.1 | 0 | 833.5 | 1723.5 | 0 | 0 | 0 | 450
22:00 | 3805 | 1543 | 908 | 0 | 200 | 1481 | 70 | 4346 | 0 | 829.5 | 1709.5 | 0 | 0 | 0 | 419
22:30 | 3686 | 1542.5 | 907 | 0 | 196 | 1484 | 70 | 4295.5 | 0 | 822.25 | 1484.5 | 0 | 0 | 0 | 647.5
23:00 | 3567 | 1542 | 906 | 0 | 192 | 1487 | 70 | 4245 | 0 | 815 | 1259.5 | 0 | 0 | 0 | 876
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 16-04-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 389 | 04:00 | 377 | 12:00 | Madunaghat | 398 | 07:00 | 393 | 10:00
Amtali | 412 | 05:00 | 406 | 21:00 | Meghnaghat | 391 | 07:00 | 379 | 20:00
Ashuganj | 402 | 05:00 | 388 | 12:00 | Payra | 413 | 03:00 | 408 | 22:00
Bhulta | 397 | 03:00 | 380 | 12:00 | Rahanpur | 409 | 13:00 | 400 | 01:00
Bibiana | 408 | 00:00 | 397 | 20:00 | Rampal | 401 | 15:00 | 391 | 12:00
BIPTC | 397 | 07:00 | 390 | 00:00
Bogura | 399 | 14:00 | 390 | 18:00
Gopalganj | 398 | 05:00 | 388 | 12:00
Kaliakoir | 385 | 00:00 | 371 | 12:00
Korerhat | 400 | 07:00 | 392 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 04:00 | 221 | 12:00 | Jhenaidah | 227 | 13:00 | 214 | 20:00
AKSML | 231.6 | 23:00 | 223.7 | 19:30 | Kachua | 228 | 18:00 | 221 | 02:00
Aminbazar | 232 | 04:00 | 221 | 12:00 | Kaliakoir | 233 | 00:00 | 224 | 12:00
Ashuganj | 234 | 00:00 | 223 | 12:00 | Keranigonj | 229 | 04:00 | 219 | 12:00
Ashuganj-400 | 234 | 00:00 | 223 | 12:00 | Khulna(S) | 232 | 15:00 | 220 | 01:00
Baghabari | 233 | 00:00 | 228 | 16:00 | Korerhat | 230 | 07:00 | 222 | 19:30
Barapukuria | 228 | 14:00 | 212 | 15:00 | Madunaghat | 229 | 23:00 | 223 | 01:00
Barapukuria-230 | 228 | 14:00 | 212 | 15:00 | Madunaghat-400 | 229 | 00:00 | 225 | 01:00
Barishal | 227 | 00:00 | 221 | 22:00 | Maniknagar | 228 | 03:00 | 218 | 12:00
Bheramara | 230 | 13:00 | 222 | 21:00 | Meghnaghat | 236 | 04:00 | 226 | 11:00
Bhulta | 229 | 03:00 | 218 | 12:00 | Meghnaghat-400 | 230 | 04:00 | 222 | 11:00
Bibiana | 235 | 00:00 | 229 | 19:30 | Mirsorai | 228 | 23:00 | 220 | 11:00
BIPTC | 233 | 13:00 | 222 | 21:00 | Naogaon | 226 | 10:00 | 217 | 01:00
Bogura | 233 | 13:00 | 227 | 01:00 | Purbasadipur | 224 | 19:30 | 210 | 15:00
Bogura-400 | 232 | 13:00 | 226 | 18:00 | Rajshahi | 229 | 13:00 | 220 | 01:00
Borhanuddin | 260 | 06:00 | 227 | 23:00 | Rampal | 231 | 15:00 | 219 | 21:00
BSRM | 228 | 07:00 | 223 | 01:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 225 | 07:00 | 219 | 10:00 | Rampura | 229 | 04:00 | 217 | 12:00
Cumilla(N) | 229 | 03:00 | 222 | 19:30 | Shikalbaha | 229 | 07:00 | 223 | 01:00
Faridpur | 222 | 04:00 | 215 | 22:00 | Shyampur | 229 | 04:00 | 219 | 12:00
Fenchuganj | 240 | 00:00 | 231 | 20:00 | Siddhirganj | 229 | 04:00 | 220 | 12:00
Feni | 228 | 00:00 | 224 | 01:00 | Sirajgonj | 240 | 00:00 | 235 | 20:00
Ghorashal | 232 | 07:00 | 225 | 10:00 | Sreepur | 232 | 00:00 | 221 | 21:00
Ghorashal-230 | 228 | 00:00 | 217 | 12:00 | Tongi | 234 | 02:00 | 215 | 10:00
Gopalganj | 222 | 00:00 | 216 | 21:00
GPH | 230 | 07:00 | 223 | 19:30
Haripur | 229 | 04:00 | 220 | 12:00
Hasnabad | 229 | 04:00 | 218 | 12:00
Hathazari | 233 | 20:00 | 223 | 19:30
Ishurdi | 233 | 14:00 | 225 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 05:00 | 125 | 12:00 | Madunaghat | 134 | 23:00 | 130 | 01:00
Agargaon | 136 | 04:00 | 128 | 12:00 | Magura | 135 | 13:00 | 123 | 20:00
Agrabad | 132 | 06:00 | 125 | 20:00 | Mahasthangarh | 131 | 11:00 | 126 | 18:00
AKS | 130 | 05:00 | 125 | 19:30 | Maijdee | 126 | 07:00 | 122 | 01:00
Aminbazar | 133 | 04:00 | 126 | 11:00 | Manikganj | 128 | 06:00 | 119 | 20:00
Amnura | 136 | 13:00 | 127 | 01:00 | Maniknagar | 135 | 04:00 | 125 | 13:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 122 | 10:00 | 103 | 19:30
Ashuganj-230 | 142 | 00:00 | 135 | 12:00 | Matuail | 133 | 04:00 | 128 | 11:00
Bagerhat | 130 | 15:00 | 116 | 22:00 | Metrorail_Motijheel | 135 | 04:00 | 125 | 13:00
Bajitpur | 139 | 00:00 | 128 | 19:30 | Metrorail_Uttara | 133 | 01:00 | 123 | 12:00
Bakerganj | 133 | 00:00 | 128 | 22:00 | Millgate | 134 | 05:00 | 123 | 13:00
Bakulia | 132 | 23:00 | 126 | 19:30 | Mirpur | 131 | 04:00 | 125 | 11:00
Banani | 135 | 05:00 | 125 | 12:00 | Mirzapur | 138 | 00:00 | 128 | 12:00
Bangabhaban | 135 | 06:00 | 126 | 12:00 | Mithapukur | 131 | 19:30 | 123 | 16:00
Barapukuria | 134 | 22:00 | 125 | 15:00 | MI_Cement | 131 | 06:00 | 121 | 12:00
Barguna | 133 | 00:00 | 127 | 22:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 134 | 00:00 | 129 | 21:00 | Mogbazar | 136 | 06:00 | 125 | 12:00
Barishal-230 | 133 | 00:00 | 127 | 22:00 | Mongla | 130 | 15:00 | 115 | 22:00
Baroaulia | 132 | 00:00 | 126 | 19:30 | Motijheel | 135 | 06:00 | 126 | 12:00
Baroirhat | 130 | 06:00 | 127 | 01:00 | Muktagacha | 135 | 00:00 | 121 | 21:00
Bashundhara | 134 | 02:00 | 123 | 11:00 | Munshiganj | 131 | 05:00 | 126 | 19:30
BashundharaCement | 132 | 00:00 | 127 | 20:00 | Muradnagar | 130 | 00:00 | 123 | 21:00
Beanibazar | 131 | 07:00 | 120 | 19:30 | Mymensingh | 140 | 00:00 | 120 | 21:00
Benapole | 135 | 14:00 | 118 | 22:00 | Nabinagar | 132 | 01:00 | 124 | 19:30
Bhaluka | 142 | 00:00 | 129 | 18:30 | Naogaon | 137 | 13:00 | 119 | 16:00
Bhandaria | 132 | 00:00 | 120 | 22:00 | Narail | 136 | 13:00 | 122 | 19:00
Bhangura | 131 | 11:00 | 126 | 18:00 | Narinda | 135 | 04:00 | 125 | 13:00
Bheramara | 135 | 00:00 | 130 | 22:00 | Narshingdi | 138 | 00:00 | 121 | 20:00
Bheramara(GK) | 134 | 00:00 | 130 | 22:00 | Natore | 132 | 13:00 | 126 | 16:00
Bhulta | 126 | 15:00 | 122 | 13:00 | Nawabganj | 134 | 03:00 | 126 | 19:30
Bog-Sherpur | 133 | 13:00 | 128 | 01:00 | Netrakona | 138 | 00:00 | 121 | 19:30
Bogura | 135 | 13:00 | 129 | 18:00 | New | 135 | 03:00 | 125 | 12:00
Bogura-230 | 135 | 13:00 | 130 | 01:00 | Niamatpur | 138 | 13:00 | 133 | 06:00
Brahmanbaria | 136 | 00:00 | 124 | 20:00 | Noapara | 134 | 14:00 | 121 | 22:00
Cantonment | 135 | 02:00 | 127 | 12:00 | Pabna | 133 | 00:00 | 128 | 22:00
Chandina | 132 | 07:00 | 127 | 21:00 | Palashbari | 128 | 02:00 | 120 | 18:00
Chandpur | 134 | 18:30 | 123 | 01:00 | Panchagarh | 137 | 19:30 | 124 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 135 | 23:00 | 130 | 19:30 | Patiya | 132 | 23:00 | 123 | 19:30
Chapai | 137 | 13:00 | 132 | 06:00 | Patuakhali | 132 | 00:00 | 128 | 22:00
Charsaidpur | 132 | 07:00 | 127 | 21:00 | Payra | 135 | 00:00 | 132 | 22:00
Chauddagram | 128 | 00:00 | 125 | 20:00 | PHP | 129 | 00:00 | 126 | 01:00
Chhatak | 132 | 03:00 | 121 | 19:30 | Postogola | 133 | 04:00 | 124 | 11:00
Chowmuhani | 127 | 22:00 | 124 | 00:00 | Pubail | 140 | 00:00 | 130 | 20:00
Chuadanga | 134 | 13:00 | 120 | 21:00 | Purbachal | 135 | 05:00 | 123 | 13:00
Coxsbazar | 124 | 23:00 | 104 | 19:30 | Purbasadipur | 131 | 19:30 | 120 | 15:00
Cumilla(N) | 132 | 03:00 | 128 | 10:00 | Rahanpur | 139 | 13:00 | 136 | 06:00
Cumilla(S) | 130 | 00:00 | 121 | 16:00 | Rahanpur-400 | 139 | 10:00 | 136 | 01:00
Daganbhuiyan | 128 | 18:00 | 125 | 01:00 | Rahim | 133 | 04:00 | 127 | 12:00
Daudkandi | 128 | 00:00 | 120 | 21:00 | Rajbari | 127 | 08:00 | 121 | 22:00
DhakaUniversity | 133 | 01:00 | 125 | 12:00 | Rajendrapur | 141 | 00:00 | 128 | 19:30
Dhamrai | 131 | 00:00 | 124 | 19:00 | Rajshahi | 130 | 13:00 | 125 | 15:00
Dhanmondi | 134 | 04:00 | 128 | 12:00 | Rajshahi-230 | 132 | 13:00 | 126 | 01:00
Dohazari | 132 | 23:00 | 120 | 19:30 | Ramganj | 129 | 18:00 | 120 | 01:00
Faridpur | 129 | 07:00 | 125 | 19:00 | Rampur | 133 | 23:00 | 126 | 19:30
Fatullah | 130 | 00:00 | 122 | 12:00 | Rampura | 134 | 04:00 | 125 | 12:00
Fenchuganj | 136 | 00:00 | 130 | 19:30 | Rangamati | 133 | 06:00 | 128 | 19:30
Feni | 128 | 00:00 | 124 | 11:00 | Rangpur | 131 | 10:00 | 122 | 18:00
Feni-230 | 128 | 07:00 | 125 | 01:00 | Ruppur | 135 | 00:00 | 130 | 22:00
Ghatail | 132 | 00:00 | 120 | 21:00 | Saidpur | 130 | 13:00 | 122 | 15:00
Ghorashal | 138 | 07:00 | 133 | 11:00 | Satkhira | 131 | 14:00 | 116 | 21:00
Goalpara | 135 | 15:00 | 123 | 22:00 | Satmasjid | 135 | 03:00 | 127 | 12:00
Gollamari | 133 | 14:00 | 124 | 21:00 | Savar | 130 | 03:00 | 125 | 11:00
Gopalganj | 133 | 15:00 | 125 | 22:00 | SevenRings | 139 | 00:00 | 132 | 13:00
Gopalganj-400 | 132 | 00:00 | 128 | 21:00 | ShahCement | 132 | 05:00 | 127 | 21:00
Gulshan | 133 | 07:00 | 125 | 12:00 | Shahjadpur | 135 | 00:00 | 132 | 21:00
Halishahar | 133 | 07:00 | 126 | 19:30 | Shahjibazar | 138 | 00:00 | 123 | 21:00
Haripur | 133 | 01:00 | 128 | 20:00 | Shahmirpur | 132 | 23:00 | 126 | 19:30
HaripurSBU | 133 | 01:00 | 128 | 20:00 | Shariatpur | 131 | 07:00 | 125 | 22:00
Hasnabad | 132 | 03:00 | 123 | 13:00 | Sherpur | 132 | 01:00 | 113 | 21:00
Hathazari | 134 | 06:00 | 131 | 09:00 | Shikalbaha | 122 | 01:00 | 118 | 17:00
Hatirjheel | 134 | 04:00 | 125 | 12:00 | Shikalbaha-230 | 133 | 07:00 | 127 | 19:30
Ishurdi | 136 | 13:00 | 131 | 22:00 | Shitalakhya | 131 | 06:00 | 121 | 12:00
Jaldhaka | 129 | 10:00 | 121 | 15:00 | Sholosohor | 133 | 07:00 | 128 | 19:30
Jamalpur | 133 | 04:00 | 118 | 21:00 | Shyampur | 130 | 07:00 | 123 | 10:00
Jashore | 135 | 14:00 | 120 | 21:00 | Shyampur-230 | 132 | 04:00 | 125 | 11:00
Jhenaidah | 134 | 13:00 | 122 | 18:30 | Siddhirganj | 133 | 03:00 | 128 | 10:00
Jhenaidah-230 | 136 | 13:00 | 125 | 20:00 | Sirajganj | 131 | 01:00 | 126 | 07:00
Joydebpur | 138 | 00:00 | 129 | 20:00 | Sonargaon | 130 | 00:00 | 125 | 22:00
Joypurhat | 126 | 03:00 | 117 | 16:00 | Sreemongol | 137 | 00:00 | 124 | 19:30
Juldah | 132 | 23:00 | 126 | 19:30 | Sreepur | 140 | 00:00 | 131 | 20:00
Kabirpur | 140 | 00:00 | 120 | 13:00 | Srinagar | 135 | 04:00 | 126 | 19:30
Kachua | 131 | 18:00 | 125 | 01:00 | SSM | 138 | 00:00 | 130 | 19:30
Kaliakoir | 140 | 00:00 | 127 | 19:30 | Sunamganj | 131 | 03:00 | 119 | 21:00
Kaliganj | 135 | 13:00 | 125 | 21:00 | Sylhet | 133 | 03:00 | 125 | 19:30
Kallyanpur | 131 | 02:00 | 125 | 12:00 | Sylhet-132 | 132 | 03:00 | 126 | 19:30
Kalurghat | 133 | 23:00 | 129 | 19:30 | Tangail | 136 | 00:00 | 123 | 21:00
Kamrangirchar | 134 | 03:00 | 123 | 19:30 | Taraganj | 129 | 13:00 | 122 | 15:00
Kaptai | N/A | N/A | N/A | N/A | Tasnim | 130 | 00:00 | 125 | 20:00
Kasba | 129 | 00:00 | 123 | 19:30 | Thakurgaon | 136 | 19:30 | 122 | 15:00
Kazla | 134 | 04:00 | 126 | 12:00 | TK | 134 | 06:00 | 128 | 19:30
Keranigonj | 135 | 04:00 | 127 | 19:30 | Tongi | 135 | 04:00 | 127 | 12:00
Khagrachori | 132 | 02:00 | 127 | 19:30 | Ullahpara | 133 | 13:00 | 128 | 01:00
Khulna | 133 | 14:00 | 123 | 20:00 | Ullon | 133 | 02:00 | 125 | 11:00
Khulna(S) | 134 | 14:00 | 124 | 21:00 | Uttara | 133 | 01:00 | 123 | 13:00
Khulshi | 131 | 23:00 | 124 | 19:30 | UttaraNew | 133 | 01:00 | 123 | 12:00
Kishoreganj | 138 | 00:00 | 127 | 19:30 | Zigatola | 135 | 05:00 | 127 | 13:00
Kodda | 139 | 00:00 | 128 | 19:30
Korerhat | 131 | 07:00 | 129 | 01:00
KSRM | 133 | 07:00 | 128 | 19:30
Kulaura | 135 | 00:00 | 128 | 19:30
Kurigram | 128 | 19:00 | 118 | 18:00
Kushtia | 133 | 13:00 | 126 | 19:00
Laksam | 131 | 18:00 | 124 | 01:00
Lakshmipur | 127 | 18:00 | 123 | 01:00
Lalbag | 134 | 06:00 | 126 | 19:00
Lalmonirhat | 128 | 00:00 | 117 | 18:00
Madanganj | 132 | 00:00 | 127 | 20:00
Madaripur | 132 | 03:00 | 128 | 19:30
Madartek | 134 | 04:00 | 124 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 16-04-2026 | [28 empty] | Date: | 16-04-2026 | [28 empty] | Date: | 16-04-2026 | [28 empty] | Date: | 16-04-2026 | [28 empty] | Date: | 16-04-2026 | [17 empty] | Date: | 16-04-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [17 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 35 | 149 | 123 | 293 | 48 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 108 | 24 | 22 | 0 | 400 | 0 | 16 | 38 | 0 | 0 | 67 | 40 | 18 | 12 | 12 | 0 | 70 | 55 | 30 | 160 | 17 | 0 | 19 | 25.5 | 51 | 222 | 0 | 0 | 0 | 612 | 0 | 20 | 53 | 375 | 0 | 345 | 44 | 5 | 179 | 42 | 18 | 0 | 52 | 0 | 20 | 0 | 184 | 0 | 0 | 28 | 290 | 0 | 348 | 41 | 30 | 141 | 0 | 17 | 0 | 33 | 30 | 100 | 0 | 98 | 0 | 9 | 58 | 65 | 0 | 0 | 12 | 6298.5 | 907 | 250 | 0 | 19 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 1465.89 | 0 | 43 | 0 | 35 | 35 | 0 | 0 | 27 | 0 | 0 | 0 | 25 | 0 | 0 | 172 | 0 | 0 | 0 | 172 | 0 | 340 | 0 | 0 | 0 | 53 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 267 | 120 | 180 | 0 | 398 | 1227 | 17 | 6530.89 | 12829.39 | 79.74
01:00 | 0 | 88 | 34 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 0 | 30 | 126 | 230 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 84 | 18 | 22 | 0 | 473 | 0 | 16 | 37 | 0 | 0 | 0 | 40 | 18 | 0 | 12 | 0 | 70 | 55 | 28 | 160 | 17 | 0 | 19 | 25.5 | 34 | 219 | 0 | 0 | 0 | 612 | 0 | 18 | 40 | 360 | 74 | 345 | 44 | 5 | 189 | 42 | 17 | 0 | 17 | 0 | 20 | 0 | 182 | 0 | 0 | 29 | 290 | 0 | 348 | 41 | 30 | 142 | 0 | 17 | 0 | 33 | 30 | 99 | 0 | 98 | 0 | 9 | 58 | 44 | 0 | 0 | 12 | 5995.5 | 907 | 250 | 0 | 18 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 1460.83 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 26 | 0 | 0 | 172 | 0 | 0 | 0 | 173 | 0 | 414 | 0 | 0 | 0 | 54 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 299 | 130 | 220 | 0 | 400 | 1190 | 17 | 6467.83 | 12463.33 | 79.72
02:00 | 0 | 88 | 51 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 20 | 126 | 60 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 104 | 23 | 22 | 0 | 480 | 0 | 16 | 24 | 0 | 3 | 0 | 40 | 18 | 0 | 12 | 0 | 70 | 55 | 28 | 160 | 17 | 0 | 19 | 25.5 | 34 | 219 | 0 | 0 | 0 | 612 | 0 | 20 | 8 | 260 | 153 | 300 | 44 | 5 | 157 | 5 | 17 | 0 | 17 | 0 | 20 | 0 | 176 | 0 | 0 | 29 | 290 | 0 | 348 | 41 | 30 | 158 | 0 | 17 | 0 | 33 | 30 | 100 | 0 | 98 | 0 | 9 | 58 | 41 | 0 | 0 | 12 | 5727.5 | 908 | 250 | 0 | 18 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605 | 0 | 0 | 0 | 1462.36 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 26 | 0 | 0 | 197 | 0 | 0 | 0 | 192 | 0 | 414 | 0 | 0 | 0 | 54 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 130 | 220 | 0 | 379 | 1212 | 17 | 6538.36 | 12265.86 | 79.7
03:00 | 0 | 88 | 51 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 126 | 45 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 108 | 0 | 22 | 0 | 470 | 0 | 16 | 18 | 0 | 13 | 0 | 40 | 18 | 0 | 12 | 0 | 70 | 55 | 28 | 160 | 17 | 0 | 19 | 25.5 | 34 | 219 | 0 | 0 | 0 | 500 | 0 | 20 | 8 | 265 | 153 | 300 | 44 | 5 | 195 | 5 | 17 | 0 | 17 | 0 | 20 | 0 | 172 | 0 | 0 | 30 | 295 | 0 | 370 | 41 | 30 | 159 | 0 | 17 | 0 | 33 | 30 | 100 | 0 | 98 | 0 | 9 | 58 | 68 | 0 | 0 | 0 | 5654.5 | 908 | 250 | 0 | 18 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 0 | 0 | 0 | 1457.91 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 26 | 0 | 0 | 194 | 0 | 0 | 0 | 190 | 0 | 414 | 0 | 0 | 0 | 54 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 130 | 220 | 0 | 254 | 1212 | 17 | 6406.91 | 12061.41 | 79.68
04:00 | 0 | 88 | 51 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 126 | 45 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 125 | 22 | 22 | 0 | 430 | 0 | 16 | 18 | 0 | 20 | 0 | 39 | 0 | 0 | 12 | 0 | 70 | 55 | 28 | 160 | 17 | 0 | 19 | 25.5 | 34 | 220 | 0 | 0 | 0 | 451 | 0 | 20 | 8 | 275 | 153 | 345 | 44 | 5 | 199 | 5 | 18 | 0 | 17 | 0 | 20 | 0 | 166 | 0 | 0 | 22 | 295 | 0 | 378 | 41 | 30 | 159 | 0 | 17 | 0 | 33 | 30 | 100 | 0 | 98 | 0 | 9 | 58 | 69 | 0 | 0 | 0 | 5648.5 | 908 | 250 | 0 | 18 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 0 | 0 | 0 | 1466.42 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 25 | 0 | 0 | 196 | 0 | 0 | 0 | 200 | 0 | 414 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 130 | 220 | 0 | 255 | 1212 | 17 | 6394.42 | 12042.92 | 79.66
05:00 | 0 | 88 | 51 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 126 | 45 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 125 | 22 | 22 | 0 | 430 | 0 | 16 | 19 | 0 | 14 | 0 | 39 | 0 | 0 | 12 | 0 | 70 | 55 | 28 | 160 | 17 | 0 | 19 | 25.5 | 34 | 220 | 0 | 0 | 0 | 451 | 0 | 20 | 45 | 393 | 0 | 345 | 44 | 5 | 197 | 36 | 17 | 0 | 17 | 0 | 20 | 0 | 162 | 0 | 0 | 22 | 290 | 0 | 378 | 41 | 30 | 159 | 0 | 17 | 0 | 77 | 30 | 0 | 0 | 98 | 0 | 9 | 58 | 66 | 0 | 0 | 0 | 5605.5 | 907 | 250 | 0 | 18 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 0 | 0 | 0 | 1466.49 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 25 | 0 | 0 | 186 | 0 | 0 | 0 | 202 | 0 | 414 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 130 | 220 | 0 | 255 | 1210 | 17 | 6380.49 | 11985.99 | 79.64
06:00 | 0 | 88 | 51 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 126 | 45 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 1 | 125 | 22 | 22 | 0 | 420 | 0 | 16 | 18 | 0 | 8 | 0 | 39 | 0 | 0 | 12 | 0 | 70 | 55 | 33 | 160 | 17 | 0 | 19 | 25.5 | 34 | 219 | 0 | 0 | 0 | 425 | 0 | 20 | 53 | 393 | 0 | 345 | 44 | 5 | 200 | 39 | 17 | 0 | 17 | 0 | 20 | 0 | 150 | 0 | 1 | 22 | 290 | 0 | 378 | 41 | 30 | 159 | 0 | 17 | 0 | 77 | 30 | 0 | 0 | 98 | 0 | 9 | 58 | 63 | 0.02 | 0.39 | 0 | 5629.91 | 908 | 250 | 0 | 18 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 608 | 0 | 0 | 0 | 1462.73 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0.62 | 0 | 25 | 0 | 0.55 | 187 | 0 | 0 | 0 | 203 | 0 | 414 | 0 | 0.06 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 16 | 278 | 130 | 220 | 0 | 254 | 1204 | 17 | 6344.96 | 11974.87 | 79.62
07:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 111 | 45 | 30 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 3 | 128 | 24 | 22 | 0 | 400 | 0 | 16 | 18 | 0 | 6 | 0 | 39 | 0 | 0 | 12 | 0 | 70 | 55 | 29 | 160 | 17 | 0 | 19 | 25.5 | 34 | 220 | 0 | 0 | 0 | 352 | 2 | 20 | 81 | 393 | 0 | 345 | 44 | 5 | 195 | 39 | 17 | 0 | 17 | 0 | 20 | 0 | 150 | 0 | 2 | 22 | 290 | 0 | 378 | 41 | 30 | 159 | 1 | 17 | 0 | 77 | 30 | 0 | 0 | 98 | 0 | 9 | 58 | 41 | 0.21 | 5.74 | 0 | 5523.45 | 908 | 246 | 0 | 18 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 607 | 0 | 0 | 0 | 1461.84 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 4.26 | 9 | 0 | 0 | 5.51 | 188 | 0 | 0 | 0 | 200 | 0 | 414 | 0 | 0.5 | 0 | 51 | 0 | 3 | 0 | 0 | 0 | 0 | 0.9 | 23 | 0.06 | 16 | 307 | 130 | 220 | 0 | 254 | 1210 | 17 | 6399.07 | 11922.52 | 79.6
08:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 112 | 45 | 55 | 6 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 7 | 128 | 25 | 22 | 0 | 430 | 0 | 16 | 19 | 0 | 1 | 0 | 39 | 0 | 0 | 12 | 1.59 | 70 | 55 | 3 | 160 | 17 | 0 | 19 | 18 | 34 | 219 | 0 | 0 | 0 | 292 | 6 | 20 | 81 | 390 | 0 | 345 | 44 | 5 | 195 | 43 | 17 | 0 | 17 | 0 | 20 | 0 | 134 | 0 | 18 | 22 | 290 | 0 | 378 | 41 | 30 | 158 | 4 | 17 | 0 | 76 | 30 | 0 | 0 | 98 | 0 | 9 | 58 | 30 | 0.35 | 9.55 | 0 | 5492.49 | 908 | 233 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 602 | 0 | 0 | 0 | 1462.78 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 9.64 | 33 | 0 | 0 | 12.4 | 194 | 0 | 0 | 0 | 202 | 0 | 414 | 0 | 1.03 | 0 | 51 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 53 | 0.18 | 16 | 307 | 130 | 220 | 0 | 254 | 1205 | 17 | 6455.03 | 11947.52 | 79.59
09:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 111 | 45 | 55 | 17 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 14 | 140 | 25 | 22 | 0 | 430 | 0 | 16 | 19 | 0 | 4 | 0 | 39 | 0 | 0 | 12 | 2.51 | 70 | 55 | 2 | 160 | 17 | 0 | 19 | 17 | 34 | 217 | 0 | 0 | 0 | 293 | 13 | 20 | 53 | 355 | 0 | 345 | 44 | 0 | 215 | 43 | 21 | 0 | 17 | 0 | 20 | 0 | 140 | 0 | 40 | 15 | 290 | 0 | 380 | 42 | 30 | 156 | 8 | 0 | 0 | 76 | 30 | 0 | 0 | 98 | 0 | 9 | 58 | 31 | 0.95 | 22.08 | 0 | 5533.54 | 907 | 247 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 600 | 0 | 0 | 0 | 1470 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 22.26 | 39 | 0 | 0 | 45 | 190 | 0 | 0 | 0 | 140 | 0 | 376 | 0 | 3.7 | 0 | 51 | 0 | 9 | 0 | 0 | 0 | 0 | 2.1 | 77 | 0.35 | 16 | 307 | 130 | 220 | 0 | 254 | 1205 | 17 | 6470.41 | 12003.95 | 79.58
10:00 | 0 | 88 | 40 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 1 | 17 | 110 | 45 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 26 | 142 | 19 | 22 | 0 | 530 | 0 | 16 | 19 | 0 | 1 | 0 | 39 | 0 | 0 | 12 | 3.68 | 70 | 55 | 2 | 160 | 17 | 0 | 19 | 16 | 34 | 216 | 0 | 0 | 0 | 293 | 15 | 20 | 26 | 380 | 0 | 345 | 44 | 1 | 198 | 43 | 18 | 0 | 17 | 0 | 17 | 0 | 154 | 0 | 54 | 0 | 290 | 0 | 348 | 42 | 30 | 155 | 10 | 0 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 31 | 1.9 | 31.38 | 0 | 5484.96 | 908 | 239 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 598 | 0 | 0 | 0 | 1460 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 28.83 | 78 | 0 | 0 | 45.92 | 183 | 0 | 0 | 0 | 140 | 0 | 370 | 0 | 4.32 | 0 | 51 | 0 | 15 | 0 | 0 | 0 | 0 | 2.2 | 128 | 0.32 | 16 | 307 | 128 | 220 | 0 | 254 | 1205 | 17 | 6532.59 | 12017.55 | 79.57
11:00 | 0 | 88 | 40 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 18 | 17 | 21 | 110 | 45 | 55 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 27 | 142 | 23.5 | 22 | 0 | 550 | 0 | 16 | 19 | 0 | 14 | 0 | 39 | 0 | 0 | 12 | 3.53 | 70 | 55 | 2 | 160 | 17 | 0 | 19 | 16 | 34 | 215 | 0 | 0 | 0 | 296 | 18 | 20 | 43 | 393 | 0 | 340 | 44 | 10 | 202 | 43 | 17 | 0 | 17 | 3 | 20 | 0 | 160 | 0 | 68 | 0 | 300 | 0 | 348 | 42 | 30 | 157 | 11 | 8 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 30 | 2.16 | 42.23 | 0 | 5654.42 | 908 | 235 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 591 | 0 | 0 | 0 | 1472 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 45.09 | 85 | 0 | 0 | 58 | 174 | 0 | 0 | 0 | 140 | 0 | 365 | 0 | 5.06 | 0 | 50 | 0 | 13 | 0 | 0 | 0 | 0 | 4.1 | 129 | 0.53 | 16 | 307 | 128 | 220 | 0 | 253 | 1205 | 17 | 6568.78 | 12223.2 | 79.56
12:00 | 0 | 88 | 40 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 18 | 17 | 17 | 93 | 45 | 55 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 28 | 142 | 24.5 | 22 | 0 | 530 | 0 | 16 | 20 | 0 | 18 | 0 | 39 | 0 | 0 | 12 | 3.7 | 70 | 55 | 3 | 160 | 17 | 0 | 19 | 16 | 34 | 214 | 0 | 0 | 0 | 353 | 18 | 20 | 63 | 393 | 0 | 335 | 44 | 11 | 202 | 39 | 16 | 0 | 17 | 6 | 20 | 0 | 160 | 0 | 52 | 0 | 295 | 0 | 349 | 42 | 30 | 154 | 11 | 8 | 0 | 79 | 30 | 0 | 0 | 0 | 2 | 9 | 58 | 30 | 2.13 | 46.4 | 0 | 5696.73 | 908 | 233 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 593 | 0 | 0 | 0 | 1474 | 0 | 39 | 0 | 0 | 1 | 0 | 0 | 14 | 0 | 32.75 | 67 | 0 | 0 | 52.28 | 178 | 0 | 0 | 0 | 170 | 0 | 403 | 0 | 4.78 | 0 | 50 | 0 | 15 | 0 | 0 | 0 | 0 | 5.7 | 162 | 0.41 | 16 | 307 | 125 | 220 | 0 | 353 | 1220 | 17 | 6724.92 | 12421.65 | 79.55
13:00 | 0 | 88 | 40 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 18 | 17 | 17 | 93 | 45 | 55 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 9 | 142 | 5 | 22 | 0 | 530 | 0 | 16 | 19 | 0 | 25 | 0 | 32 | 0 | 0 | 12 | 2.41 | 70 | 55 | 6 | 160 | 17 | 0 | 19 | 16 | 34 | 213 | 0 | 0 | 0 | 350 | 17 | 20 | 63 | 385 | 0 | 340 | 44 | 15 | 193 | 42 | 17 | 0 | 25 | 6 | 20 | 0 | 170 | 0 | 39 | 6 | 310 | 0 | 349 | 42 | 30 | 153 | 10 | 8 | 0 | 78 | 30 | 20 | 0 | 0 | 17 | 9 | 58 | 28 | 1.99 | 47.38 | 0 | 5700.78 | 908 | 225 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 587 | 0 | 0 | 0 | 1448 | 0 | 32 | 0 | 0 | 29 | 0 | 0 | 13 | 0 | 23.54 | 47 | 0 | 0 | 46.1 | 165 | 0 | 0 | 0 | 140 | 0 | 391 | 0 | 4.45 | 0 | 50 | 0 | 24 | 0 | 0 | 0 | 0 | 4 | 168 | 0.59 | 16 | 307 | 125 | 220 | 0 | 353 | 1220 | 17 | 6626.68 | 12327.46 | 79.54
14:00 | 0 | 88 | 31 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 18 | 17 | 26 | 108 | 45 | 30 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 17 | 322 | 0 | 0 | 14 | 142 | 20 | 22 | 0 | 540 | 0 | 16 | 19 | 0 | 24 | 0 | 32 | 0 | 0 | 12 | 2.52 | 66 | 55 | 3 | 160 | 17 | 0 | 19 | 16 | 34 | 214 | 0 | 0 | 0 | 350 | 15 | 20 | 53 | 393 | 0 | 335 | 44 | 12 | 200 | 10 | 17 | 0 | 20 | 9 | 20 | 0 | 168 | 0 | 38 | 7 | 305 | 0 | 349 | 42 | 30 | 146 | 9 | 8 | 0 | 78 | 30 | 100 | 0 | 0 | 17 | 9 | 58 | 28 | 1.45 | 36.08 | 0 | 5728.05 | 908 | 216 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 3.19 | 588 | 0 | 0 | 0 | 1469 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 13 | 0 | 44.53 | 20 | 0 | 0 | 28.95 | 176 | 0 | 0 | 0 | 162 | 0 | 391 | 0 | 0 | 0 | 50 | 0 | 28 | 0 | 0 | 0 | 0 | 5 | 161 | 0.3 | 16 | 307 | 125 | 220 | 0 | 353 | 1220 | 17 | 6652.97 | 12381.02 | 79.53
15:00 | 0 | 88 | 31 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 18 | 17 | 34 | 106 | 45 | 30 | 4 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 324 | 0 | 0 | 18 | 142 | 13 | 22 | 0 | 555 | 0 | 16 | 19 | 0 | 23 | 0 | 33 | 0 | 0 | 12 | 2.33 | 66 | 55 | 2 | 160 | 17 | 0 | 19 | 25.5 | 34 | 212 | 0 | 0 | 0 | 350 | 10 | 20 | 53 | 393 | 0 | 331 | 44 | 5 | 206 | 10 | 17 | 0 | 17 | 0 | 20 | 0 | 172 | 0 | 26 | 10 | 300 | 0 | 350 | 42 | 30 | 149 | 7 | 8 | 0 | 78 | 30 | 102 | 0 | 0 | 17 | 9 | 58 | 28 | 1.21 | 31.03 | 0 | 5759.07 | 907 | 206 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 3.26 | 725 | 0 | 0 | 0 | 1469 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 14 | 0 | 16.51 | 29 | 0 | 0 | 21 | 200 | 0 | 0 | 0 | 170 | 0 | 377 | 0 | 1.87 | 0 | 51 | 0 | 21 | 0 | 0 | 0 | 0 | 4.4 | 120 | 0.01 | 16 | 307 | 125 | 220 | 0 | 303 | 1220 | 17 | 6677.05 | 12436.12 | 79.52
16:00 | 0 | 88 | 32 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 18 | 17 | 49 | 107 | 45 | 30 | 20 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 322 | 0 | 0 | 10 | 142 | 23 | 22 | 0 | 530 | 0 | 16 | 18 | 0 | 7 | 0 | 47 | 0 | 0 | 12 | 0.98 | 68 | 55 | 2 | 160 | 17 | 0 | 19 | 25.5 | 34 | 213 | 0 | 0 | 0 | 360 | 7 | 20 | 55 | 393 | 0 | 338 | 44 | 5 | 199 | 10 | 17 | 0 | 17 | 0 | 20 | 0 | 194 | 0 | 6 | 16 | 300 | 0 | 284 | 42 | 30 | 152 | 3 | 8 | 0 | 75 | 30 | 100 | 0 | 0 | 17 | 9 | 58 | 30 | 0.65 | 15.72 | 4 | 5700.85 | 907 | 206 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 942 | 0 | 0 | 0 | 1475 | 0 | 40 | 0 | 35 | 35 | 0 | 8.9 | 14 | 0 | 14.2 | 12 | 0 | 0 | 17 | 203 | 0 | 0 | 0 | 170 | 0 | 358 | 0 | 1.64 | 0 | 51 | 35 | 13 | 0 | 0 | 0 | 0 | 1.4 | 80 | 0.03 | 16 | 307 | 125 | 220 | 0 | 302 | 1220 | 17 | 6864.17 | 12565.02 | 79.51
17:00 | 0 | 88 | 40 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 18 | 17 | 70 | 124 | 45 | 15 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 55 | 323 | 0 | 0 | 4 | 142 | 22 | 22 | 0 | 460 | 0 | 16 | 19 | 0 | 3 | 0 | 48 | 0 | 0 | 12 | 0.21 | 68 | 66 | 4 | 240 | 163 | 0 | 19 | 25.5 | 36 | 214 | 0 | 0 | 0 | 390 | 2 | 20 | 53 | 360 | 0 | 342 | 44 | 5 | 207 | 10 | 17 | 0 | 98 | 0 | 20 | 0 | 192 | 0 | 0 | 14 | 305 | 0 | 308 | 42 | 30 | 151 | 1 | 16 | 0 | 75 | 30 | 102 | 0 | 35 | 17 | 9 | 58 | 30 | 0.25 | 6.83 | 10 | 6037.79 | 908 | 198 | 0 | 10 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 1101 | 0 | 0 | 0 | 1480 | 0 | 40 | 0 | 35 | 35 | 0 | 27 | 15 | 0 | 4.06 | 9 | 32 | 0 | 3 | 205 | 0 | 0 | 0 | 180 | 0 | 382 | 0 | 0.31 | 0 | 45 | 35 | 6 | 81 | 0 | 0 | 0 | 0.6 | 33 | 0.03 | 16 | 307 | 125 | 180 | 0 | 352 | 1222 | 17 | 7113.8 | 13151.59 | 79.49
18:00 | 0 | 88 | 49 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 18 | 17 | 70 | 125 | 145 | 15 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 55 | 325 | 0 | 0 | 0 | 142 | 23 | 22 | 0 | 450 | 0 | 16 | 18 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 70 | 55 | 7 | 360 | 163 | 0 | 27 | 25.5 | 51 | 216 | 0 | 0 | 0 | 440 | 0 | 20 | 53 | 393 | 0 | 342 | 44 | 5 | 199 | 10 | 17 | 0 | 196 | 6 | 20 | 0 | 174 | 0 | 1 | 15 | 300 | 0 | 330 | 42 | 20 | 152 | 0 | 16 | 0 | 77 | 30 | 100 | 0 | 100 | 17 | 9 | 58 | 30 | 0 | 1 | 12 | 6489.5 | 908 | 196 | 0 | 26 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1085 | 0 | 0 | 0 | 1505 | 0 | 40 | 0 | 35 | 35 | 0 | 85 | 26 | 0 | 0.55 | 3 | 32 | 0 | 1 | 205 | 0 | 0 | 0 | 191 | 0 | 360 | 0 | 0.1 | 0 | 48 | 50 | 1 | 92 | 0 | 0 | 0 | 0.1 | 2 | 0.02 | 16 | 247 | 125 | 220 | 0 | 324 | 1180 | 17 | 7092.77 | 13582.27 | 79.47
19:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 20 | 101 | 140 | 278 | 15 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 327 | 0 | 0 | 0 | 142 | 23 | 22 | 0 | 400 | 0 | 16 | 18 | 0 | 0 | 50 | 56 | 0 | 0 | 0 | 0 | 70 | 55 | 12 | 470 | 163 | 0 | 49 | 25.5 | 51 | 217 | 0 | 0 | 0 | 573 | 0 | 76 | 53 | 393 | 0 | 345 | 44 | 5 | 200 | 10 | 47 | 0 | 196 | 8 | 20 | 0 | 190 | 0 | 0 | 15 | 305 | 0 | 330 | 42 | 30 | 152 | 0 | 16 | 0 | 77 | 30 | 100 | 0 | 100 | 17 | 9 | 58 | 30 | 0 | 0 | 12 | 7173.5 | 907 | 191 | 0 | 32 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1211 | 0 | 0 | 0 | 1494 | 0 | 40 | 0 | 35 | 45 | 0 | 83 | 28 | 0 | 0 | 0 | 32 | 0 | 0 | 205 | 0 | 0 | 0 | 190 | 0 | 369 | 0 | 0 | 0 | 48 | 70 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 307 | 125 | 180 | 0 | 361 | 1190 | 17 | 7322 | 14495.5 | 79.45
19:30 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 54 | 35 | 105 | 142 | 278 | 15 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 328 | 0 | 0 | 0 | 142 | 23 | 22 | 0 | 540 | 0 | 16 | 18 | 0 | 0 | 68 | 55 | 0 | 0 | 0 | 0 | 70 | 55 | 15 | 470 | 163 | 0 | 50 | 25.5 | 51 | 217 | 0 | 0 | 0 | 612 | 0 | 142 | 53 | 345 | 0 | 345 | 44 | 5 | 200 | 10 | 51 | 0 | 196 | 8 | 20 | 0 | 182 | 0 | 0 | 15 | 300 | 0 | 330 | 42 | 30 | 156 | 0 | 16 | 0 | 77 | 30 | 102 | 0 | 100 | 17 | 9 | 58 | 31 | 0 | 0 | 12 | 7379.5 | 908 | 191 | 0 | 21 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 1489 | 0 | 40 | 0 | 35 | 50 | 0 | 83 | 28 | 0 | 0 | 0 | 32 | 0 | 0 | 201 | 0 | 0 | 0 | 190 | 0 | 355 | 0 | 0 | 0 | 48 | 70 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 290 | 125 | 220 | 0 | 405 | 1195 | 17 | 7397.2 | 14776.7
20:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 54 | 35 | 105 | 142 | 278 | 15 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 327 | 0 | 0 | 0 | 142 | 23 | 22 | 0 | 560 | 0 | 16 | 18 | 0 | 0 | 68 | 55 | 0 | 0 | 0 | 0 | 70 | 55 | 19 | 470 | 163 | 0 | 50 | 25.5 | 51 | 216 | 0 | 0 | 0 | 612 | 0 | 143 | 53 | 354 | 0 | 345 | 44 | 5 | 203 | 10 | 52 | 0 | 197 | 9 | 20 | 0 | 180 | 0 | 0 | 15 | 295 | 0 | 330 | 42 | 30 | 154 | 0 | 17 | 0 | 78 | 30 | 100 | 0 | 100 | 17 | 9 | 58 | 31 | 0 | 0 | 12 | 7411.5 | 907 | 188 | 0 | 27.5 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 0 | 0 | 0 | 1482 | 0 | 40 | 0 | 35 | 50 | 0 | 84 | 30 | 0 | 0 | 0 | 32 | 0 | 0 | 200 | 0 | 0 | 0 | 190 | 0 | 371 | 0 | 0 | 0 | 48 | 70 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 290 | 125 | 220 | 0 | 405 | 1200 | 17 | 7405.5 | 14817 | 79.43
21:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 18 | 35 | 113 | 142 | 294 | 15 | 35 | 35 | 0 | 225 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 142 | 23 | 22 | 0 | 570 | 0 | 16 | 19 | 0 | 0 | 67 | 55 | 18 | 0 | 0 | 0 | 70 | 55 | 12 | 470 | 163 | 0 | 50 | 25.5 | 51 | 218 | 0 | 0 | 0 | 612 | 0 | 147 | 53 | 365 | 0 | 345 | 44 | 5 | 207 | 10 | 51 | 0 | 196 | 9 | 20 | 0 | 164 | 0 | 0 | 22 | 295 | 0 | 330 | 42 | 30 | 156 | 0 | 17 | 0 | 78 | 30 | 101 | 0 | 99 | 17 | 9 | 58 | 35 | 0 | 0 | 12 | 7412.5 | 908 | 182 | 0 | 27.5 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 0 | 0 | 1472 | 0 | 40 | 0 | 35 | 50 | 0 | 85 | 28 | 0 | 0 | 0 | 32 | 0 | 0 | 199 | 0 | 0 | 0 | 190 | 0 | 382 | 0 | 0 | 0 | 50 | 70 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 290 | 125 | 220 | 0 | 432 | 1200 | 17 | 7434.7 | 14847.2 | 79.41
22:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 18 | 17 | 110 | 142 | 294 | 15 | 35 | 35 | 0 | 180 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 142 | 23 | 22 | 0 | 470 | 0 | 16 | 18 | 0 | 0 | 68 | 55 | 18 | 0 | 0 | 0 | 70 | 54 | 17 | 470 | 163 | 0 | 50 | 25.5 | 51 | 218 | 0 | 0 | 0 | 612 | 0 | 143 | 0 | 355 | 230 | 345 | 44 | 0 | 200 | 0 | 49 | 0 | 197 | 9 | 20 | 0 | 200 | 0 | 0 | 22 | 295 | 0 | 330 | 42 | 30 | 157 | 0 | 17 | 0 | 78 | 30 | 100 | 0 | 99 | 17 | 9 | 58 | 33 | 0 | 0 | 12 | 7427.5 | 908 | 179 | 0 | 27.5 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1228 | 0 | 0 | 0 | 1481 | 0 | 40 | 0 | 35 | 50 | 0 | 85 | 21 | 0 | 0 | 0 | 32 | 0 | 0 | 194 | 0 | 0 | 0 | 190 | 0 | 362 | 0 | 0 | 0 | 50 | 70 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 290 | 125 | 220 | 0 | 496 | 1200 | 17 | 7464.5 | 14892 | 79.39
23:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 0 | 17 | 122 | 142 | 30 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 142 | 23 | 22 | 0 | 470 | 0 | 16 | 19 | 0 | 0 | 67 | 55 | 18 | 0 | 0 | 0 | 70 | 55 | 19 | 470 | 163 | 0 | 50 | 25.5 | 51 | 220 | 0 | 0 | 0 | 545 | 0 | 43 | 0 | 393 | 0 | 345 | 44 | 0 | 194 | 0 | 23 | 0 | 195 | 8 | 20 | 0 | 192 | 0 | 0 | 15 | 295 | 0 | 330 | 42 | 30 | 154 | 0 | 17 | 0 | 78 | 30 | 100 | 0 | 99 | 17 | 9 | 58 | 33 | 0 | 0 | 12 | 6695.5 | 906 | 173 | 0 | 30 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1230 | 0 | 0 | 0 | 1487 | 0 | 40 | 0 | 35 | 50 | 0 | 85 | 21 | 0 | 0 | 0 | 32 | 0 | 0 | 183 | 0 | 0 | 0 | 190 | 0 | 339 | 0 | 0 | 0 | 50 | 70 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 290 | 125 | 220 | 0 | 446 | 1214 | 17 | 7388 | 14083.5 | 79.37
Total KWH | 0 | 2184000 | 1069440 | 0 | 0 | 0 | 0 | 0 | 9522000 | 0 | 0 | 261720 | 301680 | 1121760 | 2903040 | 2510847 | 720394 | 266882 | 803520 | 0 | 4747100 | 0 | 0 | 0 | 267344 | 7618858 | 0 | 0 | 153104 | 3240480 | 519600 | 524160 | 0 | 11785454.55 | 0 | 391418 | 476160 | 0 | 171840 | 362476 | 933216 | 138339 | 0 | 211200 | 19680 | 1669880 | 1368291 | 354720 | 5512727.27 | 1438545 | 0 | 637920 | 544892.4 | 979382 | 5286892 | 0 | 0 | 0 | 10674544 | 125685 | 933381 | 1037090 | 8814500 | 724300 | 8184000 | 1052768 | 140640 | 4952000 | 567288 | 557760 | 0 | 1767360 | 80640 | 484100 | 0 | 4110720 | 0 | 372391 | 388608 | 7141000 | 0 | 8657000 | 981000 | 688320 | 3720354.54 | 73050 | 312528 | 0 | 1652160 | 710688 | 1503600 | 0 | 1571950 | 217080 | 218400 | 1389600 | 860160 | 12450 | 303720 | 127680 | 146127477.76 | 21941818 | 5541408 | 0 | 310080 | 736256 | 0 | 0 | 0 | 0 | 0 | 0 | 386640 | 19258178 | 0 | 0 | 0 | 35580000 | 0 | 996135 | 0 | 403296 | 537696 | 0 | 566432 | 418671 | 0 | 251504 | 436670 | 379400 | 0 | 293248 | 4612545 | 0 | 0 | 0 | 4589536 | 0 | 9444218 | 0 | 24000 | 0 | 1224436 | 553441 | 156362 | 769036 | 0 | 0 | 0 | 30157.44 | 1202400 | 3064 | 512064 | 7200000 | 3075000 | 5355830 | 0 | 7825455 | 29186909.09 | 439200 | 164241085.53 | 310368563.29