## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 17-04-2026 | [28 empty] | Date: | 17-04-2026 | [28 empty] | Date: | 17-04-2026 | [28 empty] | Date: | 17-04-2026 | [28 empty] | Date: | 17-04-2026 | [17 empty] | Date: | 17-04-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [17 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 94 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 17 | 53 | 143 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 142 | 23 | 22 | 0 | 470 | 0 | 16 | 19 | 0 | 0 | 67 | 55 | 18 | 0 | 0 | 0 | 70 | 55 | 22 | 470 | 72 | 0 | 19 | 25.5 | 51 | 220 | 0 | 0 | 0 | 410 | 0 | 18 | 0 | 393 | 0 | 345 | 44 | 0 | 197 | 0 | 17 | 0 | 197 | 0 | 20 | 0 | 178 | 0 | 0 | 15 | 295 | 0 | 330 | 42 | 30 | 156 | 0 | 17 | 0 | 79 | 30 | 100 | 0 | 100 | 17 | 9 | 58 | 34 | 0 | 0 | 12 | 6320.5 | 908 | 172 | 0 | 29 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 0 | 0 | 0 | 1470 | 0 | 40 | 0 | 35 | 35 | 0 | 60 | 20 | 0 | 0 | 0 | 32 | 0 | 0 | 183 | 0 | 0 | 0 | 188 | 0 | 346 | 0 | 0 | 0 | 50 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 290 | 130 | 220 | 0 | 283 | 1215 | 17 | 7107 | 13427.5 | 79.35
01:00 | 0 | 96 | 50 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 0 | 17 | 143 | 30 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 142 | 23 | 22 | 0 | 470 | 0 | 16 | 13 | 0 | 0 | 0 | 55 | 18 | 0 | 0 | 0 | 68 | 55 | 21 | 470 | 17 | 0 | 19 | 25.5 | 34 | 220 | 0 | 0 | 0 | 350 | 0 | 20 | 16 | 330 | 0 | 345 | 44 | 0 | 197 | 20 | 16 | 0 | 99 | 0 | 20 | 0 | 176 | 0 | 0 | 15 | 300 | 0 | 330 | 41 | 30 | 157 | 0 | 17 | 0 | 79 | 30 | 100 | 0 | 100 | 0 | 56 | 9 | 34 | 0 | 0 | 12 | 5916.5 | 908 | 172 | 0 | 29 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1222 | 0 | 0 | 0 | 1463 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 32 | 0 | 0 | 182 | 0 | 0 | 0 | 182 | 0 | 348 | 0 | 0 | 0 | 50 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 254 | 1212 | 17 | 6842 | 12758.5 | 79.33
02:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 143 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 142 | 23 | 22 | 0 | 470 | 0 | 16 | 12 | 0 | 0 | 0 | 55 | 18 | 0 | 0 | 0 | 67 | 55 | 28 | 470 | 17 | 0 | 19 | 25.5 | 34 | 220 | 0 | 0 | 0 | 304 | 0 | 20 | 16 | 325 | 0 | 345 | 44 | 0 | 192 | 20 | 17 | 0 | 17 | 0 | 20 | 0 | 166 | 0 | 0 | 15 | 300 | 0 | 342 | 41 | 30 | 155 | 0 | 17 | 0 | 79 | 30 | 100 | 0 | 100 | 0 | 56 | 9 | 34 | 0 | 0 | 12 | 5782.5 | 908 | 175 | 0 | 29 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1210 | 0 | 0 | 0 | 1471 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 32 | 0 | 0 | 177 | 0 | 0 | 0 | 182 | 0 | 338 | 0 | 0 | 0 | 52 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 255 | 1212 | 17 | 6829 | 12611.5 | 79.31
03:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 143 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 142 | 23 | 22 | 0 | 450 | 0 | 16 | 13 | 0 | 0 | 0 | 55 | 18 | 0 | 0 | 0 | 67 | 55 | 28 | 470 | 17 | 0 | 19 | 25.5 | 34 | 219 | 0 | 0 | 0 | 305 | 0 | 20 | 43 | 335 | 0 | 345 | 44 | 0 | 194 | 20 | 0 | 0 | 17 | 0 | 20 | 0 | 168 | 0 | 0 | 15 | 300 | 0 | 342 | 41 | 30 | 154 | 0 | 17 | 0 | 79 | 30 | 100 | 0 | 100 | 0 | 59 | 9 | 34 | 0 | 0 | 0 | 5797.5 | 907 | 175 | 0 | 29 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1225 | 0 | 0 | 0 | 1465 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 32 | 0 | 0 | 177 | 0 | 0 | 0 | 184 | 0 | 339 | 0 | 0 | 0 | 50 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 254 | 1212 | 17 | 6837 | 12634.5 | 79.29
04:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 17 | 143 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 142 | 0 | 22 | 0 | 450 | 0 | 16 | 12 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 68 | 53 | 29 | 470 | 17 | 0 | 19 | 25.5 | 34 | 218 | 0 | 0 | 0 | 302 | 0 | 20 | 45 | 320 | 0 | 345 | 44 | 0 | 189 | 20 | 0 | 0 | 17 | 0 | 20 | 0 | 162 | 0 | 0 | 15 | 300 | 0 | 354 | 41 | 30 | 153 | 0 | 17 | 0 | 79 | 30 | 99 | 0 | 100 | 0 | 59 | 9 | 34 | 0 | 0 | 0 | 5740.5 | 907 | 179 | 0 | 24 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1210 | 0 | 0 | 0 | 1470 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 32 | 0 | 0 | 180 | 0 | 0 | 0 | 186 | 0 | 333 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 254 | 1212 | 17 | 6791 | 12531.5 | 79.27
05:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 17 | 143 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 142 | 0 | 22 | 0 | 400 | 0 | 16 | 13 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 69 | 45 | 29 | 470 | 17 | 0 | 19 | 25.5 | 34 | 219 | 0 | 0 | 0 | 302 | 0 | 20 | 63 | 335 | 0 | 345 | 44 | 0 | 193 | 20 | 0 | 0 | 98 | 0 | 20 | 0 | 172 | 0 | 0 | 15 | 295 | 0 | 354 | 41 | 30 | 140 | 0 | 8 | 0 | 79 | 30 | 100 | 0 | 100 | 0 | 59 | 9 | 34 | 0 | 0 | 0 | 5787.5 | 907 | 180 | 0 | 24 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1225 | 0 | 0 | 0 | 1469 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 32 | 0 | 0 | 169 | 0 | 0 | 0 | 187 | 0 | 340 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 254 | 1212 | 17 | 6805 | 12592.5 | 79.25
06:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 17 | 143 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 142 | 0 | 22 | 0 | 400 | 0 | 16 | 12 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0.07 | 70 | 55 | 23 | 470 | 17 | 0 | 19 | 25.5 | 34 | 220 | 0 | 0 | 0 | 302 | 1 | 20 | 63 | 325 | 0 | 345 | 44 | 0 | 175 | 20 | 0 | 0 | 196 | 0 | 20 | 0 | 140 | 0 | 2 | 15 | 300 | 0 | 353 | 41 | 30 | 136 | 0 | 8 | 0 | 79 | 30 | 100 | 0 | 100 | 0 | 59 | 9 | 34 | 0.05 | 0.35 | 0 | 5851.97 | 907 | 186 | 0 | 20 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 1.22 | 1200 | 0 | 0 | 0 | 1469 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0.94 | 1 | 32 | 0 | 0.99 | 148 | 0 | 0 | 0 | 188 | 0 | 332 | 0 | 0.09 | 0 | 52 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 16 | 290 | 130 | 220 | 0 | 253 | 1212 | 17 | 6762.24 | 12614.21 | 79.23
07:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 17 | 127 | 32 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 17 | 320 | 0 | 0 | 4 | 142 | 0 | 22 | 0 | 320 | 0 | 16 | 13 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0.26 | 70 | 55 | 18 | 470 | 17 | 0 | 19 | 25.5 | 34 | 220 | 0 | 0 | 0 | 302 | 3 | 20 | 63 | 315 | 0 | 345 | 44 | 0 | 172 | 20 | 0 | 0 | 196 | 0 | 20 | 0 | 134 | 0 | 13 | 15 | 295 | 0 | 353 | 41 | 30 | 134 | 1 | 0 | 0 | 79 | 30 | 99 | 0 | 100 | 0 | 59 | 9 | 34 | 0.31 | 8.56 | 0 | 5745.63 | 907 | 190 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.52 | 1202 | 0 | 0 | 0 | 1469 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8.27 | 15 | 32 | 0 | 9.4 | 144 | 0 | 0 | 0 | 191 | 0 | 323 | 0 | 0.77 | 0 | 50 | 0 | 4 | 0 | 0 | 0 | 0 | 0.8 | 34 | 0.11 | 16 | 290 | 130 | 220 | 0 | 254 | 1212 | 17 | 6808.87 | 12554.5 | 79.21
08:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 0 | 17 | 127 | 32 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 11 | 142 | 23 | 15 | 0 | 360 | 0 | 16 | 12 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 1.3 | 70 | 55 | 5 | 470 | 17 | 0 | 19 | 25.5 | 34 | 220 | 0 | 0 | 0 | 300 | 7 | 20 | 63 | 325 | 0 | 345 | 44 | 0 | 188 | 20 | 0 | 0 | 118 | 0 | 20 | 0 | 144 | 0 | 34 | 15 | 300 | 0 | 353 | 41 | 30 | 141 | 5 | 0 | 0 | 79 | 30 | 101 | 0 | 100 | 0 | 59 | 9 | 34 | 0.62 | 21.26 | 0 | 5796.68 | 910 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.68 | 1218 | 0 | 0 | 0 | 1466 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 20.51 | 26 | 0 | 0 | 21.62 | 158 | 0 | 0 | 0 | 195 | 0 | 404 | 0 | 1.88 | 0 | 50 | 0 | 13 | 0 | 0 | 0 | 0 | 2.8 | 75 | 0.21 | 16 | 290 | 130 | 220 | 0 | 254 | 1207 | 17 | 6983.7 | 12780.38 | 79.19
09:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 127 | 32 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 22 | 142 | 0 | 15 | 0 | 360 | 0 | 16 | 12 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 2.28 | 70 | 55 | 7 | 470 | 17 | 0 | 19 | 25.5 | 34 | 217 | 0 | 0 | 0 | 305 | 12 | 20 | 63 | 345 | 0 | 345 | 44 | 0 | 201 | 20 | 0 | 0 | 22 | 0 | 20 | 0 | 154 | 0 | 51 | 15 | 300 | 0 | 353 | 42 | 30 | 152 | 5 | 0 | 0 | 78 | 30 | 100 | 0 | 100 | 0 | 59 | 9 | 34 | 0.86 | 34.19 | 0 | 5803.83 | 910 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.81 | 1226 | 0 | 0 | 0 | 1462.41 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 34.13 | 66 | 0 | 0 | 16.28 | 198 | 0 | 0 | 0 | 195 | 0 | 350 | 0 | 3.62 | 0 | 50 | 0 | 22 | 0 | 0 | 0 | 0 | 4.5 | 120 | 0.26 | 16 | 290 | 130 | 220 | 0 | 253 | 1170 | 17 | 7031.01 | 12834.84 | 79.18
10:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 127 | 32 | 15 | 6 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 27 | 142 | 0 | 22 | 0 | 390 | 0 | 16 | 12 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 1.72 | 70 | 55 | 7 | 470 | 17 | 0 | 19 | 25.5 | 34 | 215 | 0 | 0 | 0 | 300 | 16 | 20 | 63 | 345 | 0 | 335 | 44 | 0 | 213 | 20 | 0 | 0 | 17 | 0 | 20 | 0 | 148 | 0 | 59 | 14 | 300 | 0 | 353 | 42 | 30 | 144 | 9 | 0 | 0 | 78 | 30 | 101 | 0 | 100 | 0 | 59 | 9 | 31 | 1.94 | 25.46 | 0 | 5772.62 | 909 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 1226 | 0 | 0 | 0 | 1474.14 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 47.45 | 87 | 0 | 0 | 15 | 203 | 0 | 0 | 0 | 198 | 0 | 406 | 0 | 0 | 0 | 50 | 0 | 28 | 0 | 0 | 0 | 0 | 5.8 | 160 | 0.56 | 16 | 280 | 130 | 220 | 0 | 253 | 1125 | 17 | 7133.95 | 12906.57 | 79.17
11:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 0 | 4 | 18 | 125 | 48 | 15 | 17 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 30 | 142 | 0 | 22 | 0 | 360 | 0 | 16 | 11 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 2.45 | 70 | 61 | 8 | 470 | 17 | 0 | 19 | 25.5 | 34 | 214 | 0 | 0 | 0 | 370 | 17 | 20 | 63 | 345 | 0 | 335 | 44 | 0 | 203 | 20 | 0 | 0 | 17 | 1 | 20 | 0 | 154 | 0 | 66 | 14 | 305 | 0 | 353 | 42 | 30 | 153 | 10 | 0 | 0 | 5 | 30 | 101 | 0 | 100 | 0 | 59 | 9 | 31 | 1.93 | 35.6 | 0 | 5861.48 | 909 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 1224 | 0 | 0 | 0 | 1511.5 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 53.44 | 68 | 0 | 0 | 20 | 204 | 0 | 0 | 0 | 197 | 0 | 408 | 0 | 5.27 | 0 | 50 | 0 | 31 | 0 | 0 | 0 | 0 | 6.9 | 179 | 0.54 | 16 | 277 | 130 | 220 | 0 | 253 | 1115 | 17 | 7174.65 | 13036.13 | 79.16
12:00 | 0 | 105 | 41 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 17 | 54 | 139 | 48 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 31 | 142 | 14 | 22 | 0 | 360 | 0 | 16 | 11 | 0 | 1 | 0 | 38 | 0 | 0 | 0 | 1.54 | 70 | 65 | 8 | 470 | 17 | 0 | 19 | 25.5 | 34 | 214 | 0 | 0 | 0 | 500 | 17 | 20 | 63 | 320 | 0 | 335 | 44 | 0 | 195 | 35 | 1 | 0 | 17 | 9 | 20 | 0 | 164 | 0 | 70 | 21 | 310 | 0 | 353 | 42 | 30 | 153 | 11 | 0 | 0 | 35 | 30 | 100 | 0 | 100 | 0 | 59 | 9 | 28 | 2.21 | 42.7 | 0 | 6087.95 | 910 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 1194 | 0 | 0 | 0 | 1505.78 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 51.49 | 86 | 0 | 0 | 15 | 204 | 0 | 0 | 0 | 195 | 0 | 395 | 0 | 5.57 | 0 | 49 | 0 | 23 | 0 | 0 | 0 | 0 | 7.1 | 187 | 0.45 | 16 | 274 | 130 | 220 | 0 | 253 | 1180 | 17 | 7210.39 | 13298.34 | 79.15
13:00 | 0 | 105 | 41 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 17 | 55 | 138 | 48 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 30 | 142 | 14 | 15 | 0 | 400 | 0 | 16 | 12 | 0 | 5 | 0 | 38 | 0 | 0 | 0 | 3.06 | 70 | 55 | 20 | 470 | 17 | 0 | 19 | 25.5 | 34 | 213 | 0 | 0 | 0 | 600 | 17 | 20 | 98 | 315 | 0 | 335 | 44 | 0 | 191 | 38 | 16 | 0 | 17 | 9 | 20 | 0 | 176 | 0 | 66 | 25 | 305 | 0 | 353 | 42 | 30 | 152 | 2 | 0 | 0 | 35 | 30 | 100 | 0 | 100 | 0 | 59 | 9 | 28 | 0.67 | 38.3 | 0 | 6262.53 | 909 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 1210 | 0 | 0 | 0 | 1496.23 | 0 | 39 | 0 | 0 | 6 | 0 | 0 | 14 | 0 | 53.22 | 81 | 0 | 0 | 59 | 199 | 0 | 0 | 0 | 193 | 0 | 386 | 0 | 5.36 | 0 | 49 | 0 | 30 | 0 | 0 | 0 | 6 | 6.9 | 152 | 0.65 | 16 | 271 | 130 | 220 | 0 | 253 | 1180 | 17 | 7188.36 | 13450.89 | 79.14
14:00 | 0 | 105 | 40 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 18 | 17 | 62 | 135 | 48 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 26 | 142 | 14 | 15 | 0 | 380 | 0 | 16 | 11 | 0 | 8 | 0 | 38 | 0 | 0 | 0 | 3.06 | 68 | 55 | 24 | 470 | 17 | 0 | 19 | 25.5 | 34 | 213 | 0 | 0 | 0 | 580 | 15 | 20 | 98 | 333 | 0 | 320 | 44 | 2 | 196 | 38 | 17 | 0 | 17 | 9 | 20 | 0 | 176 | 0 | 56 | 28 | 300 | 0 | 356 | 42 | 30 | 141 | 9 | 0 | 0 | 35 | 30 | 99 | 0 | 100 | 0 | 59 | 9 | 28 | 1.88 | 35.53 | 0 | 6212.97 | 910 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 1142 | 0 | 0 | 0 | 1488.71 | 0 | 39 | 0 | 35 | 33 | 0 | 0 | 14 | 0 | 45.93 | 30 | 0 | 0 | 26 | 191 | 0 | 0 | 0 | 192 | 0 | 395 | 0 | 4.97 | 0 | 48 | 0 | 28 | 0 | 0 | 0 | 7 | 6 | 146 | 0.56 | 16 | 245 | 125 | 220 | 0 | 253 | 1200 | 17 | 7098.17 | 13311.14 | 79.13
15:00 | 0 | 105 | 40 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 18 | 17 | 62 | 135 | 48 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 21 | 142 | 14 | 14 | 0 | 420 | 0 | 16 | 12 | 0 | 8 | 0 | 38 | 0 | 0 | 0 | 2.27 | 66 | 55 | 13 | 470 | 17 | 0 | 19 | 25.5 | 34 | 213 | 0 | 0 | 0 | 585 | 11 | 20 | 98 | 328 | 0 | 330 | 44 | 12 | 197 | 38 | 18 | 0 | 17 | 0 | 20 | 0 | 176 | 0 | 44 | 28 | 310 | 0 | 0 | 42 | 30 | 149 | 8 | 0 | 0 | 77 | 30 | 102 | 0 | 98 | 0.36 | 59 | 9 | 33 | 1.49 | 33.32 | 0 | 5953.94 | 910 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 1228 | 0 | 0 | 0 | 1480.17 | 0 | 39 | 0 | 35 | 35 | 0 | 0 | 14 | 0 | 36.85 | 50 | 0 | 0 | 39 | 192 | 0 | 0 | 0 | 191 | 0 | 347 | 0 | 3.79 | 0 | 49 | 0 | 21 | 0 | 0 | 0 | 0 | 4.8 | 101 | 0.44 | 16 | 276 | 125 | 180 | 0 | 304 | 1200 | 17 | 7118.05 | 13071.99 | 79.12
16:00 | 0 | 105 | 40 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 18 | 17 | 52 | 120 | 48 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 17 | 317 | 0 | 0 | 13 | 108 | 20 | 14 | 0 | 440 | 0 | 16 | 12 | 0 | 11 | 0 | 30 | 0 | 0 | 0 | 1.47 | 67 | 55 | 13 | 470 | 152 | 0 | 19 | 25.5 | 34 | 213 | 0 | 0 | 0 | 585 | 6 | 20 | 128 | 344 | 0 | 330 | 44 | 20 | 207 | 41 | 17 | 0 | 17 | 0 | 20 | 0 | 162 | 0 | 29 | 22 | 310 | 0 | 0 | 42 | 29 | 149 | 4 | 0 | 0 | 73 | 30 | 100 | 0 | 99 | 17 | 58 | 9 | 32 | 1.01 | 18.19 | 6 | 6081.17 | 909 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 1222 | 0 | 0 | 0 | 1472.78 | 0 | 39 | 0 | 35 | 35 | 0 | 0 | 14 | 0 | 21.54 | 47 | 0 | 0 | 26 | 192 | 0 | 0 | 0 | 191 | 0 | 376 | 0 | 2.37 | 0 | 48 | 35 | 13 | 0 | 0 | 0 | 0 | 3 | 67 | 0.31 | 16 | 279 | 125 | 220 | 0 | 304 | 1140 | 17 | 7040 | 13121.17 | 79.11
17:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 18 | 17 | 52 | 120 | 48 | 15 | 0 | 17 | 0 | 190 | 0 | 0 | 0 | 17 | 318 | 0 | 0 | 6 | 108 | 20 | 15 | 0 | 400 | 0 | 16 | 12 | 0 | 6 | 0 | 38 | 0 | 0 | 0 | 0.53 | 69 | 55 | 10 | 470 | 140 | 0 | 19 | 25.5 | 34 | 214 | 0 | 0 | 0 | 576 | 3 | 20 | 132 | 326 | 0 | 340 | 44 | 20 | 197 | 41 | 17 | 0 | 120 | 0 | 14 | 0 | 160 | 0 | 11 | 22 | 315 | 0 | 32 | 42 | 29 | 150 | 2 | 0 | 0 | 73 | 30 | 100 | 0 | 99 | 17 | 58 | 9 | 32 | 0.34 | 10.11 | 12 | 6083.48 | 910 | 173 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 1219 | 0 | 0 | 0 | 1472.88 | 0 | 31 | 0 | 35 | 35 | 0 | 30 | 14 | 0 | 3.97 | 19 | 32 | 0 | 9 | 192 | 0 | 0 | 0 | 191 | 0 | 345 | 0 | 0.95 | 0 | 48 | 35 | 5 | 81 | 0 | 0 | 0 | 0.8 | 30 | 0.12 | 16 | 275 | 125 | 220 | 0 | 304 | 1100 | 17 | 6999.72 | 13083.2 | 79.1
18:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 18 | 17 | 67 | 121 | 135 | 15 | 17 | 17 | 0 | 190 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 1 | 108 | 20 | 18 | 0 | 400 | 0 | 16 | 12 | 0 | 0 | 33 | 35 | 0 | 0 | 0 | 0.01 | 70 | 55 | 20 | 520 | 117 | 0 | 24 | 25.5 | 45 | 216 | 0 | 0 | 0 | 580 | 0 | 18 | 93 | 235 | 166 | 340 | 44 | 18 | 155 | 41 | 18 | 0 | 182 | 5 | 20 | 0 | 152 | 0 | 1 | 22 | 310 | 0 | 112 | 42 | 29 | 138 | 0 | 0 | 0 | 73 | 30 | 99 | 0 | 99 | 17 | 59 | 9 | 32 | 0 | 0.79 | 12 | 6343.3 | 910 | 173 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.53 | 1226 | 0 | 0 | 0 | 1472.75 | 0 | 40 | 0 | 35 | 35 | 0 | 81 | 27 | 0 | 1.13 | 3 | 32 | 0 | 1 | 160 | 0 | 0 | 0 | 160 | 0 | 348 | 0 | 0.12 | 0 | 50 | 50 | 1 | 92 | 0 | 0 | 0 | 0.2 | 4 | 0.01 | 16 | 277 | 125 | 220 | 0 | 304 | 1155 | 17 | 7046.74 | 13390.04 | 79.09
19:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 18 | 17 | 92 | 138 | 294 | 15 | 35 | 17 | 0 | 190 | 0 | 0 | 0 | 17 | 322 | 0 | 0 | 0 | 134 | 20 | 18 | 0 | 420 | 0 | 16 | 12 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 70 | 55 | 16 | 520 | 150 | 0 | 46 | 25.5 | 51 | 218 | 0 | 0 | 0 | 612 | 0 | 61 | 16 | 230 | 222 | 270 | 44 | 0 | 165 | 10 | 33 | 0 | 185 | 9 | 20 | 0 | 158 | 0 | 0 | 22 | 320 | 0 | 112 | 42 | 30 | 141 | 0 | 0 | 0 | 77 | 30 | 100 | 0 | 99 | 17 | 59 | 9 | 33 | 0 | 0 | 12 | 6718.5 | 909 | 184 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1213 | 0 | 0 | 0 | 1469.37 | 0 | 40 | 0 | 35 | 45 | 0 | 82 | 28 | 0 | 0 | 0 | 32 | 0 | 0 | 180 | 0 | 0 | 0 | 183 | 0 | 351 | 0 | 0 | 0 | 50 | 70 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 350 | 1200 | 17 | 7214.37 | 13932.87 | 79.08
19:30 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 18 | 17 | 96 | 138 | 278 | 55 | 35 | 17 | 0 | 190 | 0 | 0 | 0 | 17 | 325 | 0 | 0 | 0 | 142 | 21 | 22 | 0 | 420 | 0 | 16 | 12 | 0 | 0 | 51 | 47 | 0 | 0 | 0 | 0 | 70 | 55 | 20 | 520 | 134 | 0 | 50 | 25.5 | 51 | 218 | 0 | 0 | 0 | 612 | 0 | 144 | 8 | 225 | 225 | 270 | 44 | 0 | 178 | 10 | 34 | 0 | 175 | 9 | 20 | 0 | 154 | 0 | 0 | 22 | 310 | 0 | 112 | 42 | 30 | 142 | 0 | 0 | 0 | 77 | 30 | 99 | 0 | 99 | 17 | 59 | 9 | 33 | 0 | 0 | 12 | 6829.5 | 815 | 184 | 0 | 32 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1219 | 0 | 0 | 0 | 1471.17 | 0 | 39 | 0 | 35 | 50 | 0 | 83 | 28 | 0 | 0 | 0 | 32 | 0 | 0 | 192 | 0 | 0 | 0 | 200 | 0 | 337 | 0 | 0 | 0 | 50 | 70 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 405 | 1210 | 17 | 7225.17 | 14054.67
20:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 18 | 17 | 95 | 138 | 278 | 50 | 35 | 17 | 0 | 225 | 0 | 0 | 0 | 17 | 319 | 0 | 0 | 0 | 142 | 21 | 22 | 0 | 460 | 0 | 16 | 12 | 0 | 0 | 51 | 47 | 0 | 0 | 0 | 0 | 70 | 55 | 25 | 560 | 155 | 0 | 50 | 25.5 | 51 | 217 | 0 | 0 | 0 | 612 | 0 | 145 | 8 | 220 | 222 | 270 | 44 | 0 | 184 | 10 | 34 | 0 | 184 | 8 | 20 | 0 | 160 | 0 | 0 | 22 | 310 | 0 | 158 | 42 | 30 | 142 | 0 | 0 | 0 | 77 | 30 | 100 | 0 | 99 | 17 | 59 | 9 | 51 | 0 | 0 | 12 | 7032.5 | 767 | 188 | 0 | 29 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1229 | 0 | 0 | 0 | 1476.54 | 0 | 40 | 0 | 35 | 50 | 0 | 83 | 28 | 0 | 0 | 0 | 32 | 0 | 0 | 192 | 0 | 0 | 0 | 195 | 0 | 414 | 0 | 0 | 0 | 50 | 70 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 405 | 1215 | 17 | 7284.54 | 14317.04 | 79.07
21:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 17 | 95 | 139 | 285 | 55 | 35 | 17 | 0 | 225 | 0 | 0 | 0 | 17 | 325 | 0 | 0 | 0 | 142 | 21 | 22 | 0 | 450 | 0 | 16 | 12 | 0 | 0 | 51 | 47 | 14 | 0 | 0 | 0 | 70 | 55 | 27 | 560 | 145 | 0 | 50 | 25.5 | 51 | 217 | 0 | 0 | 0 | 612 | 0 | 140 | 8 | 245 | 0 | 342 | 44 | 0 | 213 | 10 | 23 | 0 | 185 | 9 | 20 | 0 | 148 | 0 | 0 | 22 | 315 | 0 | 263 | 42 | 30 | 154 | 0 | 0 | 0 | 77 | 30 | 100 | 0 | 99 | 17 | 59 | 9 | 70 | 0 | 0 | 12 | 7046.5 | 767 | 190 | 0 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1215 | 0 | 0 | 0 | 1444.37 | 0 | 40 | 0 | 35 | 50 | 0 | 83 | 28 | 0 | 0 | 0 | 32 | 0 | 0 | 193 | 0 | 0 | 0 | 197 | 0 | 404 | 0 | 0 | 0 | 48 | 70 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 404 | 1218 | 17 | 7239.37 | 14285.87 | 79.06
22:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 17 | 95 | 141 | 294 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 450 | 0 | 16 | 13 | 0 | 0 | 51 | 47 | 18 | 0 | 0 | 0 | 70 | 55 | 28 | 720 | 150 | 0 | 50 | 25.5 | 51 | 220 | 0 | 0 | 0 | 612 | 0 | 125 | 45 | 393 | 0 | 345 | 44 | 0 | 200 | 39 | 17 | 0 | 185 | 8 | 20 | 0 | 156 | 0 | 0 | 22 | 310 | 0 | 268 | 42 | 30 | 153 | 0 | 0 | 0 | 77 | 30 | 100 | 0 | 99 | 17 | 59 | 9 | 70 | 0 | 0 | 12 | 7287.5 | 767 | 190 | 0 | 24 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234 | 0 | 0 | 0 | 1442.14 | 0 | 40 | 0 | 35 | 50 | 0 | 83 | 28 | 0 | 0 | 0 | 32 | 0 | 0 | 192 | 0 | 0 | 0 | 199 | 0 | 414 | 0 | 0 | 0 | 48 | 70 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 404 | 1217 | 17 | 7274.14 | 14561.64 | 79.05
23:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 17 | 91 | 142 | 198 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 450 | 0 | 16 | 12 | 0 | 0 | 50 | 47 | 18 | 0 | 0 | 0 | 70 | 54 | 21 | 780 | 150 | 0 | 50 | 25.5 | 51 | 220 | 0 | 0 | 0 | 612 | 0 | 53 | 95 | 393 | 0 | 345 | 44 | 3 | 200 | 42 | 17 | 0 | 183 | 9 | 20 | 0 | 156 | 0 | 0 | 22 | 300 | 0 | 259 | 42 | 30 | 156 | 0 | 0 | 0 | 78 | 30 | 100 | 0 | 100 | 17 | 59 | 9 | 67 | 0 | 0 | 12 | 7198.5 | 862 | 190 | 0 | 24 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1227 | 0 | 0 | 0 | 1461.14 | 0 | 40 | 0 | 35 | 50 | 0 | 83 | 24 | 0 | 0 | 0 | 32 | 0 | 0 | 191 | 0 | 0 | 0 | 160 | 0 | 358 | 0 | 0 | 0 | 48 | 70 | 0 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 355 | 1220 | 17 | 7232.14 | 14430.64 | 79.04
Total KWH | 0 | 2491200 | 1140960 | 0 | 0 | 0 | 0 | 0 | 9867600 | 0 | 0 | 129960 | 242640 | 1137744 | 3238560 | 2195956 | 454581 | 137067 | 423360 | 0 | 4704000 | 0 | 0 | 0 | 137160 | 7667158 | 0 | 0 | 219522 | 3403200 | 347400 | 467640 | 0 | 10075454.55 | 0 | 386400 | 301440 | 0 | 42240 | 348325 | 1084800 | 138912 | 0 | 0 | 20879 | 1655120 | 1354073 | 480480 | 11840000 | 1443564 | 0 | 655680 | 601934.4 | 972691 | 4972640 | 0 | 0 | 0 | 10990908 | 123930 | 906618 | 1522181 | 7950000 | 697100 | 8072000 | 1049600 | 87840 | 4802000 | 617904 | 284160 | 0 | 2199360 | 82320 | 472310 | 0 | 3763200 | 0 | 500145 | 450096 | 7373000 | 0 | 6625000 | 1001000 | 715680 | 3566045.46 | 67400 | 108288 | 0 | 1617600 | 719712 | 2376000 | 0 | 2394050 | 149760 | 1380000 | 230400 | 843840 | 12600 | 305340 | 129840 | 148967568.41 | 21527273 | 4461984 | 0 | 372960 | 318464 | 0 | 0 | 0 | 0 | 0 | 0 | 505440 | 29200000 | 0 | 0 | 0 | 35327599 | 0 | 839333 | 0 | 391872 | 502176 | 0 | 562112 | 398829 | 0 | 381616 | 626700 | 259500 | 0 | 274496 | 4455727 | 0 | 0 | 0 | 4790300 | 0 | 8820290 | 0 | 33060 | 0 | 1124072 | 552998 | 220681 | 757910 | 0 | 0 | 9000 | 48412.56 | 1254960 | 3784 | 394944 | 6873000 | 3076000 | 5395670 | 0 | 6930909 | 29050181.82 | 438000 | 170180253.38 | 319147821.79

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 18-04-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-04-2026 | during | 18-04-2026 | during | 18-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 408 | 411 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 450 | 450 | 226 | 226 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 50 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 324 | 319 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 18 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 139 | 138 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 14 | 21 | 33 | 33 | 29 | 29 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 41 | 49 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 48 | 278 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 54 | 95 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 17 | 162 | 162 | 35 | 35 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 360 | 460 | 584 | 584 | 526 | 526 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 142 | 142 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1962 | 2419 | 5947.22 | 5915.22 | 2637.55 | 2659.55
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50 | 19 | 50 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 | 70 | 70 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 217 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 51 | 105 | 105 | 34 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 38 | 47 | 56 | 56 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 68 | 68 | 34 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 8 | 25 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 11 | 12 | 108 | 108 | 38 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.54 | 0 | 3.69 | 0 | 3.69 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 0 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 65 | 55 | 110 | 110 | 54 | 54 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 17 | 155 | 163 | 163 | 17 | 163 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 500 | 612 | 1224 | 1224 | 612 | 612 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 0 | 3 | 0 | 3 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 470 | 560 | 935 | 935 | 935 | 935 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1507.04 | 1946.5 | 3829.55 | 3828.86 | 2295.19 | 2547.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 195 | 184 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 0 | 222 | 240 | 240 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 335 | 270 | 342.01 | 342.01 | 342.01 | 342.01 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 320 | 220 | 393 | 393 | 350 | 350 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 35 | 10 | 41.65 | 41.65 | 37 | 37 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 6 | 6 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 63 | 8 | 195 | 195 | 96 | 96 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Machine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 145 | 150 | 150 | 20 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 21 | 22 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 184 | 200 | 200 | 35 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 164 | 160 | 84 | 76 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 8 | 113 | 113 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 1 | 34 | 115 | 115 | 17 | 51 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 70 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.745 | 1314 | 1531 | 2654.18 | 2576.18 | 1443.01 | 1672.01
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-04-2026 | during | 18-04-2026 | during | 18-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 28 | 51 | 157.5 | 157.5 | 50 | 50 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.21 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 10 | 10 | 10 | 10 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 59 | 70 | 70 | 10 | 10 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 42.7 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 140.91 | 148 | 361.9 | 314 | 146.9 | 99
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 142 | 163 | 163 | 153 | 153 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 100 | 100 | 100 | 100 | 110 | 110 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 35 | 77 | 83 | 83 | 76 | 76 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 99 | 98 | 98 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25 | 17 | 17 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 353 | 158 | 350 | 350 | 350 | 350 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1164 | 988 | 1262 | 1262 | 1185 | 1185
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 910 | 767 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 29 | 32 | 32 | 25 | 25 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 21 | 50 | 50 | 30 | 30 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 180 | 188 | 410 | 410 | 250.03 | 250.03 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 66 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1194 | 1229 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2350 | 2234 | 3581.2 | 3496.2 | 2639.33 | 2554.33
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 253 | 405 | 250 | 400 | 250 | 400 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 16 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1180 | 1215 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 274 | 290 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.45 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2090.45 | 2293 | 2412 | 2561 | 2268 | 2417
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 51.49 | 0 | 62 | 0 | 62 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 32 | 40 | 32 | 32 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 14 | 28 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 204 | 192 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 195 | 195 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 395 | 414 | 413.79 | 413.79 | 408 | 408 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 32 | 32 | 25 | 25 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 83 | 90 | 90 | 0 | 51 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 0 | 50 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.57 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1505.78 | 1476.54 | 1435.88 | 1435.88 | 1512 | 1512 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 15 | 0 | 68 | 0 | 68 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 86 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2503.84 | 2545.54 | 3235.72 | 2999.87 | 2672.45 | 2572.6
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 50 | 52 | 52 | 51 | 51 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 92 | 113 | 113 | 35 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.1 | 0 | 6.8 | 0 | 6.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 35 | 50 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 23 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 187 | 0 | 181.25 | 0 | 181.25 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 266.1 | 212 | 512.05 | 294 | 339.05 | 136
System Total |  |  |  |  | 28823.2 | 29269.987 | 13298.34 | 14317.04 | 23795.82 | 23247.33 | 15626.48 | 15842.99
Forecast Scenario (18-04-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14179.84 |  | 477.6528 |  | 14680
|  |  |  | 1:00 | 14055.84 |  | 280.9228 |  | 14350
|  |  |  | 2:00 | 14055.84 |  | 89.9228 |  | 14150
|  |  |  | 3:00 | 13640 |  | 0 |  | 13640
|  |  |  | 4:00 | 13440 |  | 0 |  | 13440
|  |  |  | 5:00 | 13000 |  | 0 |  | 13000
|  |  |  | 6:00 | 12930 |  | 0 |  | 12930
|  |  |  | 7:00 | 13150 |  | 0 |  | 13150
|  |  |  | 8:00 | 13120 |  | 0 |  | 13120
|  |  |  | 9:00 | 13200 |  | 0 |  | 13200
|  |  |  | 10:00 | 13020 |  | 0 |  | 13020
|  |  |  | 11:00 | 13320 |  | 0 |  | 13320
|  |  |  | 12:00 | 13920 |  | 0 |  | 13920
|  |  |  | 13:00 | 14220 |  | 0 |  | 14220
|  |  |  | 14:00 | 14300 |  | 0 |  | 14300
|  |  |  | 15:00 | 14350 |  | 0 |  | 14350
|  |  |  | 16:00 | 14350 |  | 0 |  | 14350
|  |  |  | 17:00 | 14300 |  | 0 |  | 14300
|  |  |  | 18:00 | 14500 |  | 0 |  | 14500
|  |  |  | 18:30 | 14936.43 |  | 60.7094 |  | 15000
|  |  |  | 19:00 | 15130.16 |  | 295.8972 |  | 15440
|  |  |  | 19:30 | 15138.16 |  | 393.3072 |  | 15550
|  |  |  | 20:00 | 15145.16 |  | 529.8722 |  | 15700
|  |  |  | 21:00 | 15048.43 |  | 612.6993 |  | 15690
|  |  |  | 22:00 | 15048.43 |  | 431.2493 |  | 15500
|  |  |  | 23:00 | 15055.43 |  | 300.4144 |  | 15370
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 13920.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15700.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15145.16 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 336.47913 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:24 hrs on 18-04-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 17-04-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13298.34 | MW | 12:00 Hr. | Energy Generated |  |  | 319.1478 |  | MKWHr.
| Day Peak Demand |  |  | 14162.56 | MW | 12:00 Hr. | Energy Unserverd |  |  | 18.239 |  | MKWHr.
| Evening Peak Generation |  |  | 14317.04 | MW | 20:00 Hr. | Energy Demand |  |  | 337.3868 |  | MKWHr.
| Evening Peak Demand |  |  | 15299.04 | MW | 20:00 Hr. | Maximum Temperature |  |  | 35.6 |  | °C
| Minimum Generation of the Day |  |  | 12531.5 | MW | 04:00 Hr. | Total Gas Supplied |  |  | 898.77 |  | MMCFD
| Maximum Generation of the Day |  |  | 14561.64 | MW | 22:00 Hr. | Production Cost per KWHr |  |  | 6.67 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.1293 | 0 | 15.1324 | 0 | 0 | 0.21952 | 0 | 0 | 48.4812 | Gas | 122.1935 | Gas | 432831845.1667
| Chattogram Zone |  |  | 5.4531 | 22.8309 | 7.2878 | 0 | 1.6551 | 0.14481 | 0 | 0.04224 | 37.414 | Coal | 96.0091 | Coal | 655674723.2306
| Cumilla Zone |  |  | 25.2709 | 0 | 3.9226 | 0 | 0 | 0.50014 | 3.7632 | 0 | 33.4568 | HFO | 34.0219 | HFO | 611010136.57
| Mymensingh Zone |  |  | 0.84384 | 0 | 1.89 | 0 | 0 | 0.31794 | 0 | 0 | 3.0518 | HSD | 0.009 | HSD | 392130
| Sylhet Zone |  |  | 26.4964 | 0 | 0 | 0 | 0 | 0.0674 | 0 | 0 | 26.5638 | Hydro | 1.6551 | Hydro | 165512
| Khulna Zone |  |  | 4.462 | 29.2 | 0.69142 | 0 | 0 | 0.50544 | 21.5273 | 0 | 56.3861 | Solar | 4.599 | Solar | 74012081.652
| Barishal Zone |  |  | 8.4717 | 42.8541 | 0.83294 | 0 | 0 | 0.003784 | 0 | 0 | 52.1625 | Import | 60.6181 | Import | 353993606.36
| Rajshahi Zone |  |  | 18.0663 | 0 | 2.9538 | 0 | 0 | 1.3159 | 35.3276 | 0 | 57.6636 | Wind | 0.04224 | Wind | 621350.4
| Rangpur Zone |  |  | 0 | 1.1241 | 1.3109 | 0.009 | 0 | 1.5241 | 0 | 0 | 3.968
| Total |  |  | 122.1935 | 96.0091 | 34.0219 | 0.009 | 1.6551 | 4.599 | 60.6181 | 0.04224 | 319.1478
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 432831845.1667 |  | Hydro | 165512
|  |  |  | Coal | 655674723.2306 |  | Solar | 74012081.652
|  |  |  | HFO | 611010136.57 |  | Import | 353993606.36
|  |  |  | HSD | 392130 |  | Wind | 621350.4
[5 empty] | Total: | 212,87,01,385 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5273 | Peak Hr Flow | 767.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 59394000 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 35.3276 | Peak Hr Flow | 1476.54 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2748 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.7632 | Peak Hr Flow | 160.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2989 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 60.6181 | Peak Hr Flow | 2403.54 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5284
|  |  |  | Chattogram |  | 100 |  | 1474
|  |  |  | Cumilla |  | 120 |  | 1479
|  |  |  | Mymensingh |  | 150 |  | 1113
|  |  |  | Sylhet |  | 50 |  | 566
|  |  |  | Khulna |  | 210 |  | 1816
|  |  |  | Barishal |  | 45 |  | 440
|  |  |  | Rajshahi |  | 145 |  | 1592
|  |  |  | Rangpur |  | 120 |  | 979
|  |  |  | Total |  | 940 |  | 14743
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 320
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:01 | 11:35 | Gollamari 132/33kV S/S Tr-1 LT Scheduled S/D
| 08:02 | 11:34 | Gollamari 132/33kV S/S Tr-1 HT Scheduled S/D Due to Paint job
|  | 08:08 | Fenchuganj -Sylhet 132kV Ckt-1 is restored.
| 08:10 | 01:02 | Baroaulia-Hathazari 132 kV Ckt-2 Scheduled S/D from Hathazari 230/132/33kV end.
|  | 08:11 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 is restored.
|  | 08:11 | Fenchuganj-Sylhet (South) 132KV Ckt-1 is restored.
| 08:40 | 09:30 | Amtali 400/132kV S/S Amtali - Payra 400 kV Ckt - 1 Project Work S/D Due to DS problem of
8052S
| 08:58 | 11:23 | Goalpara 132/33kV S/S Goalpara-NWPGCL Scheduled S/D Due to Maintenence works.
|  | 10:01 | Ashuganj-Brahmanbaria 132kV Ckt-2 is restored.
|  | 11:10 | Maniknagar 132/33kV S/S Transformer GT-1 HT is restored.
|  | 11:12 | Goalpara 132/33kV S/S T1 HT is restored.
|  | 11:13 | Goalpara 132/33kV S/S T1 LT is restored.
| 11:25 | 12:03 | Jaldhaka 132/33kV S/S 406T-1 HT Forced S/D Due to 33 kV PBS Dimla feeder sky wire | [7 empty] | 15.0MW load
|  |  | maintenance work | [7 empty] | interrup.
| 11:25 | 12:04 | Jaldhaka 132/33kV S/S 406T-1 LT Forced S/D Due to PBS Dimla feeder sky wire maintenance | [7 empty] | 15.0MW load
|  |  | work. | [7 empty] | interrup.
|  | 13:00 | Chandpur 132/33kV S/S 402T (T-01) LT is restored.
| 14:34 |  | Bibiyana-III 400 MW CCPP Tripped with remarks:- GT
| 14:34 |  | Bibiyana-3 400 MW CCPP tripped.
| 15:02 |  | Matarbari 2*600 MW (CPGCBL) unit-2 was sync.
| 16:49 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- GT
| 16:49 |  | Bibiyana-3 400 MW CCPP GT was sync.
| 17:05 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- gt
| 17:05 |  | Ashuganj North 360 MW GT was sync.
| 18:13 | 18:15 | Barishal 230/132kV S/S T-5 LT Forced S/D Due to Sound on 33kv Busbar DS B-phase
| 20:00 |  | Evening Peak Generation: 14316 MW.
| 20:53 |  | Matarbari 2*600 MW (CPGCBL) unit-2 was sync.
| 20:54 |  | Matarbari 2*600 MW (CPGCBL) Synchronized with remarks:- U2
| 20:57 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
| 20:57 |  | Ashuganj North 360 MW was shut down.
| 01:00 |  | Minimum generation 13115 MW
|  | 01:02 | Baroaulia-Hathazari 132 kV Ckt-2 is restored.
| 05:56 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- ST
| 07:05 |  | Jamalpur 132/33kV S/S T-2 HT Scheduled S/D Due to 33 kv T-2 and Extension bus bus coupler | [7 empty] | 45.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 07:05 |  | Jamalpur 132/33kV S/S T-2 LT Scheduled S/D Due to 33kv bus work | [7 empty] | 45.0MW load
interrup.
| 07:09 |  | Haripur 230/132kV S/S Auto TR-1 LT Scheduled S/D Due to High temperature maintenance.
| 07:11 |  | Haripur 230/132kV S/S Auto TR-1 HT Scheduled S/D Due to High temperature maintenance.
| 07:23 |  | Aminbazar-Airport(Old) 230kV Ckt-2 Scheduled S/D from Agargaon 230/132kV end Due to Deep
cleaning
| 07:30 |  | Aminbazar 400/230/132kV S/S Bus-2 (400kV) Project Work S/D Due to Connect with existing
Bus
| 07:35 |  | Haripur 230/132kV S/S 132kV Main Bus Sec-1 Scheduled S/D Due to High temperature
maintenance.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 17-04-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 411 | 9867600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4704000 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 50 | 454581 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 319 | 7667158 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 18 | 129960 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 138 | 3238560 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 137067 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 137160 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 347400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 467640 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 49 | 1140960 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 278 | 2195956 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 95 | 1137744 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2491200 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 423360 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 219522 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 242640 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 460 | 10075454.55 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3403200 | Engine Problem
Dhaka Area Total |  |  |  |  | 6668.974 | 2419 | 48481162.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 601934.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 123930 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 655680 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1655120 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 4972640 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 972691 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 47 | 1084800 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 348325 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 25 | 480480 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 301440 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20879 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 386400 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 138912 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1354073 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Liquid fuel shortage
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 155 | 1443564 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 10990908 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 42240 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 560 | 11840000 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 1946.5 | 37414016.4
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 184 | 4802000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 222 | 697100 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 270 | 8072000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 220 | 7950000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 10 | 617904 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 87840 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 1522181 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1049600 | Machine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 145 | 906618 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 22 | 450096 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 184 | 2199360 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 160 | 3763200 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 472310 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 8 | 82320 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 34 | 284160 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 500145 | -
Cumilla Area Total |  |  |  |  | 2870.745 | 1531 | 33456834
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 51 | 843840 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 230400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 59 | 1380000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 305340 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 129840 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 149760 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 148 | 3051780
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 67400 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 1001000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 715680 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 142 | 3566045.46 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 100 | 2376000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719712 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 1617600 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 99 | 2394050 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 108288 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7373000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 158 | 6625000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 988 | 26563775.46
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 767 | 21527273 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 29 | 372960 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 21 | 318464 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 188 | 4461984 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 505440 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1229 | 29200000 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2234 | 56386121
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 405 | 6930909 | Plant availability less
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 394944 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3076000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1215 | 29050181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5395670 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 438000 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 290 | 6873000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3784 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2293 | 52162488.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 381616 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 839333 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 398829 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 192 | 4455727 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 195 | 4790300 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 8820290 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 259500 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 83 | 562112 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 502176 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 391872 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 33060 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1476.54 | 35327599 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 274496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 626700 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2545.54 | 57663610
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1124072 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 9000 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 92 | 757910 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 48412.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 552998 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 220681 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1254960 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 212 | 3968033.56
Eastern Grid Total |  |  |  |  | 17417.792 | 7032.5 | 148967568.41
Western Grid Total |  |  |  |  | 11852.195 | 7284.54 | 170180253.38
National Grid Total |  |  |  |  | 29269.987 | 14317.04 | 319147821.79
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 17-04-2026
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9495.69 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4307 | MW
i) Dhaka area |  |  | 5283.99 |  | MW | i) Khulna area |  |  |  | 1606 | MW
ii) Chattogram area |  |  | 1373.7 |  | MW | ii) Barishal area |  |  |  | 395 | MW
iii) Cumilla area |  |  | 1359 |  | MW | iii) Rajshahi area |  |  |  | 1447 | MW
iv) Mymensingh area |  |  | 963 |  | MW | iv) Rangpur area |  |  |  | 859 | MW
v) Sylhet area |  |  | 516 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13802.69 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 11 | 17:00 | 67 | Hasnabad | 95 | 22:00 | 133 | Natore | 158 | 18:00
2 | AKSML | 9.2 | 05:00 | 68 | Hathazari | 91 | 20:00 | 134 | Nawabganj | 59 | 20:00
3 | Aftabnagar | 42 | 23:00 | 69 | Hatirjheel | 38 | 18:00 | 135 | Netrakona | 112 | 20:00
4 | Agargaon | 114 | 23:00 | 70 | Ishurdi | 70 | 09:00 | 136 | New | 63.7 | 12:00
5 | Agrabad | 52 | 00:00 | 71 | Jaldhaka | 99 | 20:00 | 137 | Niamatpur | 107 | 07:00
6 | Amnura | 44 | 08:00 | 72 | Jamalpur | 98 | 21:00 | 138 | Noapara | 41 | 19:00
7 | Ashuganj | 95 | 23:00 | 73 | Jashore | 146 | 21:00 | 139 | PHP | 6 | 16:00
8 | BSRM | 194 | 23:00 | 74 | Jhenaidah | 118 | 19:00 | 140 | Pabna | 91 | 22:00
9 | Bagerhat | 79 | 19:00 | 75 | Joydebpur | 135 | 19:00 | 141 | Palashbari | 136 | 19:30
10 | Bajitpur | 90 | 18:30 | 76 | Joypurhat | 70 | 07:00 | 142 | Panchagarh | 45 | 18:00
11 | Bakerganj | 13 | 13:00 | 77 | Juldah | 19 | 19:00 | 143 | Patiya | 11 | 00:00
12 | Bakulia | 94 | 00:00 | 78 | KSRM | 10 | 04:00 | 144 | Patuakhali | 58 | 13:00
13 | Banani | 32.4 | 19:00 | 79 | Kabirpur | 248 | 20:00 | 145 | Payra | 28 | 03:00
14 | Bangabhaban | 5 | 14:00 | 80 | Kachua | 88 | 21:00 | 146 | Postogola | 52 | 00:00
15 | Barapukuria | 64 | 10:00 | 81 | Kaliganj | 31 | 19:00 | 147 | Pubail | 27 | 00:00
16 | Barguna | 18 | 04:00 | 82 | Kallyanpur | 117 | 12:00 | 148 | Purbachal | 33 | 19:00
17 | Barishal | 92 | 12:00 | 83 | Kalurghat | 33 | 16:00 | 149 | Purbasadipur | 128 | 11:00
18 | Barishal-230 | 98 | 18:30 | 84 | Kamrangirchar | 73 | 00:00 | 150 | Rahanpur | 37 | 21:00
19 | Baroaulia | 58 | 06:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 20 | 03:00
20 | Baroirhat | 47 | 14:00 | 86 | Kasba | 39 | 18:30 | 152 | Rajbari | 88 | 19:00
21 | Bashundhara | 199 | 13:00 | 87 | Kazla | 113 | 13:00 | 153 | Rajendrapur | 126 | 20:00
22 | BashundharaCement | 7 | 00:00 | 88 | Keranigonj | 78 | 21:00 | 154 | Rajshahi | 135 | 13:00
23 | Beanibazar | 64 | 18:00 | 89 | Khagrachori | 32 | 18:30 | 155 | Rajshahi-230 | 82 | 14:00
24 | Benapole | 73 | 23:00 | 90 | Khulna | 79 | 13:00 | 156 | Ramganj | 110 | 21:00
25 | Bhaluka | 116 | 21:00 | 91 | Khulshi | 170 | 19:30 | 157 | Rampur | 42 | 18:30
26 | Bhandaria | 47 | 15:00 | 92 | Kishoreganj | 98 | 22:00 | 158 | Rangamati | 19 | 18:30
27 | Bhangura | 48 | 09:00 | 93 | Kodda | 280 | 11:00 | 159 | Rangpur | 122 | 19:30
28 | Bheramara(GK) | 73 | 19:00 | 94 | Kulaura | 46 | 23:00 | 160 | Ruppur | 4 | 10:00
29 | Bhulta | 211 | 20:00 | 95 | Kurigram | 68 | 18:00 | 161 | SSM | 11 | 06:00
30 | Bog-Sherpur | 78 | 00:00 | 96 | Kushtia | 150 | 19:00 | 162 | Saidpur | 100 | 12:00
31 | Bogura | 167 | 00:00 | 97 | Laksam | 25 | 19:00 | 163 | Satkhira | 141 | 19:30
32 | Borhanuddin | 88 | 18:30 | 98 | Lakshmipur | 35 | 04:00 | 164 | Satmasjid | 103 | 19:00
33 | Brahmanbaria | 127 | 22:00 | 99 | Lalbag | 65 | 00:00 | 165 | Savar | 196 | 21:00
34 | Cantonment | 128 | 13:00 | 100 | Lalmonirhat | 44 | 19:30 | 166 | SevenRings | 18.65 | 03:00
35 | Chandina | 40 | 21:00 | 101 | MI_Cement | 17.6 | 12:00 | 167 | ShahCement | 43 | 01:00
36 | Chandpur | 74 | 21:00 | 102 | Madanganj | 41 | 18:30 | 168 | Shahjadpur | 86 | 07:00
37 | Chandraghona | 37 | 21:00 | 103 | Madaripur | 117 | 19:00 | 169 | Shahjibazar | 114 | 22:00
38 | Chapai | 83 | 06:00 | 104 | Madartek | 88 | 23:00 | 170 | Shahmirpur | 46 | 20:00
39 | Charsaidpur | 39 | 02:00 | 105 | Madunaghat | 48 | 18:00 | 171 | Shariatpur | 89 | 19:00
40 | Chauddagram | 74 | 18:00 | 106 | Magura | 80 | 19:00 | 172 | Sherpur | 118 | 22:00
41 | Chhatak | 36 | 18:00 | 107 | Mahasthangarh | 84 | 15:00 | 173 | Shikalbaha | 27 | 03:00
42 | Chowmuhani | 134 | 22:00 | 108 | Maijdee | 41 | 19:00 | 174 | Shitalakhya | 62.1 | 12:00
43 | Chuadanga | 126 | 19:00 | 109 | Manikganj | 142 | 22:00 | 175 | Sholosohor | 42 | 22:00
44 | Coxsbazar | 131 | 18:30 | 110 | Maniknagar | 57 | 00:00 | 176 | Shyampur | 170 | 00:00
45 | Cumilla(N) | 121 | 23:00 | 111 | Matarbari | 61 | 19:00 | 177 | Siddhirganj | 115 | 00:00
46 | Cumilla(S) | 178 | 18:30 | 112 | Matuail | 75 | 00:00 | 178 | Sirajganj | 128 | 19:30
47 | Daganbhuiyan | 38 | 23:00 | 113 | Metrorail_Motijheel | 22 | 19:00 | 179 | Sonargaon | 135 | 22:00
48 | Daudkandi | 139 | 18:30 | 114 | Metrorail_Uttara | 6 | 18:00 | 180 | Sreemongol | 70 | 18:00
49 | DhakaUniversity | 44 | 15:00 | 115 | Millgate | 83 | 12:00 | 181 | Sreepur | 105 | 20:00
50 | Dhamrai | 116 | 21:00 | 116 | Mirpur | 135 | 12:00 | 182 | Srinagar | 54.4 | 20:00
51 | Dhanmondi | 108 | 18:30 | 117 | Mirsorai | 56 | 01:00 | 183 | Sunamganj | 54 | 18:00
52 | Dohazari | 98 | 18:00 | 118 | Mirzapur | 41 | 15:00 | 184 | Sylhet | 62 | 18:30
53 | Faridpur | 161 | 23:00 | 119 | Mithapukur | 62 | 18:00 | 185 | Sylhet-132 | 101 | 22:00
54 | Fatullah | 86 | 00:00 | 120 | Modern | N/A | N/A | 186 | TK | 21 | 06:00
55 | Fenchuganj | 41 | 21:00 | 121 | Mogbazar | 67.4 | 18:30 | 187 | Tangail | 163 | 21:00
56 | Feni | 107 | 18:30 | 122 | Mongla | 42 | 00:00 | 188 | Taraganj | 24 | 18:30
57 | GPH | 74 | 06:00 | 123 | Motijheel | 39 | 13:00 | 189 | Tasnim | 34 | 19:30
58 | Ghatail | 72 | 23:00 | 124 | Muktagacha | 32 | 23:00 | 190 | Thakurgaon | 85 | 18:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 114 | 21:00 | 191 | Tongi | 153 | 00:00
60 | Ghorashal-230 | 108 | 22:00 | 126 | Muradnagar | 47 | 18:30 | 192 | Ullahpara | 47 | 08:00
61 | Goalpara | 39 | 22:00 | 127 | Mymensingh | 197 | 22:00 | 193 | Ullon | 70 | 23:00
62 | Gollamari | 96 | 20:00 | 128 | Nabinagar | 11 | 20:00 | 194 | Uttara | 89 | 18:30
63 | Gopalganj | 113 | 19:00 | 129 | Naogaon | 144 | 23:00 | 195 | UttaraNew | 54 | 23:00
64 | Gulshan | 96 | 15:00 | 130 | Narail | 65 | 19:00 | 196 | Zigatola | 84 | 13:00
65 | Halishahar | 74 | 19:00 | 131 | Narinda | 50 | 00:00
66 | HaripurSBU | 129 | 22:00 | 132 | Narshingdi | 187 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 17-04-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13427.5 | 1025 |  | 14498.5
1:00 | 12758.5 | 1234 |  | 14048.5
2:00 | 12611.5 | 1231 |  | 13897.5
3:00 | 12634.5 | 1114 |  | 13798.5
4:00 | 12531.5 | 1069 |  | 13648.5
5:00 | 12592.5 | 533 |  | 13149.5
6:00 | 12614.21 | 496 |  | 13132.21
7:00 | 12554.5 | 478 |  | 13054.5
8:00 | 12780.38 | 406 |  | 13204.38
9:00 | 12834.84 | 497 |  | 13353.84
10:00 | 12906.57 | 495 |  | 13423.57
11:00 | 13036.13 | 524 |  | 13584.13
12:00 | 13298.34 | 827 |  | 14162.56
13:00 | 13450.89 | 862 |  | 14351.89
14:00 | 13311.14 | 777 |  | 14123.14
15:00 | 13071.99 | 862 |  | 13972.99
16:00 | 13121.17 | 623 |  | 13772.17
17:00 | 13083.2 | 518 |  | 13624.2
18:00 | 13390.04 | 270 |  | 13672.04
19:00 | 13932.87 | 877 |  | 14848.87
19:30 | 14054.67 | 903 |  | 14998.67
20:00 | 14317.04 | 940 |  | 15299.04
21:00 | 14285.87 | 902 |  | 15228.87
22:00 | 14561.64 | 753 |  | 15348.64
23:00 | 14430.64 | 926 |  | 15398.64
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 17-04-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6320.5 | 7107 | 13427.5 | DAILY GENERATION CURVE
00:30 | 6118.5 | 6974.5 | 13093
01:00 | 5916.5 | 6842 | 12758.5 | 17-04-2026
01:30 | 5849.5 | 6835.5 | 12685
02:00 | 5782.5 | 6829 | 12611.5
02:30 | 5790 | 6833 | 12623
03:00 | 5797.5 | 6837 | 12634.5
03:30 | 5769 | 6814 | 12583
04:00 | 5740.5 | 6791 | 12531.5
04:30 | 5764 | 6798 | 12562
05:00 | 5787.5 | 6805 | 12592.5
05:30 | 5819.735 | 6783.62 | 12603.355
06:00 | 5851.97 | 6762.24 | 12614.21
06:30 | 5798.8 | 6785.555 | 12584.355
07:00 | 5745.63 | 6808.87 | 12554.5
07:30 | 5771.155 | 6896.285 | 12667.44
08:00 | 5796.68 | 6983.7 | 12780.38
08:30 | 5800.255 | 7007.355 | 12807.61
09:00 | 5803.83 | 7031.01 | 12834.84
09:30 | 5788.225 | 7082.48 | 12870.705
10:00 | 5772.62 | 7133.95 | 12906.57
10:30 | 5817.05 | 7154.3 | 12971.35
11:00 | 5861.48 | 7174.65 | 13036.13
11:30 | 5974.715 | 7192.52 | 13167.235
12:00 | 6087.95 | 7210.39 | 13298.34
12:30 | 6175.24 | 7199.375 | 13374.615
13:00 | 6262.53 | 7188.36 | 13450.89
13:30 | 6237.75 | 7143.265 | 13381.015
14:00 | 6212.97 | 7098.17 | 13311.14
14:30 | 6083.455 | 7108.11 | 13191.565
15:00 | 5953.94 | 7118.05 | 13071.99
15:30 | 6017.555 | 7079.025 | 13096.58
16:00 | 6081.17 | 7040 | 13121.17
16:30 | 6082.325 | 7019.86 | 13102.185
17:00 | 6083.48 | 6999.72 | 13083.2
17:30 | 6213.39 | 7023.23 | 13236.62
18:00 | 6343.3 | 7046.74 | 13390.04
18:30 | 6530.9 | 7130.555 | 13661.455
19:00 | 6718.5 | 7214.37 | 13932.87
19:30 | 6829.5 | 7225.17 | 14054.67
20:00 | 7032.5 | 7284.54 | 14317.04
20:30 | 7039.5 | 7261.955 | 14301.455 |  | Executive Engineer
21:00 | 7046.5 | 7239.37 | 14285.87 |  | Network Operation Division
21:30 | 7167 | 7256.755 | 14423.755
22:00 | 7287.5 | 7274.14 | 14561.64
22:30 | 7243 | 7253.14 | 14496.14
23:00 | 7198.5 | 7232.14 | 14430.64

## En-Curve
QF-LDC-12
Date | 17-04-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3580 | 1548 | 908 | 0 | 178 | 1470 | 70 | 3938 | 0 | 775 | 960.5 | 0 | 0 | 0 | 1025 | DAILY ENERGY CURVE
00:30 | 3554 | 1558.5 | 908 | 0 | 177 | 1466.5 | 69 | 3893 | 0 | 709 | 758 | 0 | 0 | 0 | 1129.5 | 17-04-2026
01:00 | 3528 | 1569 | 908 | 0 | 176 | 1463 | 68 | 3848 | 0 | 643 | 555.5 | 0 | 0 | 0 | 1234
01:30 | 3525 | 1571.5 | 908 | 0 | 171 | 1467 | 67.5 | 3820.5 | 0 | 639 | 515.5 | 0 | 0 | 0 | 1232.5 | Energy Generated | 319.1478 |  | MKWHr
02:00 | 3522 | 1574 | 908 | 0 | 166 | 1471 | 67 | 3793 | 0 | 635 | 475.5 | 0 | 0 | 0 | 1231 | Energy not Served | 18.239 |  | MKWHr
02:30 | 3530.5 | 1577 | 907.5 | 0 | 167 | 1468 | 67 | 3799.5 | 0 | 643.5 | 463 | 0 | 0 | 0 | 1172.5 | Total Energy Requirement | 337.3868 |  | MKWHr
03:00 | 3539 | 1580 | 907 | 0 | 168 | 1465 | 67 | 3806 | 0 | 652 | 450.5 | 0 | 0 | 0 | 1114
03:30 | 3537 | 1569.5 | 907 | 0 | 165 | 1467.5 | 67.5 | 3797 | 0 | 649.5 | 423 | 0 | 0 | 0 | 1091.5
04:00 | 3535 | 1559 | 907 | 0 | 162 | 1470 | 68 | 3788 | 0 | 647 | 395.5 | 0 | 0 | 0 | 1069
04:30 | 3544.5 | 1529.5 | 907 | 0 | 167 | 1469.5 | 68.5 | 3796.5 | 0 | 647 | 432.5 | 0 | 0 | 0 | 801
05:00 | 3554 | 1500 | 907 | 0 | 172 | 1469 | 69 | 3805 | 0 | 647 | 469.5 | 0 | 0 | 0 | 533
05:30 | 3529.5 | 1497.5 | 907 | 0 | 156 | 1469 | 69.5 | 3792 | 6.355 | 645 | 531.5 | 0 | 0 | 0 | 514.5
06:00 | 3505 | 1495 | 907 | 0 | 140 | 1469 | 70 | 3779 | 12.71 | 643 | 593.5 | 0 | 0 | 0 | 496
06:30 | 3473.5 | 1467.5 | 907 | 0 | 137 | 1469 | 70 | 3779.5 | 65.855 | 621 | 594 | 0 | 0 | 0 | 487
07:00 | 3442 | 1440 | 907 | 0 | 134 | 1469 | 70 | 3780 | 119 | 599 | 594.5 | 0 | 0 | 0 | 478
07:30 | 3517 | 1467.5 | 908.5 | 0 | 139 | 1467.5 | 70 | 3784.5 | 198.44 | 568.5 | 546.5 | 0 | 0 | 0 | 442
08:00 | 3592 | 1495 | 910 | 0 | 144 | 1466 | 70 | 3789 | 277.88 | 538 | 498.5 | 0 | 0 | 0 | 406
08:30 | 3610 | 1489.5 | 910 | 0 | 149 | 1464.205 | 70 | 3776.5 | 353.405 | 534.5 | 450.5 | 0 | 0 | 0 | 451.5
09:00 | 3628 | 1484 | 910 | 0 | 154 | 1462.41 | 70 | 3764 | 428.93 | 531 | 402.5 | 0 | 0 | 0 | 497
09:30 | 3626 | 1498.5 | 909.5 | 0 | 151 | 1468.275 | 70 | 3734 | 479.93 | 530.5 | 403 | 0 | 0 | 0 | 496
10:00 | 3624 | 1513 | 909 | 0 | 148 | 1474.14 | 70 | 3704 | 530.93 | 530 | 403.5 | 0 | 0 | 0 | 495
10:30 | 3642.5 | 1469 | 909 | 0 | 151 | 1492.82 | 70 | 3731.5 | 554.03 | 529 | 422.5 | 0 | 0 | 0 | 509.5
11:00 | 3661 | 1425 | 909 | 0 | 154 | 1511.5 | 70 | 3759 | 577.13 | 528 | 441.5 | 0 | 0 | 0 | 524
11:30 | 3639.5 | 1449.5 | 909.5 | 0 | 159 | 1508.64 | 70 | 3839.5 | 597.095 | 530 | 464 | 0 | 0 | 0.5 | 675.5
12:00 | 3618 | 1474 | 910 | 0 | 164 | 1505.78 | 70 | 3920 | 617.06 | 532 | 486.5 | 0 | 0 | 1 | 827
12:30 | 3602.5 | 1511 | 909.5 | 0 | 170 | 1501.005 | 70 | 3976.5 | 598.11 | 537 | 493 | 3 | 0 | 3 | 844.5
13:00 | 3587 | 1548 | 909 | 0 | 176 | 1496.23 | 70 | 4033 | 579.16 | 542 | 499.5 | 6 | 0 | 5 | 862
13:30 | 3577.5 | 1533 | 909.5 | 0 | 176 | 1492.47 | 69 | 3985.5 | 540.545 | 541.5 | 543 | 6.5 | 0 | 6.5 | 819.5
14:00 | 3568 | 1518 | 910 | 0 | 176 | 1488.71 | 68 | 3938 | 501.93 | 541 | 586.5 | 7 | 0 | 8 | 777
14:30 | 3379 | 1547 | 910 | 0 | 176 | 1484.44 | 67 | 4025 | 466.445 | 541 | 584.18 | 3.5 | 0 | 8 | 819.5
15:00 | 3190 | 1576 | 910 | 0 | 176 | 1480.17 | 66 | 4112 | 430.96 | 541 | 581.86 | 0 | 0 | 8 | 862
15:30 | 3217.5 | 1626 | 909.5 | 0 | 169 | 1476.475 | 66.5 | 4080 | 351.925 | 509.5 | 680.68 | 0 | 0 | 9.5 | 742.5
16:00 | 3245 | 1676 | 909 | 0 | 162 | 1472.78 | 67 | 4048 | 272.89 | 478 | 779.5 | 0 | 0 | 11 | 623
16:30 | 3239 | 1639.5 | 909.5 | 0 | 161 | 1472.83 | 68 | 4020 | 196.355 | 519 | 868.5 | 0 | 0 | 8.5 | 570.5
17:00 | 3233 | 1603 | 910 | 0 | 160 | 1472.88 | 69 | 3992 | 119.82 | 560 | 957.5 | 0 | 0 | 6 | 518
17:30 | 3242 | 1583.5 | 910 | 0 | 156 | 1472.815 | 69.5 | 4052 | 67.805 | 620 | 1060 | 0 | 0 | 3 | 394
18:00 | 3251 | 1564 | 910 | 0 | 152 | 1472.75 | 70 | 4112 | 15.79 | 680 | 1162.5 | 0 | 0 | 0 | 270
18:30 | 3286.5 | 1533 | 909.5 | 0 | 155 | 1471.06 | 70 | 4173.5 | 7.895 | 713.5 | 1341.5 | 0 | 0 | 0 | 573.5
19:00 | 3322 | 1502 | 909 | 0 | 158 | 1469.37 | 70 | 4235 | 0 | 747 | 1520.5 | 0 | 0 | 0 | 877
19:30 | 3353 | 1494 | 815 | 0 | 154 | 1471.17 | 70 | 4306 | 0 | 776 | 1615.5 | 0 | 0 | 0 | 903
20:00 | 3482 | 1574 | 767 | 0 | 160 | 1476.54 | 70 | 4361 | 0 | 787 | 1639.5 | 0 | 0 | 0 | 940
20:30 | 3495.5 | 1578.5 | 767 | 0 | 154 | 1460.455 | 70 | 4354 | 0 | 790.5 | 1631.5 | 0 | 0 | 0 | 921
21:00 | 3509 | 1583 | 767 | 0 | 148 | 1444.37 | 70 | 4347 | 0 | 794 | 1623.5 | 0 | 0 | 0 | 902
21:30 | 3604.5 | 1576 | 767 | 0 | 152 | 1443.255 | 70 | 4436 | 0 | 799 | 1576 | 0 | 0 | 0 | 827.5
22:00 | 3700 | 1569 | 767 | 0 | 156 | 1442.14 | 70 | 4525 | 0 | 804 | 1528.5 | 0 | 0 | 0 | 753
22:30 | 3645 | 1589 | 814.5 | 0 | 156 | 1451.64 | 70 | 4528.5 | 0 | 802 | 1439.5 | 0 | 0 | 0 | 839.5
23:00 | 3590 | 1609 | 862 | 0 | 156 | 1461.14 | 70 | 4532 | 0 | 800 | 1350.5 | 0 | 0 | 0 | 926
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 17-04-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 386 | 07:00 | 378 | 13:00 | Madunaghat | 401 | 00:00 | 391 | 13:00
Amtali | 440 | 05:00 | 408 | 01:00 | Meghnaghat | 391 | 19:30 | 379 | 11:00
Ashuganj | 407 | 7:00 | 392 | 12:00 | Payra | 413 | 18:00 | 410 | 11:00
Bhulta | 400 | 19:30 | 385 | 11:00 | Rahanpur | 409 | 21:00 | 395 | 11:00
Bibiana | 402 | 00:00 | 394 | 15:00 | Rampal | 401 | 04:00 | 392 | 13:00
BIPTC | 399 | 21:00 | 388 | 16:00
Bogura | 403 | 21:00 | 385 | 11:00
Gopalganj | 396 | 07:00 | 390 | 13:00
Kaliakoir | 382 | 18:30 | 372 | 10:00
Korerhat | 401 | 19:30 | 391 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 19:30 | 222 | 12:00 | Jhenaidah | 227 | 21:00 | 218 | 19:00
AKSML | 231.5 | 00:00 | 223 | 15:00 | Kachua | 231 | 19:30 | 219 | 11:00
Aminbazar | 233 | 18:30 | 222 | 13:00 | Kaliakoir | 232 | 19:00 | 225 | 12:00
Ashuganj | 232 | 19:30 | 223 | 12:00 | Keranigonj | 227 | 07:00 | 220 | 11:00
Ashuganj-400 | 232 | 19:30 | 223 | 12:00 | Khulna(S) | 229 | 21:00 | 222 | 12:00
Baghabari | 234 | 19:30 | 225 | 10:00 | Korerhat | 228 | 19:30 | 221 | 10:00
Barapukuria | 224 | 19:00 | 206 | 11:00 | Madunaghat | 230 | 00:00 | 223 | 11:00
Barapukuria-230 | 224 | 19:00 | 206 | 11:00 | Madunaghat-400 | 232 | 00:00 | 225 | 12:00
Barishal | 226 | 07:00 | 222 | 13:00 | Maniknagar | 227 | 19:00 | 222 | 10:00
Bheramara | 234 | 21:00 | 222 | 08:00 | Meghnaghat | 232 | 01:00 | 228 | 09:00
Bhulta | 229 | 19:30 | 222 | 11:00 | Meghnaghat-400 | 229 | 07:00 | 222 | 11:00
Bibiana | 234 | 07:00 | 229 | 15:00 | Mirsorai | 228 | 19:00 | 219 | 12:00
BIPTC | 236 | 19:30 | 222 | 10:00 | Naogaon | 228 | 01:00 | 213 | 09:00
Bogura | 234 | 19:30 | 223 | 08:00 | Purbasadipur | 228 | 21:00 | 204 | 11:00
Bogura-400 | 234 | 19:00 | 222 | 11:00 | Rajshahi | 234 | 19:30 | 219 | 11:00
Borhanuddin | 231 | 07:00 | 228 | 01:00 | Rampal | 228 | 02:00 | 222 | 12:00
BSRM | 227 | 00:00 | 222 | 10:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 227 | 07:00 | 222 | 03:00 | Rampura | 227 | 07:00 | 221 | 11:00
Cumilla(N) | 227 | 07:00 | 221 | 11:00 | Shikalbaha | 229 | 00:00 | 222 | 13:00
Faridpur | 221 | 02:00 | 216 | 12:00 | Shyampur | 227 | 07:00 | 221 | 12:00
Fenchuganj | 238 | 08:00 | 233 | 11:00 | Siddhirganj | 228 | 06:00 | 223 | 11:00
Feni | 228 | 19:00 | 222 | 10:00 | Sirajgonj | 239 | 19:30 | 233 | 09:00
Ghorashal | 230 | 03:00 | 222 | 00:00 | Sreepur | 227 | 01:00 | 221 | 10:00
Ghorashal-230 | 227 | 07:00 | 219 | 11:00 | Tongi | 226 | 18:30 | 219 | 11:00
Gopalganj | 221 | 02:00 | 218 | 13:00
GPH | 230 | 00:00 | 224 | 10:00
Haripur | 228 | 19:00 | 222 | 12:00
Hasnabad | 228 | 19:30 | 220 | 11:00
Hathazari | 229 | 00:00 | 223 | 13:00
Ishurdi | 235 | 19:30 | 224 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 06:00 | 128 | 11:00 | Madunaghat | 134 | 00:00 | 131 | 11:00
Agargaon | 134 | 04:00 | 129 | 12:00 | Magura | 132 | 04:00 | 121 | 19:00
Agrabad | 134 | 19:30 | 129 | 01:00 | Mahasthangarh | 132 | 19:00 | 122 | 08:00
AKS | 130 | 00:00 | 126 | 05:00 | Maijdee | 127 | 00:00 | 121 | 13:00
Aminbazar | 131 | 06:00 | 126 | 12:00 | Manikganj | 127 | 19:30 | 122 | 10:00
Amnura | 137 | 19:30 | 126 | 11:00 | Maniknagar | 134 | 07:00 | 130 | 11:00
Ashuganj | 137 | 19:00 | 135 | 00:00 | Matarbari | 122 | 01:00 | 112 | 06:00
Ashuganj-230 | 137 | 19:00 | 135 | 00:00 | Matuail | 132 | 04:00 | 129 | 00:00
Bagerhat | 126 | 18:00 | 118 | 19:00 | Metrorail_Motijheel | 134 | 07:00 | 130 | 11:00
Bajitpur | 133 | 7:00 | 128 | 10:00 | Metrorail_Uttara | 131 | 07:00 | 126 | 12:00
Bakerganj | 132 | 17:00 | 129 | 13:00 | Millgate | 133 | 19:30 | 126 | 14:00
Bakulia | 134 | 17:00 | 130 | 3:00 | Mirpur | 130 | 03:00 | 125 | 12:00
Banani | 133 | 06:00 | 128 | 11:00 | Mirzapur | 132 | 19:00 | 127 | 11:00
Bangabhaban | 135 | 19:30 | 129 | 12:00 | Mithapukur | 132 | 19:00 | 118 | 10:00
Barapukuria | 133 | 19:00 | 121 | 09:00 | MI_Cement | 130.7 | 19:30 | 123.8 | 12:00
Barguna | 132 | 17:00 | 129 | 13:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 18:00 | 129 | 12:00 | Mogbazar | 134 | 05:00 | 130 | 00:00
Barishal-230 | 132 | 04:00 | 129 | 12:00 | Mongla | 127 | 18:00 | 118 | 19:00
Baroaulia | 132 | 00:00 | 130 | 05:00 | Motijheel | 135 | 19:30 | 129 | 12:00
Baroirhat | 131 | 19:30 | 127 | 09:00 | Muktagacha | 126 | 22:00 | 120 | 06:00
Bashundhara | 133 | 19:30 | 125 | 11:00 | Munshiganj | 132 | 19:30 | 127 | 12:00
BashundharaCement | 133 | 17:00 | 129 | 12:00 | Muradnagar | 129 | 19:30 | 122 | 03:00
Beanibazar | 128 | 00:00 | 124 | 10:00 | Mymensingh | 133 | 06:00 | 118 | 06:00
Benapole | 129 | 05:00 | 121 | 19:00 | Nabinagar | 130 | 19:00 | 125 | 12:00
Bhaluka | 136 | 07:00 | 129 | 10:00 | Naogaon | 137 | 01:00 | 117 | 07:00
Bhandaria | 133 | 04:00 | 122 | 00:00 | Narail | 131 | 21:00 | 121 | 19:00
Bhangura | 133 | 19:30 | 127 | 01:00 | Narinda | 134 | 07:00 | 130 | 11:00
Bheramara | 136 | 21:00 | 130 | 08:00 | Narshingdi | 130 | 06:00 | 122 | 20:00
Bheramara(GK) | 136 | 21:00 | 130 | 09:00 | Natore | 132 | 21:00 | 123 | 12:00
Bhulta | 125 | 13:00 | 122 | 22:00 | Nawabganj | 132 | 04:00 | 128 | 11:00
Bog-Sherpur | 133 | 19:00 | 124 | 10:00 | Netrakona | 133 | 06:00 | 121 | 20:00
Bogura | 134 | 19:30 | 126 | 8:00 | New | 134 | 19:30 | 128 | 11:00
Bogura-230 | 135 | 19:00 | 126 | 08:00 | Niamatpur | 137 | 03:00 | 130 | 08:00
Brahmanbaria | 132 | 06:00 | 127 | 11:00 | Noapara | 129 | 04:00 | 121 | 19:00
Cantonment | 134 | 05:00 | 129 | 12:00 | Pabna | 133 | 19:30 | 127 | 11:00
Chandina | 131 | 07:00 | 127 | 11:00 | Palashbari | 128 | 19:00 | 116 | 09:00
Chandpur | 133 | 18:00 | 122 | 10:00 | Panchagarh | 138 | 19:00 | 121 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 134 | 00:00 | 132 | 03:00 | Patiya | 132 | 00:00 | 127 | 04:00
Chapai | 135 | 17:00 | 128 | 11:00 | Patuakhali | 132 | 05:00 | 129 | 12:00
Charsaidpur | 133 | 19:30 | 129 | 00:00 | Payra | 135 | 08:00 | 133 | 00:00
Chauddagram | 129 | 19:30 | 124 | 14:00 | PHP | 130 | 00:00 | 125 | 13:00
Chhatak | 130 | 07:00 | 122 | 18:00 | Postogola | 132 | 19:00 | 127 | 10:00
Chowmuhani | 128 | 18:30 | 122 | 13:00 | Pubail | 138 | 18:30 | 133 | 10:00
Chuadanga | 129 | 03:00 | 120 | 19:00 | Purbachal | 133 | 05:00 | 126 | 12:00
Coxsbazar | 123 | 00:00 | 114 | 21:00 | Purbasadipur | 133 | 21:00 | 117 | 09:00
Cumilla(N) | 132 | 19:30 | 127 | 11:00 | Rahanpur | 139 | 19:30 | 134 | 08:00
Cumilla(S) | 130 | 05:00 | 121 | 13:00 | Rahanpur-400 | 140 | 21:00 | 134 | 11:00
Daganbhuiyan | 128 | 07:00 | 123 | 13:00 | Rahim | 132 | 06:00 | 129 | 12:00
Daudkandi | 127 | 19:00 | 123 | 09:00 | Rajbari | 126 | 02:00 | 122 | 11:00
DhakaUniversity | 133 | 03:00 | 127 | 11:00 | Rajendrapur | 134 | 02:00 | 128 | 10:00
Dhamrai | 130 | 12:00 | 126 | 14:00 | Rajshahi | 132 | 21:00 | 123 | 11:00
Dhanmondi | 134.5 | 19:30 | 130 | 11:00 | Rajshahi-230 | 134 | 21:00 | 125 | 11:00
Dohazari | 130 | 00:00 | 124 | 04:00 | Ramganj | 129 | 00:00 | 120 | 13:00
Faridpur | 129 | 00:00 | 125 | 12:00 | Rampur | 133 | 00:00 | 129 | 01:00
Fatullah | 132 | 19:30 | 125 | 12:00 | Rampura | 133 | 07:00 | 128 | 11:00
Fenchuganj | 135 | 07:00 | 131 | 11:00 | Rangamati | 133 | 00:00 | 130 | 18:30
Feni | 127 | 17:00 | 124 | 08:00 | Rangpur | 132 | 19:00 | 118 | 10:00
Feni-230 | 128 | 00:00 | 124 | 10:00 | Ruppur | 136 | 19:30 | 129 | 12:00
Ghatail | 126 | 22:00 | 119 | 06:00 | Saidpur | 132 | 19:00 | 120 | 09:00
Ghorashal | 138 | 18:30 | 134 | 10:00 | Satkhira | 126 | 08:00 | 116 | 19:00
Goalpara | 132 | 05:00 | 125 | 19:00 | Satmasjid | 134 | 07:00 | 129 | 13:00
Gollamari | 131 | 06:00 | 125 | 19:00 | Savar | 129 | 02:00 | 123 | 11:00
Gopalganj | 130 | 04:00 | 125 | 19:00 | SevenRings | 138 | 07:00 | 134 | 10:00
Gopalganj-400 | 131 | 00:00 | 129 | 13:00 | ShahCement | 139 | 13:00 | 129 | 00:00
Gulshan | 133 | 19:30 | 128 | 11:00 | Shahjadpur | 136 | 21:00 | 130 | 08:00
Halishahar | 134 | 19:30 | 129 | 03:00 | Shahjibazar | 133 | 07:00 | 124 | 11:00
Haripur | 133 | 06:00 | 130 | 10:00 | Shahmirpur | 134 | 17:00 | 130 | 01:00
HaripurSBU | 133 | 06:00 | 130 | 11:00 | Shariatpur | 136 | 15:00 | 126 | 19:00
Hasnabad | 132 | 18:30 | 126 | 12:00 | Sherpur | 122 | 07:00 | 112 | 17:00
Hathazari | 135 | 00:00 | 131 | 13:00 | Shikalbaha | 123 | 12:00 | 121 | 00:00
Hatirjheel | 133 | 07:00 | 128 | 12:00 | Shikalbaha-230 | 136 | 19:30 | 130 | 04:00
Ishurdi | 137 | 21:00 | 131 | 08:00 | Shitalakhya | 130.8 | 19:30 | 123.8 | 12:00
Jaldhaka | 130 | 19:30 | 116 | 09:00 | Sholosohor | 133 | 00:00 | 130 | 04:00
Jamalpur | 125 | 07:00 | 115 | 19:30 | Shyampur | 130 | 18:30 | 125 | 11:00
Jashore | 132 | 07:00 | 121 | 19:00 | Shyampur-230 | 132 | 19:30 | 127 | 12:00
Jhenaidah | 134 | 04:00 | 121 | 19:00 | Siddhirganj | 133 | 19:00 | 130 | 00:00
Jhenaidah-230 | 134 | 05:00 | 127 | 19:00 | Sirajganj | 135 | 04:00 | 123 | 08:00
Joydebpur | 137 | 19:30 | 131 | 00:00 | Sonargaon | 131 | 19:30 | 126 | 00:00
Joypurhat | 127 | 19:30 | 112 | 08:00 | Sreemongol | 131 | 01:00 | 125 | 11:00
Juldah | 134 | 16:00 | 130 | 01:00 | Sreepur | 136 | 01:00 | 131 | 10:00
Kabirpur | 139 | 19:30 | 124 | 11:00 | Srinagar | 133 | 05:00 | 127 | 12:00
Kachua | 131 | 19:30 | 124 | 10:00 | SSM | 138 | 00:00 | 136 | 07:00
Kaliakoir | 137 | 01:00 | 127 | 14:00 | Sunamganj | 128 | 08:00 | 120 | 18:00
Kaliganj | 133 | 04:00 | 125 | 19:00 | Sylhet | 132 | 07:00 | 126 | 18:00
Kallyanpur | 130 | 06:00 | 125 | 12:00 | Sylhet-132 | 133 | 04:00 | 127 | 11:00
Kalurghat | 134 | 00:00 | 131 | 04:00 | Tangail | 127 | 08:00 | 123 | 10:00
Kamrangirchar | 134 | 04:00 | 123 | 11:00 | Taraganj | 131 | 19:00 | 118 | 08:00
Kaptai | 135 | 1:00 | 134 | 6:00 | Tasnim | 131 | 05:00 | 125 | 00:00
Kasba | 128 | 02:00 | 124 | 11:00 | Thakurgaon | 137 | 19:00 | 119 | 10:00
Kazla | 133 | 06:00 | 129 | 12:00 | TK | 134 | 00:00 | 131 | 10:00
Keranigonj | 133 | 05:00 | 129 | 11:00 | Tongi | 133 | 03:00 | 129 | 00:00
Khagrachori | 132 | 00:00 | 129 | 18:30 | Ullahpara | 132 | 19:30 | 126 | 08:00
Khulna | 129 | 00:00 | 124 | 19:00 | Ullon | 132 | 03:00 | 128 | 11:00
Khulna(S) | 131 | 04:00 | 125 | 19:00 | Uttara | 132 | 19:30 | 125 | 12:00
Khulshi | 132 | 19:30 | 128 | 04:00 | UttaraNew | 131 | 07:00 | 126 | 12:00
Kishoreganj | 133 | 04:00 | 127 | 10:00 | Zigatola | 134 | 19:30 | 128 | 12:00
Kodda | 138 | 19:00 | 130 | 10:00
Korerhat | 132 | 00:00 | 128 | 10:00
KSRM | 134 | 00:00 | 130 | 04:00
Kulaura | 134 | 06:00 | 130 | 11:00
Kurigram | 129 | 19:00 | 116 | 09:00
Kushtia | 132 | 06:00 | 126 | 08:00
Laksam | 131 | 18:00 | 124 | 11:00
Lakshmipur | 127 | 00:00 | 121 | 13:00
Lalbag | 133 | 19:30 | 128 | 12:00
Lalmonirhat | 130 | 20:00 | 117 | 08:00
Madanganj | 133 | 17:00 | 129 | 12:00
Madaripur | 132 | 04:00 | 128 | 19:00
Madartek | 132 | 04:00 | 127 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division