## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 18-04-2026 | [28 empty] | Date: | 18-04-2026 | [28 empty] | Date: | 18-04-2026 | [28 empty] | Date: | 18-04-2026 | [28 empty] | Date: | 18-04-2026 | [17 empty] | Date: | 18-04-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 17 | 38 | 142 | 130 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 450 | 0 | 16 | 12 | 0 | 0 | 50 | 47 | 18 | 0 | 0 | 0 | 70 | 62 | 23 | 835 | 54 | 0 | 50 | 25.5 | 51 | 221 | 0 | 0 | 0 | 612 | 0 | 20 | 90 | 393 | 0 | 345 | 44 | 10 | 197 | 42 | 16 | 0 | 65 | 0 | 20 | 0 | 156 | 0 | 0 | 22 | 300 | 0 | 130 | 42 | 30 | 156 | 0 | 8 | 0 | 78 | 30 | 100 | 0 | 100 | 0 | 59 | 9 | 66 | 0 | 0 | 12 | 6720.5 | 909 | 190 | 0 | 24 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1222 | 0 | 0 | 0 | 1480.84 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 160 | 0 | 344 | 0 | 0 | 0 | 48 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 259 | 1220 | 17 | 6883.84 | 13604.34 | 79.03
01:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 17 | 143 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 450 | 0 | 16 | 12 | 0 | 0 | 0 | 47 | 18 | 0 | 0 | 0 | 70 | 55 | 24 | 900 | 17 | 0 | 20 | 25.5 | 34 | 220 | 0 | 0 | 0 | 612 | 0 | 20 | 63 | 380 | 0 | 345 | 44 | 7 | 191 | 42 | 17 | 0 | 17 | 0 | 20 | 0 | 158 | 0 | 0 | 22 | 310 | 0 | 15 | 42 | 30 | 156 | 0 | 8 | 0 | 78 | 30 | 100 | 0 | 100 | 0 | 59 | 9 | 65 | 0 | 0 | 12 | 6307.5 | 850 | 199 | 0 | 24 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1227 | 0 | 0 | 0 | 1478.02 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 32 | 0 | 0 | 170 | 0 | 0 | 0 | 160 | 0 | 348 | 0 | 0 | 0 | 48 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 253 | 1220 | 17 | 6808.02 | 13115.52 | 79.01
02:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 0 | 0 | 17 | 144 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 450 | 23 | 16 | 12 | 0 | 0 | 0 | 47 | 18 | 0 | 0 | 0 | 66 | 54 | 20 | 925 | 17 | 0 | 19 | 25.5 | 34 | 220 | 0 | 0 | 0 | 612 | 0 | 20 | 63 | 393 | 0 | 345 | 44 | 5 | 188 | 42 | 18 | 0 | 17 | 0 | 20 | 0 | 158 | 0 | 0 | 22 | 305 | 0 | 65 | 42 | 30 | 156 | 0 | 8 | 0 | 78 | 30 | 100 | 0 | 100 | 0 | 59 | 9 | 71 | 0 | 0 | 12 | 6413.5 | 815 | 207 | 0 | 24 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1222 | 0 | 0 | 0 | 1476.5 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 32 | 0 | 0 | 170 | 0 | 0 | 0 | 160 | 0 | 340 | 0 | 0 | 0 | 48 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 254 | 1212 | 17 | 6753.5 | 13167 | 78.99
03:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 144 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 455 | 90 | 0 | 12 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 66 | 55 | 22 | 925 | 17 | 0 | 19 | 25.5 | 34 | 221 | 0 | 0 | 0 | 612 | 0 | 20 | 63 | 393 | 0 | 345 | 44 | 5 | 192 | 42 | 17 | 0 | 17 | 0 | 20 | 0 | 156 | 0 | 0 | 22 | 310 | 0 | 3 | 42 | 30 | 158 | 0 | 8 | 0 | 78 | 30 | 101 | 0 | 100 | 0 | 59 | 9 | 74 | 0 | 0 | 0 | 6394.5 | 909 | 215 | 0 | 24 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1219 | 0 | 0 | 0 | 1478.65 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 32 | 0 | 0 | 170 | 0 | 0 | 0 | 160 | 0 | 353 | 0 | 0 | 0 | 48 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 254 | 1212 | 17 | 6868.65 | 13263.15 | 78.97
04:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 144 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 450 | 90 | 0 | 12 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 66 | 54 | 23 | 925 | 17 | 0 | 19 | 25.5 | 34 | 221 | 0 | 0 | 0 | 612 | 0 | 20 | 63 | 393 | 0 | 345 | 44 | 5 | 191 | 42 | 17 | 0 | 17 | 0 | 20 | 0 | 152 | 0 | 0 | 22 | 310 | 0 | 66 | 42 | 30 | 158 | 0 | 8 | 0 | 78 | 30 | 100 | 0 | 100 | 0 | 59 | 9 | 74 | 0 | 0 | 0 | 6446.5 | 910 | 228 | 0 | 24 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1214 | 0 | 0 | 0 | 1481.27 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 25 | 0 | 0 | 170 | 0 | 0 | 0 | 160 | 0 | 342 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 254 | 1212 | 17 | 6828.27 | 13274.77 | 78.95
05:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 144 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 450 | 89 | 0 | 13 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 68 | 54 | 25 | 925 | 17 | 0 | 19 | 25.5 | 34 | 221 | 0 | 0 | 0 | 612 | 0 | 20 | 63 | 393 | 0 | 345 | 44 | 5 | 199 | 42 | 18 | 0 | 17 | 0 | 20 | 0 | 148 | 0 | 0 | 22 | 305 | 0 | 71 | 42 | 30 | 159 | 0 | 8 | 0 | 78 | 30 | 101 | 0 | 100 | 0 | 59 | 9 | 75 | 0 | 0 | 0 | 6458.5 | 909 | 238 | 0 | 24 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1116 | 0 | 0 | 0 | 1487.87 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 25 | 0 | 0 | 170 | 0 | 0 | 0 | 160 | 0 | 356 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 254 | 1212 | 17 | 6759.87 | 13218.37 | 78.93
06:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 17 | 144 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 142 | 20 | 22 | 0 | 450 | 87 | 0 | 12 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0.11 | 69 | 55 | 31 | 925 | 17 | 0 | 19 | 25.5 | 34 | 221 | 0 | 0 | 0 | 612 | 1 | 20 | 63 | 393 | 0 | 345 | 44 | 5 | 188 | 42 | 17 | 0 | 17 | 0 | 20 | 0 | 136 | 0 | 3 | 22 | 310 | 0 | 84 | 42 | 30 | 157 | 0 | 8 | 0 | 78 | 30 | 100 | 0 | 100 | 0 | 59 | 9 | 75 | 0.06 | 0 | 0 | 6476.67 | 910 | 239 | 0 | 24 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 1.23 | 1117 | 0 | 0 | 0 | 1480.06 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0.55 | 0 | 25 | 0 | 1.17 | 170 | 0 | 0 | 0 | 160 | 0 | 338 | 0 | 0.1 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.01 | 16 | 290 | 130 | 220 | 0 | 254 | 1212 | 17 | 6741.12 | 13217.79 | 78.91
07:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 144 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 6 | 125 | 22 | 22 | 0 | 450 | 91 | 0 | 12 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0.74 | 70 | 55 | 27 | 925 | 17 | 0 | 19 | 16 | 34 | 221 | 0 | 0 | 0 | 612 | 4 | 20 | 63 | 393 | 0 | 345 | 44 | 5 | 190 | 42 | 17 | 0 | 17 | 0 | 14 | 0 | 138 | 0 | 10 | 22 | 315 | 0 | 140 | 42 | 30 | 159 | 2 | 8 | 0 | 78 | 30 | 100 | 0 | 100 | 0 | 59 | 9 | 74 | 0.37 | 3.05 | 0 | 6517.16 | 910 | 250 | 0 | 24 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1113 | 0 | 0 | 0 | 1509.72 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 3.26 | 9 | 25 | 0 | 9.2 | 170 | 0 | 0 | 0 | 160 | 0 | 347 | 0 | 0.78 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 4 | 0.05 | 16 | 290 | 130 | 220 | 0 | 251 | 1212 | 17 | 6822.61 | 13339.77 | 78.89
08:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 17 | 144 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 14 | 125 | 22 | 22 | 0 | 370 | 60 | 0 | 12 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 1.64 | 70 | 55 | 27 | 935 | 17 | 0 | 19 | 16 | 34 | 220 | 0 | 0 | 0 | 612 | 9 | 20 | 63 | 393 | 0 | 345 | 44 | 5 | 195 | 43 | 17 | 0 | 17 | 0 | 6 | 0 | 140 | 0 | 31 | 22 | 310 | 0 | 244 | 42 | 30 | 144 | 5 | 8 | 0 | 78 | 30 | 100 | 0 | 100 | 0 | 58 | 9 | 69 | 0.84 | 5.46 | 0 | 6534.94 | 884 | 250 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 1208 | 0 | 0 | 0 | 1509.72 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 15.44 | 17 | 25 | 0 | 18.48 | 140 | 0 | 0 | 0 | 140 | 0 | 351 | 0 | 1.6 | 0 | 49 | 0 | 1 | 0 | 0 | 0 | 0 | 1.9 | 3 | 0.23 | 16 | 290 | 100 | 180 | 0 | 253 | 1210 | 17 | 6796.37 | 13331.31 | 78.87
09:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 144 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 21 | 125 | 18 | 22 | 0 | 400 | 45 | 0 | 12 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 1.45 | 70 | 55 | 2 | 935 | 17 | 0 | 19 | 16 | 34 | 219 | 0 | 0 | 0 | 612 | 0 | 20 | 63 | 393 | 0 | 345 | 44 | 5 | 190 | 43 | 18 | 0 | 17 | 0 | 6 | 0 | 144 | 0 | 48 | 22 | 315 | 0 | 307 | 42 | 30 | 137 | 9 | 8 | 0 | 78 | 30 | 100 | 0 | 100 | 0 | 58 | 9 | 67 | 0.95 | 34.42 | 0 | 6625.82 | 883 | 250 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 1178 | 0 | 0 | 0 | 1506 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 36.47 | 61 | 0 | 0 | 37 | 140 | 0 | 0 | 0 | 140 | 0 | 333 | 0 | 3.26 | 0 | 47 | 0 | 5 | 0 | 0 | 0 | 0 | 1.1 | 53 | 0.16 | 16 | 290 | 100 | 180 | 0 | 252 | 1200 | 17 | 6878.99 | 13504.81 | 78.86
10:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 17 | 127 | 32 | 15 | 17 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 27 | 90 | 20 | 0 | 0 | 480 | 15 | 0 | 12 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 3.26 | 70 | 34 | 2 | 935 | 17 | 0 | 19 | 16 | 35 | 216 | 0 | 0 | 0 | 558 | 0 | 20 | 92 | 361 | 0 | 340 | 44 | 7 | 205 | 43 | 17 | 0 | 17 | 0 | 10 | 0 | 152 | 0 | 63 | 15 | 305 | 0 | 322 | 42 | 30 | 150 | 7 | 8 | 0 | 78 | 30 | 101 | 0 | 100 | 0 | 68 | 9 | 35 | 0.77 | 41.99 | 0 | 6566.02 | 883 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.54 | 1150 | 0 | 0 | 0 | 1469.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.88 | 44 | 0 | 0 | 35 | 162 | 0 | 0 | 0 | 170 | 0 | 409 | 0 | 3.4 | 0 | 47 | 0 | 2 | 0 | 0 | 0 | 0 | 5.5 | 49 | 0.41 | 0 | 290 | 126 | 220 | 0 | 252 | 1180 | 0 | 6859.02 | 13425.04 | 78.85
11:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 17 | 94 | 48 | 15 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 33 | 90 | 20 | 0 | 0 | 450 | 15 | 0 | 12 | 0 | 2 | 0 | 47 | 0 | 0 | 0 | 2.77 | 70 | 34 | 2 | 935 | 17 | 0 | 19 | 8 | 47 | 215 | 0 | 0 | 0 | 586 | 0 | 20 | 127 | 341 | 0 | 342 | 44 | 20 | 200 | 39 | 17 | 0 | 17 | 2 | 14 | 0 | 172 | 0 | 68 | 22 | 310 | 0 | 324 | 42 | 30 | 156 | 11 | 8 | 0 | 50 | 30 | 100 | 0 | 101 | 0 | 68 | 9 | 35 | 1.34 | 39.18 | 0 | 6668.29 | 884 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.01 | 1156 | 0 | 0 | 0 | 1468.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.78 | 96 | 0 | 0 | 40 | 200 | 0 | 0 | 0 | 190 | 0 | 406 | 0 | 4.72 | 0 | 48 | 0 | 8 | 0 | 0 | 0 | 0 | 2.8 | 117 | 0.64 | 0 | 290 | 126 | 220 | 0 | 252 | 1165 | 0 | 7064.3 | 13732.59 | 78.84
12:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 18 | 0 | 23 | 94 | 48 | 15 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 20 | 92 | 20 | 0 | 0 | 420 | 20 | 0 | 11 | 0 | 12 | 0 | 40 | 0 | 0 | 0 | 3.79 | 70 | 34 | 7 | 935 | 17 | 0 | 19 | 8 | 52 | 215 | 0 | 0 | 0 | 570 | 18 | 20 | 145 | 345 | 0 | 340 | 44 | 22 | 193 | 42 | 17 | 0 | 17 | 9 | 14 | 0 | 186 | 0 | 70 | 20 | 300 | 0 | 325 | 42 | 30 | 151 | 7 | 8 | 0 | 52 | 30 | 100 | 0 | 100 | 0 | 68 | 9 | 35 | 1.65 | 16.32 | 0 | 6689.76 | 883 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.4 | 1178 | 0 | 0 | 0 | 1478.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.82 | 88 | 0 | 0 | 52 | 198 | 0 | 0 | 0 | 204 | 0 | 396 | 0 | 4.58 | 0 | 47 | 0 | 30 | 0 | 0 | 0 | 0 | 4.9 | 0 | 0.31 | 0 | 290 | 126 | 220 | 0 | 251 | 1150 | 0 | 6997.22 | 13686.98 | 78.83
13:00 | 0 | 105 | 45 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 18 | 0 | 51 | 94 | 48 | 15 | 0 | 48 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 15 | 125 | 21 | 0 | 0 | 450 | 28 | 0 | 12 | 0 | 14 | 0 | 40 | 0 | 0 | 0 | 1.61 | 60 | 34 | 7 | 935 | 17 | 0 | 19 | 16 | 52 | 212 | 0 | 0 | 0 | 560 | 17 | 20 | 80 | 393 | 0 | 340 | 44 | 24 | 184 | 42 | 18 | 0 | 17 | 9 | 14 | 0 | 198 | 0 | 66 | 22 | 295 | 0 | 317 | 42 | 18 | 153 | 4 | 8 | 0 | 52 | 30 | 100 | 0 | 100 | 1 | 68 | 13 | 30 | 1.07 | 2.48 | 0 | 6696.16 | 883 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.55 | 1202 | 0 | 0 | 0 | 1506.28 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 37.28 | 90 | 0 | 0 | 26 | 201 | 0 | 0 | 0 | 202 | 0 | 394 | 0 | 5.07 | 0 | 49 | 0 | 33 | 0 | 0 | 0 | 0 | 4.5 | 32 | 0.31 | 0 | 290 | 126 | 220 | 0 | 250 | 1170 | 0 | 7054.99 | 13751.15 | 78.82
14:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 18 | 0 | 52 | 94 | 48 | 15 | 0 | 54 | 0 | 180 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 24 | 142 | 21 | 0 | 0 | 420 | 28 | 0 | 12 | 0 | 12 | 0 | 45 | 0 | 0 | 0 | 2.71 | 60 | 34 | 7 | 935 | 17 | 0 | 19 | 8 | 51 | 213 | 0 | 0 | 0 | 570 | 16 | 20 | 45 | 392 | 0 | 330 | 44 | 19 | 208 | 38 | 17 | 0 | 17 | 9 | 14 | 0 | 198 | 0 | 61 | 22 | 310 | 0 | 318 | 42 | 18 | 143 | 0 | 8 | 0 | 52 | 30 | 102 | 0 | 100 | 17 | 68 | 15 | 30 | 1.88 | 46.03 | 0 | 6631.62 | 883 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.77 | 1200 | 0 | 0 | 0 | 1510.29 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 32.07 | 84 | 0 | 0 | 44 | 201 | 0 | 0 | 0 | 200 | 0 | 396 | 0 | 4.46 | 0 | 49 | 0 | 27 | 0 | 0 | 0 | 0 | 2.6 | 87 | 0.24 | 0 | 290 | 124 | 220 | 0 | 251 | 1125 | 0 | 7082.43 | 13714.05 | 78.81
15:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 18 | 0 | 52 | 95 | 48 | 15 | 17 | 54 | 0 | 180 | 0 | 0 | 0 | 20 | 319 | 0 | 0 | 19 | 142 | 21 | 0 | 0 | 420 | 31 | 0 | 12 | 0 | 12 | 0 | 45 | 0 | 0 | 0 | 2.41 | 60 | 34 | 2 | 935 | 17 | 0 | 19 | 8 | 52 | 213 | 0 | 0 | 0 | 580 | 13 | 20 | 45 | 393 | 0 | 345 | 44 | 10 | 198 | 38 | 18 | 0 | 16 | 0 | 14 | 0 | 206 | 0 | 44 | 22 | 285 | 0 | 324 | 42 | 18 | 149 | 2 | 17 | 0 | 52 | 30 | 100 | 0 | 100 | 0 | 68 | 11 | 32 | 0.19 | 7.89 | 0 | 6579.49 | 883 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.52 | 1222 | 0 | 0 | 0 | 1512.61 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 22.94 | 75 | 0 | 0 | 36 | 202 | 0 | 0 | 0 | 191 | 0 | 401 | 0 | 3.07 | 0 | 50 | 0 | 20 | 0 | 0 | 0 | 0 | 3.5 | 126 | 0.31 | 0 | 290 | 124 | 220 | 0 | 301 | 950 | 0 | 7006.95 | 13586.44 | 78.8
16:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 18 | 0 | 52 | 96 | 48 | 15 | 35 | 54 | 0 | 180 | 0 | 0 | 0 | 35 | 318 | 0 | 0 | 9 | 142 | 21 | 0 | 0 | 460 | 30 | 0 | 13 | 0 | 8 | 0 | 45 | 0 | 0 | 0 | 1.34 | 30 | 34 | 2 | 935 | 120 | 0 | 19 | 8 | 51 | 213 | 0 | 0 | 0 | 580 | 8 | 20 | 45 | 393 | 0 | 300 | 44 | 3 | 197 | 42 | 18 | 0 | 16 | 0 | 19 | 0 | 194 | 0 | 27 | 22 | 285 | 0 | 336 | 42 | 24 | 148 | 2 | 17 | 0 | 0 | 0 | 100 | 0 | 100 | 0 | 68 | 16 | 32 | 0.83 | 27.25 | 4 | 6598.42 | 860 | 222 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.1 | 1219 | 0 | 0 | 0 | 1511.37 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 21.59 | 46 | 0 | 0 | 9 | 202 | 0 | 0 | 0 | 191 | 0 | 402 | 0 | 0.82 | 0 | 50 | 35 | 12 | 0 | 0 | 0 | 0 | 0 | 82 | 0.07 | 1 | 290 | 124 | 220 | 0 | 301 | 875 | 0 | 6797.95 | 13396.37 | 78.79
17:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 18 | 2 | 52 | 143 | 48 | 15 | 35 | 54 | 0 | 160 | 0 | 0 | 0 | 35 | 316 | 0 | 0 | 5 | 142 | 21 | 0 | 0 | 400 | 35 | 16 | 14 | 0 | 5 | 0 | 45 | 0 | 0 | 0 | 0.54 | 60 | 42 | 3 | 935 | 163 | 0 | 19 | 8 | 51 | 213 | 0 | 0 | 0 | 560 | 3 | 20 | 45 | 393 | 0 | 342 | 44 | 15 | 188 | 42 | 17 | 0 | 16 | 0 | 20 | 0 | 176 | 0 | 11 | 30 | 285 | 0 | 336 | 42 | 23 | 153 | 1 | 17 | 0 | 50 | 30 | 101 | 0 | 100 | 5 | 68 | 12 | 31 | 0.33 | 9.11 | 12 | 6735.98 | 860 | 200 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.03 | 1209 | 0 | 0 | 0 | 1503.89 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 9.68 | 14 | 0 | 0 | 8 | 200 | 0 | 0 | 0 | 170 | 0 | 331 | 0 | 0.6 | 0 | 50 | 45 | 4 | 81 | 0 | 0 | 0 | 0 | 34 | 0.06 | 14 | 290 | 124 | 220 | 0 | 303 | 910 | 15 | 6703.26 | 13439.24 | 78.78
18:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 18 | 17 | 70 | 146 | 195 | 15 | 35 | 72 | 0 | 160 | 0 | 0 | 0 | 35 | 310 | 0 | 0 | 1 | 142 | 21 | 0 | 0 | 310 | 43 | 16 | 12 | 0 | 2 | 0 | 45 | 0 | 0 | 0 | 0.01 | 60 | 55 | 5 | 935 | 163 | 0 | 23 | 14 | 51 | 216 | 0 | 0 | 0 | 570 | 0 | 18 | 45 | 393 | 0 | 342 | 44 | 20 | 188 | 42 | 17 | 0 | 69 | 6 | 20 | 0 | 160 | 0 | 1 | 30 | 280 | 0 | 336 | 42 | 24 | 137 | 0 | 17 | 0 | 50 | 30 | 101 | 0 | 100 | 17 | 68 | 18 | 32 | 0 | 0.94 | 12 | 6951.95 | 861 | 200 | 0 | 23 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 3.03 | 1194 | 0 | 0 | 0 | 1508.16 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0.91 | 3 | 0 | 0 | 1.2 | 200 | 0 | 0 | 0 | 150 | 0 | 332 | 0 | 0.12 | 0 | 50 | 50 | 1 | 85 | 0 | 0 | 0 | 0 | 5 | 0.01 | 16 | 290 | 124 | 180 | 0 | 304 | 970 | 17 | 6644.43 | 13596.38 | 78.76
19:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 54 | 17 | 122 | 147 | 294 | 15 | 55 | 54 | 0 | 160 | 0 | 0 | 0 | 35 | 320 | 0 | 0 | 0 | 142 | 21 | 0 | 0 | 350 | 72 | 16 | 12 | 0 | 5 | 34 | 45 | 0 | 0 | 0 | 0 | 60 | 55 | 5 | 935 | 163 | 0 | 47 | 16 | 51 | 216 | 0 | 0 | 0 | 550 | 0 | 66 | 8 | 350 | 91 | 345 | 44 | 14 | 193 | 10 | 48 | 0 | 102 | 9 | 20 | 0 | 146 | 0 | 0 | 30 | 280 | 0 | 349 | 42 | 24 | 143 | 0 | 17 | 0 | 50 | 30 | 100 | 0 | 100 | 17 | 68 | 9 | 33 | 0 | 0 | 12 | 7385 | 843 | 200 | 0 | 27 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1184 | 0 | 0 | 0 | 1509.12 | 0 | 30 | 0 | 35 | 50 | 0 | 75 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 192 | 0 | 0 | 0 | 165 | 0 | 355 | 0 | 0 | 0 | 50 | 70 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 124 | 220 | 0 | 303 | 1050 | 54 | 7026.12 | 14411.12 | 78.74
19:30 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 54 | 17 | 132 | 147 | 294 | 55 | 55 | 54 | 0 | 160 | 0 | 0 | 0 | 35 | 320 | 0 | 0 | 0 | 142 | 21 | 17 | 0 | 400 | 84 | 16 | 12 | 0 | 11 | 34 | 45 | 5 | 0 | 0 | 0 | 60 | 55 | 7 | 935 | 143 | 0 | 50 | 1 | 51 | 217 | 0 | 0 | 0 | 590 | 0 | 142 | 8 | 300 | 15 | 345 | 44 | 5 | 200 | 10 | 54 | 0 | 102 | 9 | 20 | 0 | 142 | 0 | 0 | 30 | 285 | 0 | 349 | 42 | 24 | 144 | 0 | 17 | 0 | 50 | 30 | 101 | 0 | 100 | 17 | 68 | 9 | 33 | 0 | 0 | 12 | 7491 | 774 | 200 | 0 | 33 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1202 | 0 | 0 | 0 | 1497 | 0 | 35 | 0 | 35 | 50 | 0 | 84 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 197 | 0 | 0 | 0 | 192 | 0 | 409 | 0 | 0 | 0 | 50 | 70 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 115 | 220 | 0 | 403 | 1090 | 54 | 7208 | 14699
20:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 54 | 17 | 132 | 147 | 294 | 55 | 55 | 54 | 0 | 160 | 0 | 0 | 0 | 35 | 324 | 0 | 0 | 0 | 142 | 21 | 22 | 0 | 400 | 90 | 16 | 12 | 0 | 4 | 34 | 45 | 14 | 0 | 0 | 0 | 60 | 54 | 7 | 935 | 143 | 0 | 50 | 4 | 51 | 217 | 0 | 0 | 0 | 590 | 0 | 143 | 8 | 310 | 14 | 345 | 44 | 5 | 208 | 10 | 54 | 0 | 103 | 9 | 20 | 0 | 142 | 0 | 0 | 30 | 280 | 0 | 349 | 42 | 24 | 149 | 0 | 17 | 0 | 50 | 30 | 100 | 0 | 100 | 17 | 68 | 9 | 33 | 0 | 0 | 12 | 7528 | 768 | 195 | 0 | 29 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1205 | 0 | 0 | 0 | 1501.85 | 0 | 35 | 0 | 35 | 50 | 0 | 84 | 28 | 0 | 0 | 0 | 24 | 0 | 0 | 197 | 0 | 0 | 0 | 193 | 0 | 408 | 0 | 0 | 0 | 50 | 70 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 126 | 220 | 0 | 393 | 1120 | 54 | 7239.85 | 14767.85 | 78.72
21:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 35 | 17 | 104 | 147 | 294 | 55 | 35 | 35 | 0 | 160 | 0 | 0 | 0 | 35 | 328 | 0 | 0 | 0 | 142 | 21 | 22 | 0 | 340 | 85 | 16 | 11 | 0 | 1 | 34 | 62 | 18 | 0 | 0 | 0 | 60 | 55 | 12 | 935 | 145 | 0 | 50 | 25.5 | 51 | 217 | 0 | 0 | 0 | 580 | 0 | 145 | 8 | 320 | 7 | 330 | 44 | 5 | 211 | 10 | 54 | 0 | 102 | 9 | 20 | 0 | 150 | 0 | 0 | 30 | 270 | 0 | 354 | 42 | 24 | 141 | 0 | 17 | 0 | 50 | 28 | 100 | 0 | 100 | 17 | 68 | 9 | 33 | 0 | 0 | 12 | 7405.5 | 824 | 190 | 0 | 29 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1188 | 0 | 0 | 0 | 1491.54 | 0 | 33 | 0 | 35 | 50 | 0 | 84 | 26 | 0 | 0 | 0 | 24 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 332 | 0 | 0 | 0 | 50 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 290 | 126 | 180 | 0 | 402 | 1182 | 54 | 6998.54 | 14404.04 | 78.7
22:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 17.5 | 17 | 72 | 147 | 294 | 15 | 0 | 35 | 0 | 160 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 142 | 21 | 22 | 0 | 340 | 89 | 16 | 12 | 0 | 0 | 34 | 62 | 18 | 0 | 0 | 0 | 60 | 54 | 22 | 1050 | 145 | 0 | 50 | 25.5 | 51 | 218 | 0 | 0 | 0 | 580 | 0 | 145 | 8 | 335 | 7 | 345 | 44 | 5 | 209 | 10 | 43 | 0 | 103 | 9 | 20 | 0 | 148 | 0 | 0 | 30 | 280 | 0 | 355 | 42 | 24 | 138 | 0 | 17 | 0 | 50 | 25 | 100 | 0 | 100 | 17 | 59 | 9 | 33 | 0 | 0 | 12 | 7388 | 723 | 190 | 0 | 29 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1207 | 0 | 0 | 0 | 1318.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 270 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 120 | 180 | 0 | 403 | 1170 | 26 | 6314.39 | 13702.39 | 78.68
23:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 17 | 62 | 147 | 198 | 15 | 0 | 17 | 0 | 160 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 142 | 21 | 22 | 0 | 435 | 94 | 16 | 12 | 0 | 0 | 34 | 55 | 18 | 0 | 0 | 0 | 60 | 55 | 27 | 1050 | 163 | 0 | 50 | 25.5 | 51 | 218 | 0 | 0 | 0 | 590 | 0 | 36 | 8 | 335 | 7 | 345 | 44 | 5 | 209 | 10 | 23 | 0 | 102 | 9 | 20 | 0 | 156 | 0 | 0 | 30 | 300 | 0 | 355 | 42 | 24 | 144 | 0 | 17 | 0 | 50 | 28 | 101 | 0 | 100 | 17 | 59 | 9 | 33 | 0 | 0 | 12 | 7279.5 | 823 | 194 | 0 | 28 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1172 | 0 | 0 | 0 | 1143.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 250 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 305 | 110 | 180 | 0 | 388 | 1140 | 17 | 6130.26 | 13409.76 | 78.66
Total KWH | 0 | 2217600 | 1061760 | 0 | 0 | 0 | 0 | 0 | 9835200 | 0 | 0 | 258984 | 132840 | 1095264 | 3075360 | 2241371 | 461083 | 264673 | 796320 | 0 | 4338300 | 0 | 0 | 0 | 266289 | 7481694 | 0 | 0 | 195385 | 3256800 | 506400 | 304560 | 0 | 10175454.55 | 1396309 | 158073 | 301440 | 0 | 74880 | 206582 | 1146864 | 132969 | 0 | 0 | 24602 | 1520320 | 1199340 | 330720 | 22574545.46 | 1438545 | 0 | 636000 | 407973.6 | 1101491 | 5164618 | 0 | 0 | 0 | 14170907 | 85185 | 918327 | 1354909 | 8943000 | 175100 | 8208000 | 1053292 | 237600 | 4910000 | 835344 | 557760 | 89515 | 910080 | 89040 | 401610 | 0 | 3878400 | 0 | 508509 | 592128 | 7230000 | 0 | 6202000 | 988000 | 634920 | 3601800 | 47160 | 282768 | 0 | 1428480 | 670176 | 2376000 | 0 | 2404430 | 164880 | 1483200 | 244800 | 1070400 | 11550 | 226810 | 128400 | 162895089.61 | 20801455 | 5493888 | 0 | 367680 | 486400 | 0 | 0 | 0 | 0 | 0 | 0 | 648000 | 28545450 | 0 | 0 | 0 | 35088378 | 0 | 475808 | 0 | 288576 | 377856 | 0 | 311728 | 181874 | 0 | 331800 | 628710 | 312115 | 0 | 309744 | 4301000 | 0 | 0 | 0 | 4342936 | 0 | 8751709 | 0 | 30780 | 0 | 1164218 | 328664 | 148523 | 529161 | 0 | 0 | 0 | 25881.36 | 664560 | 3450 | 298944 | 6981000 | 2963000 | 5301620 | 0 | 6901818 | 27778909.09 | 430800 | 165596435.45 | 328491525.06

## Forecast (2)
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 19-04-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-04-2026 | during | 19-04-2026 | during | 19-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 410 | 410 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 160 | 450 | 450 | 226 | 226 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 322 | 324 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 94 | 147 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 21 | 33 | 33 | 29 | 29 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 50 | 50 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 48 | 294 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 132 | 52 | 132 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 54 | 162 | 162 | 35 | 35 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 450 | 400 | 584 | 584 | 526 | 526 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 142 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1897 | 2477 | 5850.22 | 5898.22 | 2637.55 | 2659.55
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 4 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50 | 19 | 48 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 60 | 70 | 70 | 70 | 70 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 217 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 47 | 51 | 105 | 105 | 34 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 47 | 45 | 56 | 64 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 68 | 68 | 34 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 7 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 12 | 12 | 108 | 108 | 38 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.77 | 0 | 1.54 | 0 | 1.54 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 14 | 54.36 | 54.36 | 0 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 34 | 54 | 110 | 110 | 54 | 54 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 15 | 90 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 17 | 143 | 163 | 163 | 17 | 163 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 586 | 590 | 1224 | 1224 | 612 | 612 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 2 | 4 | 6 | 5 | 6 | 5 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 935 | 935 | 935 | 935 | 935 | 935 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2011.77 | 2326 | 3830.4 | 3824.86 | 2296.04 | 2533.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 200 | 208 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 0 | 14 | 240 | 240 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 342 | 345 | 342.01 | 342.01 | 342.01 | 342.01 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 341 | 310 | 393 | 393 | 350 | 350 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 39 | 10 | 41.65 | 41.65 | 37 | 37 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 20 | 5 | 52.82 | 52.82 | 6 | 6 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 127 | 8 | 195 | 195 | 96 | 96 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Machine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 143 | 150 | 150 | 20 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 22 | 30 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 103 | 200 | 200 | 35 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 172 | 142 | 84 | 82 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 2 | 9 | 113 | 113 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 54 | 115 | 115 | 17 | 51 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.745 | 1445 | 1445 | 2654.18 | 2582.18 | 1443.01 | 1672.01
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-04-2026 | during | 19-04-2026 | during | 19-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 35 | 33 | 157.5 | 157.5 | 50 | 50 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.34 | 0 | 1.8 | 0 | 1.8 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 70 | 70 | 10 | 10 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 68 | 10 | 10 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 39.18 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 152.52 | 139 | 357.8 | 314 | 192.8 | 149
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 24 | 30 | 30 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 149 | 163 | 163 | 153 | 153 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 100 | 100 | 100 | 100 | 110 | 110 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 50 | 83 | 83 | 76 | 76 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 100 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 17 | 25 | 25 | 17 | 17 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 280 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 324 | 349 | 350 | 350 | 350 | 350 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1162 | 1141 | 1264 | 1264 | 1185 | 1185
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 884 | 768 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 29 | 32 | 32 | 25 | 25 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 48 | 50 | 50 | 30 | 30 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 195 | 410 | 410 | 250.03 | 250.03 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 97.01 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1156 | 1205 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2387.01 | 2245 | 3581.2 | 3496.2 | 2639.33 | 2554.33
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 252 | 393 | 250 | 400 | 250 | 400 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 126 | 126 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1165 | 1120 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 290 | 290 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.64 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2053.64 | 2219 | 2412 | 2561 | 2268 | 2417
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 42.78 | 0 | 60 | 0 | 60 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 35 | 40 | 40 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 200 | 197 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 190 | 193 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 406 | 408 | 413.79 | 413.79 | 408 | 408 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 32 | 32 | 25 | 25 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 84 | 100 | 100 | 0 | 51 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 1 | 1 | BPDB event of default
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.72 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1468.35 | 1501.85 | 1435.88 | 1435.88 | 1356 | 1356 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 40 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 96 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2447.85 | 2555.85 | 3244.72 | 3017.87 | 2508.45 | 2367.6
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 50 | 48 | 48 | 51 | 51 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 100 | 113 | 113 | 35 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.8 | 0 | 6.8 | 0 | 6.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 0.01 | 0.01 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 8 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 117 | 0 | 71 | 0 | 71 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 175.8 | 220 | 397.8 | 290 | 193.81 | 86.01
System Total |  |  |  |  | 28823.2 | 29269.987 | 13732.59 | 14767.85 | 23592.32 | 23248.33 | 15363.99 | 15624
Forecast Scenario (19-04-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13550 |  | 0 |  | 13550
|  |  |  | 1:00 | 12900 |  | 0 |  | 12900
|  |  |  | 2:00 | 13190 |  | 0 |  | 13190
|  |  |  | 3:00 | 13090 |  | 0 |  | 13090
|  |  |  | 4:00 | 12990 |  | 0 |  | 12990
|  |  |  | 5:00 | 12890 |  | 0 |  | 12890
|  |  |  | 6:00 | 12800 |  | 0 |  | 12800
|  |  |  | 7:00 | 13000 |  | 0 |  | 13000
|  |  |  | 8:00 | 13050 |  | 0 |  | 13050
|  |  |  | 9:00 | 13300 |  | 0 |  | 13300
|  |  |  | 10:00 | 13700 |  | 0 |  | 13700
|  |  |  | 11:00 | 14300 |  | 0 |  | 14300
|  |  |  | 12:00 | 14500 |  | 0 |  | 14500
|  |  |  | 13:00 | 14700 |  | 0 |  | 14700
|  |  |  | 14:00 | 14750 |  | 0 |  | 14750
|  |  |  | 15:00 | 14650 |  | 0 |  | 14650
|  |  |  | 16:00 | 14450 |  | 0 |  | 14450
|  |  |  | 17:00 | 14200 |  | 0 |  | 14200
|  |  |  | 18:00 | 14550 |  | 0 |  | 14550
|  |  |  | 18:30 | 14943.43 |  | 339.5693 |  | 15299
|  |  |  | 19:00 | 15139.16 |  | 1300 |  | 16500
|  |  |  | 19:30 | 15150.16 |  | 744.7472 |  | 15930
|  |  |  | 20:00 | 15156.16 |  | 557.5672 |  | 15740
|  |  |  | 21:00 | 15000 |  | 0 |  | 15000
|  |  |  | 22:00 | 14500 |  | 0 |  | 14500
|  |  |  | 23:00 | 14200 |  | 0 |  | 14200
Probable Maximum Temperature: |  |  | 35.60°C
Probable Maximum Demand at Day Peak: |  |  | 14500.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15156.16 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 334.55532 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:30 hrs on 19-04-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 19-04-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-04-2026 | during | 19-04-2026 | during | 19-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 410 | 410 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 160 | 450 | 450 | 226 | 226 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 322 | 324 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 94 | 147 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 21 | 33 | 33 | 29 | 29 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 50 | 50 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 48 | 294 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 132 | 52 | 132 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 54 | 162 | 162 | 35 | 35 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 450 | 400 | 584 | 584 | 526 | 526 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 142 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1897 | 2477 | 5850.22 | 5898.22 | 2637.55 | 2659.55
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 4 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50 | 19 | 48 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 60 | 70 | 70 | 70 | 70 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 217 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 47 | 51 | 105 | 105 | 34 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 47 | 45 | 56 | 64 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 68 | 68 | 34 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 7 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 12 | 12 | 108 | 108 | 38 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.77 | 0 | 1.54 | 0 | 1.54 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 14 | 54.36 | 54.36 | 0 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 34 | 54 | 110 | 110 | 54 | 54 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 15 | 90 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 17 | 143 | 163 | 163 | 17 | 163 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 586 | 590 | 1224 | 1224 | 612 | 612 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 2 | 4 | 6 | 5 | 6 | 5 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 935 | 935 | 935 | 935 | 935 | 935 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2011.77 | 2326 | 3830.4 | 3824.86 | 2296.04 | 2533.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 200 | 208 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 0 | 14 | 240 | 240 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 342 | 345 | 342.01 | 342.01 | 342.01 | 342.01 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 341 | 310 | 393 | 393 | 350 | 350 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 39 | 10 | 41.65 | 41.65 | 37 | 37 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 20 | 5 | 52.82 | 52.82 | 6 | 6 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 127 | 8 | 195 | 195 | 96 | 96 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Machine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 143 | 150 | 150 | 20 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 22 | 30 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 103 | 200 | 200 | 35 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 172 | 142 | 84 | 82 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 2 | 9 | 113 | 113 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 54 | 115 | 115 | 17 | 51 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.745 | 1445 | 1445 | 2654.18 | 2582.18 | 1443.01 | 1672.01
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-04-2026 | during | 19-04-2026 | during | 19-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 35 | 33 | 157.5 | 157.5 | 50 | 50 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.34 | 0 | 1.8 | 0 | 1.8 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 70 | 70 | 10 | 10 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 68 | 10 | 10 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 39.18 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 152.52 | 139 | 357.8 | 314 | 192.8 | 149
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 24 | 30 | 30 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 149 | 163 | 163 | 153 | 153 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 100 | 100 | 100 | 100 | 110 | 110 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 50 | 83 | 83 | 76 | 76 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 100 | 100 | 100 | 100 | 100 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 17 | 25 | 25 | 17 | 17 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 280 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 324 | 349 | 350 | 350 | 350 | 350 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1162 | 1141 | 1264 | 1264 | 1185 | 1185
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 884 | 768 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 29 | 32 | 32 | 25 | 25 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 48 | 50 | 50 | 30 | 30 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 195 | 410 | 410 | 250.03 | 250.03 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 97.01 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1156 | 1205 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2387.01 | 2245 | 3581.2 | 3496.2 | 2639.33 | 2554.33
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 252 | 393 | 250 | 400 | 250 | 400 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 126 | 126 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1165 | 1120 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 290 | 290 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.64 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2053.64 | 2219 | 2412 | 2561 | 2268 | 2417
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 42.78 | 0 | 60 | 0 | 60 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 35 | 40 | 40 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 200 | 197 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 190 | 193 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 406 | 408 | 413.79 | 413.79 | 408 | 408 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 32 | 32 | 25 | 25 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 84 | 100 | 100 | 0 | 51 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 1 | 1 | BPDB event of default
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.72 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1468.35 | 1501.85 | 1435.88 | 1435.88 | 1356 | 1356 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 40 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 96 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2447.85 | 2555.85 | 3244.72 | 3017.87 | 2508.45 | 2367.6
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 50 | 48 | 48 | 51 | 51 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 100 | 113 | 113 | 35 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.8 | 0 | 6.8 | 0 | 6.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 0.01 | 0.01 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 8 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 117 | 0 | 71 | 0 | 71 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 175.8 | 220 | 397.8 | 290 | 193.81 | 86.01
System Total |  |  |  |  | 28823.2 | 29269.987 | 13732.59 | 14767.85 | 23592.32 | 23248.33 | 15363.99 | 15624
Forecast Scenario (19-04-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13550 |  | 0 |  | 13550
|  |  |  | 1:00 | 12900 |  | 0 |  | 12900
|  |  |  | 2:00 | 13190 |  | 0 |  | 13190
|  |  |  | 3:00 | 13090 |  | 0 |  | 13090
|  |  |  | 4:00 | 12990 |  | 0 |  | 12990
|  |  |  | 5:00 | 12890 |  | 0 |  | 12890
|  |  |  | 6:00 | 12800 |  | 0 |  | 12800
|  |  |  | 7:00 | 13000 |  | 0 |  | 13000
|  |  |  | 8:00 | 13050 |  | 0 |  | 13050
|  |  |  | 9:00 | 13300 |  | 0 |  | 13300
|  |  |  | 10:00 | 13700 |  | 0 |  | 13700
|  |  |  | 11:00 | 14300 |  | 0 |  | 14300
|  |  |  | 12:00 | 14500 |  | 0 |  | 14500
|  |  |  | 13:00 | 14700 |  | 0 |  | 14700
|  |  |  | 14:00 | 14750 |  | 0 |  | 14750
|  |  |  | 15:00 | 14650 |  | 0 |  | 14650
|  |  |  | 16:00 | 14450 |  | 0 |  | 14450
|  |  |  | 17:00 | 14200 |  | 0 |  | 14200
|  |  |  | 18:00 | 14550 |  | 0 |  | 14550
|  |  |  | 18:30 | 14943.43 |  | 339.5693 |  | 15299
|  |  |  | 19:00 | 15139.16 |  | 822.1022 |  | 16000
|  |  |  | 19:30 | 15150.16 |  | 744.7472 |  | 15930
|  |  |  | 20:00 | 15156.16 |  | 557.5672 |  | 15740
|  |  |  | 21:00 | 15000 |  | 0 |  | 15000
|  |  |  | 22:00 | 14500 |  | 0 |  | 14500
|  |  |  | 23:00 | 14200 |  | 0 |  | 14200
Probable Maximum Temperature: |  |  | 35.60°C
Probable Maximum Demand at Day Peak: |  |  | 14500.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15156.16 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 334.55532 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:30 hrs on 19-04-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 18-04-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13732.59 | MW | 11:00 Hr. | Energy Generated |  |  | 328.4915 |  | MKWHr.
| Day Peak Demand |  |  | 14452.98 | MW | 12:00 Hr. | Energy Unserverd |  |  | 13.807 |  | MKWHr.
| Evening Peak Generation |  |  | 14767.85 | MW | 20:00 Hr. | Energy Demand |  |  | 342.2985 |  | MKWHr.
| Evening Peak Demand |  |  | 15722.12 | MW | 19:00 Hr. | Maximum Temperature |  |  | 35.5 |  | °C
| Minimum Generation of the Day |  |  | 13115.52 | MW | 01:00 Hr. | Total Gas Supplied |  |  | 895.63 |  | MMCFD
| Maximum Generation of the Day |  |  | 14767.85 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 6.5968 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.6416 | 0 | 15.1283 | 0 | 0 | 0.19539 | 0 | 0 | 47.9653 | Gas | 122.3884 | Gas | 432526561.8735
| Chattogram Zone |  |  | 5.4953 | 36.7455 | 8.1256 | 0 | 1.5203 | 0.10979 | 0 | 0.07488 | 52.0714 | Coal | 108.1168 | Coal | 735618553.7835
| Cumilla Zone |  |  | 26.2084 | 0 | 3.0673 | 0 | 0 | 0.50851 | 3.8784 | 0 | 33.6626 | HFO | 32.7322 | HFO | 586244662.96
| Mymensingh Zone |  |  | 1.0704 | 0 | 2.0213 | 0 | 0 | 0.23836 | 0 | 0 | 3.33 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.8186 | 0 | 0 | 0 | 0 | 0.04716 | 0 | 0 | 25.8657 | Hydro | 1.5203 | Hydro | 152032
| Khulna Zone |  |  | 5.4939 | 28.5454 | 0.85408 | 0 | 0 | 0.648 | 20.8015 | 0 | 56.3429 | Solar | 3.8906 | Solar | 60702401.822
| Barishal Zone |  |  | 8.2646 | 41.6617 | 0.72974 | 0 | 0 | 0.00345 | 0 | 0 | 50.6595 | Import | 59.7682 | Import | 350663266.57
| Rajshahi Zone |  |  | 17.3956 | 0 | 1.948 | 0 | 0 | 1.301 | 35.0884 | 0 | 55.733 | Wind | 0.07488 | Wind | 1101484.8
| Rangpur Zone |  |  | 0 | 1.1642 | 0.85782 | 0 | 0 | 0.83896 | 0 | 0 | 2.861
| Total |  |  | 122.3884 | 108.1168 | 32.7322 | 0 | 1.5203 | 3.8906 | 59.7682 | 0.07488 | 328.4915
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 432526561.8735 |  | Hydro | 152032
|  |  |  | Coal | 735618553.7835 |  | Solar | 60702401.822
|  |  |  | HFO | 586244662.96 |  | Import | 350663266.57
|  |  |  | HSD | 0 |  | Wind | 1101484.8
[5 empty] | Total: | 216,70,08,963 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.8015 | Peak Hr Flow | 768.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 51588000 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 35.0884 | Peak Hr Flow | 1501.85 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2795 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.8784 | Peak Hr Flow | 142.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2953 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 59.7682 | Peak Hr Flow | 2411.85 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5618
|  |  |  | Chattogram |  | 95 |  | 1520
|  |  |  | Cumilla |  | 110 |  | 1488
|  |  |  | Mymensingh |  | 100 |  | 1119
|  |  |  | Sylhet |  | 30 |  | 610
|  |  |  | Khulna |  | 145 |  | 1899
|  |  |  | Barishal |  | 0 |  | 488
|  |  |  | Rajshahi |  | 110 |  | 1601
|  |  |  | Rangpur |  | 53 |  | 615
|  |  |  | Total |  | 643 |  | 14958
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 320
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:01 | 18:07 | Gollamari 132/33kV S/S Tr-2 LT Scheduled S/D Due to Paint job
| 08:02 | 18:06 | Gollamari 132/33kV S/S Tr-2 HT Scheduled S/D
|  | 09:02 | Jamalpur 132/33kV S/S T-2 LT is restored.
|  | 09:02 | Jamalpur 132/33kV S/S T-2 HT is restored.
| 10:15 | 12:20 | Pubail 132/33kV S/S TRX-2 LT Project Work S/D Due to Incommer-2 CT maintenance
| 10:18 | 12:17 | Pubail 132/33kV S/S TRX-2 HT Project Work S/D Due to Ct maintenance
| 10:30 | 18:07 | Thakurgaon 132/33kV S/S Panchagar CKT-2 Scheduled S/D Due to RTU communication works
| 10:31 | 18:08 | Panchagarh 132/33kV S/S Thakurgaon- 2 Scheduled S/D Due to RTU Integration with NLDC
|  | 10:35 | Haripur 230/132kV S/S Auto TR-1 LT is restored.
|  | 10:35 | Haripur 230/132kV S/S Auto TR-1 HT is restored.
| 10:40 | 12:35 | Haripur 230/132kV S/S Auto TR-2 LT Scheduled S/D Due to Corrective maintenance of
different high temperature junction points of ATR-2 230and 132 kV bays.
| 10:40 | 12:34 | Haripur 230/132kV S/S Auto TR-2 HT Scheduled S/D Due to Corrective maintenance of
different high temperature junction points of ATR-2 230and 132 kV bays.
| 10:52 | 20:56 | BIPTC S/S Baharampur-2 Scheduled S/D
| 11:00 |  | Day Peak Generation is 13728 MW.
| 11:00 | 12:20 | Haripur 230/132kV S/S 132kV Bus Coupler Scheduled S/D Due to Corrective maintenance of
different high temperature junction points of ATR-2 230and 132 kV bays.
| 11:00 | 12:20 | Haripur 230/132kV S/S 132kV Main Bus Sec-2 Scheduled S/D Due to Corrective maintenance of
different high temperature junction points of ATR-2 132 kV bays.
| 11:27 | 15:32 | Chowmuhani-Feni 132 kV Ckt-1 Tripped from Feni 230/132kV end showing K861 & K862 relays
Due to Due to fault at 33kv side at Feni 132/33 kv substation and from Feni 132/33kV end
showing Distance and O/C Relay relays Due to Due increase Sag
|  | 12:21 | Haripur 230/132kV S/S 132kV Main Bus Sec-1 is restored.
| 12:22 | 14:12 | Pubail 132/33kV S/S TRX-1 HT Project Work S/D Due to 33kV CT Maintenance.
| 12:22 | 14:12 | Pubail 132/33kV S/S TRX-1 LT Project Work S/D Due to 33kV CT Maintenance.
| 13:16 | 15:33 | Chowmuhani-Feni 132 kV Ckt-2 Scheduled S/D from Feni 132/33kV end Due to For BPDB
Required and from Feni 230/132kV end Due to Due to work at feni 132/33 kv grid end
| 15:04 |  | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Tripped from Shahjibazar 132/33kV end showing
Distance Relay relays Due to Bad Weather and from Brahmanbaria 132/33kV end showing MiCOM
relays.
| 15:17 | 15:30 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Tripped from Brahmanbaria 132/33kV end showing ABB
relays.
| 15:17 | 15:35 | Brahmanbaria-Shahjibazar 132 kV Ckt-1 Tripped from Shahjibazar 132/33kV end showing
Distance Realy relays Due to Bad Weather and from Brahmanbaria 132/33kV end showing MiCOM
relays.
| 15:31 | 16:23 | Shahjibazar 132/33kV S/S BPDB 60 MW Tripped showing CB Tripping Relay relays Due to Bad
weather
| 15:34 | 15:57 | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 LT Scheduled S/D Due to Due to High
temperature of DS-181S .
|  | 16:00 | Aminbazar-Airport(Old) 230kV Ckt-2 is restored.
| 16:34 | 17:13 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT Tripped showing P40 Agile relays Due to PDB 33 KV | [7 empty] | 15.0MW load
|  |  | Mollapara feeder trip | [7 empty] | interrup.
| 16:34 | 17:13 | Kishoreganj 132/33kV S/S Tr-2 (414T) LT Tripped showing P40 Agile relays Due to PDB 33 KV | [7 empty] | 15.0MW load
|  |  | Mollapara feeder trip | [7 empty] | interrup.
| 16:42 | 16:55 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-1 Tripped showing Distant relay Operated
at 24.2km relays Due to Distance relay trip
|  | 18:15 | Aminbazar 400/230/132kV S/S Bus-2 (400kV) is restored.
| 18:21 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- gt
| 19:40 |  | Shahjadpur 132/33kV S/S T-1(405T) HT Forced S/D Due to Red hot Maintenance
| 19:41 |  | Shahjadpur 132/33kV S/S T-1(405T) LT Forced S/D Due to Red-hot maintenance work.
| 20:19 | 20:37 | Kushtia 132/33kV S/S T-3 HT Tripped showing Protection Relay relays Due to HV O/C | [7 empty] | 104.0MW load
interrup.
| 20:19 | 20:38 | Kushtia 132/33kV S/S T-3 LT Tripped showing Protection relay relays Due to HV O/C | [7 empty] | 103.0MW load
interrup.
| 20:28 |  | Juldah 132/33kV S/S 132/33 KV 406T T-1 HT Tripped showing Over current relay. relays Due
to Due to the explosion of the R-phase cable on the 33 KV side of the transformer.
| 20:28 |  | Juldah 132/33kV S/S 132/33 KV 406T T-1 LT Tripped showing Over Current relay. relays Due
to Due to the explosion of the R-phase cable on the 33 KV side of the transformer.
| 23:04 |  | Chandpur CCPP GT was synchronized
| 00:26 | 01:11 | Rahanpur 132/33kV S/S TR-2 (414T) LT Tripped showing Agile relays. | [7 empty] | 3.0MW load
interrup.
| 00:26 | 01:08 | Rahanpur 132/33kV S/S TR-1 404T HT Tripped showing Simens 7UT85 relays Due to Over
Voltage
| 00:26 | 01:09 | Rahanpur 132/33kV S/S TR-1 404T LT Tripped showing Agile relays.
| 00:26 | 01:11 | Rahanpur 132/33kV S/S TR-2 (414T) HT Tripped showing Siemens 7UT85 relays Due to Over | [7 empty] | 3.0MW load
|  |  | Voltage | [7 empty] | interrup.
| 00:30 | 01:40 | Niamatpur 132/33kV S/S Transformer-2 (417T) HT Tripped showing SIEMENS-7UT85 relays Due | [7 empty] | 28.0MW load
|  |  | to Overvolt, Definite, Overexcitation | [7 empty] | interrup.
| 00:30 | 01:40 | Niamatpur 132/33kV S/S Transformer-2 (417T) LT Tripped showing SIEMENS relays Due to | [7 empty] | 28.0MW load
|  |  | Overvolt | [7 empty] | interrup.
| 01:19 | 01:40 | Chattak-Sunamganj 132 kV Ckt-1 Tripped from Sunamganj 132/33kV end showing REL670 relays | [7 empty] | 19.0MW load
|  |  | Due to Tripped chhatak-sunamgonj CKT-1 from sylhet for northwester | [7 empty] | interrup. Sunamganj
132/33kV end
| 01:19 | 01:40 | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 Tripped showing REC670 And REL670 relays | [7 empty] | 19.0MW load
|  |  | Due to Tripped chhatak-sunamgonj CKT-2 from sylhet for northwester | [7 empty] | interrup.
| 01:20 | 01:41 | Chattak-Sylhet 132 kV Ckt-2 Tripped from Sylhet 132/33kV end showing Distance Realay | [7 empty] | 20.0MW load
|  |  | relays Due to Thundering | [7 empty] | interrup. Sylhet
132/33kV end
| 02:04 |  | Ishwardi-Rooppur 132kV Ckt-1 Tripped from Ruppur 132/11kV end showing Distance
relay,K31. relays.
| 02:05 |  | Ishwardi-Rooppur 132kV Ckt-2 Tripped from Ishurdi 132/33kV end showing Distance
protection relay relays.
| 02:26 | 03:24 | Fenchuganj-Sreemangal 132kV Ckt-1 Tripped from Sreemongol 132/33kV end showing Distance
Relay relays Due to distance relay phase A
| 06:00 |  | Minimum generation 11690 MW
| 06:00 |  | Minimum generation 11690 MW
| 06:24 |  | Jhenaidah 132/33kV S/S Transformer T-3 LT Forced S/D Due to 33kV CB B-Phase Redhot
Maintenance.
| 06:24 |  | Jhenaidah 132/33kV S/S Transformer T-3 HT Forced S/D Due to 33kV CB B-Phase Redhot
Maintenance.
| 07:32 |  | Gollamari 132/33kV S/S Tr-2 HT Project Work S/D Due to TR-02 Body painitng work.
| 07:32 |  | Gollamari 132/33kV S/S Tr-2 LT Project Work S/D
| 07:33 |  | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT Forced S/D
| 07:35 |  | Rajshahi 132/33kV S/S Transformer T-2(415T) HT Forced S/D Due to T2 T3 bus coupler DS er | [7 empty] | 25.0MW load
|  |  | post insulator change | [7 empty] | interrup.
| 07:40 |  | Pabna 132/33kV S/S T-2 LT Scheduled S/D Due to None | [7 empty] | 14.0MW load
interrup.
| 07:40 |  | Pabna 132/33kV S/S T-2 HT Scheduled S/D | [7 empty] | 14.0MW load
interrup.
| 07:57 |  | Ashuganj 450 MW CCPP(South), FGMO is OFF with remarks:-
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 18-04-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 410 | 9835200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 160 | 4338300 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 461083 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 324 | 7481694 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 258984 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 147 | 3075360 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 264673 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 266289 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 506400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 304560 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 1061760 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 294 | 2241371 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 1095264 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2217600 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 796320 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 195385 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 132840 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 10175454.55 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3256800 | Engine Problem
Dhaka Area Total |  |  |  |  | 6668.974 | 2477 | 47965337.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 4 | 407973.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 85185 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 636000 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 60 | 1520320 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5164618 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 1101491 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 45 | 1146864 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 206582 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 7 | 330720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 301440 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24602 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 158073 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 14 | 132969 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 54 | 1199340 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 90 | 1396309 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 143 | 1438545 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 590 | 14170907 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 4 | 74880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 935 | 22574545.46 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 2326 | 52071364.06
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 208 | 4910000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 14 | 175100 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 345 | 8208000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 310 | 8943000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 10 | 835344 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 5 | 237600 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 1354909 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1053292 | Machine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 143 | 918327 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 30 | 592128 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 89515 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 103 | 910080 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 142 | 3878400 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 401610 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 89040 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 54 | 557760 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 508509 | -
Cumilla Area Total |  |  |  |  | 2870.745 | 1445 | 33662614
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 33 | 1070400 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11550 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 244800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1483200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 226810 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 128400 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 164880 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 139 | 3330040
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 47160 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 988000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 24 | 634920 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 149 | 3601800 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 100 | 2376000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 670176 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 50 | 1428480 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2404430 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 282768 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7230000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 349 | 6202000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1141 | 25865734
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 768 | 20801455 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 29 | 367680 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 48 | 486400 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 195 | 5493888 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 648000 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1205 | 28545450 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2245 | 56342873
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 393 | 6901818 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 298944 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 126 | 2963000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1120 | 27778909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5301620 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 430800 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 290 | 6981000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3450 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2219 | 50659541.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 331800 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 35 | 475808 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 181874 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 197 | 4301000 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 193 | 4342936 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 408 | 8751709 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 312115 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 84 | 311728 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 377856 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 288576 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30780 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1501.85 | 35088378 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 309744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 628710 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2555.85 | 55733014
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1164218 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 100 | 529161 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 25881.36 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 328664 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 148523 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 664560 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 220 | 2861007.36
Eastern Grid Total |  |  |  |  | 17417.792 | 7528 | 162895089.61
Western Grid Total |  |  |  |  | 11852.195 | 7239.85 | 165596435.45
National Grid Total |  |  |  |  | 29269.987 | 14767.85 | 328491525.06
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 18-04-2026
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10020.29 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4295 | MW
i) Dhaka area |  |  | 5618.49 |  | MW | i) Khulna area |  |  |  | 1754 | MW
ii) Chattogram area |  |  | 1424.8 |  | MW | ii) Barishal area |  |  |  | 488 | MW
iii) Cumilla area |  |  | 1378 |  | MW | iii) Rajshahi area |  |  |  | 1491 | MW
iv) Mymensingh area |  |  | 1019 |  | MW | iv) Rangpur area |  |  |  | 562 | MW
v) Sylhet area |  |  | 580 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14315.29 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 00:00 | 67 | Hasnabad | 110 | 19:30 | 133 | Natore | 192 | 19:30
2 | AKSML | 10 | 23:00 | 68 | Hathazari | 95 | 18:30 | 134 | Nawabganj | 58.6 | 20:00
3 | Aftabnagar | 42 | 19:00 | 69 | Hatirjheel | 43 | 15:00 | 135 | Netrakona | 117 | 18:30
4 | Agargaon | 118 | 13:00 | 70 | Ishurdi | 95 | 19:30 | 136 | New | 78.7 | 12:00
5 | Agrabad | 70 | 15:00 | 71 | Jaldhaka | 64 | 18:00 | 137 | Niamatpur | 112 | 07:00
6 | Amnura | 45 | 18:30 | 72 | Jamalpur | 98 | 00:00 | 138 | Noapara | 47 | 22:00
7 | Ashuganj | 70 | 23:00 | 73 | Jashore | 160 | 21:00 | 139 | PHP | 6 | 14:00
8 | BSRM | 196 | 16:00 | 74 | Jhenaidah | 106 | 21:00 | 140 | Pabna | 116 | 20:00
9 | Bagerhat | 90 | 22:00 | 75 | Joydebpur | 165 | 19:00 | 141 | Palashbari | 116 | 12:00
10 | Bajitpur | 86 | 03:00 | 76 | Joypurhat | 68 | 07:00 | 142 | Panchagarh | 40 | 07:00
11 | Bakerganj | 15 | 20:00 | 77 | Juldah | 22 | 17:00 | 143 | Patiya | 10 | 15:00
12 | Bakulia | 94 | 00:00 | 78 | KSRM | 14 | 16:00 | 144 | Patuakhali | 71 | 20:00
13 | Banani | 38.6 | 15:00 | 79 | Kabirpur | 264 | 19:00 | 145 | Payra | 32 | 20:00
14 | Bangabhaban | 8 | 11:00 | 80 | Kachua | 95 | 23:00 | 146 | Postogola | 58 | 13:00
15 | Barapukuria | 63 | 09:00 | 81 | Kaliganj | 32 | 19:00 | 147 | Pubail | 35 | 21:00
16 | Barguna | 22 | 19:30 | 82 | Kallyanpur | 120 | 14:00 | 148 | Purbachal | 35 | 13:00
17 | Barishal | 113 | 12:00 | 83 | Kalurghat | 41 | 19:30 | 149 | Purbasadipur | 115 | 11:00
18 | Barishal-230 | 102 | 19:30 | 84 | Kamrangirchar | 82 | 12:00 | 150 | Rahanpur | 37 | 06:00
19 | Baroaulia | 66 | 14:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 26 | 17:00
20 | Baroirhat | 55 | 20:00 | 86 | Kasba | 37 | 22:00 | 152 | Rajbari | 80 | 23:00
21 | Bashundhara | 207 | 14:00 | 87 | Kazla | 125 | 12:00 | 153 | Rajendrapur | 129 | 19:00
22 | BashundharaCement | 12 | 16:00 | 88 | Keranigonj | 94 | 19:30 | 154 | Rajshahi | 114 | 02:00
23 | Beanibazar | 72 | 20:00 | 89 | Khagrachori | 36 | 19:00 | 155 | Rajshahi-230 | 94 | 17:00
24 | Benapole | 82 | 23:00 | 90 | Khulna | 94 | 13:00 | 156 | Ramganj | 122 | 21:00
25 | Bhaluka | 133 | 21:00 | 91 | Khulshi | 165 | 01:00 | 157 | Rampur | 46 | 23:00
26 | Bhandaria | 57 | 22:00 | 92 | Kishoreganj | 110 | 21:00 | 158 | Rangamati | 19 | 19:00
27 | Bhangura | 48 | 21:00 | 93 | Kodda | 313 | 21:00 | 159 | Rangpur | 132 | 19:30
28 | Bheramara(GK) | 67 | 13:00 | 94 | Kulaura | 50 | 18:30 | 160 | Ruppur | 2.6 | 12:00
29 | Bhulta | 222 | 07:00 | 95 | Kurigram | 54 | 18:00 | 161 | SSM | 5 | 23:00
30 | Bog-Sherpur | 88 | 21:00 | 96 | Kushtia | 148 | 13:00 | 162 | Saidpur | 105 | 10:00
31 | Bogura | 186 | 19:30 | 97 | Laksam | 22 | 23:00 | 163 | Satkhira | 142 | 22:00
32 | Borhanuddin | 94 | 19:30 | 98 | Lakshmipur | 43 | 22:00 | 164 | Satmasjid | 111 | 13:00
33 | Brahmanbaria | 120 | 05:00 | 99 | Lalbag | 78 | 13:00 | 165 | Savar | 231 | 19:30
34 | Cantonment | 140 | 12:00 | 100 | Lalmonirhat | 40 | 05:00 | 166 | SevenRings | 8.89 | 20:00
35 | Chandina | 43 | 18:30 | 101 | MI_Cement | 17.6 | 00:00 | 167 | ShahCement | 46 | 19:30
36 | Chandpur | 89 | 19:30 | 102 | Madanganj | 43 | 21:00 | 168 | Shahjadpur | 87 | 07:00
37 | Chandraghona | 39 | 18:30 | 103 | Madaripur | 127 | 21:00 | 169 | Shahjibazar | 119 | 21:00
38 | Chapai | 81 | 05:00 | 104 | Madartek | 94 | 23:00 | 170 | Shahmirpur | 56 | 20:00
39 | Charsaidpur | 43 | 12:00 | 105 | Madunaghat | 58 | 20:00 | 171 | Shariatpur | 94 | 22:00
40 | Chauddagram | 90 | 20:00 | 106 | Magura | 63 | 13:00 | 172 | Sherpur | 118 | 07:00
41 | Chhatak | 40 | 22:00 | 107 | Mahasthangarh | 84 | 21:00 | 173 | Shikalbaha | 27 | 19:30
42 | Chowmuhani | 137 | 21:00 | 108 | Maijdee | 45 | 23:00 | 174 | Shitalakhya | 90.1 | 16:00
43 | Chuadanga | 131 | 20:00 | 109 | Manikganj | 139 | 21:00 | 175 | Sholosohor | 48 | 18:30
44 | Coxsbazar | 128 | 20:00 | 110 | Maniknagar | 55 | 22:00 | 176 | Shyampur | 180 | 12:00
45 | Cumilla(N) | 137 | 22:00 | 111 | Matarbari | 56 | 20:00 | 177 | Siddhirganj | 135 | 15:00
46 | Cumilla(S) | 205 | 15:00 | 112 | Matuail | 82 | 12:00 | 178 | Sirajganj | 132 | 20:00
47 | Daganbhuiyan | 39 | 22:00 | 113 | Metrorail_Motijheel | 23 | 19:00 | 179 | Sonargaon | 158 | 08:00
48 | Daudkandi | 137 | 22:00 | 114 | Metrorail_Uttara | 5 | 11:00 | 180 | Sreemongol | 79 | 22:00
49 | DhakaUniversity | 76 | 13:00 | 115 | Millgate | 108 | 15:00 | 181 | Sreepur | 115 | 19:30
50 | Dhamrai | 130 | 19:30 | 116 | Mirpur | 146 | 15:00 | 182 | Srinagar | 54.9 | 21:00
51 | Dhanmondi | 128 | 13:00 | 117 | Mirsorai | 51 | 12:00 | 183 | Sunamganj | 54 | 21:00
52 | Dohazari | 86 | 00:00 | 118 | Mirzapur | 43 | 04:00 | 184 | Sylhet | 62 | 19:30
53 | Faridpur | 183 | 21:00 | 119 | Mithapukur | 58 | 07:00 | 185 | Sylhet-132 | 112 | 19:30
54 | Fatullah | 94 | 16:00 | 120 | Modern | N/A | N/A | 186 | TK | 28.5 | 20:00
55 | Fenchuganj | 48 | 21:00 | 121 | Mogbazar | 84 | 13:00 | 187 | Tangail | 201 | 18:30
56 | Feni | 115 | 19:30 | 122 | Mongla | 48 | 23:00 | 188 | Taraganj | 25 | 19:30
57 | GPH | 1 | 00:00 | 123 | Motijheel | 48 | 13:00 | 189 | Tasnim | 35 | 16:00
58 | Ghatail | 74 | 08:00 | 124 | Muktagacha | 33 | 00:00 | 190 | Thakurgaon | 84 | 15:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 117 | 22:00 | 191 | Tongi | 158 | 11:00
60 | Ghorashal-230 | 108 | 21:00 | 126 | Muradnagar | 48 | 22:00 | 192 | Ullahpara | 46 | 06:00
61 | Goalpara | 45 | 23:00 | 127 | Mymensingh | 195 | 19:00 | 193 | Ullon | 76 | 15:00
62 | Gollamari | 108 | 23:00 | 128 | Nabinagar | 11 | 03:00 | 194 | Uttara | 94 | 13:00
63 | Gopalganj | 118.2 | 22:00 | 129 | Naogaon | 164 | 20:00 | 195 | UttaraNew | 57 | 23:00
64 | Gulshan | 114 | 13:00 | 130 | Narail | 68 | 22:00 | 196 | Zigatola | 90 | 13:00
65 | Halishahar | 102.5 | 09:00 | 131 | Narinda | 73 | 13:00
66 | HaripurSBU | 135 | 09:00 | 132 | Narshingdi | 194 | 22:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 18-04-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13604.34 | 1106 |  | 14760.11
1:00 | 13115.52 | 1036 |  | 14198.52
2:00 | 13167 | 844 |  | 14049
3:00 | 13263.15 | 562 |  | 13850.15
4:00 | 13274.77 | 168 |  | 13450.77
5:00 | 13218.37 | 127 |  | 13351.37
6:00 | 13217.79 | 118 |  | 13340.79
7:00 | 13339.77 | 128 |  | 13473.77
8:00 | 13331.31 | 142 |  | 13479.7
9:00 | 13504.81 | 74 |  | 13581.81
10:00 | 13425.04 | 141 |  | 13572.04
11:00 | 13732.59 | 451 |  | 14203.59
12:00 | 13686.98 | 733 |  | 14452.98
13:00 | 13751.15 | 814 |  | 14602.15
14:00 | 13714.05 | 898 |  | 14652.05
15:00 | 13586.44 | 953 |  | 14582.44
16:00 | 13396.37 | 914 |  | 14351.37
17:00 | 13439.24 | 682 |  | 14152.24
18:00 | 13596.38 | 770 |  | 14401.38
19:00 | 14411.12 | 1255 |  | 15722.12
19:30 | 14699 | 890 |  | 15629.05
20:00 | 14767.85 | 643 |  | 15439.85
21:00 | 14404.04 | 360 |  | 14780.04
22:00 | 13702.39 | 209 |  | 13920.39
23:00 | 13409.76 | 679 |  | 14119.76
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 18-04-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6720.5 | 6883.84 | 13604.34 | DAILY GENERATION CURVE
00:30 | 6514 | 6845.93 | 13359.93
01:00 | 6307.5 | 6808.02 | 13115.52 | 18-04-2026
01:30 | 6360.5 | 6780.76 | 13141.26
02:00 | 6413.5 | 6753.5 | 13167
02:30 | 6404 | 6811.075 | 13215.075
03:00 | 6394.5 | 6868.65 | 13263.15
03:30 | 6420.5 | 6848.46 | 13268.96
04:00 | 6446.5 | 6828.27 | 13274.77
04:30 | 6452.5 | 6794.07 | 13246.57
05:00 | 6458.5 | 6759.87 | 13218.37
05:30 | 6467.585 | 6750.495 | 13218.08
06:00 | 6476.67 | 6741.12 | 13217.79
06:30 | 6496.915 | 6781.865 | 13278.78
07:00 | 6517.16 | 6822.61 | 13339.77
07:30 | 6526.05 | 6809.49 | 13335.54
08:00 | 6534.94 | 6796.37 | 13331.31
08:30 | 6580.38 | 6837.68 | 13418.06
09:00 | 6625.82 | 6878.99 | 13504.81
09:30 | 6595.92 | 6869.005 | 13464.925
10:00 | 6566.02 | 6859.02 | 13425.04
10:30 | 6617.155 | 6961.66 | 13578.815
11:00 | 6668.29 | 7064.3 | 13732.59
11:30 | 6679.025 | 7030.76 | 13709.785
12:00 | 6689.76 | 6997.22 | 13686.98
12:30 | 6692.96 | 7026.105 | 13719.065
13:00 | 6696.16 | 7054.99 | 13751.15
13:30 | 6663.89 | 7068.71 | 13732.6
14:00 | 6631.62 | 7082.43 | 13714.05
14:30 | 6605.555 | 7044.69 | 13650.245
15:00 | 6579.49 | 7006.95 | 13586.44
15:30 | 6588.955 | 6902.45 | 13491.405
16:00 | 6598.42 | 6797.95 | 13396.37
16:30 | 6667.2 | 6750.605 | 13417.805
17:00 | 6735.98 | 6703.26 | 13439.24
17:30 | 6843.965 | 6673.845 | 13517.81
18:00 | 6951.95 | 6644.43 | 13596.38
18:30 | 7168.475 | 6835.275 | 14003.75
19:00 | 7385 | 7026.12 | 14411.12
19:30 | 7491 | 7208 | 14699
20:00 | 7528 | 7239.85 | 14767.85
20:30 | 7466.75 | 7119.195 | 14585.945 |  | Executive Engineer
21:00 | 7405.5 | 6998.54 | 14404.04 |  | Network Operation Division
21:30 | 7396.75 | 6656.465 | 14053.215
22:00 | 7388 | 6314.39 | 13702.39
22:30 | 7333.75 | 6222.325 | 13556.075
23:00 | 7279.5 | 6130.26 | 13409.76

## En-Curve
QF-LDC-12
Date | 18-04-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3396 | 1621 | 909 | 0 | 156 | 1480.84 | 70 | 4486 | 0 | 662 | 823.5 | 0 | 0 | 0 | 1106 | DAILY ENERGY CURVE
00:30 | 3333.5 | 1611.5 | 879.5 | 0 | 157 | 1479.43 | 70 | 4518 | 0 | 659.5 | 651.5 | 0 | 0 | 0 | 1071 | 18-04-2026
01:00 | 3271 | 1602 | 850 | 0 | 158 | 1478.02 | 70 | 4550 | 0 | 657 | 479.5 | 0 | 0 | 0 | 1036
01:30 | 3307.5 | 1596.5 | 832.5 | 0 | 158 | 1477.26 | 68 | 4556.5 | 0 | 654.5 | 490.5 | 0 | 0 | 0 | 940 | Energy Generated | 328.4915 |  | MKWHr
02:00 | 3344 | 1591 | 815 | 0 | 158 | 1476.5 | 66 | 4563 | 0 | 652 | 501.5 | 0 | 0 | 0 | 844 | Energy not Served | 13.807 |  | MKWHr
02:30 | 3328.5 | 1598 | 862 | 0 | 157 | 1477.575 | 66 | 4561.5 | 0 | 652.5 | 512 | 0 | 0 | 0 | 703 | Total Energy Requirement | 342.2985 |  | MKWHr
03:00 | 3313 | 1605 | 909 | 0 | 156 | 1478.65 | 66 | 4560 | 0 | 653 | 522.5 | 0 | 0 | 0 | 562
03:30 | 3344.5 | 1603 | 909.5 | 0 | 154 | 1479.96 | 66 | 4557.5 | 0 | 649.5 | 505 | 0 | 0 | 0 | 365
04:00 | 3376 | 1601 | 910 | 0 | 152 | 1481.27 | 66 | 4555 | 0 | 646 | 487.5 | 0 | 0 | 0 | 168
04:30 | 3395.5 | 1600 | 909.5 | 0 | 150 | 1484.57 | 67 | 4506 | 0 | 646 | 488 | 0 | 0 | 0 | 147.5
05:00 | 3415 | 1599 | 909 | 0 | 148 | 1487.87 | 68 | 4457 | 0 | 646 | 488.5 | 0 | 0 | 0 | 127
05:30 | 3407.5 | 1603.5 | 909.5 | 0 | 142 | 1483.965 | 68.5 | 4457.5 | 4.115 | 646 | 495.5 | 0 | 0 | 0 | 122.5
06:00 | 3400 | 1608 | 910 | 0 | 136 | 1480.06 | 69 | 4458 | 8.23 | 646 | 502.5 | 0 | 0 | 0 | 118
06:30 | 3438 | 1607.5 | 910 | 0 | 137 | 1494.89 | 69.5 | 4454 | 39.14 | 637.5 | 491.25 | 0 | 0 | 0 | 123
07:00 | 3476 | 1607 | 910 | 0 | 138 | 1509.72 | 70 | 4450 | 70.05 | 629 | 480 | 0 | 0 | 0 | 128
07:30 | 3490.5 | 1533 | 897 | 0 | 139 | 1509.72 | 70 | 4503.5 | 112.32 | 616.5 | 464 | 0 | 0 | 0 | 135
08:00 | 3505 | 1459 | 884 | 0 | 140 | 1509.72 | 70 | 4557 | 154.59 | 604 | 448 | 0 | 0 | 0 | 142
08:30 | 3523 | 1458.5 | 883.5 | 0 | 142 | 1507.86 | 70 | 4535.5 | 264.7 | 592 | 441 | 0 | 0 | 0 | 108
09:00 | 3541 | 1458 | 883 | 0 | 144 | 1506 | 70 | 4514 | 374.81 | 580 | 434 | 0 | 0 | 0 | 74
09:30 | 3598 | 1527 | 883 | 0 | 148 | 1487.645 | 70 | 4463 | 384.28 | 498.5 | 405.5 | 0 | 0 | 0 | 107.5
10:00 | 3655 | 1596 | 883 | 0 | 152 | 1469.29 | 70 | 4412 | 393.75 | 417 | 377 | 0 | 0 | 0 | 141
10:30 | 3679 | 1621 | 883.5 | 0 | 162 | 1468.82 | 70 | 4422 | 478.995 | 404 | 388.5 | 0 | 0 | 1 | 296
11:00 | 3703 | 1646 | 884 | 0 | 172 | 1468.35 | 70 | 4432 | 564.24 | 391 | 400 | 0 | 0 | 2 | 451
11:30 | 3704 | 1637 | 883.5 | 0 | 179 | 1473.28 | 70 | 4426.5 | 514.005 | 395.5 | 420 | 0 | 0 | 7 | 592
12:00 | 3705 | 1628 | 883 | 0 | 186 | 1478.21 | 70 | 4421 | 463.77 | 400 | 440 | 0 | 0 | 12 | 733
12:30 | 3691.5 | 1610.5 | 883 | 0 | 192 | 1492.245 | 65 | 4438.5 | 443.32 | 415.5 | 474.5 | 0 | 0 | 13 | 773.5
13:00 | 3678 | 1593 | 883 | 0 | 198 | 1506.28 | 60 | 4456 | 422.87 | 431 | 509 | 0 | 0 | 14 | 814
13:30 | 3678.5 | 1538 | 883 | 0 | 198 | 1508.285 | 60 | 4438 | 453.315 | 405 | 557.5 | 0 | 0 | 13 | 856
14:00 | 3679 | 1483 | 883 | 0 | 198 | 1510.29 | 60 | 4420 | 483.76 | 379 | 606 | 0 | 0 | 12 | 898
14:30 | 3686 | 1471 | 883 | 0 | 202 | 1511.45 | 60 | 4374 | 468.295 | 379.5 | 603 | 0 | 0 | 12 | 925.5
15:00 | 3693 | 1459 | 883 | 0 | 206 | 1512.61 | 60 | 4328 | 452.83 | 380 | 600 | 0 | 0 | 12 | 953
15:30 | 3665.5 | 1451.5 | 871.5 | 0 | 200 | 1511.99 | 45 | 4289 | 374.415 | 382.5 | 690 | 0 | 0 | 10 | 933.5
16:00 | 3638 | 1444 | 860 | 0 | 194 | 1511.37 | 30 | 4250 | 296 | 385 | 780 | 0 | 0 | 8 | 914
16:30 | 3613.5 | 1438.5 | 860 | 0 | 185 | 1507.63 | 45 | 4253.5 | 204.675 | 422.5 | 881 | 0 | 0 | 6.5 | 798
17:00 | 3589 | 1433 | 860 | 0 | 176 | 1503.89 | 60 | 4257 | 113.35 | 460 | 982 | 0 | 0 | 5 | 682
17:30 | 3565.5 | 1361 | 860.5 | 0 | 168 | 1506.025 | 60 | 4285 | 65.285 | 503.5 | 1139.5 | 0 | 0 | 3.5 | 726
18:00 | 3542 | 1289 | 861 | 0 | 160 | 1508.16 | 60 | 4313 | 17.22 | 547 | 1297 | 0 | 0 | 2 | 770
18:30 | 3596.5 | 1310.5 | 852 | 0 | 153 | 1508.64 | 60 | 4337.5 | 8.61 | 659 | 1514.5 | 0 | 0 | 3.5 | 1012.5
19:00 | 3651 | 1332 | 843 | 0 | 146 | 1509.12 | 60 | 4362 | 0 | 771 | 1732 | 0 | 0 | 5 | 1255
19:30 | 3609 | 1398 | 774 | 0 | 142 | 1497 | 60 | 4560 | 0 | 797 | 1851 | 0 | 0 | 11 | 890
20:00 | 3635 | 1403 | 768 | 0 | 142 | 1501.85 | 60 | 4583 | 0 | 801 | 1870 | 0 | 0 | 4 | 643
20:30 | 3540 | 1346.5 | 796 | 0 | 146 | 1496.695 | 60 | 4605 | 0 | 803.5 | 1789.75 | 0 | 0 | 2.5 | 501.5
21:00 | 3445 | 1290 | 824 | 0 | 150 | 1491.54 | 60 | 4627 | 0 | 806 | 1709.5 | 0 | 0 | 1 | 360
21:30 | 3425 | 1298.5 | 773.5 | 0 | 149 | 1404.965 | 60 | 4689 | 0 | 723 | 1529.75 | 0 | 0 | 0.5 | 284.5
22:00 | 3405 | 1307 | 723 | 0 | 148 | 1318.39 | 60 | 4751 | 0 | 640 | 1350 | 0 | 0 | 0 | 209
22:30 | 3393 | 1370 | 773 | 0 | 152 | 1230.825 | 60 | 4723 | 0 | 632.5 | 1221.75 | 0 | 0 | 0 | 444
23:00 | 3381 | 1433 | 823 | 0 | 156 | 1143.26 | 60 | 4695 | 0 | 625 | 1093.5 | 0 | 0 | 0 | 679
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 18-04-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 04:00 | 369 | 12:00 | Madunaghat | 397 | 19:00 | 387 | 11:00
Amtali | 410 | 05:00 | 405 | 22:00 | Meghnaghat | 385 | 02:00 | 371 | 11:00
Ashuganj | 399 | 4:00 | 382 | 11:00 | Payra | 412 | 02:00 | 408 | 13:00
Bhulta | 391 | 02:00 | 373 | 14:00 | Rahanpur | 417 | 23:00 | 396 | 07:00
Bibiana | 401 | 07:00 | 391 | 11:00 | Rampal | 399 | 19:00 | 389 | 11:00
BIPTC | 402 | 22:00 | 386 | 15:00
Bogura | 416 | 23:00 | 384 | 07:00
Gopalganj | 394 | 01:00 | 385 | 11:00
Kaliakoir | 380 | 04:00 | 362 | 14:00
Korerhat | 397 | 19:00 | 383 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 02:00 | 213 | 11:00 | Jhenaidah | 226 | 00:00 | 217 | 20:00
AKSML | 231 | 19:00 | 219 | 11:00 | Kachua | 225 | 19:00 | 215 | 10:00
Aminbazar | 227 | 04:00 | 214 | 13:00 | Kaliakoir | 229 | 04:00 | 217 | 10:00
Ashuganj | 228 | 00:00 | 219 | 10:00 | Keranigonj | 225 | 02:00 | 213 | 11:00
Ashuganj-400 | 228 | 00:00 | 219 | 10:00 | Khulna(S) | 228 | 00:00 | 221 | 12:00
Baghabari | 236 | 21:00 | 226 | 07:00 | Korerhat | 225 | 18:00 | 217 | 11:00
Barapukuria | 234 | 23:00 | 209 | 09:00 | Madunaghat | 238 | 19:00 | 220 | 10:00
Barapukuria-230 | 234 | 23:00 | 209 | 09:00 | Madunaghat-400 | 228 | 19:00 | 221 | 12:00
Barishal | 227 | 19:00 | 220 | 13:00 | Maniknagar | 225 | 05:00 | 213 | 10:00
Bheramara | 233 | 19:00 | 223 | 07:00 | Meghnaghat | 231 | 05:00 | 221 | 10:00
Bhulta | 224 | 00:00 | 214 | 10:00 | Meghnaghat-400 | 227 | 02:00 | 217 | 11:00
Bibiana | 231 | 00:00 | 226 | 11:00 | Mirsorai | 234 | 18:00 | 215 | 11:00
BIPTC | 235 | 02:00 | 224 | 07:00 | Naogaon | 232 | 22:00 | 214 | 07:00
Bogura | 241 | 23:00 | 223 | 09:00 | Purbasadipur | 235 | 23:00 | 208 | 10:00
Bogura-400 | 242 | 23:00 | 222 | 07:00 | Rajshahi | 231 | 19:00 | 220 | 10:00
Borhanuddin | 230 | 08:00 | 226 | 21:00 | Rampal | 227 | 00:00 | 220 | 21:00
BSRM | 226 | 19:00 | 216 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 224 | 18:30 | 215 | 11:00 | Rampura | 225 | 06:00 | 212 | 12:00
Cumilla(N) | 224 | 02:00 | 217 | 22:00 | Shikalbaha | 233 | 22:00 | 217 | 10:00
Faridpur | 220 | 00:00 | 212 | 21:00 | Shyampur | 226 | 06:00 | 213 | 11:00
Fenchuganj | 236 | 00:00 | 229 | 22:00 | Siddhirganj | 225 | 00:00 | 215 | 09:00
Feni | 225 | 18:00 | 217 | 11:00 | Sirajgonj | 240 | 23:00 | 232 | 10:00
Ghorashal | 230 | 00:00 | 225 | 22:00 | Sreepur | 227 | 00:00 | 219 | 11:00
Ghorashal-230 | 224 | 02:00 | 212 | 11:00 | Tongi | 224 | 04:00 | 211 | 11:00
Gopalganj | 220 | 00:00 | 215 | 11:00
GPH | 225 | 01:00 | 221 | 09:00
Haripur | 226 | 02:00 | 215 | 12:00
Hasnabad | 225 | 04:00 | 211 | 13:00
Hathazari | 227 | 19:00 | 218 | 10:00
Ishurdi | 236 | 22:00 | 225 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 130 | 02:00 | 121 | 12:00 | Madunaghat | 134 | 19:00 | 129 | 11:00
Agargaon | 133 | 02:00 | 123 | 13:00 | Magura | 133 | 22:00 | 125 | 13:00
Agrabad | 134 | 19:00 | 127 | 10:00 | Mahasthangarh | 139 | 22:00 | 123 | 08:00
AKS | 130 | 00:00 | 126 | 10:00 | Maijdee | 125 | 18:00 | 120 | 10:00
Aminbazar | 130 | 04:00 | 121 | 13:00 | Manikganj | 125 | 02:00 | 116 | 10:00
Amnura | 139 | 20:00 | 126 | 07:00 | Maniknagar | 133 | 06:00 | 123 | 11:00
Ashuganj | 136 | 00:00 | 133 | 10:00 | Matarbari | 123 | 18:30 | 111 | 20:00
Ashuganj-230 | 136 | 00:00 | 133 | 10:00 | Matuail | 131 | 01:00 | 123 | 11:00
Bagerhat | 126 | 09:00 | 116 | 23:00 | Metrorail_Motijheel | 133 | 06:00 | 123 | 11:00
Bajitpur | 132 | 23:00 | 128 | 10:00 | Metrorail_Uttara | 130 | 02:00 | 120 | 10:00
Bakerganj | 132 | 04:00 | 127 | 23:00 | Millgate | 131 | 02:00 | 121 | 10:00
Bakulia | 135 | 18:30 | 129 | 11:00 | Mirpur | 128 | 00:00 | 120 | 11:00
Banani | 130 | 01:00 | 120 | 13:00 | Mirzapur | 133 | 23:00 | 121 | 11:00
Bangabhaban | 133 | 04:00 | 123 | 11:00 | Mithapukur | 138 | 22:00 | 120 | 10:00
Barapukuria | 140 | 23:00 | 122 | 09:00 | MI_Cement | 128.8 | 04:00 | 118 | 10:00
Barguna | 132 | 19:00 | 126 | 22:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 19:00 | 126 | 22:00 | Mogbazar | 132 | 03:00 | 123 | 10:00
Barishal-230 | 131 | 00:00 | 126 | 22:00 | Mongla | 126 | 09:00 | 117 | 22:00
Baroaulia | 133 | 18:00 | 128 | 10:00 | Motijheel | 133 | 04:00 | 123 | 11:00
Baroirhat | 128 | 06:00 | 123 | 11:00 | Muktagacha | 136 | 23:00 | 119 | 11:00
Bashundhara | 130 | 00:00 | 119 | 14:00 | Munshiganj | 131 | 04:00 | 121 | 11:00
BashundharaCement | 133 | 04:00 | 125 | 16:00 | Muradnagar | 127 | 02:00 | 119 | 22:00
Beanibazar | 127 | 00:00 | 120 | 21:00 | Mymensingh | 135 | 13:00 | 118 | 21:00
Benapole | 127 | 01:00 | 119 | 23:00 | Nabinagar | 128 | 01:00 | 118 | 10:00
Bhaluka | 136 | 00:00 | 128 | 21:00 | Naogaon | 140 | 22:00 | 116 | 07:00
Bhandaria | 127 | 01:00 | 118 | 22:00 | Narail | 131 | 00:00 | 125 | 13:00
Bhangura | 134 | 22:00 | 125 | 07:00 | Narinda | 133 | 06:00 | 123 | 11:00
Bheramara | 137 | 22:00 | 131 | 07:00 | Narshingdi | 128 | 18:30 | 118 | 22:00
Bheramara(GK) | 136 | 22:00 | 132 | 08:00 | Natore | 134 | 22:00 | 124 | 07:00
Bhulta | 123 | 06:00 | 119 | 10:00 | Nawabganj | 132 | 19:00 | 123 | 10:00
Bog-Sherpur | 137 | 23:00 | 124 | 07:00 | Netrakona | 132 | 00:00 | 119 | 18:30
Bogura | 140 | 22:00 | 126 | 09:00 | New | 132 | 01:00 | 121 | 14:00
Bogura-230 | 140 | 23:00 | 126 | 09:00 | Niamatpur | 140 | 22:00 | 131 | 06:00
Brahmanbaria | 132 | 00:00 | 125 | 11:00 | Noapara | 128 | 01:00 | 121 | 00:00
Cantonment | 133 | 04:00 | 122 | 12:00 | Pabna | 135 | 22:00 | 128 | 10:00
Chandina | 128 | 00:00 | 123 | 22:00 | Palashbari | 138 | 23:00 | 118 | 07:00
Chandpur | 130 | 19:00 | 121 | 10:00 | Panchagarh | 141 | 18:30 | 125 | 06:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 134 | 19:00 | 129 | 16:00 | Patiya | 133 | 18:00 | 127 | 10:00
Chapai | 140 | 22:00 | 132 | 06:00 | Patuakhali | 132 | 18:30 | 127 | 12:00
Charsaidpur | 131 | 06:00 | 123 | 10:00 | Payra | 135 | 02:00 | 131 | 23:00
Chauddagram | 126 | 19:00 | 121 | 22:00 | PHP | 128 | 19:00 | 123 | 11:00
Chhatak | 129 | 00:00 | 120 | 21:00 | Postogola | 133 | 05:00 | 120 | 10:00
Chowmuhani | 126 | 19:00 | 121 | 11:00 | Pubail | 136 | 02:00 | 125 | 13:00
Chuadanga | 133 | 22:00 | 121 | 20:00 | Purbachal | 131 | 03:00 | 120 | 11:00
Coxsbazar | 117 | 02:00 | 112 | 22:00 | Purbasadipur | 137 | 23:00 | 120 | 10:00
Cumilla(N) | 137 | 08:00 | 124 | 22:00 | Rahanpur | 142 | 23:00 | 134 | 10:00
Cumilla(S) | 131 | 20:00 | 119 | 13:00 | Rahanpur-400 | 142 | 22:00 | 135 | 06:00
Daganbhuiyan | 126 | 18:00 | 121 | 11:00 | Rahim | 131 | 03:00 | 123 | 12:00
Daudkandi | 125 | 00:00 | 116 | 22:00 | Rajbari | 126 | 01:00 | 119 | 22:00
DhakaUniversity | 131 | 04:00 | 122 | 11:00 | Rajendrapur | 134 | 00:00 | 126 | 11:00
Dhamrai | 128 | 00:00 | 118 | 10:00 | Rajshahi | 130 | 00:00 | 123 | 10:00
Dhanmondi | 132 | 01:00 | 124 | 10:00 | Rajshahi-230 | 133 | 21:00 | 126 | 07:00
Dohazari | 130 | 19:00 | 123 | 12:00 | Ramganj | 126 | 19:00 | 118 | 11:00
Faridpur | 127 | 00:00 | 124 | 21:00 | Rampur | 134 | 19:00 | 128 | 10:00
Fatullah | 130 | 04:00 | 118 | 12:00 | Rampura | 130 | 02:00 | 121 | 14:00
Fenchuganj | 134 | 01:00 | 128 | 22:00 | Rangamati | 132 | 04:00 | 128 | 10:00
Feni | 125 | 03:00 | 122 | 10:00 | Rangpur | 140 | 23:00 | 121 | 07:00
Feni-230 | 126 | 18:00 | 121 | 11:00 | Ruppur | 135 | 00:00 | 130 | 07:00
Ghatail | 134 | 23:00 | 117 | 14:00 | Saidpur | 137 | 20:00 | 122 | 10:00
Ghorashal | 137 | 00:00 | 130 | 11:00 | Satkhira | 127 | 09:00 | 117 | 22:00
Goalpara | 130 | 19:00 | 123 | 23:00 | Satmasjid | 133 | 04:00 | 123 | 11:00
Gollamari | 130 | 00:00 | 124 | 22:00 | Savar | 128 | 03:00 | 118 | 11:00
Gopalganj | 130 | 00:00 | 125 | 12:00 | SevenRings | 136 | 00:00 | 130 | 10:00
Gopalganj-400 | 132 | 19:00 | 120 | 21:00 | ShahCement | 130 | 02:00 | 123 | 10:00
Gulshan | 130 | 02:00 | 121 | 12:00 | Shahjadpur | 136 | 01:00 | 130 | 09:00
Halishahar | 135 | 19:00 | 129 | 10:00 | Shahjibazar | 133 | 02:00 | 121 | 21:00
Haripur | 132 | 04:00 | 124 | 11:00 | Shahmirpur | 134 | 18:30 | 129 | 11:00
HaripurSBU | 132 | 04:00 | 124 | 11:00 | Shariatpur | 129 | 00:00 | 123 | 22:00
Hasnabad | 130 | 18:00 | 121 | 11:00 | Sherpur | 142 | 23:00 | 111 | 21:00
Hathazari | 134 | 19:00 | 128 | 10:00 | Shikalbaha | 124 | 18:30 | 119 | 12:00
Hatirjheel | 131 | 02:00 | 121 | 13:00 | Shikalbaha-230 | 136 | 18:30 | 129 | 10:00
Ishurdi | 138 | 22:00 | 132 | 07:00 | Shitalakhya | 128.8 | 04:00 | 118 | 10:00
Jaldhaka | 137 | 22:00 | 119 | 10:00 | Sholosohor | 133 | 19:00 | 128 | 10:00
Jamalpur | 136 | 23:00 | 116 | 11:00 | Shyampur | 129 | 04:00 | 122 | 13:00
Jashore | 128 | 09:00 | 122 | 13:00 | Shyampur-230 | 130 | 02:00 | 121 | 11:00
Jhenaidah | 137 | 22:00 | 123 | 11:00 | Siddhirganj | 131 | 02:00 | 124 | 11:00
Jhenaidah-230 | 134 | 00:00 | 127 | 20:00 | Sirajganj | 134 | 23:00 | 124 | 07:00
Joydebpur | 136 | 00:00 | 124 | 14:00 | Sonargaon | 130 | 00:00 | 122 | 10:00
Joypurhat | 138 | 23:00 | 111 | 07:00 | Sreemongol | 131 | 01:00 | 123 | 21:00
Juldah | 135 | 19:00 | 130 | 10:00 | Sreepur | 136 | 00:00 | 130 | 11:00
Kabirpur | 138 | 19:00 | 118 | 10:00 | Srinagar | 132 | 19:00 | 123 | 10:00
Kachua | 134 | 09:00 | 122 | 10:00 | SSM | 136 | 00:00 | 132 | 09:00
Kaliakoir | 137 | 18:30 | 121 | 10:00 | Sunamganj | 130 | 00:00 | 119 | 21:00
Kaliganj | 132 | 00:00 | 126 | 13:00 | Sylhet | 130 | 00:00 | 124 | 22:00
Kallyanpur | 129 | 01:00 | 120 | 11:00 | Sylhet-132 | 130 | 00:00 | 126 | 22:00
Kalurghat | 134 | 19:00 | 129 | 10:00 | Tangail | 130 | 23:00 | 116 | 11:00
Kamrangirchar | 133 | 03:00 | 119 | 12:00 | Taraganj | 137 | 21:00 | 119 | 06:00
Kaptai | 135 | 1:00 | 132 | 10:00 | Tasnim | 129 | 01:00 | 122 | 10:00
Kasba | 126 | 02:00 | 118 | 22:00 | Thakurgaon | 141 | 20:00 | 123 | 06:00
Kazla | 132 | 00:00 | 123 | 11:00 | TK | 134 | 00:00 | 129 | 10:00
Keranigonj | 133 | 19:00 | 124 | 10:00 | Tongi | 133 | 04:00 | 124 | 11:00
Khagrachori | 131 | 06:00 | 127 | 11:00 | Ullahpara | 135 | 23:00 | 126 | 10:00
Khulna | 129 | 00:00 | 124 | 23:00 | Ullon | 130 | 02:00 | 121 | 13:00
Khulna(S) | 130 | 00:00 | 124 | 23:00 | Uttara | 131 | 04:00 | 118 | 11:00
Khulshi | 133 | 19:00 | 127 | 09:00 | UttaraNew | 130 | 02:00 | 120 | 10:00
Kishoreganj | 133 | 00:00 | 125 | 21:00 | Zigatola | 133 | 19:00 | 123 | 10:00
Kodda | 136 | 18:00 | 122 | 14:00
Korerhat | 130 | 01:00 | 126 | 11:00
KSRM | 132 | 01:00 | 128 | 14:00
Kulaura | 133 | 01:00 | 127 | 22:00
Kurigram | 135 | 20:00 | 117 | 09:00
Kushtia | 136 | 22:00 | 126 | 06:00
Laksam | 127 | 19:30 | 122 | 10:00
Lakshmipur | 125 | 19:00 | 120 | 10:00
Lalbag | 131 | 00:00 | 123 | 10:00
Lalmonirhat | 133 | 1:00 | 119 | 05:00
Madanganj | 133 | 04:00 | 125 | 16:00
Madaripur | 131 | 01:00 | 126 | 21:00
Madartek | 130 | 01:00 | 122 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division