## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 20-04-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-04-2026 | during | 20-04-2026 | during | 20-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 351 | 368 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 450 | 450 | 226 | 226 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 15 | 55 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 300 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17.5 | 36 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 45 | 146 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19 | 19 | 33 | 33 | 22 | 22 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 49 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 48 | 261 | 300 | 300 | 48 | 294 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 50 | 149 | 52 | 88 | 52 | 88 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 105 | 105 | 52 | 105 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 35 | 162 | 162 | 35 | 35 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 23 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 470 | 500 | 584 | 584 | 526 | 526 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 114 | 125 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1845.5 | 2482 | 5850.22 | 5854.22 | 2171.55 | 2585.55
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 0 | 50 | 50 | 19 | 50 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 60 | 60 | 60 | 60 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 212 | 217 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 51 | 105 | 105 | 34 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 40 | 54 | 56 | 56 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 68 | 68 | 34 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 13 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 12 | 12 | 108 | 108 | 12 | 12 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.97 | 0 | 3.79 | 0 | 3.79 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 18 | 54.36 | 54.36 | 0 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 55 | 110 | 110 | 54 | 54 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 72 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 54 | 156 | 163 | 163 | 17 | 17 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 582 | 612 | 1224 | 1224 | 612 | 612 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 25 | 0 | 25 | 6 | 25 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 935 | 935 | 935 | 935 | 935 | 935 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2070.97 | 2323.5 | 3841.65 | 3825.86 | 2246.29 | 2337.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 198 | 150 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 325 | 359 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 330 | 305 | 342.01 | 342.01 | 342.01 | 342.01 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 300 | 215 | 393 | 393 | 215 | 215 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 10 | 0 | 41.65 | 41.65 | 37 | 37 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 6 | 6 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Machine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 26 | 137 | 150 | 150 | 21 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 30 | 37 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 93 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 104 | 200 | 200 | 17 | 80 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 174 | 180 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 9 | 113 | 113 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 54 | 115 | 115 | 17 | 51 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 65 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.745 | 1657 | 1614 | 2764.19 | 2688.19 | 1545.02 | 1691.02
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-04-2026 | during | 20-04-2026 | during | 20-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 18 | 157.5 | 157.5 | 50 | 50 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.02 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 65 | 68 | 70 | 70 | 70 | 70 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 10 | 10 | 10 | 10 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 30.13 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 1 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 117.15 | 124 | 362 | 314 | 207 | 159
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 42 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 24 | 24 | 30 | 30 | 30 | 30 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 151 | 156 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 100 | 100 | 100 | 100 | 100 | 100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 53 | 83 | 83 | 50 | 50 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 98 | 98 | 98 | 98 | Plant availability less
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 17 | 17 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 348 | 349 | 350 | 350 | 350 | 350 | FGMO not available because of Cooling Tower Fan
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1161 | 1176 | 1262 | 1262 | 1171 | 1171
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 883 | 883 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 29 | 32 | 32 | 25 | 25 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 52 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 171 | 90 | 410 | 410 | 250.03 | 250.03 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 73 | 0 | 82 | 0 | 82 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1230 | 1226 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2357 | 2280 | 3578.2 | 3496.2 | 2656.33 | 2574.33
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 252 | 401 | 250 | 400 | 250 | 400 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 32 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 127 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1010 | 1244 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 290 | 290 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.62 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1899.62 | 2371 | 2412 | 2561 | 2185 | 2334
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 44.77 | 0 | 37.5 | 0 | 37.5 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 29 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 189 | 161 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 198 | 165 | 220 | 220 | 200 | 200 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 384 | 414 | 413.79 | 413.79 | 413 | 413 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 25 | 25 | 25 | 25 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 85 | 100 | 100 | 0 | 51 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 0 | 50 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.6 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1483 | 1470 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 56.95 | 0 | 54.97 | 0 | 54.97 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 50 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2410.32 | 2459 | 3209.19 | 3010.87 | 2558.2 | 2495.88
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 51 | 50 | 50 | 50 | 51 | 51 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 100 | 113 | 113 | 35 | 113 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.7 | 0 | 6.8 | 0 | 6.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 0.01 | 0.01 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 19 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 184 | 0 | 99 | 0 | 99 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 258.7 | 220 | 413.8 | 278 | 221.81 | 164.01
System Total |  |  |  |  | 28823.2 | 29269.987 | 13777.26 | 15049.5 | 23693.25 | 23290.34 | 14962.2 | 15512.29
Forecast Scenario (20-04-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13685 |  | 1829 |  | 15600
|  |  |  | 1:00 | 13198 |  | 1912 |  | 15200
|  |  |  | 2:00 | 13226 |  | 1837 |  | 15150
|  |  |  | 3:00 | 13209 |  | 1596 |  | 14880
|  |  |  | 4:00 | 13210 |  | 1471 |  | 14750
|  |  |  | 5:00 | 13200 |  | 1337 |  | 14600
|  |  |  | 6:00 | 13152 |  | 1240 |  | 14450
|  |  |  | 7:00 | 13155 |  | 1189 |  | 14400
|  |  |  | 8:00 | 12986 |  | 1112 |  | 14150
|  |  |  | 9:00 | 13257 |  | 948.315 |  | 14250
|  |  |  | 10:00 | 13444 |  | 865.23 |  | 14350
|  |  |  | 11:00 | 13500 |  | 859.5 |  | 14400
|  |  |  | 12:00 | 13550 |  | 955 |  | 14550
|  |  |  | 13:00 | 13600 |  | 1193.75 |  | 14850
|  |  |  | 14:00 | 13800 |  | 1241.5 |  | 15100
|  |  |  | 15:00 | 13700 |  | 1432.5 |  | 15200
|  |  |  | 16:00 | 13750 |  | 1289.25 |  | 15100
|  |  |  | 17:00 | 13850 |  | 1002.75 |  | 14900
|  |  |  | 18:00 | 13950 |  | 1146 |  | 15150
|  |  |  | 18:30 | 14200 |  | 1432.5 |  | 15700
|  |  |  | 19:00 | 14300 |  | 1910 |  | 16300
|  |  |  | 19:30 | 14700 |  | 1719 |  | 16500
|  |  |  | 20:00 | 15000 |  | 1480.25 |  | 16550
|  |  |  | 21:00 | 15200 |  | 1384.75 |  | 16650
|  |  |  | 22:00 | 14800 |  | 1337 |  | 16200
|  |  |  | 23:00 | 14100 |  | 1623.5 |  | 15800
Probable Maximum Temperature: |  |  | 35.50°C
Probable Maximum Demand at Day Peak: |  |  | 14550.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 16650.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15150.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 341.97 MKWHr. |  | 200 | 190 | 205 | 210 | 100 | 200 | 80 | 200 | 180 | 1385
*** This report is generated digitally from Operation Information System (OIS) at 09:15 hrs on 20-04-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 19-04-2026 | [28 empty] | Date: | 19-04-2026 | [28 empty] | Date: | 19-04-2026 | [28 empty] | Date: | 19-04-2026 | [28 empty] | Date: | 19-04-2026 | [17 empty] | Date: | 19-04-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [17 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 17 | 37 | 49 | 130 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 108 | 21 | 22 | 0 | 420 | 92 | 16 | 12 | 0 | 0 | 34 | 55 | 18 | 0 | 0 | 0 | 60 | 55 | 28 | 935 | 54 | 0 | 20 | 8 | 51 | 218 | 0 | 0 | 0 | 584 | 0 | 20 | 8 | 280 | 6 | 320 | 44 | 5 | 209 | 10 | 17 | 98 | 33 | 0 | 20 | 0 | 164 | 0 | 0 | 30 | 305 | 0 | 355 | 42 | 24 | 154 | 0 | 17 | 0 | 50 | 25 | 100 | 0 | 100 | 17 | 16 | 9 | 33 | 0 | 0 | 12 | 6612 | 788 | 201 | 0 | 28 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1223 | 0 | 0 | 0 | 1134.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 185 | 0 | 383 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 288 | 1200 | 17 | 6339.04 | 12951.04 | 78.64
01:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 0 | 17 | 15 | 32 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 70 | 22 | 22 | 0 | 350 | 92 | 16 | 10 | 0 | 0 | 0 | 55 | 18 | 0 | 0 | 0 | 60 | 44 | 29 | 935 | 17 | 0 | 19 | 8 | 34 | 220 | 0 | 0 | 0 | 585 | 0 | 20 | 0 | 330 | 43 | 300 | 44 | 0 | 198 | 10 | 17 | 98 | 17 | 0 | 20 | 0 | 162 | 0 | 0 | 30 | 300 | 0 | 355 | 42 | 24 | 154 | 0 | 17 | 0 | 50 | 25 | 100 | 0 | 100 | 0 | 8 | 9 | 35 | 0 | 0 | 12 | 6179 | 882 | 199 | 0 | 28 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1217 | 0 | 0 | 0 | 1039.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 185 | 0 | 347 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 254 | 1212 | 17 | 6289.3 | 12468.3 | 78.63
02:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 15 | 32 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 35 | 22 | 22 | 0 | 400 | 89 | 16 | 13 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 60 | 51 | 29 | 935 | 0 | 0 | 19 | 8 | 34 | 220 | 0 | 0 | 0 | 580 | 0 | 20 | 0 | 330 | 73 | 300 | 44 | 0 | 188 | 10 | 17 | 98 | 17 | 0 | 20 | 0 | 164 | 0 | 0 | 30 | 295 | 0 | 334 | 42 | 24 | 153 | 0 | 0 | 0 | 50 | 25 | 101 | 0 | 100 | 0 | 8 | 9 | 35 | 0 | 0 | 12 | 6188 | 884 | 196 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1214 | 0 | 0 | 0 | 881.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 185 | 0 | 342 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 254 | 1210 | 17 | 6087.13 | 12275.13 | 78.62
03:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 22 | 22 | 0 | 400 | 60 | 0 | 12 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 60 | 54 | 29 | 935 | 0 | 0 | 19 | 0 | 34 | 219 | 0 | 0 | 0 | 582 | 0 | 20 | 0 | 330 | 93 | 300 | 44 | 0 | 191 | 10 | 17 | 98 | 17 | 0 | 20 | 0 | 160 | 0 | 0 | 30 | 295 | 0 | 336 | 42 | 24 | 150 | 0 | 0 | 0 | 50 | 30 | 101 | 0 | 100 | 0 | 8 | 0 | 35 | 0 | 0 | 0 | 6075 | 883 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1184 | 0 | 0 | 0 | 831.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 150 | 0 | 337 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 130 | 220 | 0 | 254 | 1212 | 0 | 5889.31 | 11964.31 | 78.61
04:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 22 | 22 | 0 | 410 | 30 | 0 | 12 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 60 | 55 | 29 | 935 | 0 | 0 | 19 | 0 | 34 | 219 | 0 | 0 | 0 | 582 | 0 | 20 | 0 | 330 | 113 | 300 | 44 | 0 | 201 | 10 | 17 | 98 | 17 | 0 | 20 | 0 | 154 | 0 | 0 | 30 | 300 | 0 | 347 | 42 | 24 | 154 | 0 | 17 | 0 | 50 | 30 | 100 | 0 | 100 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 6077 | 883 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 834.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 150 | 0 | 348 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 130 | 220 | 0 | 254 | 1212 | 0 | 5815.77 | 11892.77 | 78.6
05:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 400 | 0 | 0 | 12 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 60 | 54 | 30 | 935 | 0 | 0 | 19 | 0 | 34 | 219 | 0 | 0 | 0 | 580 | 0 | 10 | 0 | 310 | 133 | 300 | 44 | 0 | 189 | 10 | 0 | 98 | 0 | 0 | 20 | 0 | 152 | 0 | 0 | 31 | 300 | 0 | 347 | 42 | 24 | 154 | 0 | 17 | 0 | 50 | 30 | 100 | 0 | 100 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 5944 | 883 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1038 | 0 | 0 | 0 | 843.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 150 | 0 | 350 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 130 | 220 | 0 | 254 | 1212 | 0 | 5774.48 | 11718.48 | 78.59
06:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 400 | 0 | 0 | 12 | 0 | 1 | 0 | 24 | 0 | 0 | 0 | 0.08 | 60 | 55 | 30 | 935 | 0 | 0 | 19 | 0 | 34 | 219 | 0 | 0 | 0 | 580 | 1 | 0 | 0 | 298 | 148 | 300 | 44 | 0 | 178 | 10 | 0 | 98 | 0 | 0 | 20 | 0 | 146 | 0 | 1 | 31 | 295 | 0 | 346 | 42 | 24 | 151 | 0 | 17 | 0 | 50 | 30 | 100 | 0 | 100 | 0 | 0 | 0 | 35 | 0.04 | 1.25 | 0 | 5916.37 | 884 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1038 | 0 | 0 | 0 | 840.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.76 | 0 | 0 | 0 | 0.56 | 150 | 0 | 0 | 0 | 150 | 0 | 338 | 0 | 0.04 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.01 | 0 | 290 | 130 | 220 | 0 | 254 | 1212 | 0 | 5776.27 | 11692.64 | 78.58
07:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 3 | 0 | 22 | 22 | 0 | 400 | 0 | 0 | 12 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0.81 | 60 | 55 | 28 | 935 | 0 | 0 | 19 | 0 | 34 | 220 | 0 | 0 | 0 | 585 | 4 | 0 | 0 | 334 | 163 | 345 | 44 | 0 | 187 | 10 | 0 | 98 | 0 | 0 | 20 | 0 | 146 | 0 | 13 | 30 | 305 | 0 | 346 | 42 | 24 | 158 | 0 | 17 | 0 | 50 | 30 | 100 | 0 | 100 | 0 | 2 | 24 | 35 | 0.39 | 5.45 | 0 | 6097.65 | 883 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 1116 | 0 | 0 | 0 | 924.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.06 | 10 | 0 | 0 | 9.67 | 166 | 0 | 0 | 0 | 194 | 0 | 414 | 0 | 0.8 | 0 | 50 | 0 | 4 | 0 | 0 | 0 | 0 | 0.5 | 13 | 0.1 | 0 | 290 | 130 | 220 | 0 | 253 | 1212 | 0 | 6129.43 | 12227.08 | 78.57
08:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 3 | 0 | 22 | 22 | 0 | 400 | 0 | 0 | 10 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1.59 | 60 | 55 | 7 | 935 | 0 | 0 | 19 | 0 | 34 | 217 | 0 | 0 | 0 | 580 | 9 | 0 | 0 | 310 | 190 | 345 | 44 | 0 | 182 | 10 | 0 | 97 | 0 | 0 | 20 | 0 | 148 | 0 | 32 | 30 | 305 | 0 | 346 | 42 | 24 | 153 | 0 | 17 | 0 | 50 | 30 | 100 | 0 | 100 | 0 | 9 | 24 | 31 | 0 | 13.08 | 0 | 6104.67 | 883 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 1120 | 0 | 0 | 0 | 916.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.52 | 7 | 0 | 0 | 13.66 | 191 | 0 | 0 | 0 | 199 | 0 | 405 | 0 | 1.43 | 0 | 52 | 0 | 6 | 0 | 0 | 0 | 0 | 2.5 | 63 | 0.27 | 0 | 290 | 130 | 220 | 0 | 253 | 1222 | 0 | 6233.43 | 12338.1 | 78.56
09:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 11 | 12 | 22 | 22 | 0 | 400 | 0 | 0 | 8 | 0 | 6 | 0 | 24 | 0 | 0 | 0 | 2.5 | 60 | 55 | 2 | 935 | 12 | 0 | 19 | 0 | 34 | 216 | 0 | 0 | 0 | 592 | 15 | 0 | 0 | 334 | 235 | 345 | 44 | 0 | 193 | 10 | 0 | 96 | 3 | 0 | 20 | 0 | 156 | 0 | 53 | 30 | 310 | 0 | 348 | 42 | 24 | 157 | 0 | 17 | 0 | 50 | 30 | 100 | 0 | 100 | 0 | 9 | 29 | 27 | 1.47 | 13.79 | 0 | 6286.76 | 883 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 1142 | 0 | 0 | 0 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.58 | 71 | 0 | 0 | 29.11 | 193 | 0 | 0 | 0 | 198 | 0 | 357 | 0 | 2.81 | 0 | 52 | 0 | 11 | 0 | 0 | 0 | 0 | 2.3 | 106 | 0.16 | 0 | 290 | 130 | 220 | 0 | 252 | 1200 | 0 | 6328.96 | 12615.72 | 78.55
10:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 12 | 17 | 45 | 48 | 15 | 17 | 17 | 0 | 225 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 29 | 35 | 20 | 22 | 0 | 430 | 0 | 0 | 12 | 0 | 7 | 0 | 24 | 0 | 0 | 0 | 3.3 | 30 | 55 | 2 | 935 | 17 | 0 | 19 | 0 | 34 | 215 | 0 | 0 | 0 | 585 | 13 | 18 | 0 | 352 | 270 | 340 | 44 | 0 | 198 | 10 | 9 | 95 | 16 | 0 | 20 | 0 | 156 | 0 | 43 | 30 | 305 | 0 | 348 | 42 | 24 | 157 | 0 | 17 | 0 | 50 | 30 | 100 | 0 | 100 | 0 | 9 | 65 | 27 | 1.52 | 37.12 | 0 | 6574.94 | 884 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 1155 | 0 | 0 | 0 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.35 | 76 | 0 | 0 | 51.17 | 192 | 0 | 0 | 0 | 196 | 0 | 373 | 0 | 3.54 | 0 | 52 | 0 | 10 | 0 | 0 | 0 | 0 | 6.1 | 100 | 0.64 | 0 | 290 | 130 | 220 | 0 | 252 | 1195 | 0 | 6376.8 | 12951.74 | 78.54
11:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 17 | 17 | 17 | 45 | 48 | 15 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 26 | 68 | 20 | 22 | 0 | 430 | 0 | 0 | 12 | 0 | 14 | 0 | 26 | 0 | 0 | 0 | 2.49 | 70 | 55 | 2 | 935 | 17 | 0 | 19 | 4 | 34 | 215 | 0 | 0 | 0 | 584 | 11 | 26 | 0 | 393 | 305 | 338 | 44 | 0 | 189 | 10 | 16 | 94 | 17 | 4 | 14 | 0 | 164 | 0 | 59 | 30 | 305 | 0 | 348 | 41 | 24 | 149 | 0 | 17 | 0 | 50 | 30 | 99 | 0 | 100 | 0 | 9 | 65 | 10 | 1.42 | 44.03 | 0 | 6720.94 | 883 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 1155 | 0 | 0 | 0 | 1199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.64 | 106 | 0 | 0 | 51.58 | 188 | 0 | 0 | 0 | 201 | 0 | 332 | 0 | 4.96 | 0 | 52 | 0 | 22 | 0 | 0 | 0 | 0 | 6.5 | 43 | 0.68 | 0 | 290 | 127 | 220 | 0 | 252 | 1125 | 0 | 6549.36 | 13270.3 | 78.53
12:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17.5 | 17 | 50 | 45 | 48 | 15 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 23 | 114 | 19 | 21 | 0 | 470 | 0 | 0 | 12 | 0 | 25 | 0 | 40 | 0 | 0 | 0 | 1.97 | 70 | 55 | 4 | 935 | 54 | 0 | 19 | 8 | 34 | 212 | 0 | 0 | 0 | 582 | 19 | 26 | 0 | 300 | 325 | 330 | 44 | 0 | 198 | 10 | 17 | 93 | 17 | 8 | 20 | 0 | 174 | 0 | 65 | 30 | 300 | 0 | 348 | 41 | 24 | 151 | 0 | 17 | 0 | 50 | 30 | 100 | 0 | 100 | 1 | 9 | 65 | 10 | 2.02 | 30.13 | 0 | 6851.62 | 883 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 1230 | 0 | 0 | 0 | 1483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.77 | 50 | 0 | 0 | 56.95 | 189 | 0 | 0 | 0 | 198 | 0 | 384 | 0 | 4.6 | 0 | 51 | 0 | 19 | 0 | 0 | 0 | 0 | 4.7 | 184 | 0.62 | 0 | 290 | 127 | 220 | 0 | 252 | 1010 | 0 | 6925.64 | 13777.26 | 78.52
13:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 17.5 | 17 | 68 | 45 | 48 | 15 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 22 | 125 | 19 | 21 | 0 | 430 | 0 | 0 | 15 | 0 | 24 | 0 | 40 | 0 | 0 | 0 | 1.76 | 70 | 55 | 6 | 935 | 163 | 0 | 19 | 8 | 34 | 211 | 0 | 0 | 0 | 585 | 18 | 26 | 0 | 230 | 354 | 335 | 44 | 0 | 182 | 10 | 17 | 93 | 17 | 8 | 20 | 0 | 178 | 0 | 32 | 30 | 305 | 0 | 348 | 42 | 24 | 142 | 0 | 17 | 0 | 51 | 30 | 100 | 0 | 100 | 17 | 9 | 67 | 10 | 2.07 | 43.13 | 0 | 6919.46 | 883 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 1220 | 0 | 0 | 0 | 1468 | 0 | 0 | 0 | 20 | 15 | 0 | 0 | 0 | 0 | 46.91 | 81 | 0 | 0 | 49.57 | 190 | 0 | 0 | 0 | 195 | 0 | 398 | 0 | 2.69 | 0 | 51 | 82 | 9 | 30 | 0 | 0 | 0 | 6.7 | 154 | 0.47 | 1 | 290 | 127 | 220 | 0 | 252 | 910 | 0 | 6934.34 | 13853.8 | 78.51
14:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17.5 | 10 | 51 | 45 | 48 | 15 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 17 | 320 | 0 | 0 | 21 | 125 | 0 | 21 | 0 | 420 | 25 | 0 | 15 | 0 | 30 | 0 | 40 | 0 | 0 | 0 | 2.98 | 70 | 55 | 2 | 935 | 163 | 0 | 19 | 8 | 34 | 214 | 0 | 0 | 0 | 584 | 16 | 26 | 0 | 215 | 354 | 335 | 44 | 0 | 162 | 0 | 17 | 93 | 17 | 8 | 20 | 0 | 206 | 0 | 61 | 24 | 300 | 0 | 348 | 42 | 24 | 145 | 9 | 17 | 0 | 51 | 30 | 100 | 0 | 100 | 17 | 9 | 68 | 10 | 1.14 | 24.97 | 0 | 6906.59 | 882 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 1200 | 0 | 0 | 0 | 1494 | 0 | 0 | 0 | 20 | 35 | 0 | 0 | 0 | 0 | 26.09 | 102 | 0 | 0 | 18.95 | 186 | 0 | 0 | 0 | 190 | 0 | 414 | 0 | 4.47 | 0 | 50 | 73 | 26 | 34 | 0 | 0 | 0 | 5.9 | 99 | 0.56 | 15 | 290 | 127 | 220 | 0 | 252 | 870 | 8 | 6837.97 | 13744.56 | 78.5
15:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 18 | 0 | 57 | 45 | 48 | 15 | 17 | 54 | 0 | 225 | 0 | 0 | 0 | 20 | 320 | 0 | 0 | 23 | 125 | 22 | 21 | 0 | 480 | 55 | 16 | 14 | 0 | 22 | 0 | 30 | 0 | 0 | 0 | 2.49 | 66 | 54 | 2 | 935 | 163 | 0 | 19 | 8 | 34 | 213 | 0 | 0 | 0 | 580 | 12 | 26 | 0 | 215 | 351 | 320 | 44 | 0 | 148 | 0 | 17 | 92 | 17 | 0 | 20 | 0 | 212 | 0 | 47 | 30 | 300 | 0 | 349 | 42 | 24 | 156 | 7 | 17 | 0 | 52 | 30 | 100 | 0 | 100 | 17 | 9 | 68 | 10 | 0.58 | 27.85 | 0 | 7002.92 | 883 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 1213 | 0 | 0 | 0 | 1488 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 5 | 0 | 27.05 | 46 | 0 | 0 | 30.23 | 182 | 0 | 0 | 0 | 181 | 0 | 414 | 0 | 3.71 | 0 | 51 | 35 | 17 | 34 | 0 | 0 | 0 | 3.7 | 33 | 0.44 | 16 | 290 | 127 | 220 | 0 | 302 | 890 | 17 | 6747.13 | 13750.05 | 78.49
16:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 52 | 48 | 48 | 15 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 318 | 0 | 0 | 14 | 125 | 19 | 21 | 0 | 450 | 62 | 16 | 4 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 1.63 | 66 | 55 | 2 | 935 | 163 | 0 | 19 | 8 | 34 | 215 | 0 | 0 | 0 | 585 | 7 | 26 | 0 | 215 | 352 | 305 | 44 | 0 | 149 | 0 | 16 | 93 | 17 | 0 | 20 | 0 | 204 | 0 | 30 | 38 | 305 | 0 | 349 | 42 | 24 | 155 | 4 | 17 | 0 | 52 | 30 | 101 | 0 | 100 | 17 | 9 | 68 | 11 | 0.77 | 18.87 | 4 | 6955.27 | 883 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 1216 | 0 | 0 | 0 | 1482 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 7 | 0 | 21.12 | 53 | 0 | 0 | 27.51 | 175 | 0 | 0 | 0 | 175 | 0 | 414 | 0 | 1.6 | 0 | 51 | 35 | 6 | 50 | 0 | 0 | 0 | 2.3 | 60 | 0.27 | 16 | 290 | 127 | 220 | 0 | 303 | 920 | 17 | 6788.8 | 13744.07 | 78.48
17:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 18 | 0 | 53 | 48 | 48 | 55 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 321 | 0 | 0 | 6 | 125 | 18 | 21 | 0 | 400 | 71 | 16 | 11 | 0 | 11 | 0 | 54 | 0 | 0 | 0 | 0.52 | 66 | 54 | 3 | 935 | 163 | 0 | 19 | 8 | 35 | 215 | 0 | 0 | 0 | 585 | 3 | 26 | 0 | 215 | 358 | 305 | 44 | 0 | 157 | 0 | 45 | 0 | 35 | 0 | 20 | 0 | 190 | 0 | 12 | 38 | 305 | 0 | 349 | 42 | 24 | 154 | 1 | 17 | 0 | 50 | 30 | 102 | 0 | 101 | 17 | 9 | 68 | 11 | 0.25 | 7.54 | 12 | 6882.31 | 883 | 125 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1204 | 0 | 0 | 0 | 1494 | 0 | 0 | 0 | 35 | 35 | 0 | 15 | 14 | 0 | 10.2 | 22 | 0 | 0 | 7.02 | 171 | 0 | 0 | 0 | 173 | 0 | 414 | 0 | 0.63 | 0 | 50 | 40 | 3 | 81 | 0 | 0 | 0 | 1.3 | 19 | 0.11 | 16 | 290 | 127 | 180 | 0 | 305 | 1010 | 17 | 6789.26 | 13671.57 | 78.47
18:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 36 | 17 | 66 | 102 | 147 | 55 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 125 | 18 | 21 | 0 | 480 | 72 | 16 | 12 | 0 | 6 | 0 | 61 | 1 | 0 | 0 | 0 | 66 | 55 | 2 | 935 | 163 | 0 | 43 | 20 | 51 | 215 | 0 | 0 | 0 | 580 | 0 | 26 | 0 | 215 | 354 | 305 | 44 | 0 | 155 | 0 | 54 | 0 | 103 | 7 | 20 | 0 | 156 | 0 | 1 | 38 | 310 | 0 | 349 | 42 | 24 | 140 | 0 | 17 | 0 | 50 | 30 | 98 | 0 | 100 | 17 | 9 | 68 | 11 | 0 | 0.96 | 12 | 7259.96 | 883 | 110 | 0 | 25 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1155 | 0 | 0 | 0 | 1473 | 0 | 20 | 0 | 35 | 35 | 0 | 83 | 24 | 0 | 0.31 | 1 | 25 | 0 | 0.9 | 171 | 0 | 0 | 0 | 170 | 0 | 414 | 0 | 0.11 | 0 | 50 | 74 | 0 | 84 | 0 | 0 | 0 | 0.2 | 2 | 0 | 22 | 290 | 126 | 220 | 0 | 305 | 1100 | 17 | 6940.52 | 14200.48 | 78.45
19:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 36 | 17 | 95 | 129 | 278 | 55 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 260 | 0 | 0 | 0 | 125 | 18 | 22 | 0 | 400 | 72 | 16 | 12 | 0 | 5 | 17 | 54 | 18 | 0 | 0 | 0 | 66 | 54 | 10 | 935 | 134 | 0 | 45 | 25.5 | 51 | 216 | 0 | 0 | 0 | 612 | 0 | 66 | 0 | 215 | 359 | 305 | 44 | 0 | 152 | 0 | 54 | 0 | 104 | 10 | 20 | 0 | 156 | 0 | 0 | 38 | 305 | 0 | 349 | 42 | 24 | 151 | 0 | 17 | 0 | 50 | 30 | 101 | 0 | 100 | 17 | 9 | 68 | 11 | 0 | 0 | 12 | 7413.5 | 855 | 104 | 0 | 33 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1170 | 0 | 0 | 0 | 1473 | 0 | 33 | 0 | 35 | 45 | 0 | 84 | 26 | 0 | 0 | 0 | 24 | 0 | 0 | 164 | 0 | 0 | 0 | 166 | 0 | 350 | 0 | 0 | 0 | 50 | 66 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 290 | 110 | 180 | 0 | 334 | 1160 | 54 | 6968 | 14381.5 | 78.43
19:30 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 36 | 17 | 149 | 146 | 261 | 55 | 35 | 54 | 0 | 180 | 0 | 0 | 0 | 35 | 260 | 0 | 0 | 0 | 125 | 18 | 22 | 0 | 400 | 72 | 16 | 12 | 0 | 4 | 17 | 54 | 18 | 0 | 0 | 0 | 68 | 54 | 2 | 935 | 140 | 0 | 46 | 25.5 | 51 | 217 | 0 | 0 | 0 | 612 | 0 | 148 | 0 | 217 | 359 | 305 | 44 | 0 | 150 | 0 | 54 | 0 | 103 | 9 | 20 | 0 | 166 | 0 | 0 | 38 | 310 | 0 | 349 | 42 | 24 | 143 | 0 | 17 | 0 | 53 | 30 | 99 | 0 | 100 | 17 | 9 | 68 | 11 | 0 | 0 | 12 | 7536.5 | 883 | 100 | 0 | 29 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1213 | 0 | 0 | 0 | 1473 | 0 | 33 | 0 | 35 | 50 | 0 | 85 | 26 | 0 | 0 | 0 | 24 | 0 | 0 | 163 | 0 | 0 | 0 | 165 | 0 | 350 | 0 | 0 | 0 | 50 | 70 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 290 | 110 | 180 | 0 | 400 | 1222 | 54 | 7177 | 14713.5 | 78.43
20:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 36 | 17 | 149 | 146 | 261 | 55 | 35 | 54 | 0 | 180 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 125 | 18 | 22 | 0 | 400 | 71 | 16 | 12 | 0 | 3 | 17 | 54 | 18 | 0 | 0 | 0 | 68 | 55 | 8 | 935 | 146 | 0 | 46 | 25.5 | 51 | 217 | 0 | 0 | 0 | 612 | 0 | 150 | 0 | 215 | 359 | 305 | 44 | 0 | 150 | 0 | 53 | 0 | 103 | 9 | 20 | 0 | 180 | 0 | 0 | 38 | 305 | 0 | 349 | 42 | 24 | 140 | 0 | 17 | 0 | 53 | 30 | 100 | 0 | 100 | 17 | 9 | 68 | 17 | 0 | 0 | 12 | 7592.5 | 882 | 95 | 0 | 29 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1210 | 0 | 0 | 0 | 1479 | 0 | 32 | 0 | 35 | 50 | 0 | 85 | 26 | 0 | 0 | 0 | 24 | 0 | 0 | 163 | 0 | 0 | 0 | 165 | 0 | 350 | 0 | 0 | 0 | 50 | 70 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 290 | 126 | 220 | 0 | 399 | 1222 | 54 | 7230 | 14822.5 | 78.41
21:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 36 | 17 | 149 | 146 | 261 | 55 | 35 | 35 | 0 | 225 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 125 | 19 | 22 | 0 | 500 | 72 | 16 | 12 | 0 | 0 | 17 | 54 | 18 | 0 | 0 | 0 | 70 | 55 | 13 | 935 | 156 | 0 | 0 | 25.5 | 51 | 217 | 0 | 0 | 0 | 612 | 0 | 137 | 0 | 215 | 359 | 305 | 44 | 0 | 150 | 0 | 54 | 0 | 104 | 9 | 20 | 0 | 180 | 0 | 0 | 37 | 305 | 0 | 349 | 42 | 24 | 156 | 0 | 17 | 0 | 53 | 30 | 100 | 0 | 100 | 17 | 9 | 68 | 18 | 0 | 0 | 12 | 7719.5 | 883 | 90 | 0 | 29 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1226 | 0 | 0 | 0 | 1470 | 0 | 29 | 0 | 35 | 50 | 0 | 85 | 26 | 0 | 0 | 0 | 24 | 0 | 0 | 161 | 0 | 0 | 0 | 165 | 0 | 414 | 0 | 0 | 0 | 50 | 70 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 290 | 130 | 220 | 0 | 401 | 1244 | 54 | 7330 | 15049.5 | 78.39
22:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 36 | 17 | 83 | 130 | 261 | 55 | 35 | 35 | 0 | 225 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 125 | 18 | 22 | 0 | 450 | 71 | 16 | 12 | 0 | 4 | 17 | 54 | 18 | 0 | 0 | 0 | 70 | 54 | 18 | 935 | 136 | 0 | 0 | 25.5 | 51 | 220 | 0 | 0 | 0 | 612 | 0 | 122 | 0 | 215 | 360 | 305 | 44 | 0 | 150 | 0 | 54 | 0 | 103 | 9 | 20 | 0 | 174 | 0 | 0 | 37 | 310 | 0 | 349 | 42 | 24 | 156 | 0 | 17 | 0 | 53 | 30 | 100 | 0 | 100 | 17 | 9 | 58 | 16 | 0 | 0 | 12 | 7528.5 | 883 | 86 | 0 | 28 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1194 | 0 | 0 | 0 | 1476 | 0 | 32 | 0 | 35 | 50 | 0 | 85 | 26 | 0 | 0 | 0 | 24 | 0 | 0 | 159 | 0 | 0 | 0 | 164 | 0 | 414 | 0 | 0 | 0 | 47 | 70 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 290 | 130 | 220 | 0 | 401 | 1244 | 54 | 7285 | 14813.5 | 78.37
23:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 17 | 42 | 131 | 205 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 125 | 18 | 22 | 0 | 480 | 72 | 16 | 12 | 0 | 0 | 17 | 54 | 18 | 0 | 0 | 0 | 70 | 55 | 19 | 935 | 137 | 0 | 17 | 25.5 | 51 | 219 | 0 | 0 | 0 | 614 | 0 | 83 | 0 | 215 | 345 | 300 | 44 | 0 | 160 | 0 | 25 | 0 | 104 | 9 | 20 | 0 | 186 | 0 | 0 | 37 | 310 | 0 | 348 | 42 | 24 | 155 | 0 | 17 | 0 | 53 | 30 | 102 | 0 | 100 | 17 | 9 | 58 | 12 | 0 | 0 | 12 | 7321.5 | 883 | 86 | 0 | 28 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1188 | 0 | 0 | 0 | 1477 | 0 | 33 | 0 | 35 | 50 | 0 | 85 | 26 | 0 | 0 | 0 | 24 | 0 | 0 | 144 | 0 | 0 | 0 | 160 | 0 | 360 | 0 | 0 | 0 | 47 | 70 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 290 | 130 | 180 | 0 | 346 | 1244 | 54 | 7057 | 14378.5 | 78.35
Total KWH | 0 | 1533120 | 666720 | 0 | 0 | 0 | 0 | 0 | 9190800 | 0 | 0 | 259056 | 224640 | 1100448 | 1250880 | 1939778 | 689290 | 265229 | 797760 | 0 | 4971000 | 0 | 0 | 0 | 269482 | 7274067 | 0 | 0 | 187401 | 1966800 | 467400 | 518400 | 0 | 10433181.82 | 1033745 | 193200 | 291840 | 0 | 175680 | 122015 | 1008000 | 138004 | 0 | 0 | 23281 | 1538180 | 1323121 | 318720 | 23207272.73 | 1798182 | 0 | 507360 | 229154.4 | 964327 | 5117181 | 0 | 0 | 0 | 14203635 | 128385 | 909963 | 0 | 6743000 | 6486000 | 7696000 | 1047024 | 2400 | 4344000 | 148824 | 555840 | 1532885 | 904320 | 86520 | 482270 | 0 | 4063680 | 0 | 435536 | 784080 | 7358000 | 0 | 8698000 | 1011000 | 640800 | 3658254.55 | 19335 | 371376 | 0 | 1204800 | 707136 | 2376000 | 0 | 2403550 | 218160 | 198000 | 1060800 | 456000 | 12000 | 263030 | 127200 | 163332519.5 | 21258182 | 3928896 | 0 | 241440 | 267264 | 0 | 0 | 0 | 0 | 0 | 0 | 567360 | 28240000 | 0 | 0 | 0 | 29277412 | 0 | 190520 | 0 | 411552 | 505920 | 0 | 546576 | 153970 | 0 | 325712 | 635906 | 157682 | 0 | 329248 | 4133727 | 0 | 0 | 0 | 4473200 | 0 | 9118036 | 0 | 28140 | 0 | 1174254 | 737641 | 118101 | 788073 | 0 | 0 | 0 | 42608.4 | 846720 | 4047 | 326496 | 6982000 | 3060000 | 5316810 | 0 | 6865455 | 27559272.73 | 435600 | 159047821.13 | 322380340.63

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 19-04-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13777.26 | MW | 12:00 Hr. | Energy Generated |  |  | 322.3803 |  | MKWHr.
| Day Peak Demand |  |  | 14453.26 | MW | 12:00 Hr. | Energy Unserverd |  |  | 16.511 |  | MKWHr.
| Evening Peak Generation |  |  | 15049.5 | MW | 21:00 Hr. | Energy Demand |  |  | 338.8913 |  | MKWHr.
| Evening Peak Demand |  |  | 16248.5 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.5 |  | °C
| Minimum Generation of the Day |  |  | 11692.64 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 921.87 |  | MMCFD
| Maximum Generation of the Day |  |  | 15049.5 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.3611 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.8548 | 0 | 10.9632 | 0 | 0 | 0.1874 | 0 | 0 | 44.0055 | Gas | 125.6887 | Gas | 438492645.2554
| Chattogram Zone |  |  | 5.4359 | 37.4109 | 7.6089 | 0 | 1.5382 | 0.15167 | 0 | 0.17568 | 52.3213 | Coal | 108.2319 | Coal | 736192742.6278
| Cumilla Zone |  |  | 28.4824 | 0 | 3.2407 | 0 | 0 | 0.43554 | 4.0637 | 0 | 36.2223 | HFO | 28.1798 | HFO | 495214506.74
| Mymensingh Zone |  |  | 0.456 | 0 | 1.6042 | 0 | 0 | 0.27503 | 0 | 0 | 2.3352 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.4289 | 0 | 0 | 0 | 0 | 0.019335 | 0 | 0 | 28.4483 | Hydro | 1.5382 | Hydro | 153818
| Khulna Zone |  |  | 3.9289 | 28.24 | 0.5087 | 0 | 0 | 0.56736 | 21.2582 | 0 | 54.5031 | Solar | 3.9668 | Solar | 62791172.65
| Barishal Zone |  |  | 8.3768 | 41.4067 | 0.7621 | 0 | 0 | 0.004047 | 0 | 0 | 50.5497 | Import | 54.5993 | Import | 315258290.18
| Rajshahi Zone |  |  | 17.725 | 0 | 1.9662 | 0 | 0 | 1.319 | 29.2774 | 0 | 50.2876 | Wind | 0.17568 | Wind | 2584252.8
| Rangpur Zone |  |  | 0 | 1.1743 | 1.5257 | 0 | 0 | 1.0074 | 0 | 0 | 3.7074
| Total |  |  | 125.6887 | 108.2319 | 28.1798 | 0 | 1.5382 | 3.9668 | 54.5993 | 0.17568 | 322.3803
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 438492645.2554 |  | Hydro | 153818
|  |  |  | Coal | 736192742.6278 |  | Solar | 62791172.65
|  |  |  | HFO | 495214506.74 |  | Import | 315258290.18
|  |  |  | HSD | 0 |  | Wind | 2584252.8
[5 empty] | Total: | 205,06,87,428 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.2582 | Peak Hr Flow | 883.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 58059163.63 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.2774 | Peak Hr Flow | 1470.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2497 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 4.0637 | Peak Hr Flow | 180.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2903 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.5993 | Peak Hr Flow | 2533.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 276 |  | 5872
|  |  |  | Chattogram |  | 92 |  | 1546
|  |  |  | Cumilla |  | 123 |  | 1575
|  |  |  | Mymensingh |  | 156 |  | 1135
|  |  |  | Sylhet |  | 85 |  | 558
|  |  |  | Khulna |  | 167 |  | 1963
|  |  |  | Barishal |  | 48 |  | 451
|  |  |  | Rajshahi |  | 124 |  | 1667
|  |  |  | Rangpur |  | 76 |  | 883
|  |  |  | Total |  | 1147 |  | 15650
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 320
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:22 | Jhenaidah 132/33kV S/S Transformer T-3 HT is restored.
|  | 08:23 | Jhenaidah 132/33kV S/S Transformer T-3 LT is restored.
| 08:33 | 12:56 | Ishwardi-Rooppur 132kV Ckt-1 Forced S/D from Ruppur 132/11kV end.
|  | 08:44 | Ishwardi-Rooppur 132kV Ckt-2 is restored.
| 08:45 | 12:55 | Ishwardi-Rooppur 132kV Ckt-2 Project Work S/D from Ishurdi 132/33kV end.
| 08:45 | 17:55 | Aminbazar 400/230/132kV S/S Bus-2 (400kV) Project Work S/D Due to Bay Extension
|  | 08:59 | Shahjadpur 132/33kV S/S T-1(405T) LT is restored.
|  | 09:20 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT is restored.
|  | 09:41 | Gopalganj 400/132kV S/S 400kV Rooppur is restored.
| 09:46 | 17:08 | Korerhat 400/230/132kV S/S ATR-3(7103T) LT Project Work S/D Due to Protection witness
| 09:47 | 17:07 | Korerhat 400/230/132kV S/S ATR-3(7103T) HT Project Work S/D Due to Protection Witness | [7 empty] | 258.0MW load
interrup.
|  | 09:50 | Rajshahi 132/33kV S/S Transformer T-2(415T) HT is restored.
|  | 09:58 | Shahjadpur 132/33kV S/S T-1(405T) HT is restored.
| 10:00 | 20:27 | Panchagarh 132/33kV S/S Thakurgaon- 2 Scheduled S/D Due to RTU Integrating with NLDC ,
Thakurgaon substation
| 10:10 | 20:30 | Thakurgaon 132/33kV S/S Panchagar CKT-2 Project Work S/D Due to RTU Panel commissioning
|  | 11:18 | Madunaghat 400/230kV S/S ATR-2 7106T HT is restored.
|  | 11:18 | Madunaghat 400/230kV S/S ATR-2 7106T LT is restored.
| 12:11 |  | Sylhet (South) S/S Sylhet (S)-Biyanibazar 132KV Ckt-1 Project Work S/D Due to Shutdown
for project work purpose.
| 12:11 |  | Sylhet (South) S/S Sylhet (S)-Biyanibazar 132KV Ckt-2 Project Work S/D Due to Shutdown
for project work purpose.
| 12:50 | 13:58 | Saidpur 132/33kV S/S TR-01 HT Scheduled S/D Due to QF- GMD-39 and as the instruction of
ALDC Bogura (499264)
| 14:02 | 17:29 | Amnura 132/33kV S/S T-1 (406T) LT Forced S/D Due to Oil leakage
| 14:03 | 17:24 | Amnura 132/33kV S/S T-1 (406T) HT Forced S/D Due to Oil leakage.
|  | 14:38 | Pabna 132/33kV S/S T-2 HT is restored.
|  | 14:50 | Pabna 132/33kV S/S T-2 LT is restored.
| 15:04 | 15:31 | Munshiganj 132/33kV S/S Transformer-2 LT Tripped showing DIR O/C TRIP relays Due to Banco | [7 empty] | 95.0MW load
|  |  | 33kv line-1 CB flashing | [7 empty] | interrup.
| 15:04 | 15:31 | Munshiganj 132/33kV S/S Transformer-1 LT Tripped showing DIR O/C TRIP relays Due to Banco | [7 empty] | 95.0MW load
|  |  | 33kv line-1 CB flashing | [7 empty] | interrup.
| 16:11 | 17:20 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Redhot maintenance | [7 empty] | 40.0MW load
interrup.
| 16:12 | 17:16 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Redhot maintenance | [7 empty] | 40.0MW load
interrup.
| 16:23 |  | Chandpur CCPP GT was forced shutdown due to bearing lube oil leakage.
| 16:34 |  | Naogaon 132/33kV S/S Main Bus Scheduled S/D Due to 132kV main Bus shut down for Bogura
ckt-1&2 cable termanation work.
|  | 16:40 | Bogura(New)-Naogaon 132 kV Ckt-1 is restored.
|  | 17:00 | Gollamari 132/33kV S/S Tr-2 HT is restored.
|  | 17:01 | Gollamari 132/33kV S/S Tr-2 LT is restored.
| 19:00 | 20:12 | Barishal 230/132kV S/S T-5 LT Tripped showing O/C relays Due to due to 33kv Jhalakhati | [7 empty] | 37.0MW load
|  |  | Feeder R-Phase Burn out | [7 empty] | interrup.
| 19:00 | 19:31 | Barishal 230/132kV S/S T-4 LT Tripped showing Over current relay relays Due to due to | [7 empty] | 37.0MW load
|  |  | 33kv Jhalakhati Feeder R-Phase Burn out | [7 empty] | interrup.
| 06:00 |  | Minimum Generation: 13152 MW.
| 06:26 |  | Haripur-Meghnaghat 230kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to Other end
and from Meghnaghat 230/132kV end Due to Red hot maintenance work in line ds
| 06:49 |  | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D Due to Instruction by NLDC
Dhaka. Increase system voltage.
| 07:00 |  | BIPTC S/S 10CF14 Tripped showing 87 (Defferntian Relay). relays.
| 07:04 |  | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to T-5 33kv Clamp change,Noise problem of | [7 empty] | 25.0MW load
|  |  | 33 kv Bus DS & Nut bolt tigting | [7 empty] | interrup.
| 07:05 |  | Gopalganj 132/33kV S/S T1 LT Scheduled S/D Due to Red hot maintenance | [7 empty] | 17.0MW load
interrup.
| 07:05 |  | Gopalganj 132/33kV S/S T1 LT Scheduled S/D Due to Red hot maintenance | [7 empty] | 17.0MW load
interrup.
| 07:06 |  | Gopalganj 132/33kV S/S T1 HT Scheduled S/D Due to Red hot Maintenance | [7 empty] | 17.0MW load
interrup.
| 07:09 |  | Nawabganj 132/33kV S/S TR-1 HT Forced S/D Due to Redhot maintenance.
| 07:09 |  | Nawabganj 132/33kV S/S TR-1 LT Forced S/D Due to Redhot maintenance
| 07:34 |  | Jhenaidah 132/33kV S/S Transformer T-1 LT Forced S/D Due to 33kV PBS BUS SECTION DS-3 | [7 empty] | 35.0MW load
|  |  | Redhot Maintenance work. | [7 empty] | interrup.
| 07:35 |  | Jhenaidah 132/33kV S/S Transformer T-1 HT Forced S/D Due to 33kV PBS BUS SECTION DS-3
Redhot Maintenance work.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 19-04-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 368 | 9190800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4971000 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 689290 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7274067 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 36 | 259056 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 146 | 1250880 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 265229 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 269482 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 467400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 518400 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 49 | 666720 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 261 | 1939778 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1100448 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1533120 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 797760 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 187401 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 224640 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 500 | 10433181.82 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 125 | 1966800 | Engine Problem
Dhaka Area Total |  |  |  |  | 6668.974 | 2482 | 44005452.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage.
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 229154.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 128385 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 507360 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1538180 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5117181 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 964327 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 54 | 1008000 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 122015 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 13 | 318720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 291840 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23281 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 193200 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 18 | 138004 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1323121 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 72 | 1033745 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 156 | 1798182 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 14203635 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 175680 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 935 | 23207272.73 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 2323.5 | 52321283.13
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 150 | 4344000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 359 | 6486000 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 305 | 7696000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 215 | 6743000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 148824 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 2400 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1047024 | Machine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 137 | 909963 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 784080 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 1532885 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 104 | 904320 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 180 | 4063680 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 482270 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 86520 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 54 | 555840 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 435536 | -
Cumilla Area Total |  |  |  |  | 2870.745 | 1614 | 36222342
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 18 | 456000 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 68 | 1060800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 198000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 263030 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 127200 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 218160 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 124 | 2335190
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 19335 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 1011000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 24 | 640800 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3658254.55 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 100 | 2376000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 707136 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 53 | 1204800 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2403550 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 371376 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7358000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 349 | 8698000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1176 | 28448251.55
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 883 | 21258182 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 29 | 241440 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 52 | 267264 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 90 | 3928896 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 567360 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1226 | 28240000 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2280 | 54503142
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 401 | 6865455 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 326496 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3060000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 27559272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5316810 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 435600 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 290 | 6982000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4047 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2371 | 50549680.73
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 325712 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 29 | 190520 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 153970 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 161 | 4133727 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 165 | 4473200 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9118036 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 157682 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 85 | 546576 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 505920 | BPDB event of default
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 411552 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28140 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1470 | 29277412 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 329248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 635906 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2459 | 50287601
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1174254 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 100 | 788073 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 42608.4 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 737641 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 118101 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 846720 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 220 | 3707397.4
Eastern Grid Total |  |  |  |  | 17417.792 | 7719.5 | 163332519.5
Western Grid Total |  |  |  |  | 11852.195 | 7330 | 159047821.13
National Grid Total |  |  |  |  | 29269.987 | 15049.5 | 322380340.63
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 19-04-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9954.02 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4548.9 | MW
i) Dhaka area |  |  | 5595.52 |  | MW | i) Khulna area |  |  |  | 1796 | MW
ii) Chattogram area |  |  | 1454.5 |  | MW | ii) Barishal area |  |  |  | 403.3 | MW
iii) Cumilla area |  |  | 1452 |  | MW | iii) Rajshahi area |  |  |  | 1542.6 | MW
iv) Mymensingh area |  |  | 979 |  | MW | iv) Rangpur area |  |  |  | 807 | MW
v) Sylhet area |  |  | 473 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14502.92 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 103 | 21:00 | 133 | Natore | 179 | 22:00
2 | AKSML | 14 | 18:30 | 68 | Hathazari | 80 | 22:00 | 134 | Nawabganj | 59 | 20:00
3 | Aftabnagar | 42 | 13:00 | 69 | Hatirjheel | 53 | 15:00 | 135 | Netrakona | 107 | 18:00
4 | Agargaon | 135 | 14:00 | 70 | Ishurdi | 77 | 14:00 | 136 | New | 80 | 15:00
5 | Agrabad | 70 | 18:00 | 71 | Jaldhaka | 55 | 21:00 | 137 | Niamatpur | 82 | 21:00
6 | Amnura | 34 | 14:00 | 72 | Jamalpur | 104 | 18:30 | 138 | Noapara | 44 | 00:00
7 | Ashuganj | 87 | 23:00 | 73 | Jashore | 158 | 22:00 | 139 | PHP | 6 | 18:00
8 | BSRM | 194 | 18:30 | 74 | Jhenaidah | 102 | 21:00 | 140 | Pabna | 96 | 19:30
9 | Bagerhat | 85 | 23:00 | 75 | Joydebpur | 163 | 19:00 | 141 | Palashbari | 126 | 19:00
10 | Bajitpur | 77 | 00:00 | 76 | Joypurhat | 59 | 20:00 | 142 | Panchagarh | 38 | 21:00
11 | Bakerganj | 14.3 | 19:00 | 77 | Juldah | 19 | 14:00 | 143 | Patiya | 9 | 02:00
12 | Bakulia | 97 | 17:00 | 78 | KSRM | 16 | 04:00 | 144 | Patuakhali | 69 | 02:00
13 | Banani | 51 | 13:00 | 79 | Kabirpur | 266 | 19:30 | 145 | Payra | 32 | 01:00
14 | Bangabhaban | 22 | 10:00 | 80 | Kachua | 93 | 02:00 | 146 | Postogola | 58 | 23:00
15 | Barapukuria | 60 | 21:00 | 81 | Kaliganj | 28 | 21:00 | 147 | Pubail | 32 | 18:30
16 | Barguna | 22 | 01:00 | 82 | Kallyanpur | 129 | 22:00 | 148 | Purbachal | 37 | 13:00
17 | Barishal | 104 | 12:00 | 83 | Kalurghat | 42 | 15:00 | 149 | Purbasadipur | 109 | 21:00
18 | Barishal-230 | 94 | 01:00 | 84 | Kamrangirchar | 85 | 19:00 | 150 | Rahanpur | 33 | 00:00
19 | Baroaulia | 69 | 15:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 26 | 13:00
20 | Baroirhat | 51 | 01:00 | 86 | Kasba | 39 | 22:00 | 152 | Rajbari | 83 | 00:00
21 | Bashundhara | 224 | 19:00 | 87 | Kazla | 110 | 19:30 | 153 | Rajendrapur | 129 | 18:00
22 | BashundharaCement | 13 | 18:00 | 88 | Keranigonj | 84 | 01:00 | 154 | Rajshahi | 128 | 00:00
23 | Beanibazar | 66 | 00:00 | 89 | Khagrachori | 30 | 00:00 | 155 | Rajshahi-230 | 96 | 13:00
24 | Benapole | 80 | 00:00 | 90 | Khulna | 93 | 12:00 | 156 | Ramganj | 106 | 21:00
25 | Bhaluka | 128 | 18:00 | 91 | Khulshi | 183 | 20:00 | 157 | Rampur | 44 | 22:00
26 | Bhandaria | 55 | 02:00 | 92 | Kishoreganj | 112 | 21:00 | 158 | Rangamati | 20 | 19:00
27 | Bhangura | 44 | 14:00 | 93 | Kodda | 286 | 10:00 | 159 | Rangpur | 124 | 20:00
28 | Bheramara(GK) | 63 | 21:00 | 94 | Kulaura | 44 | 00:00 | 160 | Ruppur | 4.4 | 16:00
29 | Bhulta | 232 | 10:00 | 95 | Kurigram | 52 | 19:00 | 161 | SSM | 10 | 00:00
30 | Bog-Sherpur | 80 | 13:00 | 96 | Kushtia | 132 | 21:00 | 162 | Saidpur | 86 | 14:00
31 | Bogura | 198 | 23:00 | 97 | Laksam | 22 | 00:00 | 163 | Satkhira | 135 | 00:00
32 | Borhanuddin | 94 | 01:00 | 98 | Lakshmipur | 40 | 22:00 | 164 | Satmasjid | 117 | 19:00
33 | Brahmanbaria | 121 | 22:00 | 99 | Lalbag | 80 | 13:00 | 165 | Savar | 232 | 19:30
34 | Cantonment | 146 | 13:00 | 100 | Lalmonirhat | 41 | 21:00 | 166 | SevenRings | 5.21 | 13:00
35 | Chandina | 40 | 02:00 | 101 | MI_Cement | 13 | 04:00 | 167 | ShahCement | 45 | 00:00
36 | Chandpur | 83 | 02:00 | 102 | Madanganj | 44 | 20:00 | 168 | Shahjadpur | 87 | 23:00
37 | Chandraghona | 39 | 18:30 | 103 | Madaripur | 127 | 21:00 | 169 | Shahjibazar | 115 | 00:00
38 | Chapai | 73 | 00:00 | 104 | Madartek | 93.44 | 23:00 | 170 | Shahmirpur | 56 | 00:00
39 | Charsaidpur | 40 | 17:00 | 105 | Madunaghat | 60 | 19:30 | 171 | Shariatpur | 96 | 00:00
40 | Chauddagram | 82 | 02:00 | 106 | Magura | 61 | 22:00 | 172 | Sherpur | 98 | 20:00
41 | Chhatak | 36 | 00:00 | 107 | Mahasthangarh | 72 | 18:30 | 173 | Shikalbaha | 28 | 01:00
42 | Chowmuhani | 138 | 02:00 | 108 | Maijdee | 45 | 02:00 | 174 | Shitalakhya | 92.7 | 12:00
43 | Chuadanga | 129 | 22:00 | 109 | Manikganj | 126 | 20:00 | 175 | Sholosohor | 49 | 16:00
44 | Coxsbazar | 117 | 13:00 | 110 | Maniknagar | 67 | 14:00 | 176 | Shyampur | 206 | 13:00
45 | Cumilla(N) | 131 | 22:00 | 111 | Matarbari | 50 | 21:00 | 177 | Siddhirganj | 137 | 12:00
46 | Cumilla(S) | 212 | 15:00 | 112 | Matuail | 84 | 13:00 | 178 | Sirajganj | 144 | 20:00
47 | Daganbhuiyan | 38 | 20:00 | 113 | Metrorail_Motijheel | 25 | 14:00 | 179 | Sonargaon | 145 | 09:00
48 | Daudkandi | 140 | 03:00 | 114 | Metrorail_Uttara | 8 | 11:00 | 180 | Sreemongol | 75 | 00:00
49 | DhakaUniversity | 92 | 13:00 | 115 | Millgate | 106 | 15:00 | 181 | Sreepur | 114 | 18:00
50 | Dhamrai | 124 | 18:00 | 116 | Mirpur | 167 | 23:00 | 182 | Srinagar | 56.6 | 19:00
51 | Dhanmondi | 149.3 | 13:00 | 117 | Mirsorai | 59 | 03:00 | 183 | Sunamganj | 49 | 00:00
52 | Dohazari | 95 | 18:00 | 118 | Mirzapur | 47 | 10:00 | 184 | Sylhet | 54 | 01:00
53 | Faridpur | 172 | 00:00 | 119 | Mithapukur | 50 | 19:30 | 185 | Sylhet-132 | 98 | 00:00
54 | Fatullah | 97 | 16:00 | 120 | Modern | N/A | N/A | 186 | TK | 22 | 03:00
55 | Fenchuganj | 37 | 01:00 | 121 | Mogbazar | 96.8 | 15:00 | 187 | Tangail | 168 | 19:30
56 | Feni | 109 | 22:00 | 122 | Mongla | 52 | 18:30 | 188 | Taraganj | 20 | 21:00
57 | GPH | 67 | 14:00 | 123 | Motijheel | 54 | 13:00 | 189 | Tasnim | 33 | 15:00
58 | Ghatail | 62 | 18:00 | 124 | Muktagacha | 34 | 13:00 | 190 | Thakurgaon | 81 | 19:30
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 105 | 18:00 | 191 | Tongi | 160 | 15:00
60 | Ghorashal-230 | 111 | 21:00 | 126 | Muradnagar | 49 | 22:00 | 192 | Ullahpara | 43 | 13:00
61 | Goalpara | 42 | 00:00 | 127 | Mymensingh | 185 | 19:00 | 193 | Ullon | 73 | 19:00
62 | Gollamari | 110 | 20:00 | 128 | Nabinagar | 12 | 22:00 | 194 | Uttara | 101 | 16:00
63 | Gopalganj | 104 | 01:00 | 129 | Naogaon | 138 | 14:00 | 195 | UttaraNew | 60 | 23:00
64 | Gulshan | 142 | 13:00 | 130 | Narail | 62 | 00:00 | 196 | Zigatola | 92 | 13:00
65 | Halishahar | 104 | 15:00 | 131 | Narinda | 74 | 13:00
66 | HaripurSBU | 140 | 10:00 | 132 | Narshingdi | 177 | 02:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 19-04-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 12951.04 | 572 |  | 13549.04
1:00 | 12468.3 | 317 |  | 12799.3
2:00 | 12275.13 | 138 |  | 12419.13
3:00 | 11964.31 | 130 |  | 12100.31
4:00 | 11892.77 | 122 |  | 12019.77
5:00 | 11718.48 | 117 |  | 11840.48
6:00 | 11692.64 | 105 |  | 11802.64
7:00 | 12227.08 | 121 |  | 12353.08
8:00 | 12338.1 | 110 |  | 12453.1
9:00 | 12615.72 | 132 |  | 12753.72
10:00 | 12951.74 | 192 |  | 13152.74
11:00 | 13270.3 | 510 |  | 13803.3
12:00 | 13777.26 | 647 |  | 14453.26
13:00 | 13853.8 | 860 |  | 14752.8
14:00 | 13744.56 | 1204 |  | 15002.74
15:00 | 13750.05 | 1293 |  | 15101.05
16:00 | 13744.07 | 1203 |  | 15001.07
17:00 | 13671.57 | 1080 |  | 14800.57
18:00 | 14200.48 | 747 |  | 14981.48
19:00 | 14381.5 | 1451 |  | 15897.5
19:30 | 14713.5 | 1325 |  | 16098.5
20:00 | 14822.5 | 1220 |  | 16097.5
21:00 | 15049.5 | 1147 |  | 16248.5
22:00 | 14813.5 | 1363 |  | 16237.5
23:00 | 14378.5 | 1730 |  | 16186.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 19-04-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6612 | 6339.04 | 12951.04 | DAILY GENERATION CURVE
00:30 | 6395.5 | 6314.17 | 12709.67
01:00 | 6179 | 6289.3 | 12468.3 | 19-04-2026
01:30 | 6183.5 | 6188.215 | 12371.715
02:00 | 6188 | 6087.13 | 12275.13
02:30 | 6131.5 | 5988.22 | 12119.72
03:00 | 6075 | 5889.31 | 11964.31
03:30 | 6076 | 5852.54 | 11928.54
04:00 | 6077 | 5815.77 | 11892.77
04:30 | 6010.5 | 5795.125 | 11805.625
05:00 | 5944 | 5774.48 | 11718.48
05:30 | 5930.185 | 5775.375 | 11705.56
06:00 | 5916.37 | 5776.27 | 11692.64
06:30 | 6007.01 | 5952.85 | 11959.86
07:00 | 6097.65 | 6129.43 | 12227.08
07:30 | 6101.16 | 6181.43 | 12282.59
08:00 | 6104.67 | 6233.43 | 12338.1
08:30 | 6195.715 | 6281.195 | 12476.91
09:00 | 6286.76 | 6328.96 | 12615.72
09:30 | 6430.85 | 6352.88 | 12783.73
10:00 | 6574.94 | 6376.8 | 12951.74
10:30 | 6647.94 | 6463.08 | 13111.02
11:00 | 6720.94 | 6549.36 | 13270.3
11:30 | 6786.28 | 6737.5 | 13523.78
12:00 | 6851.62 | 6925.64 | 13777.26
12:30 | 6885.54 | 6929.99 | 13815.53
13:00 | 6919.46 | 6934.34 | 13853.8
13:30 | 6913.025 | 6886.155 | 13799.18
14:00 | 6906.59 | 6837.97 | 13744.56
14:30 | 6954.755 | 6792.55 | 13747.305
15:00 | 7002.92 | 6747.13 | 13750.05
15:30 | 6979.095 | 6767.965 | 13747.06
16:00 | 6955.27 | 6788.8 | 13744.07
16:30 | 6918.79 | 6789.03 | 13707.82
17:00 | 6882.31 | 6789.26 | 13671.57
17:30 | 7071.135 | 6864.89 | 13936.025
18:00 | 7259.96 | 6940.52 | 14200.48
18:30 | 7336.73 | 6954.26 | 14290.99
19:00 | 7413.5 | 6968 | 14381.5
19:30 | 7536.5 | 7177 | 14713.5
20:00 | 7592.5 | 7230 | 14822.5
20:30 | 7656 | 7280 | 14936 |  | Executive Engineer
21:00 | 7719.5 | 7330 | 15049.5 |  | Network Operation Division
21:30 | 7624 | 7307.5 | 14931.5
22:00 | 7528.5 | 7285 | 14813.5
22:30 | 7425 | 7171 | 14596
23:00 | 7321.5 | 7057 | 14378.5

## En-Curve
QF-LDC-12
Date | 19-04-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3586 | 1539 | 788 | 0 | 164 | 1134.04 | 60 | 4570 | 0 | 411 | 699 | 0 | 0 | 0 | 572 | DAILY ENERGY CURVE
00:30 | 3577.5 | 1496 | 835 | 0 | 163 | 1086.67 | 60 | 4556.5 | 0 | 358 | 577 | 0 | 0 | 0 | 444.5 | 19-04-2026
01:00 | 3569 | 1453 | 882 | 0 | 162 | 1039.3 | 60 | 4543 | 0 | 305 | 455 | 0 | 0 | 0 | 317
01:30 | 3594 | 1466.5 | 883 | 0 | 163 | 960.215 | 60 | 4538.5 | 0 | 265.5 | 441 | 0 | 0 | 0 | 227.5 | Energy Generated | 322.3803 |  | MKWHr
02:00 | 3619 | 1480 | 884 | 0 | 164 | 881.13 | 60 | 4534 | 0 | 226 | 427 | 0 | 0 | 0 | 138 | Energy not Served | 16.511 |  | MKWHr
02:30 | 3602.5 | 1478.5 | 883.5 | 0 | 162 | 856.22 | 60 | 4520.5 | 0 | 198 | 358.5 | 0 | 0 | 0 | 134 | Total Energy Requirement | 338.8913 |  | MKWHr
03:00 | 3586 | 1477 | 883 | 0 | 160 | 831.31 | 60 | 4507 | 0 | 170 | 290 | 0 | 0 | 0 | 130
03:30 | 3612.5 | 1495 | 883 | 0 | 157 | 833.04 | 60 | 4462 | 0 | 154.5 | 271.5 | 0 | 0 | 0 | 126
04:00 | 3639 | 1513 | 883 | 0 | 154 | 834.77 | 60 | 4417 | 0 | 139 | 253 | 0 | 0 | 0 | 122
04:30 | 3636.5 | 1508.5 | 883 | 0 | 153 | 839.125 | 60 | 4387.5 | 0 | 131 | 207 | 0 | 0 | 0 | 119.5
05:00 | 3634 | 1504 | 883 | 0 | 152 | 843.48 | 60 | 4358 | 0 | 123 | 161 | 0 | 0 | 0 | 117
05:30 | 3628 | 1500 | 883.5 | 0 | 149 | 842.19 | 60 | 4358.5 | 4.37 | 123 | 156.5 | 0 | 0 | 0.5 | 111
06:00 | 3622 | 1496 | 884 | 0 | 146 | 840.9 | 60 | 4359 | 8.74 | 123 | 152 | 0 | 0 | 1 | 105
06:30 | 3744 | 1503.5 | 883.5 | 0 | 146 | 882.6 | 60 | 4400 | 48.26 | 126.5 | 165 | 0 | 0 | 0.5 | 113
07:00 | 3866 | 1511 | 883 | 0 | 146 | 924.3 | 60 | 4441 | 87.78 | 130 | 178 | 0 | 0 | 0 | 121
07:30 | 3868 | 1498 | 883 | 0 | 147 | 920.175 | 60 | 4446.5 | 144.915 | 130 | 185 | 0 | 0 | 0 | 115.5
08:00 | 3870 | 1485 | 883 | 0 | 148 | 916.05 | 60 | 4452 | 202.05 | 130 | 192 | 0 | 0 | 0 | 110
08:30 | 3878 | 1487 | 883 | 0 | 152 | 920.525 | 60 | 4457.5 | 294.885 | 136 | 205 | 0 | 0 | 3 | 121
09:00 | 3886 | 1489 | 883 | 0 | 156 | 925 | 60 | 4463 | 387.72 | 142 | 218 | 0 | 0 | 6 | 132
09:30 | 3895 | 1500.5 | 883.5 | 0 | 156 | 923.5 | 45 | 4463.5 | 426.73 | 176 | 307.5 | 0 | 0 | 6.5 | 162
10:00 | 3904 | 1512 | 884 | 0 | 156 | 922 | 30 | 4464 | 465.74 | 210 | 397 | 0 | 0 | 7 | 192
10:30 | 3885.5 | 1505 | 883.5 | 0 | 160 | 1060.5 | 50 | 4428.5 | 479.52 | 227.5 | 420.5 | 0 | 0 | 10.5 | 351
11:00 | 3867 | 1498 | 883 | 0 | 164 | 1199 | 70 | 4393 | 493.3 | 245 | 444 | 0 | 0 | 14 | 510
11:30 | 3854 | 1519.5 | 883 | 0 | 169 | 1341 | 70 | 4371.5 | 536.03 | 275 | 485.25 | 0 | 0 | 19.5 | 578.5
12:00 | 3841 | 1541 | 883 | 0 | 174 | 1483 | 70 | 4350 | 578.76 | 305 | 526.5 | 0 | 0 | 25 | 647
12:30 | 3825 | 1520.5 | 883 | 0 | 176 | 1475.5 | 70 | 4296.5 | 559.53 | 310.5 | 674.5 | 0 | 0 | 24.5 | 753.5
13:00 | 3809 | 1500 | 883 | 0 | 178 | 1468 | 70 | 4243 | 540.3 | 316 | 822.5 | 0 | 0 | 24 | 860
13:30 | 3784 | 1482.5 | 882.5 | 0 | 192 | 1481 | 70 | 4212 | 504.68 | 313 | 850.5 | 0 | 0 | 27 | 1032
14:00 | 3759 | 1465 | 882 | 0 | 206 | 1494 | 70 | 4181 | 469.06 | 310 | 878.5 | 0 | 0 | 30 | 1204
14:30 | 3736.5 | 1512 | 882.5 | 0 | 209 | 1491 | 68 | 4221 | 392.555 | 310.5 | 898.25 | 0 | 0 | 26 | 1248.5
15:00 | 3714 | 1559 | 883 | 0 | 212 | 1488 | 66 | 4261 | 316.05 | 311 | 918 | 0 | 0 | 22 | 1293
15:30 | 3700 | 1544.5 | 883 | 0 | 208 | 1485 | 66 | 4280.5 | 300.06 | 329 | 931.5 | 0 | 0 | 19.5 | 1248
16:00 | 3686 | 1530 | 883 | 0 | 204 | 1482 | 66 | 4300 | 284.07 | 347 | 945 | 0 | 0 | 17 | 1203
16:30 | 3638 | 1483.5 | 883 | 0 | 197 | 1488 | 66 | 4339.5 | 196.32 | 374.5 | 1028 | 0 | 0 | 14 | 1141.5
17:00 | 3590 | 1437 | 883 | 0 | 190 | 1494 | 66 | 4379 | 108.57 | 402 | 1111 | 0 | 0 | 11 | 1080
17:30 | 3557.5 | 1492 | 883 | 0 | 173 | 1483.5 | 66 | 4397 | 58.025 | 541.5 | 1276 | 0 | 0 | 8.5 | 913.5
18:00 | 3525 | 1547 | 883 | 0 | 156 | 1473 | 66 | 4415 | 7.48 | 681 | 1441 | 0 | 0 | 6 | 747
18:30 | 3453.5 | 1494.5 | 869 | 0 | 156 | 1473 | 66 | 4483 | 3.74 | 714.5 | 1572.25 | 0 | 0 | 5.5 | 1099
19:00 | 3382 | 1442 | 855 | 0 | 156 | 1473 | 66 | 4551 | 0 | 748 | 1703.5 | 0 | 0 | 5 | 1451
19:30 | 3400 | 1389 | 883 | 0 | 166 | 1473 | 68 | 4722 | 0 | 771 | 1837.5 | 0 | 0 | 4 | 1325
20:00 | 3449 | 1427 | 882 | 0 | 180 | 1479 | 68 | 4718 | 0 | 772 | 1844.5 | 0 | 0 | 3 | 1220
20:30 | 3493 | 1510.5 | 882.5 | 0 | 180 | 1474.5 | 69 | 4738 | 0 | 775 | 1812 | 0 | 0 | 1.5 | 1183.5
21:00 | 3537 | 1594 | 883 | 0 | 180 | 1470 | 70 | 4758 | 0 | 778 | 1779.5 | 0 | 0 | 0 | 1147
21:30 | 3542 | 1573.5 | 883 | 0 | 177 | 1473 | 70 | 4740.5 | 0 | 765.5 | 1705 | 0 | 0 | 2 | 1255
22:00 | 3547 | 1553 | 883 | 0 | 174 | 1476 | 70 | 4723 | 0 | 753 | 1630.5 | 0 | 0 | 4 | 1363
22:30 | 3503 | 1548 | 883 | 0 | 180 | 1476.5 | 70 | 4693.5 | 0 | 751.5 | 1488.5 | 0 | 0 | 2 | 1546.5
23:00 | 3459 | 1543 | 883 | 0 | 186 | 1477 | 70 | 4664 | 0 | 750 | 1346.5 | 0 | 0 | 0 | 1730
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 19-04-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 378 | 19:00 | 368 | 12:00 | Madunaghat | 396 | 01:00 | 388 | 10:00
Amtali | 415 | 04:00 | 406 | 00:00 | Meghnaghat | 381 | 05:00 | 372 | 09:00
Ashuganj | 405 | 19:00 | 388 | 10:00 | Payra | 411 | 14:00 | 408 | 01:00
Bhulta | 395 | 19:00 | 378 | 10:00 | Rahanpur | 417 | 02:00 | 394 | 12:00
Bibiana | 400 | 04:00 | 393 | 12:00 | Rampal | 398 | 05:00 | 390 | 01:00
BIPTC | 401 | 04:00 | 392 | 15:00
Bogura | 412 | 00:00 | 382 | 12:00
Gopalganj | 392 | 06:00 | 384 | 10:00
Kaliakoir | 375 | 05:00 | 362 | 09:00
Korerhat | 397 | 19:30 | 386 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 19:00 | 213 | 12:00 | Jhenaidah | 225 | 05:00 | 216 | 20:00
AKSML | 227 | 18:30 | 220 | 10:00 | Kachua | 225 | 19:30 | 218 | 01:00
Aminbazar | 225 | 19:30 | 214 | 12:00 | Kaliakoir | 229 | 19:00 | 217 | 09:00
Ashuganj | 228 | 19:00 | 219 | 16:00 | Keranigonj | 223 | 19:00 | 212 | 12:00
Ashuganj-400 | 228 | 19:00 | 218 | 15:00 | Khulna(S) | 227 | 14:00 | 219 | 20:00
Baghabari | 235 | 05:00 | 225 | 20:00 | Korerhat | 229 | 19:00 | 218 | 10:00
Barapukuria | 232 | 00:00 | 213 | 12:00 | Madunaghat | 233 | 12:00 | 221 | 10:00
Barapukuria-230 | 232 | 23:00 | 214 | 12:00 | Madunaghat-400 | 228 | 20:00 | 221 | 10:00
Barishal | 226 | 19:00 | 221 | 01:00 | Maniknagar | 222 | 03:00 | 213 | 09:00
Bheramara | 231 | 05:00 | 223 | 12:00 | Meghnaghat | 231 | 04:00 | 221 | 10:00
Bhulta | 223 | 05:00 | 213 | 12:00 | Meghnaghat-400 | 224 | 05:00 | 216 | 12:00
Bibiana | 234 | 05:00 | 228 | 00:00 | Mirsorai | 234 | 19:00 | 224 | 02:00
BIPTC | 234 | 05:00 | 222 | 12:00 | Naogaon | 230 | 00:00 | 204 | 12:00
Bogura | 239 | 00:00 | 223 | 12:00 | Purbasadipur | 232 | 00:00 | 212 | 12:00
Bogura-400 | 239 | 00:00 | 223 | 12:00 | Rajshahi | 231 | 03:00 | 220 | 12:00
Borhanuddin | 230 | 14:00 | 226 | 00:00 | Rampal | 227 | 06:00 | 219 | 01:00
BSRM | 226 | 19:00 | 219 | 02:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 222 | 18:00 | 216 | 02:00 | Rampura | 222 | 05:00 | 211 | 12:00
Cumilla(N) | 223 | 06:00 | 216 | 09:00 | Shikalbaha | 228 | 19:00 | 219 | 09:00
Faridpur | 220 | 19:00 | 214 | 00:00 | Shyampur | 222 | 05:00 | 213 | 12:00
Fenchuganj | 237 | 05:00 | 232 | 01:00 | Siddhirganj | 223 | 04:00 | 214 | 10:00
Feni | 227 | 19:00 | 218 | 02:00 | Sirajgonj | 240 | 03:00 | 232 | 12:00
Ghorashal | 230 | 01:00 | 220 | 10:00 | Sreepur | 226 | 05:00 | 217 | 18:00
Ghorashal-230 | 222 | 19:00 | 212 | 09:00 | Tongi | 222 | 04:00 | 211 | 10:00
Gopalganj | 219 | 05:00 | 215 | 00:00
GPH | 228 | 18:30 | 221 | 08:00
Haripur | 223 | 05:00 | 214 | 10:00
Hasnabad | 221 | 19:30 | 213 | 09:00
Hathazari | 228 | 19:00 | 220 | 10:00
Ishurdi | 234 | 05:00 | 225 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 131 | 22:00 | 121 | 10:00 | Madunaghat | 134 | 19:00 | 104 | 04:00
Agargaon | 131 | 23:00 | 123 | 12:00 | Magura | 133 | 05:00 | 125 | 20:00
Agrabad | 132 | 12:00 | 126 | 10:00 | Mahasthangarh | 138 | 00:00 | 126 | 12:00
AKS | 130 | 00:00 | 126 | 15:00 | Maijdee | 126 | 19:00 | 119 | 02:00
Aminbazar | 128 | 19:00 | 121 | 12:00 | Manikganj | 123 | 03:00 | 118 | 08:00
Amnura | 139 | 00:00 | 125 | 12:00 | Maniknagar | 131 | 05:00 | 123 | 10:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 133 | 13:00 | 113 | 06:00
Ashuganj-230 | 136 | 04:00 | 133 | 12:00 | Matuail | 129 | 05:00 | 123 | 12:00
Bagerhat | 124 | 13:00 | 114 | 01:00 | Metrorail_Motijheel | 131 | 05:00 | 123 | 10:00
Bajitpur | 133 | 01:00 | 126 | 18:00 | Metrorail_Uttara | 128 | 04:00 | 120 | 09:00
Bakerganj | 132 | 19:00 | 128 | 02:00 | Millgate | 129 | 03:00 | 120 | 09:00
Bakulia | 134 | 00:00 | 130 | 02:00 | Mirpur | 127 | 19:00 | 120 | 09:00
Banani | 130 | 19:30 | 120 | 10:00 | Mirzapur | 132 | 00:00 | 123 | 16:00
Bangabhaban | 133 | 02:00 | 123 | 10:00 | Mithapukur | 135 | 01:00 | 124 | 12:00
Barapukuria | 139 | 00:00 | 125 | 12:00 | MI_Cement | 132 | 18:30 | 120 | 12:00
Barguna | 131 | 15:00 | 128 | 04:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 19:00 | 127 | 01:00 | Mogbazar | 132 | 22:00 | 122 | 10:00
Barishal-230 | 132 | 19:00 | 127 | 01:00 | Mongla | 124 | 13:00 | 115 | 00:00
Baroaulia | 135 | 06:00 | 129 | 10:00 | Motijheel | 131 | 05:00 | 123 | 10:00
Baroirhat | 129 | 19:00 | 125 | 09:00 | Muktagacha | 137 | 00:00 | 115 | 18:30
Bashundhara | 130 | 19:00 | 120 | 08:00 | Munshiganj | 127 | 18:30 | 122 | 08:00
BashundharaCement | 134 | 04:00 | 123 | 12:00 | Muradnagar | 125 | 19:00 | 120 | 02:00
Beanibazar | 133 | 03:00 | 122 | 00:00 | Mymensingh | 139 | 00:00 | 113 | 23:00
Benapole | 125 | 08:00 | 116 | 20:00 | Nabinagar | 132 | 19:00 | 121 | 08:00
Bhaluka | 134 | 00:00 | 124 | 18:00 | Naogaon | 137 | 00:00 | 123 | 12:00
Bhandaria | 128 | 19:30 | 120 | 02:00 | Narail | 132 | 05:00 | 124 | 20:00
Bhangura | 134 | 03:00 | 126 | 12:00 | Narinda | 131 | 5:00 | 123 | 10:00
Bheramara | 136 | 03:00 | 130 | 12:00 | Narshingdi | 128 | 06:00 | 118 | 10:00
Bheramara(GK) | 136 | 04:00 | 130 | 12:00 | Natore | 135 | 02:00 | 125 | 20:00
Bhulta | 123 | 19:00 | 118 | 09:00 | Nawabganj | 132 | 05:00 | 126 | 12:00
Bog-Sherpur | 138 | 02:00 | 126 | 12:00 | Netrakona | 131 | 01:00 | 116 | 18:00
Bogura | 140 | 00:00 | 128 | 12:00 | New | 129 | 04:00 | 122 | 09:00
Bogura-230 | 139 | 00:00 | 128 | 12:00 | Niamatpur | 138 | 00:00 | 126 | 12:00
Brahmanbaria | 129 | 19:00 | 125 | 18:00 | Noapara | 127 | 06:00 | 120 | 20:00
Cantonment | 131 | 04:00 | 123 | 12:00 | Pabna | 135 | 03:00 | 127 | 12:00
Chandina | 129 | 19:00 | 124 | 02:00 | Palashbari | 137 | 00:00 | 123 | 12:00
Chandpur | 130 | 19:00 | 122 | 07:00 | Panchagarh | 139 | 13:00 | 124 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 134 | 19:00 | 129 | 09:00 | Patiya | 132 | 00:00 | 129 | 05:00
Chapai | 140 | 00:00 | 128 | 12:00 | Patuakhali | 132 | 18:00 | 127 | 01:00
Charsaidpur | 129 | 22:00 | 123 | 09:00 | Payra | 134 | 06:00 | 132 | 00:00
Chauddagram | 127 | 19:00 | 122 | 02:00 | PHP | 127 | 17:00 | 124 | 02:00
Chhatak | 131 | 03:00 | 122 | 00:00 | Postogola | 134 | 19:00 | 123 | 12:00
Chowmuhani | 125 | 18:30 | 120 | 02:00 | Pubail | 134 | 18:30 | 126 | 11:00
Chuadanga | 131 | 05:00 | 119 | 20:00 | Purbachal | 131 | 00:00 | 120 | 09:00
Coxsbazar | 122 | 14:00 | 115 | 02:00 | Purbasadipur | 135 | 00:00 | 123 | 12:00
Cumilla(N) | 128 | 19:00 | 124 | 09:00 | Rahanpur | 142 | 00:00 | 130 | 12:00
Cumilla(S) | 128 | 01:00 | 115 | 15:00 | Rahanpur-400 | 143 | 00:00 | 130 | 12:00
Daganbhuiyan | 127 | 19:00 | 121 | 02:00 | Rahim | 129 | 04:00 | 123 | 16:00
Daudkandi | 123 | 19:00 | 117 | 08:00 | Rajbari | 125 | 02:00 | 121 | 00:00
DhakaUniversity | 138 | 03:00 | 121 | 10:00 | Rajendrapur | 133 | 01:00 | 123 | 18:00
Dhamrai | 130 | 19:30 | 119 | 09:00 | Rajshahi | 134 | 01:00 | 123 | 12:00
Dhanmondi | 130 | 06:00 | 124 | 12:00 | Rajshahi-230 | 133 | 02:00 | 126 | 12:00
Dohazari | 129 | 00:00 | 124 | 09:00 | Ramganj | 125 | 20:00 | 119 | 08:00
Faridpur | 127 | 19:30 | 124 | 00:00 | Rampur | 132 | 19:00 | 127 | 08:00
Fatullah | 133 | 19:00 | 121 | 10:00 | Rampura | 131 | 22:00 | 121 | 10:00
Fenchuganj | 135 | 03:00 | 131 | 01:00 | Rangamati | 133 | 19:00 | 128 | 10:00
Feni | 127 | 19:00 | 122 | 10:00 | Rangpur | 136 | 00:00 | 125 | 11:00
Feni-230 | 127 | 19:00 | 122 | 02:00 | Ruppur | 136 | 02:00 | 130 | 12:00
Ghatail | 136 | 00:00 | 117 | 23:00 | Saidpur | 136 | 00:00 | 124 | 11:00
Ghorashal | 136 | 19:30 | 128 | 09:00 | Santhia | N/A | N/A | N/A | N/A
Goalpara | 129 | 08:00 | 122 | 00:00 | Satkhira | 125 | 14:00 | 115 | 00:00
Gollamari | 129 | 08:00 | 122 | 01:00 | Satmasjid | 131 | 05:00 | 123 | 12:00
Gopalganj | 128 | 14:00 | 124 | 00:00 | Savar | 127 | 19:00 | 118 | 09:00
Gopalganj-400 | 130 | 06:00 | 127 | 00:00 | SevenRings | 136 | 19:00 | 128 | 09:00
Gulshan | 131 | 22:00 | 120 | 10:00 | ShahCement | 129 | 22:00 | 123 | 09:00
Halishahar | 133 | 19:00 | 129 | 09:00 | Shahjadpur | 135 | 00:00 | 130 | 12:00
Haripur | 130 | 05:00 | 124 | 09:00 | Shahjibazar | 132 | 06:00 | 123 | 00:00
HaripurSBU | 130 | 05:00 | 124 | 09:00 | Shahmirpur | 133 | 00:00 | 129 | 09:00
Hasnabad | 134 | 19:00 | 123 | 12:00 | Shariatpur | 128 | 08:00 | 124 | 00:00
Hathazari | 133 | 13:00 | 130 | 05:00 | Sherpur | 140 | 00:00 | 109 | 18:30
Hatirjheel | 132 | 23:00 | 120 | 10:00 | Shikalbaha | 123 | 00:00 | 119 | 09:00
Ishurdi | 137 | 03:00 | 131 | 12:00 | Shikalbaha-230 | 135 | 23:00 | 131 | 09:00
Jaldhaka | 135 | 00:00 | 123 | 11:00 | Shitalakhya | 132 | 18:30 | 120 | 12:00
Jamalpur | 140 | 00:00 | 112 | 22:00 | Sholosohor | 133 | 19:00 | 129 | 09:00
Jashore | 127 | 04:00 | 118 | 20:00 | Shyampur | 127 | 20:00 | 118 | 12:00
Jhenaidah | 134 | 04:00 | 121 | 20:00 | Shyampur-230 | 128 | 19:00 | 122 | 09:00
Jhenaidah-230 | 134 | 05:00 | 127 | 21:00 | Siddhirganj | 129 | 04:00 | 124 | 09:00
Joydebpur | 133 | 22:00 | 122 | 10:00 | Sirajganj | 135 | 02:00 | 123 | 21:00
Joypurhat | 136 | 00:00 | 121 | 12:00 | Sonargaon | 127 | 03:00 | 121 | 10:00
Juldah | 133 | 00:00 | 130 | 08:00 | Sreemongol | 133 | 06:00 | 124 | 00:00
Kabirpur | 136 | 19:00 | 116 | 09:00 | Sreepur | 137 | 01:00 | 127 | 18:00
Kachua | 129 | 19:00 | 123 | 02:00 | Srinagar | 132 | 05:00 | 126 | 12:00
Kaliakoir | 135 | 00:00 | 122 | 09:00 | SSM | 138 | 23:00 | 132 | 10:00
Kaliganj | 132 | 04:00 | 123 | 20:00 | Sunamganj | 129 | 02:00 | 120 | 00:00
Kallyanpur | 127 | 05:00 | 120 | 09:00 | Sylhet | 132 | 03:00 | 126 | 00:00
Kalurghat | 134 | 19:00 | 129 | 09:00 | Sylhet-132 | 132 | 02:00 | 126 | 00:00
Kamrangirchar | 133 | 05:00 | 118 | 12:00 | Tangail | 133 | 00:00 | 120 | 16:00
Kaptai | N/A | N/A | N/A | N/A | Taraganj | 136 | 00:00 | 124 | 10:00
Kasba | 125 | 19:00 | 119 | 02:00 | Tasnim | 127 | 05:00 | 121 | 10:00
Kazla | 130 | 05:00 | 123 | 12:00 | Thakurgaon | 136 | 13:00 | 124 | 12:00
Keranigonj | 133 | 05:00 | 127 | 10:00 | TK | 132 | 00:00 | 129 | 08:00
Khagrachori | 132 | 19:00 | 125 | 10:00 | Tongi | 132 | 04:00 | 124 | 08:00
Khulna | 129 | 15:00 | 122 | 00:00 | Ullahpara | 135 | 03:00 | 126 | 12:00
Khulna(S) | 129 | 08:00 | 123 | 00:00 | Ullon | 131 | 22:00 | 121 | 10:00
Khulshi | 131 | 00:00 | 128 | 08:00 | Uttara | 128 | 22:00 | 119 | 10:00
Kishoreganj | 133 | 02:00 | 123 | 18:00 | UttaraNew | 128 | 04:00 | 119 | 09:00
Kodda | 136 | 19:00 | 122 | 09:00 | Zigatola | 133 | 05:00 | 127 | 10:00
Korerhat | 130 | 19:30 | 127 | 02:00
KSRM | 133 | 19:00 | 129 | 07:00
Kulaura | 134 | 02:00 | 128 | 00:00
Kurigram | 132 | 00:00 | 121 | 11:00
Kushtia | 134 | 02:00 | 126 | 20:00
Laksam | 129 | 19:00 | 122 | 10:00
Lakshmipur | 124 | 17:00 | 119 | 02:00
Lalbag | 132 | 19:00 | 126 | 12:00
Lalmonirhat | 133 | 01:00 | 121 | 10:00
Madanganj | 134 | 04:00 | 123 | 12:00
Madaripur | 130 | 04:00 | 127 | 00:00
Madartek | 131 | 23:00 | 120 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division