## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 21-04-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-04-2026 | during | 21-04-2026 | during | 21-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 350 | 334 | 412 | 412 | 380 | 380 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 450 | 450 | 226 | 226 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 15 | 55 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 318 | 324 | 335 | 335 | 335 | 335 | Machine Problem
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17.5 | 36 | 53.97 | 53.97 | 17 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 46 | 144 | 149.36 | 149.36 | 48 | 48 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19 | 21.5 | 33 | 33 | 22 | 22 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 49 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 48 | 294 | 300 | 300 | 48 | 294 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 46 | 133 | 149 | 149 | 52 | 88 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 105 | 105 | 105 | 52 | 105 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 35 | 162 | 162 | 35 | 35 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 16 | 17 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 500 | 530 | 584 | 584 | 481 | 481 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 125 | 142 | 160 | 160 | 125 | 125 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1868.5 | 2496.5 | 5947.22 | 5915.22 | 1940 | 2354
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 25.5 | 25.5 | 25.5 | 0 | 25 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 3 | 50 | 50 | 50 | 19 | 50 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 60 | 70 | 70 | 70 | 70 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 213 | 217 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 34 | 105 | 105 | 34 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 54 | 50 | 56 | 64 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 68 | 68 | 34 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 10 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 12 | 13 | 108 | 108 | 12 | 12 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.95 | 0 | 3.78 | 0 | 3.78 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 14 | 54.36 | 54.36 | 0 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 56 | 54 | 110 | 110 | 109 | 109 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 116 | 116 | 18 | 18 | Liquid fuel shortage
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 17 | 145 | 163 | 163 | 17 | 17 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 612 | 1224 | 1224 | 612 | 612 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 50 | 18 | 22 | 6 | 22 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 935 | 1015 | 1015 | 1015 | 935 | 935 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2192.95 | 2367.5 | 3928.64 | 3923.86 | 2195.78 | 2315
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221 | 201 | 182 | 221 | 221 | 190 | 190 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 304 | 305 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 300 | 320 | 342.01 | 342.01 | 320 | 320 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 220 | 225 | 393 | 393 | 215 | 215 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | Machine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 15 | 137 | 20 | 150 | 21 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 36 | 0 | 0 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 103 | 200 | 200 | 17 | 80 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 176 | 164 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 18 | 113 | 113 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 19 | 51 | 115 | 115 | 17 | 51 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 37 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.745 | 1362 | 1605 | 2439.19 | 2493.19 | 1465.01 | 1611.01
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-04-2026 | during | 21-04-2026 | during | 21-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 11 | 27 | 157.5 | 157.5 | 35 | 35 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.92 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 68 | 67 | 10 | 10 | 10 | 10 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 70 | 70 | 70 | 70 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 25.47 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 114.39 | 132 | 361.9 | 314 | 179.9 | 144
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 24 | 24 | 30 | 30 | 24 | 24 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 154 | 152 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 75 | 41 | 100 | 100 | 100 | 100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 80 | 81 | 81 | 81 | 81 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 99 | 98 | 98 | 98 | 98 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 16 | 25 | 25 | 17 | 17 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 338 | 305 | 350 | 350 | 350 | 350 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1161 | 1099 | 1260 | 1260 | 1196 | 1196
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 882 | 881 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 29 | 28 | 28 | 28 | 28 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 18 | 52 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 94 | 122 | 410 | 410 | 180 | 180 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 94 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1190 | 1213 | 1234.2 | 1234.2 | 1194 | 1194 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2278 | 2297 | 3582.2 | 3492.2 | 2557.1 | 2467.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 253 | 353 | 250 | 400 | 250 | 400 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 124 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1140 | 1212 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 230 | 290 | 307 | 307 | 290 | 290 | Machine Problem
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.65 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1967.65 | 2256 | 2412 | 2561 | 2168 | 2317
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 48.48 | 0 | 52 | 0 | 52 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 40 | 31 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 164 | 150 | 214 | 214 | 150 | 150 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 169 | 140 | 220 | 220 | 170 | 170 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 413 | 413 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 25 | 25 | 0 | 25 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 75 | 85 | 85 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 70 | 113 | 113 | 113 | 0 | 50 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 113 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.16 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1481 | 1481 | 1435.88 | 1435.88 | 1356 | 1356 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 53.65 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 106 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2620.29 | 2566 | 3214.72 | 2995.87 | 2379.85 | 2356
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 46 | 0 | 0 | 50 | 50 | plant availability zero
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 92 | 99 | 113 | 113 | 35 | 113 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.3 | 0 | 6.8 | 0 | 6.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 0 | 70 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 16 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 193 | 0 | 200 | 0 | 200 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 354.3 | 380 | 478.8 | 242 | 321.8 | 233
System Total |  |  |  |  | 28823.2 | 29269.987 | 13919.08 | 15199 | 23624.67 | 23197.34 | 14403.44 | 14993.11
Forecast Scenario (21-04-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13685 |  | 2932.2798 |  | 15790
|  |  |  | 1:00 | 13198 |  | 2102 |  | 15300
|  |  |  | 2:00 | 13226 |  | 1974 |  | 15200
|  |  |  | 3:00 | 13209 |  | 1691 |  | 14900
|  |  |  | 4:00 | 13210 |  | 1590 |  | 14800
|  |  |  | 5:00 | 13200 |  | 1450 |  | 14650
|  |  |  | 6:00 | 13152 |  | 1398 |  | 14550
|  |  |  | 7:00 | 13155 |  | 1245 |  | 14400
|  |  |  | 8:00 | 12986 |  | 1214 |  | 14200
|  |  |  | 9:00 | 13257 |  | 993 |  | 14250
|  |  |  | 10:00 | 13444 |  | 956 |  | 14400
|  |  |  | 11:00 | 13550 |  | 950 |  | 14500
|  |  |  | 12:00 | 13900 |  | 1100 |  | 15000
|  |  |  | 13:00 | 14000 |  | 1200 |  | 15200
|  |  |  | 14:00 | 13900 |  | 1400 |  | 15300
|  |  |  | 15:00 | 13850 |  | 1450 |  | 15300
|  |  |  | 16:00 | 13850 |  | 1400 |  | 15250
|  |  |  | 17:00 | 13600 |  | 1400 |  | 15000
|  |  |  | 18:00 | 13900 |  | 1400 |  | 15300
|  |  |  | 18:30 | 14000 |  | 1900 |  | 15900
|  |  |  | 19:00 | 14400 |  | 1950 |  | 16350
|  |  |  | 19:30 | 14900 |  | 1450 |  | 16350
|  |  |  | 20:00 | 15100 |  | 1300 |  | 16400
|  |  |  | 21:00 | 15200 |  | 1400 |  | 16600
|  |  |  | 22:00 | 15000 |  | 1450 |  | 16450
|  |  |  | 23:00 | 14500 |  | 1700 |  | 16200
Probable Maximum Temperature: |  |  | 36.2°C
Probable Maximum Demand at Day Peak: |  |  | 15000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 1400
Probable Maximum Demand at Evening Peak: |  |  | 16600.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15200.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 309.07421 MKWHr. |  | 300 | 150 | 160 | 160 | 100 | 180 | 80 | 150 | 120 | 1400
*** This report is generated digitally from Operation Information System (OIS) at 10:21 hrs on 21-04-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 20-04-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13919.08 | MW | 12:00 Hr. | Energy Generated |  |  | 333.5565 |  | MKWHr.
| Day Peak Demand |  |  | 14953.08 | MW | 12:00 Hr. | Energy Unserverd |  |  | 32.38 |  | MKWHr.
| Evening Peak Generation |  |  | 15199 | MW | 21:00 Hr. | Energy Demand |  |  | 365.9365 |  | MKWHr.
| Evening Peak Demand |  |  | 16448.82 | MW | 21:00 Hr. | Maximum Temperature |  |  | 36.2 |  | °C
| Minimum Generation of the Day |  |  | 12990.46 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 888.61 |  | MMCFD
| Maximum Generation of the Day |  |  | 15199 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.6929 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.5758 | 0 | 12.7189 | 0 | 0 | 0.21532 | 0 | 0 | 46.51 | Gas | 120.5184 | Gas | 420655895.4667
| Chattogram Zone |  |  | 5.3385 | 37.6127 | 7.7994 | 0 | 1.5764 | 0.12832 | 0 | 0.53568 | 52.991 | Coal | 110.8481 | Coal | 753411913.5395
| Cumilla Zone |  |  | 26.9674 | 0 | 3.4266 | 0 | 0 | 0.3772 | 4.0781 | 0 | 34.8493 | HFO | 34.1937 | HFO | 603294612.48
| Mymensingh Zone |  |  | 0.38304 | 0 | 2.0399 | 0 | 0 | 0.26476 | 0 | 0 | 2.6877 | HSD | 0.74372 | HSD | 19968747.75
| Sylhet Zone |  |  | 26.8333 | 0 | 0 | 0 | 0 | 0.054965 | 0 | 0 | 26.8883 | Hydro | 1.5764 | Hydro | 157642
| Khulna Zone |  |  | 2.4808 | 29.0836 | 0.84346 | 0 | 0 | 0.67392 | 21.0284 | 0 | 54.1102 | Solar | 4.3941 | Solar | 70003482.194
| Barishal Zone |  |  | 8.1422 | 43.0276 | 0.79219 | 0 | 0 | 0.004306 | 0 | 0 | 51.9663 | Import | 60.7464 | Import | 357072160.25
| Rajshahi Zone |  |  | 16.7973 | 0 | 4.5256 | 0 | 0 | 1.4954 | 35.64 | 0 | 58.4583 | Wind | 0.53568 | Wind | 7879852.8
| Rangpur Zone |  |  | 0 | 1.1241 | 2.0477 | 0.74372 | 0 | 1.1799 | 0 | 0 | 5.0954
| Total |  |  | 120.5184 | 110.8481 | 34.1937 | 0.74372 | 1.5764 | 4.3941 | 60.7464 | 0.53568 | 333.5565
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 420655895.4667 |  | Hydro | 157642
|  |  |  | Coal | 753411913.5395 |  | Solar | 70003482.194
|  |  |  | HFO | 603294612.48 |  | Import | 357072160.25
|  |  |  | HSD | 19968747.75 |  | Wind | 7879852.8
[5 empty] | Total: | 223,24,44,306 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.0284 | Peak Hr Flow | 881.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 56039654.54 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 35.64 | Peak Hr Flow | 1481.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2676 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 4.0781 | Peak Hr Flow | 164.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2882 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 60.7464 | Peak Hr Flow | 2526.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 113 |  | 5829
|  |  |  | Chattogram |  | 50 |  | 1546
|  |  |  | Cumilla |  | 206 |  | 1527
|  |  |  | Mymensingh |  | 213 |  | 1222
|  |  |  | Sylhet |  | 76 |  | 573
|  |  |  | Khulna |  | 257 |  | 1909
|  |  |  | Barishal |  | 77 |  | 480
|  |  |  | Rajshahi |  | 86 |  | 1795
|  |  |  | Rangpur |  | 118 |  | 936
|  |  |  | Total |  | 1196 |  | 15817
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 320
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:31 | 10:26 | Gollamari 132/33kV S/S Tr-1 LT Scheduled S/D Due to Paint job
| 08:31 | 10:24 | Gollamari 132/33kV S/S Tr-1 HT Scheduled S/D
| 08:33 | 21:46 | Aminbazar 400/230/132kV S/S Bus-1 (400kV) Project Work S/D Due to Scheduled IDRNPP
project work
|  | 09:14 | Haripur-Meghnaghat 230kV Ckt-1 is restored.
| 09:16 | 09:33 | Sonargaon 132/33kV S/S Tr-2 LT Tripped showing TR/P relay,DIR O/C & E/F Relay relays Due | [7 empty] | 30.0MW load
|  |  | to due to PBS 33KV Borpa Feeder Source side isolator finger burnt | [7 empty] | interrup.
| 09:20 | 14:35 | Thakurgaon 132/33kV S/S Panchagar CKT-2 Project Work S/D Due to RTU pannel comissioning
work.
| 09:23 | 14:36 | Panchagarh 132/33kV S/S Thakurgaon- 2 Scheduled S/D Due to RTU integrating with NLDC,
tHAKURGAON substation
|  | 09:37 | Gopalganj 132/33kV S/S T1 HT is restored.
|  | 09:38 | Gopalganj 132/33kV S/S T1 LT is restored.
|  | 09:40 | Jhenaidah 132/33kV S/S Transformer T-1 HT is restored.
|  | 09:41 | Jhenaidah 132/33kV S/S Transformer T-1 LT is restored.
| 09:46 | 15:53 | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-1 Scheduled S/D from Mithapukur 132/33kV
end Due to sky wire stringing from lilo tower
| 09:46 | 15:53 | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-2 Scheduled S/D from Mithapukur 132/33kV
end Due to sky wire sringing
| 10:12 | 10:43 | BIPTC S/S 10CF14 Scheduled S/D Due to Corrective Maintenance
| 10:48 |  | Khulshi-Madunaghat 132kV Ckt-2 Forced S/D from Khulshi 132/33kV end Due to As per
instruction from NLDC AE(299725)
|  | 10:57 | Barishal 230/132kV S/S T-5 LT is restored.
|  | 11:13 | Nawabganj 132/33kV S/S TR-1 HT is restored.
|  | 11:15 | Nawabganj 132/33kV S/S TR-1 LT is restored.
| 11:16 |  | Juldah 132/33kV S/S 132/33 KV 406T T-1 HT Forced S/D Due to 132/33 KV transformer T-1 was
tripped and and termination cable (R-Phase) was burnt . Now it needs to be replaced .
| 11:24 | 13:11 | Madunaghat-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to 400
kV Korerhat ckt- 2 shutdown instructed by NLDC.
| 12:00 |  | Day Peak Generation is 13914 MW.
| 12:44 | 13:50 | Sonargaon 132/33kV S/S Tr-2 LT Forced S/D Due to PBS 33KV BORPA FEEDER ISOLATOR FINGER | [7 empty] | 60.0MW load
|  |  | CHANGING | [7 empty] | interrup.
| 12:45 | 14:43 | Feni 230/132kV S/S ATR-1 HT Project Work S/D Due to TRANSFORMER OIL LEAKAGE CHECK
| 12:45 | 14:43 | Feni 230/132kV S/S ATR-1 LT Project Work S/D Due to TRANSFORMER OIL LEAKAGE CHECK
| 12:45 | 13:49 | Sonargaon 132/33kV S/S Tr-2 HT Forced S/D Due to Due to pbs 33kv Borpa feeder isolator | [7 empty] | 60.0MW load
|  |  | finger changing | [7 empty] | interrup.
| 12:55 | 15:25 | Muradnagar 132/33kV S/S 132KV Transformar-01 HT Project Work S/D Due to 33kv DS
Maintenance work.
|  | 13:11 | Korerhat 400/230/132kV S/S Meghnaghat-2 is restored.
| 14:51 | 16:40 | Feni 230/132kV S/S ATR-3 HT Project Work S/D Due to INSPECTION OIL leakage and rust
| 14:51 | 16:41 | Feni 230/132kV S/S ATR-3 LT Project Work S/D Due to INSPECTION OIL leakage and rust
| 15:40 | 16:46 | Muradnagar 132/33kV S/S 132KV Transformar-02 HT Project Work S/D Due to 33kv DS
maintenance work
| 16:14 | 16:53 | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to For installation of a new spring
charging motor for the 33 kV breaker.
| 16:14 | 16:55 | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to For installation of a new spring
charging motor for the 33 kV breaker.
| 16:35 | 18:56 | Jhenaidah 132/33kV S/S Transformer T-1 LT Forced S/D Due to Change the conductor of 'Y' | [7 empty] | 45.0MW load
|  |  | phage busbar at bus section-3, 33KV under the T-1A. | [7 empty] | interrup.
| 16:35 | 18:55 | Jhenaidah 132/33kV S/S Transformer T-1 HT Forced S/D Due to Change the conductor of 'Y' | [7 empty] | 45.0MW load
|  |  | phage busbar at bus section-3, 33KV under the T-1A. | [7 empty] | interrup.
| 21:00 |  | Evening Peak Generation: 15198 MW.
| 07:00 |  | Minimum Generation is 13341 MW.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 20-04-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 334 | 8499600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4851000 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 702922 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 324 | 7730094 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 36 | 259920 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 144 | 1752480 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 265061 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 271217 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21.5 | 486000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 503640 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 49 | 563520 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 294 | 2273236 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 1101024 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1243200 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 792000 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 215321 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 263880 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 530 | 11505454.55 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3230400 | Engine Problem
Dhaka Area Total |  |  |  |  | 6668.974 | 2496.5 | 46509969.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 301923 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 107325 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 574560 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 60 | 1576420 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5062935 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 965999 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 50 | 1260480 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 105823 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 10 | 275520 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 13 | 348480 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21000 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 388909 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 14 | 138539 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 54 | 1347375 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 922091 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 145 | 1445236 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 14536362 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 18 | 535680 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1015 | 23076363.64 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 2367.5 | 52991020.64
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 182 | 4436000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 305 | 8114800 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 320 | 7620000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 225 | 5306500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1044752 | Machine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 137 | 909963 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 763808 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 103 | 1019040 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 164 | 4078080 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 445340 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 18 | 165480 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 51 | 568320 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 377200 | -
Cumilla Area Total |  |  |  |  | 2870.745 | 1605 | 34849283
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 27 | 383043 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 67 | 1488000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 222000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 251810 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 126480 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 203400 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 132 | 2687683
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 54965 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 963000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 24 | 631080 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3586745.46 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 41 | 884100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 714048 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1781760 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 99 | 2393500 | Plant availability less
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 302112 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7473000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 305 | 8104000 | FGMO not available because of Cooling Tower Fan
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1099 | 26888310.46
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 881 | 21028364 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 29 | 350400 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 52 | 493056 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 122 | 2480832 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 673920 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1213 | 29083630 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2297 | 54110202
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 353 | 6814545 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 348192 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 2855000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1212 | 29405090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5287180 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 444000 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 290 | 6808000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4306 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2256 | 51966313.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 379608 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 31 | 600986 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 202956 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 150 | 3688364 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 140 | 3964164 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9144800 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 220960 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 75 | 478320 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1550880 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 1471488 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 31200 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1481 | 35639985 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 354016 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 730560 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2566 | 58458287
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 165 | 743715 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 46 | 1124072 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 1462108 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 36318.72 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 585609 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 146399 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 997200 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 380 | 5095421.72
Eastern Grid Total |  |  |  |  | 17417.792 | 7700 | 163926266.65
Western Grid Total |  |  |  |  | 11852.195 | 7499 | 169630224.63
National Grid Total |  |  |  |  | 29269.987 | 15199 | 333556491.28
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 20-04-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10038.89 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4581.7 | MW
i) Dhaka area |  |  | 5715.89 |  | MW | i) Khulna area |  |  |  | 1652.3 | MW
ii) Chattogram area |  |  | 1496 |  | MW | ii) Barishal area |  |  |  | 402.8 | MW
iii) Cumilla area |  |  | 1321 |  | MW | iii) Rajshahi area |  |  |  | 1708.6 | MW
iv) Mymensingh area |  |  | 1009 |  | MW | iv) Rangpur area |  |  |  | 818 | MW
v) Sylhet area |  |  | 497 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14620.59 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 112 | 19:30 | 133 | Natore | 160 | 21:00
2 | AKSML | 13 | 23:00 | 68 | Hathazari | 93 | 20:00 | 134 | Nawabganj | 59.4 | 19:30
3 | Aftabnagar | 44 | 13:00 | 69 | Hatirjheel | 54 | 15:00 | 135 | Netrakona | 137 | 19:30
4 | Agargaon | 136 | 16:00 | 70 | Ishurdi | 79 | 13:00 | 136 | New | 82 | 12:00
5 | Agrabad | 70 | 13:00 | 71 | Jaldhaka | 68 | 22:00 | 137 | Niamatpur | 100 | 23:00
6 | Amnura | 36 | 23:00 | 72 | Jamalpur | 96 | 07:00 | 138 | Noapara | 41 | 21:00
7 | Ashuganj | 72 | 00:00 | 73 | Jashore | 152 | 13:00 | 139 | PHP | 7 | 16:00
8 | BSRM | 199 | 08:00 | 74 | Jhenaidah | 121 | 20:00 | 140 | Pabna | 108 | 19:00
9 | Bagerhat | 83 | 20:00 | 75 | Joydebpur | 166 | 20:00 | 141 | Palashbari | 136 | 22:00
10 | Bajitpur | 100 | 19:30 | 76 | Joypurhat | 64 | 06:00 | 142 | Panchagarh | 52 | 22:00
11 | Bakerganj | 14.4 | 18:30 | 77 | Juldah | 20 | 15:00 | 143 | Patiya | 9 | 01:00
12 | Bakulia | 101 | 19:30 | 78 | KSRM | 12 | 06:00 | 144 | Patuakhali | 62 | 18:30
13 | Banani | 53.2 | 13:00 | 79 | Kabirpur | 266 | 19:30 | 145 | Payra | 30 | 05:00
14 | Bangabhaban | 22 | 10:00 | 80 | Kachua | 86 | 21:00 | 146 | Postogola | 59 | 16:00
15 | Barapukuria | 72 | 22:00 | 81 | Kaliganj | 28 | 20:00 | 147 | Pubail | 30 | 20:00
16 | Barguna | 20 | 14:00 | 82 | Kallyanpur | 123 | 18:30 | 148 | Purbachal | 37 | 13:00
17 | Barishal | 109 | 16:00 | 83 | Kalurghat | 41 | 10:00 | 149 | Purbasadipur | 116 | 21:00
18 | Barishal-230 | 112 | 18:30 | 84 | Kamrangirchar | 85 | 18:30 | 150 | Rahanpur | 38 | 19:00
19 | Baroaulia | 66 | 19:30 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 26 | 18:00
20 | Baroirhat | 58 | 20:00 | 86 | Kasba | 37 | 00:00 | 152 | Rajbari | 81 | 18:30
21 | Bashundhara | 227 | 18:30 | 87 | Kazla | 125 | 13:00 | 153 | Rajendrapur | 127 | 19:30
22 | BashundharaCement | 14 | 19:00 | 88 | Keranigonj | 90 | 19:30 | 154 | Rajshahi | 116 | 23:00
23 | Beanibazar | 54 | 18:30 | 89 | Khagrachori | 36 | 20:00 | 155 | Rajshahi-230 | 111 | 21:00
24 | Benapole | 68 | 14:00 | 90 | Khulna | 94 | 12:00 | 156 | Ramganj | 90 | 21:00
25 | Bhaluka | 155 | 19:30 | 91 | Khulshi | 191 | 19:30 | 157 | Rampur | 46 | 19:30
26 | Bhandaria | 46 | 14:00 | 92 | Kishoreganj | 140 | 20:00 | 158 | Rangamati | 18 | 20:00
27 | Bhangura | 50 | 14:00 | 93 | Kodda | 312 | 20:00 | 159 | Rangpur | 140 | 22:00
28 | Bheramara(GK) | 71 | 18:30 | 94 | Kulaura | 42 | 22:00 | 160 | Ruppur | 4.4 | 12:00
29 | Bhulta | 206 | 18:30 | 95 | Kurigram | 62 | 22:00 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 88 | 19:00 | 96 | Kushtia | 150 | 13:00 | 162 | Saidpur | 97 | 22:00
31 | Bogura | 194 | 00:00 | 97 | Laksam | 22 | 01:00 | 163 | Santhia | 40 | 20:00
32 | Borhanuddin | 90 | 18:30 | 98 | Lakshmipur | 39 | 19:00 | 164 | Satkhira | 126 | 07:00
33 | Brahmanbaria | 133 | 21:00 | 99 | Lalbag | 74 | 13:00 | 165 | Satmasjid | 118 | 16:00
34 | Cantonment | 156 | 13:00 | 100 | Lalmonirhat | 56 | 22:00 | 166 | Savar | 238 | 19:30
35 | Chandina | 40 | 19:00 | 101 | MI_Cement | 13.1 | 14:00 | 167 | SevenRings | 19.24 | 16:00
36 | Chandpur | 66 | 20:00 | 102 | Madanganj | 43 | 20:00 | 168 | ShahCement | 45 | 11:00
37 | Chandraghona | 40 | 22:00 | 103 | Madaripur | 105 | 15:00 | 169 | Shahjadpur | 90 | 07:00
38 | Chapai | 71 | 12:00 | 104 | Madartek | 92.25 | 00:00 | 170 | Shahjibazar | 104 | 21:00
39 | Charsaidpur | 39 | 00:00 | 105 | Madunaghat | 58 | 20:00 | 171 | Shahmirpur | 52 | 19:30
40 | Chauddagram | 68 | 21:00 | 106 | Magura | 63 | 13:00 | 172 | Shariatpur | 79 | 15:00
41 | Chhatak | 26 | 02:00 | 107 | Mahasthangarh | 99 | 20:00 | 173 | Sherpur | 100 | 18:30
42 | Chowmuhani | 131 | 18:30 | 108 | Maijdee | 40 | 05:00 | 174 | Shikalbaha | 33 | 07:00
43 | Chuadanga | 126 | 20:00 | 109 | Manikganj | 126 | 19:30 | 175 | Shitalakhya | 91.7 | 16:00
44 | Coxsbazar | 149 | 10:00 | 110 | Maniknagar | 81 | 16:00 | 176 | Sholosohor | 48 | 09:00
45 | Cumilla(N) | 123 | 02:00 | 111 | Matarbari | 49 | 20:00 | 177 | Shyampur | 182 | 00:00
46 | Cumilla(S) | 199 | 16:00 | 112 | Matuail | 84 | 16:00 | 178 | Siddhirganj | 137 | 18:30
47 | Daganbhuiyan | 33 | 22:00 | 113 | Metrorail_Motijheel | 27 | 21:00 | 179 | Sirajganj | 150 | 20:00
48 | Daudkandi | 127 | 06:00 | 114 | Metrorail_Uttara | 8 | 18:30 | 180 | Sonargaon | 148 | 21:00
49 | DhakaUniversity | 94 | 13:00 | 115 | Millgate | 105 | 16:00 | 181 | Sreemongol | 65 | 22:00
50 | Dhamrai | 130 | 20:00 | 116 | Mirpur | 156 | 15:00 | 182 | Sreepur | 119 | 19:30
51 | Dhanmondi | 149 | 13:00 | 117 | Mirsorai | 61 | 08:00 | 183 | Srinagar | 58.6 | 22:00
52 | Dohazari | 110 | 19:30 | 118 | Mirzapur | 38 | 06:00 | 184 | Sunamganj | 38 | 19:30
53 | Faridpur | 151 | 21:00 | 119 | Mithapukur | 64 | 22:00 | 185 | Sylhet | 56 | 21:00
54 | Fatullah | 97 | 16:00 | 120 | Modern | N/A | N/A | 186 | Sylhet-132 | 103 | 22:00
55 | Fenchuganj | 36 | 21:00 | 121 | Mogbazar | 100 | 15:00 | 187 | TK | 28 | 19:30
56 | Feni | 99 | 18:30 | 122 | Mongla | 53 | 07:00 | 188 | Tangail | 152 | 02:00
57 | GPH | 77 | 05:00 | 123 | Motijheel | 55 | 16:00 | 189 | Taraganj | 21 | 22:00
58 | Ghatail | 60 | 00:00 | 124 | Muktagacha | 28 | 07:00 | 190 | Tasnim | 26 | 07:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 131 | 20:00 | 191 | Thakurgaon | 95 | 22:00
60 | Ghorashal-230 | 110 | 22:00 | 126 | Muradnagar | 48 | 22:00 | 192 | Tongi | 157 | 21:00
61 | Goalpara | 39 | 13:00 | 127 | Mymensingh | 205 | 22:00 | 193 | Ullahpara | 44 | 13:00
62 | Gollamari | 98 | 18:30 | 128 | Nabinagar | 12 | 20:00 | 194 | Ullon | 74 | 00:00
63 | Gopalganj | 102 | 13:00 | 129 | Naogaon | 148 | 21:00 | 195 | Uttara | 106 | 16:00
64 | Gulshan | 150 | 13:00 | 130 | Narail | 54 | 20:00 | 196 | UttaraNew | 58 | 00:00
65 | Halishahar | 104 | 09:00 | 131 | Narinda | 82 | 13:00 | 197 | Zigatola | 96 | 18:30
66 | HaripurSBU | 140 | 19:30 | 132 | Narshingdi | 189 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 20-04-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13685.5 | 1829 |  | 15596.81
1:00 | 13198.5 | 1912 |  | 15196.5
2:00 | 13226.5 | 1837 |  | 15146.5
3:00 | 13209.5 | 1596 |  | 14877.5
4:00 | 13210.5 | 1471 |  | 14747.5
5:00 | 13200.5 | 1337 |  | 14597.5
6:00 | 13170.66 | 1240 |  | 14466.46
7:00 | 13160.02 | 1189 |  | 14403.02
8:00 | 12990.46 | 1112 |  | 14152.46
9:00 | 13261.63 | 948 |  | 14252.63
10:00 | 13448.05 | 913 |  | 14402.05
11:00 | 13571.8 | 938 |  | 14551.8
12:00 | 13919.08 | 989 |  | 14953.08
13:00 | 14036.03 | 1164 |  | 15252.03
14:00 | 14001.51 | 1246 |  | 15303.51
15:00 | 13866.3 | 1402 |  | 15331.3
16:00 | 13851.35 | 1415 |  | 15330.35
17:00 | 13632.97 | 1339 |  | 15031.97
18:00 | 13910.24 | 1358 |  | 15329.24
19:00 | 14414 | 1840 |  | 16337
19:30 | 14915 | 1371 |  | 16348
20:00 | 15134 | 1210 |  | 16398
21:00 | 15199 | 1196 |  | 16448.82
22:00 | 15011 | 1326 |  | 16396.67
23:00 | 14554 | 1573 |  | 16198
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 20-04-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6773.5 | 6912 | 13685.5 | DAILY GENERATION CURVE
00:30 | 6659.5 | 6782.5 | 13442
01:00 | 6545.5 | 6653 | 13198.5 | 20-04-2026
01:30 | 6563 | 6649.5 | 13212.5
02:00 | 6580.5 | 6646 | 13226.5
02:30 | 6579 | 6639 | 13218
03:00 | 6577.5 | 6632 | 13209.5
03:30 | 6535 | 6675 | 13210
04:00 | 6492.5 | 6718 | 13210.5
04:30 | 6487 | 6718.5 | 13205.5
05:00 | 6481.5 | 6719 | 13200.5
05:30 | 6466.585 | 6718.995 | 13185.58
06:00 | 6451.67 | 6718.99 | 13170.66
06:30 | 6446.715 | 6718.625 | 13165.34
07:00 | 6441.76 | 6718.26 | 13160.02
07:30 | 6336.24 | 6739 | 13075.24
08:00 | 6230.72 | 6759.74 | 12990.46
08:30 | 6295.56 | 6830.485 | 13126.045
09:00 | 6360.4 | 6901.23 | 13261.63
09:30 | 6394.43 | 6960.41 | 13354.84
10:00 | 6428.46 | 7019.59 | 13448.05
10:30 | 6485.785 | 7024.14 | 13509.925
11:00 | 6543.11 | 7028.69 | 13571.8
11:30 | 6620.975 | 7124.465 | 13745.44
12:00 | 6698.84 | 7220.24 | 13919.08
12:30 | 6724.53 | 7253.025 | 13977.555
13:00 | 6750.22 | 7285.81 | 14036.03
13:30 | 6729.29 | 7289.48 | 14018.77
14:00 | 6708.36 | 7293.15 | 14001.51
14:30 | 6671.635 | 7262.27 | 13933.905
15:00 | 6634.91 | 7231.39 | 13866.3
15:30 | 6714.105 | 7144.72 | 13858.825
16:00 | 6793.3 | 7058.05 | 13851.35
16:30 | 6741.265 | 7000.895 | 13742.16
17:00 | 6689.23 | 6943.74 | 13632.97
17:30 | 6826.29 | 6945.315 | 13771.605
18:00 | 6963.35 | 6946.89 | 13910.24
18:30 | 7186.675 | 6975.445 | 14162.12
19:00 | 7410 | 7004 | 14414
19:30 | 7632 | 7283 | 14915
20:00 | 7656 | 7478 | 15134
20:30 | 7678 | 7488.5 | 15166.5 |  | Executive Engineer
21:00 | 7700 | 7499 | 15199 |  | Network Operation Division
21:30 | 7630 | 7475 | 15105
22:00 | 7560 | 7451 | 15011
22:30 | 7415 | 7367.5 | 14782.5
23:00 | 7270 | 7284 | 14554

## En-Curve
QF-LDC-12
Date | 20-04-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3521 | 1585.5 | 883 | 0 | 176 | 1471 | 70 | 4579 | 0 | 503 | 897 | 0 | 0 | 0 | 1829 | DAILY ENERGY CURVE
00:30 | 3531.5 | 1583 | 835 | 0 | 175 | 1484 | 70 | 4591 | 0 | 472.5 | 700 | 0 | 0 | 0 | 1870.5 | 20-04-2026
01:00 | 3542 | 1580.5 | 787 | 0 | 174 | 1497 | 70 | 4603 | 0 | 442 | 503 | 0 | 0 | 0 | 1912
01:30 | 3540 | 1594 | 787 | 0 | 169 | 1489 | 70 | 4607.5 | 0 | 442 | 513 | 0 | 0 | 1 | 1874.5 | Energy Generated | 333.5565 |  | MKWHr
02:00 | 3538 | 1607.5 | 787 | 0 | 164 | 1481 | 70 | 4612 | 0 | 442 | 523 | 0 | 0 | 2 | 1837 | Energy not Served | 32.38 |  | MKWHr
02:30 | 3543.5 | 1597.5 | 787 | 0 | 164 | 1480.5 | 69 | 4606.5 | 0 | 440 | 523.5 | 0 | 0 | 6.5 | 1716.5 | Total Energy Requirement | 365.9365 |  | MKWHr
03:00 | 3549 | 1587.5 | 787 | 0 | 164 | 1480 | 68 | 4601 | 0 | 438 | 524 | 0 | 0 | 11 | 1596
03:30 | 3525.5 | 1574.5 | 834 | 0 | 164 | 1478 | 67 | 4596.5 | 0 | 438 | 515.5 | 0 | 0 | 17 | 1533.5
04:00 | 3502 | 1561.5 | 881 | 0 | 164 | 1476 | 66 | 4592 | 0 | 438 | 507 | 0 | 0 | 23 | 1471
04:30 | 3478.5 | 1589 | 881 | 0 | 160 | 1485 | 66 | 4601.5 | 0 | 419.5 | 505.5 | 0 | 0 | 19.5 | 1404
05:00 | 3455 | 1616.5 | 881 | 0 | 156 | 1494 | 66 | 4611 | 0 | 401 | 504 | 0 | 0 | 16 | 1337
05:30 | 3462 | 1594.5 | 881 | 0 | 149 | 1493 | 66.5 | 4608 | 4.58 | 397.5 | 513.5 | 0 | 0 | 16 | 1288.5
06:00 | 3469 | 1572.5 | 881 | 0 | 142 | 1492 | 67 | 4605 | 9.16 | 394 | 523 | 0 | 0 | 16 | 1240
06:30 | 3466 | 1565 | 881 | 0 | 142 | 1490.5 | 67.5 | 4589.5 | 38.34 | 397.5 | 514 | 0 | 0 | 14 | 1214.5
07:00 | 3463 | 1557.5 | 881 | 0 | 142 | 1489 | 68 | 4574 | 67.52 | 401 | 505 | 0 | 0 | 12 | 1189
07:30 | 3397.5 | 1426.75 | 882 | 0 | 147 | 1487 | 68 | 4557 | 154.99 | 390 | 555.5 | 0 | 0 | 9.5 | 1150.5
08:00 | 3332 | 1296 | 883 | 0 | 152 | 1485 | 68 | 4540 | 242.46 | 379 | 606 | 0 | 0 | 7 | 1112
08:30 | 3333 | 1320.5 | 882.5 | 0 | 150 | 1485 | 69 | 4517 | 298.045 | 379 | 677.5 | 0 | 0 | 14.5 | 1030
09:00 | 3334 | 1345 | 882 | 0 | 148 | 1485 | 70 | 4494 | 353.63 | 379 | 749 | 0 | 0 | 22 | 948
09:30 | 3330.5 | 1428.5 | 882.5 | 0 | 152 | 1487.5 | 70 | 4446.5 | 431.34 | 375 | 729.5 | 0 | 0 | 21.5 | 930.5
10:00 | 3327 | 1512 | 883 | 0 | 156 | 1490 | 70 | 4399 | 509.05 | 371 | 710 | 0 | 0 | 21 | 913
10:30 | 3334 | 1522.5 | 882.5 | 0 | 158 | 1487.5 | 70 | 4401 | 546.425 | 353 | 726 | 0 | 0 | 29 | 925.5
11:00 | 3341 | 1533 | 882 | 0 | 160 | 1485 | 70 | 4403 | 583.8 | 335 | 742 | 0 | 0 | 37 | 938
11:30 | 3416 | 1562 | 882 | 0 | 168 | 1483 | 70 | 4405 | 618.69 | 334 | 763.25 | 0 | 0 | 43.5 | 963.5
12:00 | 3491 | 1591 | 882 | 0 | 176 | 1481 | 70 | 4407 | 653.58 | 333 | 784.5 | 0 | 0 | 50 | 989
12:30 | 3475 | 1624 | 882 | 0 | 183 | 1486 | 70 | 4467.5 | 595.555 | 314.5 | 837.5 | 0 | 0 | 42.5 | 1076.5
13:00 | 3459 | 1657 | 882 | 0 | 190 | 1491 | 70 | 4528 | 537.53 | 296 | 890.5 | 0 | 0 | 35 | 1164
13:30 | 3415 | 1627.25 | 882 | 0 | 191 | 1491 | 70 | 4562.5 | 536.52 | 309 | 897.5 | 0 | 0 | 37 | 1205
14:00 | 3371 | 1597.5 | 882 | 0 | 192 | 1491 | 70 | 4597 | 535.51 | 322 | 904.5 | 0 | 0 | 39 | 1246
14:30 | 3322.5 | 1592 | 882 | 0 | 191 | 1489 | 65 | 4621.5 | 487.155 | 319.5 | 922.25 | 0 | 0 | 42 | 1324
15:00 | 3274 | 1586.5 | 882 | 0 | 190 | 1487 | 60 | 4646 | 438.8 | 317 | 940 | 0 | 0 | 45 | 1402
15:30 | 3261 | 1595.25 | 882 | 0 | 195 | 1485 | 60 | 4610 | 354.575 | 325 | 1046 | 0 | 0 | 45 | 1408.5
16:00 | 3248 | 1604 | 882 | 0 | 200 | 1483 | 60 | 4574 | 270.35 | 333 | 1152 | 0 | 0 | 45 | 1415
16:30 | 3230 | 1548.25 | 882 | 0 | 193 | 1481 | 60 | 4575 | 197.41 | 374.5 | 1156 | 0 | 0 | 45 | 1377
17:00 | 3212 | 1492.5 | 882 | 0 | 186 | 1479 | 60 | 4576 | 124.47 | 416 | 1160 | 0 | 0 | 45 | 1339
17:30 | 3196 | 1443.5 | 882 | 0 | 173 | 1484.5 | 60 | 4609 | 68.605 | 544 | 1271 | 0 | 0 | 40 | 1348.5
18:00 | 3180 | 1394.5 | 882 | 0 | 160 | 1490 | 60 | 4642 | 12.74 | 672 | 1382 | 0 | 0 | 35 | 1358
18:30 | 3208.5 | 1423 | 869 | 0 | 167 | 1483.5 | 60 | 4654 | 6.37 | 696 | 1568.25 | 0 | 0 | 26.5 | 1599
19:00 | 3237 | 1451.5 | 856 | 0 | 174 | 1477 | 60 | 4666 | 0 | 720 | 1754.5 | 0 | 0 | 18 | 1840
19:30 | 3369 | 1535.5 | 882 | 0 | 174 | 1482 | 60 | 4728 | 0 | 743 | 1844.5 | 75 | 0 | 22 | 1371
20:00 | 3399 | 1619.5 | 882 | 0 | 174 | 1490 | 60 | 4730 | 0 | 762 | 1828.5 | 165 | 0 | 24 | 1210
20:30 | 3415 | 1635 | 881.5 | 0 | 169 | 1485.5 | 60 | 4735.5 | 0 | 770.5 | 1828.5 | 165 | 0 | 21 | 1203
21:00 | 3431 | 1650.5 | 881 | 0 | 164 | 1481 | 60 | 4741 | 0 | 779 | 1828.5 | 165 | 0 | 18 | 1196
21:30 | 3418.5 | 1640 | 881.5 | 0 | 167 | 1481 | 60 | 4743.5 | 0 | 765 | 1770 | 165 | 0 | 13.5 | 1261
22:00 | 3406 | 1629.5 | 882 | 0 | 170 | 1481 | 60 | 4746 | 0 | 751 | 1711.5 | 165 | 0 | 9 | 1326
22:30 | 3417 | 1650.5 | 882 | 0 | 173 | 1485.5 | 60 | 4767.5 | 0 | 748 | 1426.5 | 165 | 0 | 7.5 | 1449.5
23:00 | 3428 | 1671.5 | 882 | 0 | 176 | 1490 | 60 | 4789 | 0 | 745 | 1141.5 | 165 | 0 | 6 | 1573
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 20-04-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 381 | 19:30 | 367 | 10:00 | Madunaghat | 396 | 07:00 | 390 | 11:00
Amtali | 409 | 08:00 | 398 | 13:00 | Meghnaghat | 381 | 01:00 | 367 | 12:00
Ashuganj | 400 | 03:00 | 388 | 15:00 | Payra | 411 | 03:00 | 400 | 12:00
Bhulta | 408 | 07:00 | 375 | 12:00 | Rahanpur | 406 | 19:00 | 395 | 06:00
Bibiana | 401 | 19:00 | 392 | 12:00 | Rampal | 400 | 08:00 | 386 | 13:00
BIPTC | 400 | 03:00 | 388 | 15:00
Bogura | 397 | 09:00 | 384 | 06:00
Gopalganj | 392 | 01:00 | 379 | 12:00
Kaliakoir | 375 | 19:00 | 357 | 12:00
Korerhat | 395 | 18:00 | 386 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 03:00 | 215 | 12:00 | Jhenaidah | 228 | 08:00 | 213 | 13:00
AKSML | 228 | 22:00 | 222 | 14:00 | Kachua | 225 | 17:00 | 217 | 14:00
Aminbazar | 227 | 03:00 | 215 | 12:00 | Kaliakoir | 230 | 19:00 | 218 | 12:00
Ashuganj | 229 | 07:00 | 218 | 12:00 | Keranigonj | 224 | 03:00 | 212 | 12:00
Ashuganj-400 | 229 | 07:00 | 218 | 12:00 | Khulna(S) | 230 | 08:00 | 216 | 13:00
Baghabari | 231 | 09:00 | 225 | 12:00 | Korerhat | 228 | 00:00 | 219 | 10:00
Barapukuria | 225 | 10:00 | 209 | 07:00 | Madunaghat | 229 | 22:00 | 224 | 10:00
Barapukuria-230 | 225 | 10:00 | 209 | 07:00 | Madunaghat-400 | 230 | 23:00 | 224 | 11:00
Barishal | 226 | 09:00 | 218 | 13:00 | Maniknagar | 222 | 02:00 | 211 | 12:00
Bheramara | 234 | 01:00 | 222 | 13:00 | Meghnaghat | 233 | 08:00 | 220 | 12:00
Bhulta | 232 | 07:00 | 211 | 12:00 | Meghnaghat-400 | 225 | 03:00 | 215 | 12:00
Bibiana | 232 | 19:00 | 226 | 12:00 | Mirsorai | 233 | 18:00 | 225 | 10:00
BIPTC | 237 | 19:00 | 221 | 13:00 | Naogaon | 215 | 19:00 | 204 | 23:00
Bogura | 234 | 19:00 | 223 | 06:00 | Purbasadipur | 227 | 20:00 | 208 | 07:00
Bogura-400 | 232 | 09:00 | 223 | 06:00 | Rajshahi | 232 | 19:00 | 218 | 13:00
Borhanuddin | 230 | 00:00 | 225 | 13:00 | Rampal | 228 | 01:00 | 217 | 13:00
BSRM | 226 | 19:00 | 219 | 14:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 228 | 13:00 | 218 | 10:00 | Rampura | 230 | 07:00 | 209 | 13:00
Cumilla(N) | 224 | 19:00 | 215 | 12:00 | Shikalbaha | 228 | 22:00 | 224 | 05:00
Faridpur | 220 | 01:00 | 210 | 13:00 | Shyampur | 224 | 04:00 | 213 | 12:00
Fenchuganj | 236 | 06:00 | 230 | 12:00 | Siddhirganj | 224 | 03:00 | 219 | 08:00
Feni | 226 | 19:00 | 220 | 10:00 | Sirajgonj | 237 | 08:00 | 233 | 06:00
Ghorashal | 230 | 00:00 | 225 | 09:00 | Sreepur | 227 | 01:00 | 217 | 19:30
Ghorashal-230 | 229 | 09:00 | 211 | 12:00 | Tongi | 226 | 07:00 | 208 | 13:00
Gopalganj | 220 | 01:00 | 212 | 12:00
GPH | 228 | 22:00 | 222 | 10:00
Haripur | 224 | 02:00 | 213 | 12:00
Hasnabad | 223 | 01:00 | 213 | 12:00
Hathazari | 227 | 23:00 | 222 | 14:00
Ishurdi | 236 | 19:00 | 223 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 07:00 | 125 | 12:00 | Madunaghat | 134 | 22:00 | 130 | 10:00
Agargaon | 133 | 03:00 | 123 | 13:00 | Magura | 133 | 08:00 | 122 | 13:00
Agrabad | 131 | 00:00 | 128 | 10:00 | Mahasthangarh | 133 | 09:00 | 125 | 07:00
AKS | 129 | 00:00 | 126 | 10:00 | Maijdee | 125 | 17:00 | 121 | 15:00
Aminbazar | 129 | 03:00 | 121 | 10:00 | Manikganj | 123 | 04:00 | 118 | 19:30
Amnura | 136 | 19:00 | 124 | 13:00 | Maniknagar | 131 | 02:00 | 120 | 13:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 127 | 01:00 | 111 | 19:30
Ashuganj-230 | 136 | 03:00 | 134 | 10:00 | Matuail | 131 | 06:00 | 123 | 12:00
Bagerhat | 124 | 01:00 | 113 | 13:00 | Metrorail_Motijheel | 131 | 01:00 | 120 | 13:00
Bajitpur | 132 | 16:00 | 123 | 19:30 | Metrorail_Uttara | 131 | 04:00 | 120 | 10:00
Bakerganj | 132 | 00:00 | 126 | 12:00 | Millgate | 130 | 03:00 | 121 | 12:00
Bakulia | 133 | 01:00 | 129 | 19:30 | Mirpur | 128 | 03:00 | 120 | 12:00
Banani | 138 | 07:00 | 123 | 12:00 | Mirzapur | 130 | 19:00 | 122 | 11:00
Bangabhaban | 131 | 04:00 | 121 | 12:00 | Mithapukur | 133 | 09:00 | 122 | 07:00
Barapukuria | 135 | 10:00 | 123 | 07:00 | MI_Cement | 134 | 05:00 | 124.2 | 12:00
Barguna | 132 | 00:00 | 125 | 12:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 132 | 00:00 | 125 | 12:00 | Mogbazar | 140 | 06:00 | 125 | 12:00
Barishal-230 | 131 | 00:00 | 125 | 12:00 | Mongla | 126 | 08:00 | 114 | 13:00
Baroaulia | 132 | 02:00 | 129 | 09:00 | Motijheel | 131 | 04:00 | 121 | 12:00
Baroirhat | 128 | 17:00 | 125 | 09:00 | Muktagacha | 125 | 05:00 | 115 | 02:00
Bashundhara | 138 | 07:00 | 118 | 13:00 | Munshiganj | 129 | 03:00 | 122 | 12:00
BashundharaCement | 131 | 01:00 | 123 | 12:00 | Muradnagar | 132 | 16:00 | 116 | 12:00
Beanibazar | 131 | 06:00 | 125 | 12:00 | Mymensingh | 130 | 16:00 | 108 | 19:30
Benapole | 128 | 01:00 | 114 | 13:00 | Nabinagar | 132 | 04:00 | 123 | 12:00
Bhaluka | 135 | 01:00 | 122 | 20:00 | Naogaon | 133 | 08:00 | 123 | 12:00
Bhandaria | 127 | 04:00 | 120 | 12:00 | Narail | 134 | 19:00 | 121 | 13:00
Bhangura | 132 | 02:00 | 126 | 13:00 | Narinda | 131 | 02:00 | 120 | 13:00
Bheramara | 135 | 19:00 | 129 | 13:00 | Narshingdi | 130 | 01:00 | 116 | 12:00
Bheramara(GK) | 135 | 19:00 | 128 | 13:00 | Natore | 132 | 19:00 | 125 | 13:00
Bhulta | 122 | 01:00 | 119 | 15:00 | Nawabganj | 133 | 01:00 | 127 | 12:00
Bog-Sherpur | 133 | 09:00 | 126 | 06:00 | Netrakona | 129 | 16:00 | 111 | 19:30
Bogura | 135 | 09:00 | 127 | 07:00 | New | 131 | 07:00 | 122 | 10:00
Bogura-230 | 136 | 19:00 | 127 | 07:00 | Niamatpur | 130 | 09:00 | 125 | 23:00
Brahmanbaria | 132 | 18:00 | 120 | 12:00 | Noapara | 129 | 01:00 | 117 | 13:00
Cantonment | 132 | 03:00 | 123 | 12:00 | Pabna | 133 | 19:00 | 126 | 13:00
Chandina | 128 | 01:00 | 122 | 12:00 | Palashbari | 130 | 09:00 | 120 | 07:00
Chandpur | 130 | 18:00 | 123 | 00:00 | Panchagarh | 139 | 19:00 | 124 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 133 | 06:00 | 131 | 01:00 | Patiya | 131 | 01:00 | 127 | 10:00
Chapai | 131 | 01:00 | 127 | 06:00 | Patuakhali | 131 | 00:00 | 126 | 12:00
Charsaidpur | 131 | 06:00 | 123 | 12:00 | Payra | 134 | 00:00 | 130 | 12:00
Chauddagram | 127 | 19:00 | 122 | 10:00 | PHP | 127 | 07:00 | 125 | 05:00
Chhatak | 131 | 04:00 | 125 | 12:00 | Postogola | 136 | 04:00 | 128 | 10:00
Chowmuhani | 126 | 18:00 | 121 | 10:00 | Pubail | 135 | 19:00 | 125 | 12:00
Chuadanga | 132 | 08:00 | 118 | 13:00 | Purbachal | 138 | 07:00 | 119 | 12:00
Coxsbazar | 121 | 15:00 | 113 | 10:00 | Purbasadipur | 133 | 20:00 | 119 | 07:00
Cumilla(N) | 128 | 17:00 | 124 | 11:00 | Rahanpur | 133 | 19:00 | 130 | 02:00
Cumilla(S) | 129 | 19:00 | 118 | 14:00 | Rahanpur-400 | 134 | 09:00 | 130 | 05:00
Daganbhuiyan | 126 | 17:00 | 122 | 10:00 | Rahim | 130 | 04:00 | 123 | 12:00
Daudkandi | 125 | 19:00 | 112 | 12:00 | Rajbari | 125 | 02:00 | 118 | 13:00
DhakaUniversity | 137 | 06:00 | 124 | 12:00 | Rajendrapur | 132 | 01:00 | 122 | 19:30
Dhamrai | 131 | 00:00 | 125 | 11:00 | Rajshahi | 130 | 09:00 | 122 | 13:00
Dhanmondi | 134.5 | 22:00 | 124 | 12:00 | Rajshahi-230 | 133 | 19:00 | 124 | 13:00
Dohazari | 129 | 19:00 | 122 | 19:30 | Ramganj | 126 | 17:00 | 119 | 10:00
Faridpur | 127 | 00:00 | 123 | 12:00 | Rampur | 131 | 00:00 | 128 | 13:00
Fatullah | 135 | 06:00 | 122 | 12:00 | Rampura | 137 | 07:00 | 124 | 12:00
Fenchuganj | 134 | 06:00 | 131 | 12:00 | Rangamati | 132 | 00:00 | 129 | 14:00
Feni | 126 | 23:00 | 122 | 15:00 | Rangpur | 135 | 10:00 | 124 | 07:00
Feni-230 | 126 | 01:00 | 123 | 10:00 | Ruppur | 135 | 09:00 | 129 | 13:00
Ghatail | 124 | 06:00 | 116 | 02:00 | Saidpur | 133 | 20:00 | 121 | 07:00
Ghorashal | 135 | 00:00 | 128 | 12:00 | Santhia | 133 | 19:00 | 128 | 13:00
Goalpara | 131 | 08:00 | 120 | 13:00 | Satkhira | 126 | 08:00 | 114 | 13:00
Gollamari | 129 | 01:00 | 121 | 13:00 | Satmasjid | 132 | 03:00 | 122 | 13:00
Gopalganj | 130 | 08:00 | 121 | 13:00 | Savar | 128 | 19:00 | 119 | 12:00
Gopalganj-400 | 131 | 01:00 | 120 | 11:00 | SevenRings | 137 | 08:00 | 128 | 12:00
Gulshan | 134 | 00:00 | 123 | 12:00 | ShahCement | 131 | 06:00 | 123 | 12:00
Halishahar | 132 | 01:00 | 129 | 10:00 | Shahjadpur | 136 | 05:00 | 130 | 12:00
Haripur | 131 | 06:00 | 124 | 12:00 | Shahjibazar | 131 | 06:00 | 126 | 12:00
HaripurSBU | 130 | 03:00 | 124 | 12:00 | Shahmirpur | 133 | 02:00 | 129 | 19:30
Hasnabad | 136 | 04:00 | 126 | 12:00 | Shariatpur | 129 | 02:00 | 123 | 13:00
Hathazari | 133 | 00:00 | 130 | 09:00 | Sherpur | 120 | 04:00 | 106 | 02:00
Hatirjheel | 137 | 07:00 | 123 | 12:00 | Shikalbaha | 123 | 00:00 | 119 | 10:00
Ishurdi | 136 | 09:00 | 130 | 13:00 | Shikalbaha-230 | 134 | 01:00 | 130 | 04:00
Jaldhaka | 132 | 10:00 | 119 | 07:00 | Shitalakhya | 134 | 05:00 | 124.2 | 12:00
Jamalpur | 125 | 05:00 | 112 | 02:00 | Sholosohor | 133 | 19:00 | 129 | 10:00
Jashore | 129 | 08:00 | 116 | 13:00 | Shyampur | 127 | 06:00 | 123 | 12:00
Jhenaidah | 135 | 08:00 | 118 | 13:00 | Shyampur-230 | 129 | 03:00 | 121 | 10:00
Jhenaidah-230 | 135 | 08:00 | 124 | 13:00 | Siddhirganj | 131 | 03:00 | 124 | 12:00
Joydebpur | 134 | 18:00 | 123 | 12:00 | Sirajganj | 130 | 09:00 | 124 | 22:00
Joypurhat | 128 | 09:00 | 118 | 06:00 | Sonargaon | 131 | 06:00 | 122 | 12:00
Juldah | 132 | 00:00 | 129 | 10:00 | Sreemongol | 131 | 17:00 | 127 | 10:00
Kabirpur | 137 | 19:00 | 117 | 10:00 | Sreepur | 134 | 01:00 | 125 | 19:30
Kachua | 128 | 17:00 | 124 | 02:00 | Srinagar | 134 | 03:00 | 127 | 12:00
Kaliakoir | 136 | 19:00 | 126 | 12:00 | SSM | 138 | 01:00 | 136 | 00:00
Kaliganj | 134 | 19:00 | 121 | 13:00 | Sunamganj | 130 | 06:00 | 124 | 12:00
Kallyanpur | 128 | 05:00 | 120 | 12:00 | Sylhet | 132 | 06:00 | 128 | 12:00
Kalurghat | 135 | 22:00 | 130 | 10:00 | Sylhet-132 | 130 | 00:00 | 129 | 11:00
Kamrangirchar | 134 | 04:00 | 118 | 12:00 | Tangail | 127 | 22:00 | 119 | 10:00
Kaptai | N/A | N/A | N/A | N/A | Taraganj | 134 | 10:00 | 121 | 07:00
Kasba | 126 | 01:00 | 117 | 12:00 | Tasnim | 129 | 04:00 | 123 | 12:00
Kazla | 131 | 04:00 | 120 | 13:00 | Thakurgaon | 138 | 19:00 | 121 | 07:00
Keranigonj | 135 | 03:00 | 127 | 12:00 | TK | 133 | 00:00 | 130 | 14:00
Khagrachori | 132 | 22:00 | 128 | 10:00 | Tongi | 133 | 07:00 | 123 | 11:00
Khulna | 130 | 08:00 | 120 | 13:00 | Ullahpara | 131 | 09:00 | 126 | 05:00
Khulna(S) | 131 | 01:00 | 121 | 13:00 | Ullon | 136 | 07:00 | 122 | 12:00
Khulshi | 130 | 01:00 | 126 | 19:30 | Uttara | 131 | 07:00 | 118 | 12:00
Kishoreganj | 133 | 01:00 | 120 | 19:30 | UttaraNew | 130 | 03:00 | 120 | 10:00
Kodda | 136 | 19:00 | 121 | 12:00 | Zigatola | 135 | 04:00 | 18 | 13:00
Korerhat | 131 | 18:00 | 126 | 07:00
KSRM | 133 | 16:00 | 130 | 02:00
Kulaura | 133 | 05:00 | 130 | 12:00
Kurigram | 134 | 10:00 | 117 | 07:00
Kushtia | 132 | 19:00 | 124 | 13:00
Laksam | 128 | 17:00 | 123 | 05:00
Lakshmipur | 125 | 17:00 | 120 | 05:00
Lalbag | 134 | 06:00 | 126 | 12:00
Lalmonirhat | 132 | 10:00 | 118 | 07:00
Madanganj | 131 | 01:00 | 123 | 12:00
Madaripur | 130 | 00:00 | 126 | 13:00
Madartek | 138 | 07:00 | 123 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 20-04-2026 | [28 empty] | Date: | 20-04-2026 | [28 empty] | Date: | 20-04-2026 | [28 empty] | Date: | 20-04-2026 | [28 empty] | Date: | 20-04-2026 | [17 empty] | Date: | 20-04-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [17 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.000 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 17 | 18 | 49 | 145 | 52 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 125 | 18.5 | 22 | 0 | 480 | 71 | 16 | 12 | 0 | 0 | 17 | 54 | 18 | 0 | 0 | 0 | 70 | 55 | 20 | 935 | 54 | 0 | 0 | 8 | 34 | 219 | 0 | 0 | 0 | 612 | 0 | 21 | 0 | 215 | 345 | 300 | 44 | 0 | 171 | 0 | 17 | 0 | 40 | 0 | 20 | 0 | 176 | 0 | 0 | 38 | 310 | 0 | 350 | 42 | 24 | 156 | 0 | 17 | 0 | 53 | 30 | 100 | 0 | 100 | 17 | 9 | 58 | 11 | 0 | 0 | 12 | 6773.5 | 883 | 86 | 0 | 28 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1195 | 0 | 0 | 0 | 1471 | 0 | 32 | 0 | 35 | 35 | 0 | 36 | 13 | 0 | 0 | 0 | 24 | 0 | 0 | 143 | 0 | 0 | 0 | 158 | 0 | 414 | 0 | 0 | 0 | 51 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 290 | 130 | 220 | 0 | 252 | 1244 | 35 | 6912 | 13685.5 | 78.33
01:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 17 | 48 | 30 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 125 | 18.5 | 22 | 0 | 480 | 72 | 16 | 12 | 0 | 0 | 0 | 54 | 18 | 0 | 0 | 0 | 70 | 41 | 20 | 935 | 17 | 0 | 0 | 8 | 34 | 219 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 215 | 350 | 300 | 44 | 0 | 174 | 0 | 17 | 0 | 17 | 0 | 20 | 0 | 174 | 0 | 0 | 38 | 305 | 0 | 348 | 42 | 24 | 156 | 0 | 17 | 0 | 53 | 30 | 100 | 0 | 100 | 0 | 9 | 58 | 11 | 0 | 0 | 12 | 6545.5 | 787 | 86 | 0 | 22 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1218 | 0 | 0 | 0 | 1497 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 24 | 0 | 0 | 145 | 0 | 0 | 0 | 158 | 0 | 414 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 253 | 1244 | 17 | 6653 | 13198.5 | 78.31
02:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 17 | 48 | 30 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 125 | 19.5 | 22 | 0 | 510 | 71 | 16 | 12 | 0 | 2 | 0 | 54 | 18 | 0 | 0 | 0 | 70 | 54 | 20 | 935 | 17 | 0 | 8 | 8 | 34 | 219 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 215 | 350 | 300 | 44 | 0 | 171 | 0 | 17 | 0 | 17 | 0 | 20 | 0 | 164 | 0 | 0 | 38 | 300 | 0 | 348 | 42 | 24 | 157 | 0 | 17 | 0 | 53 | 30 | 100 | 0 | 100 | 0 | 9 | 58 | 20 | 0 | 0 | 12 | 6580.5 | 787 | 85 | 0 | 22 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1227 | 0 | 0 | 0 | 1481 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 24 | 0 | 0 | 146 | 0 | 0 | 0 | 158 | 0 | 414 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 253 | 1244 | 17 | 6646 | 13226.5 | 78.29
03:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 17 | 48 | 30 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 125 | 19.5 | 22 | 0 | 480 | 72 | 16 | 12 | 0 | 11 | 0 | 54 | 18 | 0 | 0 | 0 | 68 | 55 | 26 | 935 | 17 | 0 | 19 | 8 | 34 | 219 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 215 | 350 | 300 | 44 | 0 | 169 | 0 | 17 | 0 | 17 | 0 | 20 | 0 | 164 | 0 | 0 | 38 | 305 | 0 | 348 | 42 | 24 | 156 | 0 | 17 | 0 | 53 | 30 | 100 | 0 | 100 | 0 | 9 | 58 | 32 | 0 | 0 | 0 | 6577.5 | 787 | 88 | 0 | 22 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1216 | 0 | 0 | 0 | 1480 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 24 | 0 | 0 | 146 | 0 | 0 | 0 | 157 | 0 | 414 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 254 | 1244 | 17 | 6632 | 13209.5 | 78.27
04:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 17 | 48 | 30 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 125 | 19.5 | 22 | 0 | 480 | 72 | 16 | 12 | 0 | 23 | 0 | 54 | 0 | 0 | 0 | 0 | 66 | 55 | 24 | 935 | 17 | 0 | 19 | 8 | 34 | 219 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 215 | 350 | 300 | 44 | 0 | 169 | 0 | 18 | 0 | 17 | 0 | 20 | 0 | 164 | 0 | 0 | 38 | 300 | 0 | 348 | 42 | 24 | 154 | 0 | 0 | 0 | 53 | 30 | 55 | 0 | 100 | 0 | 9 | 58 | 32 | 0 | 0 | 0 | 6492.5 | 881 | 92 | 0 | 22 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1208 | 0 | 0 | 0 | 1476 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 24 | 0 | 0 | 146 | 0 | 0 | 0 | 158 | 0 | 414 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 253 | 1244 | 17 | 6718 | 13210.5 | 78.25
05:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 17 | 48 | 30 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 125 | 19.5 | 22 | 0 | 500 | 71 | 16 | 12 | 0 | 16 | 0 | 54 | 0 | 0 | 0 | 0 | 66 | 54 | 26 | 935 | 17 | 0 | 19 | 8 | 34 | 219 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 215 | 350 | 300 | 44 | 0 | 180 | 0 | 17 | 0 | 17 | 0 | 20 | 0 | 156 | 0 | 0 | 38 | 300 | 0 | 348 | 42 | 24 | 154 | 0 | 5 | 0 | 81 | 30 | 0 | 0 | 100 | 0 | 9 | 58 | 32 | 0 | 0 | 0 | 6481.5 | 881 | 92 | 0 | 22 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1226 | 0 | 0 | 0 | 1494 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 159 | 0 | 414 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 254 | 1244 | 17 | 6719 | 13200.5 | 78.23
06:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 17 | 48 | 30 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 17 | 330 | 0 | 0 | 0 | 125 | 19.5 | 22 | 0 | 440 | 72 | 16 | 12 | 0 | 16 | 0 | 54 | 0 | 0 | 0 | 0.14 | 67 | 55 | 30 | 935 | 17 | 0 | 19 | 8 | 34 | 220 | 0 | 0 | 0 | 612 | 1 | 20 | 0 | 215 | 350 | 300 | 44 | 0 | 182 | 0 | 17 | 0 | 17 | 0 | 20 | 0 | 142 | 0 | 3 | 31 | 305 | 0 | 348 | 42 | 24 | 149 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 100 | 0 | 9 | 58 | 34 | 0 | 0.03 | 0 | 6451.67 | 881 | 96 | 0 | 22 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25 | 1233 | 0 | 0 | 0 | 1492 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | 0 | 0 | 1.36 | 143 | 0 | 0 | 0 | 161 | 0 | 414 | 0 | 0.14 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.02 | 16 | 290 | 130 | 220 | 0 | 253 | 1232 | 17 | 6718.99 | 13170.66 | 78.21
07:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 17 | 48 | 30 | 55 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 4 | 125 | 19.5 | 22 | 0 | 440 | 71 | 16 | 12 | 0 | 12 | 0 | 54 | 0 | 0 | 0 | 0.72 | 68 | 55 | 28 | 935 | 17 | 0 | 19 | 8 | 34 | 221 | 0 | 0 | 0 | 612 | 4 | 20 | 0 | 215 | 350 | 300 | 44 | 0 | 175 | 0 | 17 | 0 | 17 | 0 | 20 | 0 | 142 | 0 | 13 | 38 | 300 | 0 | 348 | 42 | 24 | 141 | 2 | 17 | 0 | 81 | 30 | 0 | 0 | 100 | 0 | 9 | 58 | 29 | 0.01 | 5.53 | 0 | 6441.76 | 881 | 96 | 0 | 22 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 10.78 | 1212 | 0 | 0 | 0 | 1489 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.85 | 8 | 0 | 0 | 6.36 | 142 | 0 | 0 | 0 | 162 | 0 | 414 | 0 | 0.34 | 0 | 50 | 0 | 2 | 0 | 0 | 0 | 0 | 0.8 | 4 | 0.13 | 16 | 290 | 130 | 220 | 0 | 253 | 1222 | 17 | 6718.26 | 13160.02 | 78.19
08:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 17 | 48 | 30 | 55 | 0 | 17 | 0 | 160 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 12 | 125 | 19 | 22 | 0 | 320 | 72 | 16 | 12 | 0 | 7 | 0 | 54 | 0 | 0 | 0 | 1.18 | 68 | 55 | 4 | 935 | 17 | 0 | 19 | 8 | 34 | 220 | 0 | 0 | 0 | 600 | 8 | 20 | 0 | 215 | 350 | 300 | 44 | 0 | 163 | 0 | 17 | 0 | 17 | 0 | 20 | 0 | 152 | 0 | 15 | 38 | 295 | 0 | 348 | 42 | 24 | 134 | 2 | 17 | 0 | 81 | 30 | 0 | 0 | 100 | 9 | 9 | 58 | 11 | 0.66 | 21.88 | 0 | 6230.72 | 883 | 96 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 40.61 | 1192 | 0 | 0 | 0 | 1485 | 0 | 33 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 22.78 | 25 | 0 | 0 | 20.37 | 144 | 0 | 0 | 0 | 167 | 0 | 300 | 0 | 1.4 | 0 | 50 | 0 | 6 | 40 | 0 | 0 | 0 | 2.3 | 63 | 0.28 | 16 | 290 | 130 | 180 | 0 | 253 | 1220 | 17 | 6759.74 | 12990.46 | 78.17
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 17 | 48 | 30 | 55 | 17 | 17 | 0 | 160 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 18 | 125 | 19 | 22 | 0 | 370 | 71 | 16 | 12 | 0 | 22 | 0 | 54 | 0 | 0 | 0 | 2.55 | 70 | 64 | 2 | 935 | 17 | 0 | 19 | 8 | 34 | 217 | 0 | 0 | 0 | 575 | 5 | 20 | 0 | 215 | 350 | 300 | 44 | 0 | 163 | 0 | 18 | 0 | 17 | 0 | 20 | 0 | 148 | 0 | 39 | 38 | 300 | 0 | 338 | 42 | 24 | 136 | 8 | 17 | 0 | 75 | 30 | 0 | 0 | 100 | 17 | 9 | 58 | 11 | 1.53 | 13.32 | 0 | 6360.4 | 882 | 93 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 1185 | 0 | 0 | 0 | 1485 | 0 | 33 | 0 | 75 | 50 | 0 | 0 | 0 | 0 | 31.33 | 59 | 0 | 0 | 41.97 | 146 | 0 | 0 | 0 | 168 | 0 | 300 | 0 | 3.57 | 0 | 50 | 0 | 2 | 75 | 0 | 0 | 0 | 1.9 | 63 | 0.46 | 16 | 285 | 100 | 180 | 0 | 254 | 1210 | 17 | 6901.23 | 13261.63 | 78.15
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 12 | 17 | 47 | 30 | 0 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 24 | 125 | 14 | 22 | 0 | 500 | 28 | 16 | 12 | 0 | 21 | 0 | 54 | 0 | 0 | 0 | 3.37 | 70 | 55 | 2 | 935 | 17 | 0 | 19 | 8 | 34 | 215 | 0 | 0 | 0 | 580 | 14 | 20 | 0 | 215 | 334 | 300 | 44 | 0 | 180 | 0 | 17 | 0 | 17 | 0 | 15 | 0 | 156 | 0 | 61 | 38 | 310 | 0 | 338 | 42 | 24 | 150 | 6 | 17 | 0 | 78 | 30 | 0 | 0 | 100 | 17 | 9 | 68 | 11 | 1.98 | 20.11 | 0 | 6428.46 | 883 | 96 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 1155 | 0 | 0 | 0 | 1490 | 0 | 33 | 0 | 113 | 92 | 0 | 0 | 0 | 0 | 50.36 | 88 | 0 | 0 | 46.49 | 154 | 0 | 0 | 0 | 170 | 0 | 330 | 0 | 4.68 | 0 | 47 | 0 | 1 | 92 | 0 | 0 | 0 | 5.5 | 103 | 0.56 | 0 | 249 | 100 | 180 | 0 | 253 | 1180 | 0 | 7019.59 | 13448.05 | 78.13
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 6 | 17 | 17 | 46 | 48 | 0 | 0 | 35 | 0 | 200 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 32 | 125 | 19 | 21 | 0 | 500 | 17 | 16 | 12 | 0 | 37 | 0 | 54 | 0 | 0 | 0 | 1.45 | 70 | 55 | 2 | 935 | 17 | 0 | 0 | 8 | 105 | 215 | 0 | 0 | 0 | 584 | 19 | 20 | 0 | 215 | 305 | 300 | 44 | 0 | 200 | 0 | 17 | 0 | 17 | 4 | 8 | 0 | 160 | 0 | 65 | 0 | 310 | 0 | 341 | 42 | 24 | 155 | 8 | 17 | 0 | 77 | 30 | 0 | 0 | 100 | 17 | 9 | 68 | 11 | 2.35 | 47.31 | 0 | 6543.11 | 882 | 96 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 1185 | 0 | 0 | 0 | 1485 | 0 | 40 | 0 | 70 | 70 | 0 | 0 | 0 | 0 | 54.48 | 105 | 0 | 0 | 40.69 | 156 | 0 | 0 | 0 | 170 | 0 | 370 | 0 | 2.59 | 0 | 48 | 0 | 30 | 97 | 0 | 0 | 0 | 6.3 | 80 | 0.63 | 0 | 228 | 100 | 180 | 0 | 253 | 1170 | 0 | 7028.69 | 13571.8 | 78.11
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17.5 | 16 | 46 | 46 | 48 | 0 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 33 | 125 | 19 | 21 | 0 | 500 | 17 | 16 | 12 | 0 | 50 | 0 | 54 | 0 | 0 | 0 | 3.95 | 70 | 56 | 2 | 935 | 17 | 0 | 3 | 8 | 105 | 213 | 0 | 0 | 0 | 612 | 19 | 15 | 0 | 220 | 304 | 300 | 44 | 0 | 201 | 0 | 19 | 0 | 17 | 9 | 20 | 0 | 176 | 0 | 37 | 0 | 310 | 0 | 338 | 42 | 24 | 154 | 12 | 0 | 0 | 76 | 30 | 75 | 0 | 100 | 0 | 9 | 68 | 11 | 0.92 | 25.47 | 0 | 6698.84 | 882 | 94 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 1190 | 0 | 0 | 0 | 1481 | 0 | 40 | 0 | 70 | 70 | 0 | 0 | 0 | 0 | 48.48 | 106 | 0 | 0 | 53.65 | 164 | 0 | 0 | 0 | 169 | 0 | 414 | 0 | 4.16 | 0 | 47 | 0 | 16 | 92 | 0 | 0 | 0 | 6.3 | 193 | 0.65 | 0 | 230 | 124 | 220 | 0 | 253 | 1140 | 0 | 7220.24 | 13919.08 | 78.09
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 17.5 | 14 | 52 | 46 | 48 | 4 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 32 | 134 | 21 | 21 | 0 | 560 | 17 | 16 | 15 | 0 | 35 | 0 | 54 | 0 | 0 | 0 | 3.7 | 70 | 69 | 7 | 935 | 17 | 0 | 18 | 8 | 61 | 212 | 0 | 0 | 0 | 595 | 17 | 16 | 0 | 235 | 305 | 320 | 44 | 0 | 191 | 0 | 20 | 0 | 22 | 9 | 14 | 0 | 190 | 0 | 36 | 12 | 315 | 0 | 326 | 42 | 24 | 151 | 9 | 0 | 0 | 79 | 30 | 40 | 0 | 100 | 0 | 9 | 68 | 10 | 1.99 | 34.03 | 0 | 6750.22 | 882 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 1220 | 0 | 0 | 0 | 1491 | 0 | 0 | 0 | 113 | 108 | 0 | 0 | 0 | 0 | 56.7 | 89 | 0 | 0 | 25.27 | 171 | 0 | 0 | 0 | 166 | 0 | 414 | 0 | 3.72 | 0 | 45 | 0 | 23 | 97 | 0 | 0 | 0 | 5.5 | 109 | 0.62 | 8 | 290 | 122 | 220 | 0 | 253 | 1190 | 10 | 7285.81 | 14036.03 | 78.07
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 17.5 | 17 | 52 | 47 | 48 | 15 | 0 | 54 | 0 | 225 | 0 | 0 | 0 | 17 | 314 | 0 | 0 | 28 | 140 | 21.5 | 21 | 0 | 495 | 17 | 16 | 18 | 0 | 39 | 0 | 54 | 0 | 0 | 0 | 2.99 | 70 | 55 | 2 | 935 | 17 | 0 | 18 | 8 | 34 | 212 | 0 | 0 | 0 | 612 | 6 | 20 | 0 | 220 | 305 | 320 | 44 | 0 | 185 | 0 | 20 | 0 | 17 | 9 | 14 | 0 | 192 | 0 | 50 | 31 | 310 | 0 | 319 | 42 | 24 | 151 | 6 | 17 | 0 | 77 | 30 | 70 | 0 | 99 | 0 | 9 | 68 | 10 | 0.59 | 33.78 | 0 | 6708.36 | 882 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 1218 | 0 | 0 | 0 | 1491 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 48.06 | 93 | 0 | 0 | 41.82 | 173 | 0 | 0 | 0 | 164 | 0 | 350 | 0 | 3.81 | 0 | 45 | 0 | 15 | 99 | 0 | 0 | 0 | 5.9 | 145 | 0.56 | 16 | 290 | 122 | 220 | 0 | 253 | 1244 | 17 | 7293.15 | 14001.51 | 78.05
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 18 | 17 | 52 | 46 | 48 | 21 | 12 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 315 | 0 | 0 | 21 | 125 | 21.5 | 0 | 0 | 500 | 17 | 16 | 19 | 0 | 45 | 0 | 57 | 0 | 0 | 0 | 1.41 | 60 | 55 | 2 | 935 | 17 | 0 | 18 | 8 | 34 | 212 | 0 | 0 | 0 | 612 | 13 | 18 | 0 | 225 | 305 | 325 | 44 | 0 | 183 | 0 | 22 | 0 | 17 | 8 | 14 | 0 | 190 | 0 | 26 | 31 | 315 | 0 | 274 | 42 | 23 | 151 | 2 | 17 | 0 | 77 | 30 | 40 | 0 | 99 | 0 | 9 | 68 | 10 | 1.41 | 31.59 | 0 | 6634.91 | 882 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 1215 | 0 | 0 | 0 | 1487 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 8 | 0 | 37.53 | 72 | 0 | 0 | 29.83 | 150 | 0 | 0 | 0 | 140 | 0 | 350 | 0 | 3.6 | 0 | 47 | 0 | 19 | 98 | 0 | 0 | 0 | 2 | 111 | 0.43 | 16 | 290 | 122 | 220 | 0 | 303 | 1244 | 17 | 7231.39 | 13866.3 | 78.03
16:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 18 | 17 | 51 | 38 | 48 | 30 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 317 | 0 | 0 | 14 | 140 | 21 | 21 | 0 | 500 | 17 | 16 | 18 | 0 | 45 | 0 | 57 | 0 | 0 | 0 | 1.35 | 60 | 54 | 2 | 935 | 163 | 0 | 18 | 8 | 34 | 212 | 0 | 0 | 0 | 612 | 7 | 20 | 0 | 225 | 305 | 325 | 44 | 0 | 180 | 0 | 17 | 0 | 17 | 8 | 20 | 0 | 200 | 0 | 18 | 36 | 310 | 0 | 275 | 42 | 23 | 147 | 4 | 17 | 0 | 77 | 30 | 40 | 0 | 99 | 0 | 9 | 68 | 10 | 0.81 | 19.14 | 5 | 6793.3 | 882 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 1178 | 0 | 0 | 0 | 1483 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 12 | 0 | 23.19 | 44 | 0 | 0 | 24.53 | 150 | 0 | 0 | 0 | 140 | 0 | 350 | 0 | 1.71 | 0 | 46 | 35 | 13 | 98 | 0 | 0 | 0 | 2.3 | 54 | 0.32 | 16 | 290 | 122 | 220 | 0 | 303 | 1210 | 17 | 7058.05 | 13851.35 | 78.01
17:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 18 | 17 | 51 | 106 | 48 | 15 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 321 | 0 | 0 | 7 | 142 | 20.5 | 21 | 0 | 400 | 17 | 16 | 19 | 0 | 45 | 0 | 50 | 0 | 0 | 0 | 0.55 | 60 | 54 | 2 | 935 | 140 | 0 | 18 | 9 | 34 | 216 | 0 | 0 | 0 | 612 | 3 | 20 | 0 | 225 | 305 | 320 | 44 | 0 | 180 | 0 | 17 | 0 | 41 | 8 | 20 | 0 | 186 | 0 | 11 | 36 | 310 | 0 | 284 | 42 | 23 | 135 | 1 | 17 | 0 | 78 | 30 | 40 | 0 | 99 | 0 | 9 | 67 | 18 | 0.34 | 6.84 | 12 | 6689.23 | 882 | 89 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 1190 | 0 | 0 | 0 | 1479 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 12 | 0 | 9.7 | 20 | 0 | 0 | 10.91 | 150 | 0 | 0 | 0 | 140 | 0 | 300 | 0 | 0.96 | 0 | 46 | 50 | 3 | 97 | 0 | 0 | 0 | 1.1 | 31 | 0.07 | 16 | 290 | 122 | 220 | 0 | 303 | 1200 | 17 | 6943.74 | 13632.97 | 77.99
18:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 18 | 17 | 70 | 142 | 146 | 15 | 35 | 54 | 0 | 180 | 0 | 0 | 0 | 35 | 280 | 0 | 0 | 1 | 142 | 20.5 | 21 | 0 | 400 | 17 | 16 | 18 | 0 | 35 | 0 | 50 | 0 | 0 | 0 | 0.02 | 60 | 55 | 2 | 1015 | 138 | 0 | 24 | 22 | 34 | 216 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 225 | 305 | 320 | 44 | 0 | 184 | 0 | 24 | 0 | 102 | 16 | 20 | 0 | 160 | 0 | 1 | 35 | 305 | 0 | 292 | 42 | 23 | 135 | 0 | 8 | 0 | 79 | 30 | 39 | 0 | 98 | 11 | 9 | 67 | 16 | 0.05 | 0.78 | 12 | 6963.35 | 882 | 102 | 0 | 22 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1176 | 0 | 0 | 0 | 1490 | 0 | 31 | 0 | 113 | 113 | 0 | 70 | 24 | 0 | 1.24 | 0 | 0 | 0 | 1.31 | 150 | 0 | 0 | 0 | 140 | 0 | 300 | 0 | 0.13 | 0 | 46 | 50 | 0 | 98 | 0 | 0 | 0 | 0.2 | 5 | 0.01 | 16 | 290 | 122 | 180 | 0 | 303 | 1200 | 17 | 6946.89 | 13910.24 | 77.97
19:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 36 | 17 | 110 | 143 | 282 | 15 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 142 | 21.5 | 22 | 0 | 380 | 17 | 16 | 19 | 0 | 18 | 17 | 51 | 0 | 0 | 0 | 0 | 60 | 54 | 6 | 1015 | 140 | 0 | 46 | 25.5 | 34 | 215 | 0 | 0 | 0 | 612 | 0 | 97 | 0 | 225 | 305 | 320 | 44 | 0 | 180 | 0 | 49 | 0 | 104 | 18 | 20 | 0 | 174 | 0 | 0 | 35 | 310 | 0 | 302 | 42 | 23 | 147 | 0 | 16 | 0 | 80 | 30 | 41 | 0 | 99 | 17 | 9 | 67 | 16 | 0 | 0 | 12 | 7410 | 856 | 113 | 0 | 33 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1180 | 0 | 0 | 0 | 1477 | 0 | 31 | 0 | 113 | 113 | 0 | 83 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 140 | 0 | 300 | 0 | 0 | 0 | 49 | 70 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 125 | 180 | 0 | 320 | 1200 | 35 | 7004 | 14414 | 77.96
19:30 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 36 | 17 | 115 | 143 | 294 | 15 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 322 | 0 | 0 | 0 | 142 | 21.5 | 22 | 0 | 450 | 17 | 16 | 19 | 0 | 22 | 17 | 51 | 0 | 0 | 0 | 0 | 60 | 54 | 2 | 1015 | 155 | 0 | 50 | 25.5 | 34 | 215 | 0 | 0 | 0 | 612 | 0 | 150 | 0 | 225 | 305 | 320 | 44 | 0 | 174 | 0 | 51 | 0 | 103 | 18 | 20 | 0 | 174 | 0 | 0 | 35 | 325 | 0 | 304 | 42 | 23 | 150 | 0 | 16 | 0 | 80 | 30 | 41 | 0 | 99 | 17 | 9 | 67 | 16 | 0 | 0 | 12 | 7632 | 882 | 116 | 0 | 28 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1210 | 0 | 0 | 0 | 1482 | 0 | 30 | 0 | 113 | 113 | 0 | 83 | 24 | 0 | 0 | 0 | 16 | 0 | 0 | 150 | 0 | 0 | 0 | 140 | 0 | 380 | 0 | 0 | 0 | 48 | 70 | 0 | 99 | 0 | 75 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 180 | 0 | 353 | 1200 | 35 | 7283 | 14915 | 0
20:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 36 | 17 | 117 | 143 | 294 | 15 | 35 | 54 | 0 | 225 | 0 | 0 | 0 | 35 | 326 | 0 | 0 | 0 | 142 | 21.5 | 22 | 0 | 500 | 17 | 16 | 19 | 0 | 24 | 17 | 50 | 0 | 0 | 0 | 0 | 60 | 55 | 5 | 1015 | 136 | 0 | 50 | 25.5 | 34 | 216 | 0 | 0 | 0 | 612 | 0 | 150 | 0 | 225 | 305 | 320 | 44 | 0 | 175 | 0 | 52 | 0 | 103 | 17 | 20 | 0 | 174 | 0 | 0 | 35 | 315 | 0 | 305 | 42 | 24 | 151 | 0 | 16 | 0 | 80 | 30 | 40 | 0 | 99 | 17 | 9 | 67 | 18 | 0 | 0 | 12 | 7656 | 882 | 117 | 0 | 28 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1202 | 0 | 0 | 0 | 1490 | 0 | 31 | 0 | 113 | 113 | 0 | 83 | 24 | 0 | 0 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 48 | 70 | 0 | 99 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 353 | 1210 | 35 | 7478 | 15134 | 77.95
21:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 36 | 17 | 133 | 144 | 294 | 15 | 35 | 35 | 0 | 225 | 0 | 0 | 0 | 35 | 324 | 0 | 0 | 0 | 142 | 21.5 | 22 | 0 | 530 | 17 | 16 | 13 | 0 | 18 | 17 | 50 | 14 | 0 | 0 | 0 | 60 | 54 | 10 | 1015 | 145 | 0 | 50 | 25.5 | 34 | 217 | 0 | 0 | 0 | 612 | 0 | 137 | 0 | 225 | 305 | 320 | 44 | 0 | 182 | 0 | 51 | 0 | 103 | 18 | 20 | 0 | 164 | 0 | 0 | 36 | 310 | 0 | 305 | 42 | 24 | 152 | 0 | 16 | 0 | 80 | 30 | 41 | 0 | 99 | 17 | 9 | 67 | 27 | 0 | 0 | 12 | 7700 | 881 | 122 | 0 | 29 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1213 | 0 | 0 | 0 | 1481 | 0 | 31 | 0 | 113 | 113 | 0 | 75 | 24 | 0 | 0 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 46 | 70 | 0 | 99 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 353 | 1212 | 35 | 7499 | 15199 | 77.94
22:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 36 | 17 | 77 | 128 | 294 | 15 | 35 | 35 | 0 | 225 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 142 | 21.5 | 22 | 0 | 500 | 17 | 16 | 12 | 0 | 9 | 17 | 54 | 18 | 0 | 0 | 0 | 60 | 55 | 23 | 1015 | 140 | 0 | 50 | 25.5 | 34 | 217 | 0 | 0 | 0 | 612 | 0 | 127 | 0 | 225 | 305 | 320 | 44 | 0 | 181 | 0 | 45 | 0 | 103 | 18 | 20 | 0 | 170 | 0 | 0 | 36 | 305 | 0 | 317 | 42 | 24 | 152 | 0 | 16 | 0 | 81 | 30 | 39 | 0 | 99 | 17 | 9 | 58 | 27 | 0 | 0 | 12 | 7560 | 882 | 128 | 0 | 26 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1197 | 0 | 0 | 0 | 1481 | 0 | 31 | 0 | 113 | 113 | 0 | 75 | 24 | 0 | 0 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 140 | 0 | 370 | 0 | 0 | 0 | 47 | 70 | 0 | 99 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 353 | 1232 | 35 | 7451 | 15011 | 77.93
23:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 17 | 65 | 128 | 196 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 142 | 21.5 | 22 | 0 | 547 | 17 | 16 | 12 | 0 | 6 | 17 | 54 | 18 | 0 | 0 | 0 | 60 | 54 | 28 | 1015 | 152 | 0 | 50 | 25.5 | 34 | 217 | 0 | 0 | 0 | 612 | 0 | 26 | 0 | 225 | 305 | 320 | 44 | 0 | 181 | 0 | 17 | 0 | 103 | 18 | 20 | 0 | 176 | 0 | 0 | 36 | 310 | 0 | 324 | 41 | 24 | 153 | 0 | 0 | 0 | 81 | 30 | 0 | 0 | 99 | 17 | 9 | 58 | 27 | 0 | 0 | 12 | 7270 | 882 | 124 | 0 | 28 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1228 | 0 | 0 | 0 | 1490 | 0 | 31 | 0 | 0 | 56 | 0 | 75 | 24 | 0 | 0 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 47 | 70 | 0 | 34 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 353 | 1244 | 17 | 7284 | 14554 | 77.92
Total KWH | 0 | 1243200 | 563520 | 0 | 0 | 0 | 0 | 0 | 8499600 | 0 | 0 | 259920 | 263880 | 1101024 | 1752480 | 2273236 | 702922 | 265061 | 792000 | 0 | 4851000 | 0 | 0 | 0 | 271217 | 7730094 | 0 | 0 | 215321 | 3230400 | 486000 | 503640 | 0 | 11505454.55 | 922091 | 388909 | 348480 | 0 | 535680 | 105823 | 1260480 | 138539 | 0 | 0 | 21000 | 1576420 | 1347375 | 275520 | 23076363.64 | 1445236 | 0 | 574560 | 301923 | 965999 | 5062935 | 0 | 0 | 0 | 14536362 | 107325 | 909963 | 0 | 5306500 | 8114800 | 7620000 | 1044752 | 0 | 4436000 | 0 | 568320 | 0 | 1019040 | 165480 | 445340 | 0 | 4078080 | 0 | 377200 | 763808 | 7473000 | 0 | 8104000 | 963000 | 631080 | 3586745.46 | 54965 | 302112 | 0 | 1781760 | 714048 | 884100 | 0 | 2393500 | 203400 | 222000 | 1488000 | 383043 | 12950 | 251810 | 126480 | 163926266.65 | 21028364 | 2480832 | 0 | 350400 | 493056 | 0 | 0 | 0 | 0 | 0 | 0 | 673920 | 29083630 | 0 | 0 | 0 | 35639985 | 0 | 600986 | 0 | 1471488 | 1550880 | 0 | 478320 | 202956 | 0 | 379608 | 730560 | 220960 | 0 | 354016 | 3688364 | 0 | 0 | 0 | 3964164 | 0 | 9144800 | 0 | 31200 | 0 | 1124072 | 585609 | 146399 | 1462108 | 0 | 743715 | 0 | 36318.72 | 997200 | 4306 | 348192 | 6808000 | 2855000 | 5287180 | 0 | 6814545 | 29405090.91 | 444000 | 169630224.63 | 333556491.28