## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 23-04-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-04-2026 | during | 23-04-2026 | during | 23-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 352 | 409 | 412 | 412 | 392 | 392 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 450 | 450 | 226 | 226 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 48 | 55 | 55 | 15 | 55 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 320 | 324 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 36 | 53.97 | 53.97 | 17 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 96 | 141 | 149.36 | 149.36 | 149 | 149 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 21 | 33 | 33 | 23 | 23 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 48 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 48 | 294 | 300 | 300 | 48 | 294 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 135 | 149 | 149 | 52 | 88 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 105 | 105 | 105 | 34 | 105 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 72 | 162 | 162 | 35 | 35 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 21 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 500 | 540 | 584 | 584 | 500 | 500 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 125 | 142 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1879 | 2648 | 5947.22 | 5915.22 | 2089 | 2504
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 25.5 | 25.5 | 25.5 | 8 | 25 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 7 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50 | 19 | 50 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 37 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 217 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 51 | 105 | 105 | 34 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 22 | 54 | 56 | 64 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 65 | 0 | 68 | 0 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 3 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 12 | 12 | 108 | 108 | 12 | 12 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.81 | 0 | 3.85 | 0 | 3.85 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 0 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 54 | 54 | 110 | 110 | 54 | 54 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 65 | 69 | 116 | 116 | 18 | 18 | Liquid fuel shortage
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 17 | 155 | 163 | 163 | 17 | 17 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 612 | 1224 | 1224 | 612 | 612 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 18 | 5 | 12 | 0 | 12 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 935 | 1000 | 935 | 935 | 935 | 935 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2078.81 | 2425.5 | 3740.71 | 3807.86 | 2074.85 | 2224
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 180 | 212 | 221 | 221 | 200 | 200 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 325 | 338 | 350.01 | 350.01 | 340 | 340 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 300 | 300 | 342.01 | 342.01 | 342.01 | 342.01 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 230 | 240 | 393 | 393 | 230 | 230 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 51 | 51 | 51 | 44 | 44 | Machine Problem
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 150 | 20 | 140 | 20 | 140 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 37 | 29 | 40 | 40 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 45 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 104 | 200 | 200 | 17 | 80 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 188 | 164 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 6 | 10 | 113 | 113 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 34 | 115 | 115 | 17 | 51 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 61 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1475 | 1697 | 2622.19 | 2686.19 | 1531.01 | 1698.01
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-04-2026 | during | 23-04-2026 | during | 23-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 9 | 16 | 157.5 | 157.5 | 9 | 9 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.2 | 0 | 2.3 | 0 | 2.3 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 9 | 80 | 70 | 70 | 70 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 68 | 10 | 10 | 10 | 10 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 47.6 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 162.8 | 122 | 372.3 | 314 | 154.3 | 118
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 30 | 30 | 30 | 0 | 0 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 157 | 153 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 100 | 100 | 100 | 100 | 100 | 100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 81 | 81 | 81 | 75 | 75 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 99 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 17 | 17 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 305 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 336 | 311 | 350 | 350 | 340 | 340 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1181 | 1168 | 1262 | 1262 | 1192 | 1192
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 922 | 884 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 25 | 35 | 35 | 35 | 35 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 43 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 109 | 151 | 410 | 410 | 112 | 112 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 90 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 50 | 330 | 330 | 100 | 100 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1219 | 1225 | 1234.2 | 1234.2 | 1194.2 | 1194.2 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2340 | 2378 | 3589.2 | 3499.2 | 2596.3 | 2506.3
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 254 | 304 | 250 | 300 | 250 | 300 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 16 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 114 | 110 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1200 | 1200 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 35 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 290 | 290 | 307 | 307 | 290 | 290 | Bad quality coal
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.35 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2111.35 | 2157 | 2412 | 2461 | 2168 | 2235
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 56.14 | 0 | 58 | 0 | 58 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 17 | 30 | 30 | 30 | 30 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 170 | 140 | 214 | 214 | 170 | 170 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 140 | 220 | 220 | 141 | 141 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 380 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 30 | 30 | 0 | 25 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 81 | 80 | 80 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 0 | 50 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.57 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 751.1 | 741.54 | 748 | 748 | 708 | 708 | U-2 Under Maintenance
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 53.94 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 104 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1658.75 | 1666.54 | 2522.69 | 2297.99 | 1719.49 | 1689.79
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 44 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 91 | 113 | 113 | 35 | 113 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.4 | 0 | 6.8 | 0 | 6.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 0 | 70 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 23 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 151 | 0 | 171.5 | 0 | 171.5 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 229.4 | 205 | 500.3 | 292 | 293.3 | 233
System Total |  |  |  |  | 28823.2 | 29270.237 | 13116.11 | 14467.04 | 22968.61 | 22535.46 | 13818.25 | 14400.1
Forecast Scenario (23-04-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13300 |  | 2530 |  | 15950
|  |  |  | 1:00 | 13200 |  | 2139 |  | 15440
|  |  |  | 2:00 | 13000 |  | 2139 |  | 15240
|  |  |  | 3:00 | 12900 |  | 2139 |  | 15140
|  |  |  | 4:00 | 12800 |  | 2139 |  | 15040
|  |  |  | 5:00 | 12700 |  | 2139 |  | 14940
|  |  |  | 6:00 | 12700 |  | 2053 |  | 14850
|  |  |  | 7:00 | 12700 |  | 1957 |  | 14750
|  |  |  | 8:00 | 12700 |  | 1814 |  | 14600
|  |  |  | 9:00 | 12700 |  | 1910 |  | 14700
|  |  |  | 10:00 | 12780 |  | 2215 |  | 15100
|  |  |  | 11:00 | 13100 |  | 2120 |  | 15320
|  |  |  | 12:00 | 13200 |  | 2339 |  | 15650
|  |  |  | 13:00 | 13150 |  | 2416 |  | 15680
|  |  |  | 14:00 | 13150 |  | 2320 |  | 15580
|  |  |  | 15:00 | 13150 |  | 2339 |  | 15600
|  |  |  | 16:00 | 13100 |  | 2187 |  | 15390
|  |  |  | 17:00 | 13150 |  | 2053 |  | 15300
|  |  |  | 18:00 | 13400 |  | 1910 |  | 15400
|  |  |  | 18:30 | 13800 |  | 1767 |  | 15650
|  |  |  | 19:00 | 14200 |  | 1948 |  | 16240
|  |  |  | 19:30 | 14200 |  | 2145 |  | 16446
|  |  |  | 20:00 | 14400 |  | 2139 |  | 16640
|  |  |  | 21:00 | 14300 |  | 2292 |  | 16700
|  |  |  | 22:00 | 14100 |  | 2330 |  | 16540
|  |  |  | 23:00 | 13700 |  | 2426 |  | 16240
Probable Maximum Temperature: |  |  | 36.00°C
Probable Maximum Demand at Day Peak: |  |  | 15650.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 2139
Probable Maximum Demand at Evening Peak: |  |  | 16700.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14400.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 317.58 MKWHr. |  | 451 | 230 | 240 | 376 | 117 | 251 | 83 | 262 | 130 | 2139
*** This report is generated digitally from Operation Information System (OIS) at 08:06 hrs on 23-04-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 22-04-2026 | [28 empty] | Date: | 22-04-2026 | [28 empty] | Date: | 22-04-2026 | [28 empty] | Date: | 22-04-2026 | [28 empty] | Date: | 22-04-2026 | [17 empty] | Date: | 22-04-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 17 | 36 | 146 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 125 | 19.5 | 22 | 0 | 400 | 0 | 16 | 19 | 0 | 14 | 68 | 43 | 18 | 0 | 0 | 0 | 30 | 55 | 20 | 935 | 54 | 0 | 19 | 8 | 40 | 219 | 0 | 0 | 0 | 612 | 0 | 23 | 0 | 215 | 310 | 280 | 44 | 0 | 186 | 0 | 18 | 97 | 46 | 26 | 20 | 0 | 156 | 0 | 0 | 38 | 305 | 0 | 324 | 42 | 16 | 157 | 0 | 0 | 0 | 75 | 30 | 100 | 0 | 100 | 17 | 58 | 9 | 11 | 0 | 0 | 12 | 6584.5 | 918 | 90 | 0 | 29 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1203 | 0 | 0 | 0 | 1497.88 | 0 | 0 | 0 | 35 | 35 | 0 | 50 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 150 | 0 | 0 | 0 | 140 | 0 | 390 | 0 | 0 | 0 | 47 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 110 | 220 | 0 | 253 | 1210 | 17 | 6846.88 | 13431.38 | 77.56
01:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 17 | 145 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 125 | 19.5 | 22 | 0 | 400 | 0 | 16 | 13 | 0 | 12 | 0 | 23 | 18 | 0 | 0 | 0 | 30 | 55 | 20 | 935 | 17 | 0 | 19 | 8 | 34 | 218 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 215 | 310 | 280 | 44 | 0 | 191 | 0 | 19 | 97 | 17 | 0 | 20 | 0 | 158 | 0 | 0 | 38 | 310 | 0 | 324 | 42 | 16 | 159 | 0 | 0 | 0 | 75 | 30 | 101 | 0 | 100 | 6 | 58 | 9 | 11 | 0 | 0 | 12 | 6358.5 | 918 | 86 | 0 | 24 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 0 | 0 | 0 | 1109.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 150 | 0 | 0 | 0 | 140 | 0 | 390 | 0 | 0 | 0 | 48 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 116 | 220 | 0 | 253 | 1222 | 17 | 6310.61 | 12669.11 | 77.55
02:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 17 | 145 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 125 | 19.5 | 22 | 0 | 425 | 0 | 16 | 12 | 0 | 8 | 0 | 22 | 18 | 0 | 0 | 0 | 30 | 54 | 20 | 935 | 17 | 0 | 19 | 8 | 34 | 218 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 215 | 310 | 280 | 44 | 0 | 195 | 0 | 17 | 97 | 17 | 0 | 20 | 0 | 160 | 0 | 0 | 38 | 305 | 0 | 324 | 42 | 16 | 158 | 0 | 8 | 0 | 75 | 30 | 101 | 0 | 100 | 17 | 58 | 9 | 11 | 0 | 0 | 12 | 6397.5 | 919 | 88 | 0 | 24 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1219 | 0 | 0 | 0 | 764.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 150 | 0 | 0 | 0 | 140 | 0 | 390 | 0 | 0 | 0 | 48 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 110 | 220 | 0 | 253 | 1230 | 17 | 5969.73 | 12367.23 | 77.54
03:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 0 | 17 | 145 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 5 | 270 | 0 | 0 | 0 | 125 | 19.5 | 22 | 0 | 410 | 0 | 16 | 12 | 0 | 13 | 0 | 22 | 18 | 0 | 0 | 0 | 30 | 55 | 28 | 935 | 17 | 0 | 19 | 8 | 34 | 218 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 215 | 310 | 280 | 44 | 0 | 195 | 0 | 17 | 97 | 17 | 0 | 20 | 0 | 160 | 0 | 0 | 38 | 300 | 0 | 324 | 42 | 16 | 157 | 0 | 0 | 0 | 75 | 30 | 100 | 0 | 100 | 17 | 58 | 9 | 11 | 0 | 0 | 0 | 6380.5 | 908 | 92 | 0 | 24 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1216 | 0 | 0 | 0 | 760.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 150 | 0 | 0 | 0 | 140 | 0 | 390 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 110 | 220 | 0 | 254 | 1244 | 17 | 5936.45 | 12316.95 | 77.53
04:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 0 | 17 | 145 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 125 | 21 | 22 | 0 | 425 | 0 | 16 | 12 | 0 | 14 | 0 | 22 | 0 | 0 | 0 | 0 | 30 | 54 | 29 | 935 | 17 | 0 | 19 | 8 | 34 | 217 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 215 | 310 | 280 | 44 | 0 | 193 | 0 | 17 | 97 | 17 | 0 | 20 | 0 | 160 | 0 | 0 | 38 | 300 | 0 | 324 | 42 | 16 | 155 | 0 | 0 | 0 | 75 | 30 | 101 | 0 | 100 | 17 | 58 | 9 | 17 | 0 | 0 | 0 | 6377 | 908 | 98 | 0 | 24 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1223 | 0 | 0 | 0 | 760.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 150 | 0 | 0 | 0 | 140 | 0 | 390 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 110 | 220 | 0 | 254 | 1244 | 17 | 5949.91 | 12326.91 | 77.52
05:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 0 | 0 | 17 | 145 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 125 | 21 | 22 | 0 | 430 | 0 | 16 | 13 | 0 | 13 | 0 | 22 | 0 | 0 | 0 | 0 | 30 | 56 | 30 | 935 | 17 | 0 | 19 | 8 | 34 | 218 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 215 | 310 | 280 | 44 | 0 | 198 | 0 | 18 | 97 | 17 | 0 | 20 | 0 | 160 | 0 | 0 | 38 | 305 | 0 | 324 | 42 | 16 | 158 | 0 | 8 | 0 | 75 | 30 | 100 | 0 | 100 | 17 | 58 | 9 | 17 | 0 | 0 | 0 | 6416 | 908 | 99 | 0 | 24 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1226 | 0 | 0 | 0 | 761.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 140 | 0 | 390 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 110 | 220 | 0 | 254 | 1244 | 17 | 5930.79 | 12346.79 | 77.51
06:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 0 | 0 | 17 | 95 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 1 | 125 | 21 | 22 | 0 | 440 | 0 | 16 | 12 | 0 | 6 | 0 | 22 | 0 | 0 | 0 | 0.14 | 30 | 54 | 32 | 935 | 17 | 0 | 19 | 8 | 34 | 218 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 215 | 310 | 280 | 44 | 0 | 198 | 0 | 17 | 97 | 17 | 0 | 20 | 0 | 158 | 0 | 2 | 39 | 305 | 0 | 336 | 42 | 16 | 157 | 0 | 8 | 0 | 78 | 30 | 100 | 0 | 100 | 17 | 58 | 9 | 17 | 0 | 0.96 | 0 | 6383.1 | 908 | 109 | 0 | 24 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1224 | 0 | 0 | 0 | 763.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.25 | 0 | 0 | 0 | 0.69 | 150 | 0 | 0 | 0 | 140 | 0 | 390 | 0 | 0.07 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 4 | 0.02 | 16 | 290 | 116 | 220 | 0 | 254 | 1244 | 17 | 5955.56 | 12338.66 | 77.5
07:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 0 | 17 | 95 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 5 | 125 | 21 | 22 | 0 | 420 | 26 | 16 | 12 | 0 | 2 | 0 | 22 | 0 | 0 | 0 | 0.74 | 30 | 55 | 28 | 935 | 17 | 0 | 19 | 8 | 34 | 218 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 230 | 310 | 280 | 44 | 0 | 198 | 0 | 17 | 98 | 17 | 0 | 8 | 0 | 156 | 0 | 14 | 39 | 310 | 0 | 336 | 42 | 0 | 157 | 0 | 17 | 0 | 78 | 30 | 100 | 0 | 100 | 17 | 58 | 9 | 10 | 0.4 | 8.7 | 0 | 6394.84 | 908 | 111 | 0 | 24 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1225 | 0 | 0 | 0 | 755.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.02 | 13 | 0 | 0 | 8 | 150 | 0 | 0 | 0 | 140 | 0 | 390 | 0 | 0.22 | 0 | 48 | 0 | 2 | 0 | 0 | 0 | 0 | 0.9 | 30 | 0.11 | 16 | 290 | 110 | 220 | 0 | 254 | 1244 | 17 | 6011.68 | 12406.52 | 77.49
08:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 0 | 17 | 96 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 13 | 125 | 21 | 22 | 0 | 400 | 47 | 16 | 11 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 1.65 | 30 | 55 | 5 | 935 | 17 | 0 | 19 | 8 | 34 | 217 | 0 | 0 | 0 | 612 | 8 | 20 | 0 | 230 | 310 | 280 | 44 | 0 | 198 | 0 | 17 | 40 | 17 | 0 | 20 | 0 | 160 | 0 | 30 | 39 | 305 | 0 | 336 | 42 | 0 | 157 | 1 | 17 | 0 | 78 | 30 | 100 | 0 | 100 | 17 | 58 | 9 | 9 | 0.4 | 15.09 | 0 | 6351.14 | 923 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 1225 | 0 | 0 | 0 | 748.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.38 | 31 | 0 | 0 | 12.12 | 150 | 0 | 0 | 0 | 140 | 0 | 390 | 0 | 1.54 | 0 | 49 | 0 | 8 | 0 | 0 | 0 | 0 | 2 | 38 | 0.24 | 16 | 290 | 114 | 220 | 0 | 254 | 1232 | 17 | 6023.94 | 12375.08 | 77.48
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 17 | 30 | 96 | 32 | 15 | 17 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 15 | 125 | 20.5 | 22 | 0 | 320 | 53 | 16 | 12 | 0 | 6 | 0 | 22 | 0 | 0 | 0 | 2.55 | 40 | 55 | 2 | 935 | 17 | 0 | 19 | 8 | 34 | 214 | 0 | 0 | 0 | 612 | 6 | 20 | 0 | 230 | 310 | 280 | 44 | 0 | 204 | 0 | 17 | 20 | 17 | 0 | 8 | 0 | 174 | 0 | 29 | 38 | 305 | 0 | 336 | 42 | 0 | 151 | 5 | 17 | 0 | 78 | 30 | 101 | 0 | 100 | 17 | 58 | 9 | 9 | 0.8 | 14.51 | 0 | 6357.36 | 922 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 1209 | 0 | 0 | 0 | 752.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.08 | 35 | 0 | 0 | 25.16 | 150 | 0 | 0 | 0 | 140 | 0 | 350 | 0 | 3.64 | 0 | 49 | 0 | 8 | 0 | 0 | 0 | 0 | 3.2 | 72 | 0.4 | 16 | 290 | 110 | 220 | 0 | 254 | 1200 | 17 | 6015.58 | 12372.94 | 77.47
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 17 | 33 | 96 | 32 | 15 | 0 | 17 | 0 | 180 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 18 | 125 | 20.5 | 22 | 0 | 440 | 53 | 16 | 12 | 0 | 14 | 0 | 22 | 0 | 0 | 0 | 3.22 | 40 | 55 | 2 | 935 | 17 | 0 | 18 | 8 | 34 | 214 | 0 | 0 | 0 | 612 | 11 | 20 | 0 | 230 | 320 | 280 | 44 | 0 | 202 | 0 | 17 | 20 | 17 | 0 | 20 | 0 | 180 | 0 | 26 | 38 | 305 | 0 | 336 | 42 | 0 | 157 | 10 | 17 | 0 | 75 | 30 | 99 | 0 | 100 | 17 | 68 | 9 | 9 | 0.8 | 44.3 | 0 | 6548.82 | 923 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 1211 | 0 | 0 | 0 | 761.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.47 | 91 | 0 | 0 | 51.18 | 170 | 0 | 0 | 0 | 140 | 0 | 380 | 0 | 4.88 | 0 | 49 | 0 | 19 | 0 | 0 | 0 | 0 | 5.7 | 92 | 0.55 | 16 | 290 | 110 | 220 | 0 | 253 | 1200 | 17 | 6220.88 | 12769.7 | 77.47
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 17 | 34 | 96 | 48 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 17 | 320 | 0 | 0 | 21 | 125 | 21 | 21 | 0 | 500 | 65 | 16 | 12 | 0 | 18 | 0 | 22 | 0 | 0 | 0 | 3.81 | 40 | 54 | 2 | 935 | 17 | 0 | 19 | 8 | 34 | 214 | 0 | 0 | 0 | 612 | 7 | 20 | 0 | 230 | 325 | 300 | 44 | 0 | 180 | 0 | 17 | 30 | 17 | 6 | 20 | 0 | 188 | 0 | 61 | 37 | 310 | 0 | 336 | 42 | 0 | 157 | 11 | 17 | 0 | 78 | 30 | 100 | 0 | 100 | 17 | 68 | 19 | 9 | 2.2 | 47.6 | 0 | 6776.61 | 922 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 1219 | 0 | 0 | 0 | 751.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.14 | 104 | 0 | 0 | 53.94 | 170 | 0 | 0 | 0 | 140 | 0 | 380 | 0 | 3.57 | 0 | 49 | 0 | 23 | 0 | 0 | 0 | 0 | 6.4 | 151 | 0.35 | 16 | 290 | 114 | 220 | 0 | 254 | 1200 | 17 | 6339.5 | 13116.11 | 77.46
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 6 | 17 | 34 | 102 | 48 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 29 | 125 | 21 | 21 | 0 | 545 | 53 | 16 | 12 | 0 | 20 | 0 | 22 | 0 | 0 | 0 | 2.21 | 40 | 55 | 2 | 935 | 17 | 0 | 19 | 8 | 34 | 211 | 0 | 0 | 0 | 612 | 13 | 20 | 0 | 230 | 330 | 300 | 44 | 0 | 186 | 0 | 17 | 40 | 17 | 9 | 20 | 0 | 192 | 0 | 33 | 37 | 315 | 0 | 325 | 42 | 0 | 156 | 11 | 17 | 0 | 77 | 30 | 99 | 0 | 100 | 0 | 68 | 19 | 9 | 1.4 | 44.26 | 0 | 6791.87 | 923 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 1219 | 0 | 0 | 0 | 765.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.29 | 108 | 0 | 0 | 45.37 | 153 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 5.62 | 0 | 46 | 0 | 18 | 0 | 0 | 0 | 0 | 7.4 | 57 | 0.65 | 16 | 290 | 110 | 220 | 0 | 254 | 1200 | 17 | 6251.88 | 13043.75 | 77.46
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 17.5 | 17 | 49 | 108 | 48 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 31 | 138 | 17 | 21 | 0 | 440 | 53 | 16 | 12 | 0 | 23 | 0 | 24 | 0 | 0 | 0 | 2.24 | 40 | 55 | 5 | 935 | 17 | 0 | 19 | 8 | 34 | 213 | 0 | 0 | 0 | 612 | 17 | 20 | 0 | 220 | 330 | 300 | 44 | 0 | 181 | 0 | 17 | 40 | 17 | 9 | 8 | 0 | 196 | 0 | 64 | 29 | 310 | 0 | 325 | 42 | 0 | 153 | 11 | 17 | 0 | 76 | 30 | 99 | 0 | 100 | 0 | 68 | 19 | 9 | 2.2 | 45.37 | 0 | 6760.31 | 922 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 1201 | 0 | 0 | 0 | 773.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 54.87 | 102 | 0 | 0 | 60.55 | 153 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 1.87 | 0 | 46 | 0 | 13 | 0 | 0 | 0 | 0 | 6.8 | 192 | 0.71 | 16 | 290 | 110 | 180 | 0 | 253 | 1200 | 17 | 6352.67 | 13112.98 | 77.45
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 17.5 | 17 | 54 | 108 | 48 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 28 | 140 | 21 | 20 | 0 | 480 | 53 | 16 | 12 | 0 | 33 | 0 | 54 | 0 | 0 | 0 | 2.92 | 40 | 54 | 2 | 935 | 17 | 0 | 19 | 8 | 34 | 212 | 0 | 0 | 0 | 590 | 15 | 20 | 0 | 215 | 340 | 300 | 44 | 0 | 172 | 0 | 17 | 40 | 16 | 9 | 20 | 0 | 210 | 0 | 21 | 29 | 310 | 0 | 305 | 42 | 0 | 151 | 10 | 17 | 0 | 76 | 30 | 101 | 0 | 100 | 0 | 68 | 19 | 9 | 1.8 | 45.04 | 0 | 6755.26 | 922 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 1227 | 0 | 0 | 0 | 767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 47.75 | 91 | 0 | 0 | 52.07 | 152 | 0 | 0 | 0 | 140 | 0 | 380 | 0 | 2.33 | 0 | 46 | 0 | 28 | 0 | 0 | 0 | 0 | 5.8 | 164 | 0.35 | 16 | 290 | 110 | 220 | 0 | 254 | 1244 | 17 | 6372.3 | 13127.56 | 77.45
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 17.5 | 17 | 52 | 106 | 48 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 18 | 140 | 21 | 20 | 0 | 540 | 53 | 16 | 12 | 0 | 34 | 0 | 54 | 0 | 0 | 0 | 2.25 | 40 | 55 | 2 | 935 | 17 | 0 | 19 | 8 | 34 | 213 | 0 | 0 | 0 | 612 | 12 | 20 | 0 | 215 | 342 | 280 | 44 | 0 | 171 | 0 | 20 | 40 | 17 | 9 | 20 | 0 | 210 | 0 | 34 | 27 | 310 | 0 | 290 | 42 | 0 | 152 | 7 | 17 | 0 | 76 | 30 | 99 | 0 | 99 | 0 | 68 | 19 | 9 | 1.4 | 31.55 | 0 | 6788.7 | 922 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 1225 | 0 | 0 | 0 | 759.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 30.76 | 73 | 0 | 0 | 37.45 | 153 | 0 | 0 | 0 | 140 | 0 | 380 | 0 | 3.34 | 0 | 46 | 32 | 10 | 0 | 0 | 0 | 0 | 4.4 | 128 | 0.2 | 16 | 290 | 110 | 220 | 0 | 302 | 1244 | 17 | 6322.18 | 13110.88 | 77.44
16:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 18 | 17 | 52 | 108 | 48 | 15 | 17 | 17 | 0 | 225 | 0 | 0 | 0 | 17 | 317 | 0 | 0 | 14 | 132 | 21 | 20 | 0 | 450 | 53 | 16 | 12 | 0 | 30 | 0 | 54 | 0 | 0 | 0 | 0 | 40 | 54 | 2 | 935 | 163 | 0 | 19 | 8 | 34 | 214 | 0 | 0 | 0 | 608 | 7 | 20 | 0 | 215 | 334 | 260 | 44 | 0 | 189 | 0 | 17 | 40 | 17 | 8 | 20 | 0 | 212 | 0 | 28 | 27 | 310 | 0 | 288 | 42 | 0 | 152 | 5 | 17 | 0 | 75 | 30 | 101 | 0 | 99 | 0 | 68 | 9 | 10 | 0.8 | 20.38 | 4 | 6850.18 | 923 | 114 | 0 | 2 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 1222 | 0 | 0 | 0 | 746.34 | 0 | 0 | 0 | 35 | 24 | 0 | 0 | 13 | 0 | 23.17 | 48 | 0 | 0 | 23.21 | 140 | 0 | 0 | 0 | 140 | 0 | 360 | 0 | 2.16 | 0 | 46 | 35 | 14 | 0 | 0 | 0 | 0 | 2.9 | 80 | 0.14 | 16 | 290 | 110 | 220 | 0 | 304 | 1200 | 17 | 6208.92 | 13059.1 | 77.44
17:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 18 | 0 | 52 | 139 | 48 | 17 | 30 | 72 | 0 | 225 | 0 | 0 | 0 | 35 | 295 | 0 | 0 | 6 | 140 | 21 | 20 | 0 | 500 | 62 | 16 | 12 | 0 | 19 | 0 | 54 | 0 | 0 | 0 | 0.55 | 40 | 55 | 2 | 935 | 140 | 0 | 19 | 9 | 40 | 215 | 0 | 0 | 0 | 612 | 2 | 20 | 0 | 215 | 335 | 260 | 44 | 0 | 200 | 0 | 27 | 40 | 45 | 9 | 20 | 0 | 180 | 0 | 11 | 27 | 315 | 0 | 288 | 42 | 0 | 152 | 2 | 17 | 0 | 76 | 30 | 101 | 0 | 99 | 0 | 68 | 9 | 10 | 0.3 | 8.2 | 10 | 6963.05 | 923 | 130 | 0 | 19 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 1222 | 0 | 0 | 0 | 739.76 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 13 | 0 | 9.22 | 20 | 0 | 0 | 9.12 | 140 | 0 | 0 | 0 | 140 | 0 | 360 | 0 | 0.85 | 0 | 45 | 50 | 5 | 33 | 0 | 0 | 0 | 1.2 | 33 | 0.08 | 16 | 290 | 102 | 220 | 0 | 304 | 1196 | 17 | 6167.23 | 13130.28 | 77.43
18:00 | 0 | 105 | 26 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 18 | 15 | 52 | 140 | 145 | 48 | 35 | 72 | 0 | 180 | 0 | 0 | 0 | 35 | 290 | 0 | 0 | 1 | 142 | 21 | 20 | 0 | 455 | 69 | 16 | 11 | 0 | 8 | 28 | 62 | 0 | 0 | 0 | 0.01 | 40 | 54 | 2 | 935 | 140 | 0 | 26 | 25.5 | 51 | 215 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 225 | 338 | 250 | 44 | 0 | 180 | 0 | 34 | 40 | 103 | 9 | 20 | 0 | 196 | 0 | 1 | 27 | 320 | 0 | 292 | 42 | 30 | 148 | 0 | 17 | 0 | 78 | 30 | 99 | 0 | 99 | 0 | 68 | 9 | 10 | 0.3 | 0.92 | 12 | 7174.73 | 922 | 133 | 0 | 20 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1202 | 0 | 0 | 0 | 748.78 | 0 | 0 | 0 | 35 | 50 | 0 | 81 | 12 | 0 | 1.28 | 3 | 24 | 0 | 1.16 | 140 | 0 | 0 | 0 | 140 | 0 | 350 | 0 | 0.11 | 0 | 43 | 70 | 1 | 60 | 0 | 0 | 0 | 0 | 5 | 0.01 | 16 | 290 | 108 | 200 | 0 | 302 | 1198 | 17 | 6208.34 | 13383.07 | 77.43
19:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 36 | 17 | 65 | 142 | 294 | 48 | 35 | 72 | 0 | 225 | 0 | 0 | 0 | 35 | 324 | 0 | 0 | 0 | 142 | 21 | 20 | 0 | 530 | 70 | 16 | 12 | 0 | 7 | 67 | 62 | 0 | 0 | 0 | 0 | 36 | 55 | 5 | 935 | 145 | 0 | 50 | 25.5 | 51 | 217 | 0 | 0 | 0 | 612 | 0 | 100 | 0 | 270 | 338 | 300 | 44 | 0 | 191 | 0 | 34 | 45 | 104 | 9 | 20 | 0 | 186 | 0 | 0 | 29 | 310 | 0 | 292 | 42 | 30 | 153 | 0 | 17 | 0 | 80 | 30 | 100 | 0 | 99 | 6 | 68 | 9 | 16 | 0 | 0 | 12 | 7862.5 | 885 | 145 | 0 | 28 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1230 | 0 | 0 | 0 | 746.19 | 0 | 0 | 0 | 35 | 50 | 0 | 81 | 22 | 0 | 0 | 0 | 24 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 44 | 70 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 108 | 220 | 0 | 304 | 1195 | 17 | 6317.19 | 14179.69 | 77.42
19:30 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 36 | 17 | 145 | 142 | 294 | 48 | 35 | 72 | 0 | 225 | 0 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 142 | 21 | 21 | 0 | 450 | 70 | 16 | 12 | 0 | 6 | 67 | 62 | 0 | 0 | 0 | 0 | 36 | 55 | 2 | 1000 | 140 | 0 | 50 | 25.5 | 51 | 217 | 0 | 0 | 0 | 612 | 0 | 150 | 0 | 265 | 336 | 300 | 51 | 0 | 194 | 0 | 34 | 45 | 103 | 9 | 20 | 0 | 184 | 0 | 0 | 29 | 310 | 0 | 292 | 42 | 30 | 152 | 0 | 17 | 0 | 80 | 30 | 100 | 0 | 99 | 17 | 68 | 9 | 16 | 0 | 0 | 12 | 7937.5 | 834 | 146 | 0 | 26 | 48 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 737.51 | 0 | 0 | 0 | 35 | 50 | 0 | 81 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 350 | 0 | 0 | 0 | 47 | 70 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 110 | 220 | 0 | 304 | 1200 | 17 | 6254.51 | 14192.01 | 77.42
20:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 36 | 17 | 135 | 141 | 294 | 48 | 35 | 72 | 0 | 225 | 0 | 0 | 0 | 35 | 324 | 0 | 0 | 0 | 142 | 21 | 21 | 0 | 540 | 69 | 16 | 12 | 0 | 5 | 65 | 54 | 0 | 0 | 0 | 0 | 37 | 54 | 3 | 1000 | 155 | 0 | 50 | 25.5 | 51 | 217 | 0 | 0 | 0 | 612 | 0 | 150 | 0 | 240 | 338 | 300 | 51 | 0 | 212 | 0 | 34 | 45 | 104 | 10 | 20 | 0 | 164 | 0 | 0 | 29 | 305 | 0 | 311 | 42 | 30 | 153 | 0 | 17 | 0 | 81 | 30 | 100 | 0 | 99 | 17 | 68 | 9 | 16 | 0 | 0 | 12 | 8060.5 | 884 | 151 | 0 | 25 | 43 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 1225 | 0 | 0 | 0 | 741.54 | 0 | 17 | 0 | 35 | 50 | 0 | 81 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 44 | 70 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 110 | 220 | 0 | 304 | 1200 | 17 | 6406.54 | 14467.04 | 77.41
21:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 36 | 17 | 143 | 126 | 294 | 48 | 35 | 72 | 0 | 225 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 142 | 21 | 21 | 0 | 450 | 70 | 16 | 12 | 0 | 2 | 67 | 54 | 15 | 0 | 0 | 0 | 39 | 55 | 8 | 1000 | 140 | 0 | 50 | 25.5 | 51 | 219 | 0 | 0 | 0 | 612 | 0 | 140 | 0 | 240 | 338 | 285 | 51 | 0 | 205 | 0 | 34 | 45 | 104 | 15 | 20 | 0 | 172 | 0 | 0 | 29 | 310 | 0 | 316 | 42 | 30 | 154 | 0 | 17 | 0 | 81 | 30 | 101 | 0 | 99 | 17 | 68 | 9 | 16 | 0 | 0 | 0 | 7930.5 | 786 | 157 | 0 | 25 | 42 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 1220 | 0 | 0 | 0 | 738.86 | 0 | 20 | 0 | 35 | 50 | 0 | 81 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 350 | 0 | 0 | 0 | 45 | 70 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 110 | 220 | 0 | 304 | 1196 | 17 | 6286.86 | 14217.36 | 77.41
22:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 36 | 0 | 94 | 95 | 294 | 48 | 35 | 72 | 0 | 225 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 142 | 21 | 0 | 0 | 470 | 70 | 16 | 12 | 0 | 0 | 67 | 52 | 18 | 0 | 0 | 0 | 40 | 55 | 15 | 1000 | 152 | 0 | 50 | 25.5 | 51 | 218 | 0 | 0 | 0 | 612 | 0 | 110 | 0 | 240 | 338 | 300 | 44 | 0 | 213 | 0 | 34 | 98 | 104 | 16 | 20 | 0 | 182 | 0 | 0 | 29 | 295 | 0 | 358 | 42 | 30 | 155 | 0 | 17 | 0 | 81 | 30 | 100 | 0 | 100 | 17 | 58 | 9 | 15 | 0 | 0 | 0 | 7815.5 | 884 | 160 | 0 | 25 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1230 | 0 | 0 | 0 | 742.85 | 0 | 16 | 0 | 35 | 50 | 0 | 81 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 9 | 70 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 257 | 110 | 220 | 0 | 304 | 1215 | 17 | 6310.85 | 14126.35 | 77.41
23:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 18 | 6 | 47 | 95 | 210 | 48 | 35 | 72 | 0 | 225 | 0 | 0 | 0 | 35 | 331 | 0 | 0 | 0 | 142 | 21 | 19 | 0 | 530 | 69 | 16 | 12 | 0 | 3 | 67 | 51 | 18 | 0 | 0 | 0 | 40 | 55 | 19 | 935 | 140 | 0 | 50 | 25.5 | 51 | 218 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 230 | 340 | 300 | 51 | 0 | 205 | 0 | 34 | 97 | 104 | 18 | 20 | 0 | 188 | 0 | 0 | 31 | 305 | 0 | 359 | 42 | 30 | 159 | 0 | 17 | 0 | 81 | 30 | 100 | 0 | 100 | 0 | 58 | 9 | 17 | 0 | 0 | 0 | 7617.5 | 884 | 165 | 0 | 25 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1226 | 0 | 0 | 0 | 769.83 | 0 | 0 | 0 | 35 | 50 | 0 | 81 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 110 | 220 | 0 | 277 | 1244 | 17 | 6345.83 | 13963.33 | 77.4
Total KWH | 0 | 1176960 | 528000 | 0 | 0 | 0 | 0 | 0 | 9187200 | 0 | 0 | 260640 | 271080 | 1111680 | 2825760 | 2274240 | 599086 | 265764 | 836640 | 0 | 4698000 | 0 | 0 | 0 | 269729 | 7181649 | 0 | 0 | 208217 | 3235200 | 502200 | 487440 | 0 | 11265454.55 | 1070127 | 383891 | 298560 | 0 | 296640 | 422226 | 878496 | 137615 | 0 | 0 | 21727 | 862200 | 1338200 | 261120 | 22792727.27 | 1450255 | 0 | 634080 | 310575.6 | 982727 | 4901266 | 0 | 0 | 0 | 14547271 | 100440 | 938400 | 0 | 5556000 | 8144400 | 7014000 | 1081848 | 0 | 4812000 | 0 | 552960 | 1549422 | 992160 | 144480 | 444520 | 0 | 4248000 | 0 | 406473 | 809136 | 7448000 | 0 | 806000 | 994000 | 291000 | 3731645.46 | 72457 | 320784 | 0 | 1846080 | 717696 | 2370300 | 0 | 2395990 | 262080 | 1509600 | 256800 | 266880 | 13048 | 295160 | 86400 | 159252802.88 | 21963636 | 2955168 | 0 | 336960 | 509952 | 0 | 0 | 0 | 139171 | 0 | 0 | 650160 | 29236370 | 0 | 0 | 0 | 35464728 | 0 | 45822 | 0 | 318816 | 464352 | 0 | 523584 | 176201 | 0 | 368392 | 754251 | 255130 | 0 | 380256 | 3663273 | 0 | 0 | 10200 | 3626972 | 0 | 9352218 | 0 | 33960 | 0 | 843055 | 570895 | 187144 | 648720 | 0 | 0 | 0 | 44883.84 | 1088640 | 4012 | 394272 | 6938000 | 2429000 | 5340000 | 0 | 6501818 | 29678545.45 | 440400 | 166338957.29 | 325591760.17

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 22-04-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13116.11 | MW | 11:00 Hr. | Energy Generated |  |  | 325.5918 |  | MKWHr.
| Day Peak Demand |  |  | 15648.75 | MW | 12:00 Hr. | Energy Unserverd |  |  | 52.653 |  | MKWHr.
| Evening Peak Generation |  |  | 14467.04 | MW | 20:00 Hr. | Energy Demand |  |  | 378.2448 |  | MKWHr.
| Evening Peak Demand |  |  | 16647.04 | MW | 20:00 Hr. | Maximum Temperature |  |  | 35.4 |  | °C
| Minimum Generation of the Day |  |  | 12316.95 | MW | 03:00 Hr. | Total Gas Supplied |  |  | 926.1 |  | MMCFD
| Maximum Generation of the Day |  |  | 14467.04 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 6.643 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.3219 | 0 | 13.6548 | 0 | 0 | 0.20822 | 0 | 0 | 47.1849 | Gas | 115.6415 | Gas | 406107058.6467
| Chattogram Zone |  |  | 5.1624 | 37.34 | 7.9068 | 0 | 0.8622 | 0.12217 | 0 | 0.29664 | 51.6901 | Coal | 110.5378 | Coal | 750488657.2216
| Cumilla Zone |  |  | 28.6022 | 0 | 3.4371 | 0 | 0 | 0.40647 | 4.248 | 0 | 36.6938 | HFO | 31.7987 | HFO | 564274600.18
| Mymensingh Zone |  |  | 0.26688 | 0 | 2.1149 | 0 | 0 | 0.30821 | 0 | 0 | 2.69 | HSD | 0.14937 | HSD | 2484198.47
| Sylhet Zone |  |  | 20.9215 | 0 | 0 | 0 | 0 | 0.072457 | 0 | 0 | 20.994 | Hydro | 0.8622 | Hydro | 86220
| Khulna Zone |  |  | 2.9552 | 29.2364 | 0.84691 | 0.13917 | 0 | 0.65016 | 21.9636 | 0 | 55.7914 | Solar | 4.6292 | Solar | 74018638.198
| Barishal Zone |  |  | 7.769 | 43.1184 | 0.83467 | 0 | 0 | 0.004012 | 0 | 0 | 51.726 | Import | 61.6764 | Import | 361070548.92
| Rajshahi Zone |  |  | 16.6425 | 0 | 1.7839 | 0.0102 | 0 | 1.5369 | 35.4647 | 0 | 55.4382 | Wind | 0.29664 | Wind | 4363574.4
| Rangpur Zone |  |  | 0 | 0.84305 | 1.2196 | 0 | 0 | 1.3207 | 0 | 0 | 3.3833
| Total |  |  | 115.6415 | 110.5378 | 31.7987 | 0.14937 | 0.8622 | 4.6292 | 61.6764 | 0.29664 | 325.5918
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 406107058.6467 |  | Hydro | 86220
|  |  |  | Coal | 750488657.2216 |  | Solar | 74018638.198
|  |  |  | HFO | 564274600.18 |  | Import | 361070548.92
|  |  |  | HSD | 2484198.47 |  | Wind | 4363574.4
[5 empty] | Total: | 216,28,93,496 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9636 | Peak Hr Flow | 884.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 48148618.18 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 35.4647 | Peak Hr Flow | 741.54 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1827 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 4.248 | Peak Hr Flow | 164.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2816 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 61.6764 | Peak Hr Flow | 1789.54 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 450 |  | 6017
|  |  |  | Chattogram |  | 250 |  | 1588
|  |  |  | Cumilla |  | 220 |  | 1575
|  |  |  | Mymensingh |  | 180 |  | 1070
|  |  |  | Sylhet |  | 100 |  | 576
|  |  |  | Khulna |  | 380 |  | 1977
|  |  |  | Barishal |  | 60 |  | 468
|  |  |  | Rajshahi |  | 280 |  | 1808
|  |  |  | Rangpur |  | 166 |  | 1002
|  |  |  | Total |  | 2086 |  | 16081
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 320
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:10 | 17:29 | Chowmuhani 230/132/33kV S/S ATR-02 LT Project Work S/D Due to Blast Wall Painting
| 08:11 | 17:28 | Chowmuhani 230/132/33kV S/S ATR-02 HT Project Work S/D Due to Blast wall Painting
| 08:29 | 16:42 | Amtali 400/132kV S/S Amtali - RNPL 400 kV Ckt - 2 Project Work S/D Due to RNPL চাহিদা
অনুযায়ী Shutdown নেওয়া হয়েছে।
| 08:33 | 15:39 | Halishahar-Julda 132kV Ckt-1 Scheduled S/D from Juldah 132/33kV end Due to Due to
Armouring work between 4-5 No Tower.
| 09:12 | 17:53 | Feni 230/132kV S/S ATR-2 HT Project Work S/D Due to Oil Leakage and Rast check painting
works
| 09:12 | 17:53 | Feni 230/132kV S/S ATR-2 LT Project Work S/D Due to Oil Leakage and Rast check works
| 09:44 | 17:20 | Savar 132/33kV S/S T-1 LT Scheduled S/D Due to Transformer painting works.
| 09:45 | 17:20 | Savar 132/33kV S/S T-1 HT Scheduled S/D Due to Transformer painting works.
| 09:46 | 14:40 | Mithapukur-Palashbari 132kV Ckt-1 Scheduled S/D from Mithapukur 132/33kV end Due to For
pulling opzw from line tower to gantry structure.
| 09:46 | 14:48 | Mithapukur-Palashbari 132kV Ckt-2 Scheduled S/D from Mithapukur 132/33kV end Due to For
pulling opgw from line tower to gantry structure.
| 11:05 | 12:38 | BIPTC S/S 20DF43 Scheduled S/D Due to For CB Maintenance
| 11:16 | 13:13 | Jamalpur-Mymensingh 132kV Ckt-2 Scheduled S/D from Jamalpur 132/33kV end Due to Work for
Mymensingh grid
| 11:23 | 13:10 | Bogura-Bogura (New)) 132 kV Ckt-1 Scheduled S/D from Bogura 230/132kV end Due to
Maintenance work at Bogura 132kV sub-Station and from Bogura 132/33kV end Due to SF6 Gas
Leakage Maintenance work
| 11:56 | 16:04 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Scheduled S/D Due to Kaliakoir Ckt 1
Aviation Light replacement
| 12:59 | 13:37 | Ishurdi-Pabna 132kV ckt Tripped from Ishurdi 132/33kV end showing zone 2 trip,Ph R
Trip,distance 19.28 km from isd end. relays.
| 13:04 | 14:19 | Pabna- Shahjadpur 132kV Ckt-1 Tripped from Shahjadpur 132/33kV end showing 21, Zone-2 | [7 empty] | 8.0MW load
|  |  | relays Due to None | [7 empty] | interrup.
Shahjadpur 132/33kV
end
| 15:30 | 16:04 | Hasnabad-Sitalakhya 132kV Ckt-1 Scheduled S/D from Hasnabad 132/33kV end Due to shut down
by NLDC
|  | 15:43 | Keranigonj 230/132/33kV S/S ATR-3 LT is restored.
|  | 17:20 | Savar 132/33kV S/S T-1 HT is restored.
| 17:33 | 18:09 | Munshiganj 132/33kV S/S Transformer-2 LT Forced S/D Due to Shutdown to replace demaged | [7 empty] | 60.0MW load
|  |  | VCB of BANCO ckt-1 | [7 empty] | interrup.
| 17:33 | 18:08 | Munshiganj 132/33kV S/S Transformer-2 HT Forced S/D Due to Shutdown to replace damaged | [7 empty] | 60.0MW load
|  |  | VCB of BANCO ckt-1 | [7 empty] | interrup.
| 20:00 |  | Evening Peak Generation: 14466 MW.
| 20:53 | 22:38 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-2 Tripped showing Distance Relay
(F21_7SA611) relays Due to Distance Trip
| 20:56 | 23:28 | Mirzapur 132/33kV S/S Transformer-01(E05) LT Tripped showing OC OPTD 86.1 & 86.2 Trip | [7 empty] | 20.0MW load
|  |  | relay. relays Due to PBS Jamurki feeder fualt. | [7 empty] | interrup.
|  | 21:30 | Brahmanbaria-Shahjibazar 132 kV Ckt-1 is restored.
|  | 21:33 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 is restored.
| 21:40 | 00:30 | Niamatpur 132/33kV S/S Transformer-1(407T) LT Forced S/D Due to Red hot maintenance. | [7 empty] | 10.0MW load
interrup.
| 21:41 | 00:20 | Niamatpur 132/33kV S/S Transformer-1(407T) HT Forced S/D Due to Red hot maintenance. | [7 empty] | 10.0MW load
interrup.
| 01:10 | 01:26 | Niamatpur 132/33kV S/S Transformer-1(407T) LT Tripped showing O/C, E/F relays. | [7 empty] | 21.0MW load
interrup.
| 02:00 |  | Minimum generation 12521 MW
| 02:56 | 03:07 | Keranigonj 230/132/33kV S/S TR-1 LT Tripped showing 86 relays Due to Overcurrent Earth | [7 empty] | 47.0MW load
|  |  | fault by 33kV Ati bazar feeder fault. | [7 empty] | interrup.
| 05:49 | 06:27 | Madunaghat 132/33kV S/S TR-1(507T) LT Tripped showing REF-615 relays Due to Due to | [7 empty] | 20.0MW load
|  |  | Mohora-2 feeder fault | [7 empty] | interrup.
| 06:06 |  | Jashore 132/33kV S/S T-1 HT Forced S/D Due to Redhot Maintanance to Auxiliary Tx. (East) | [7 empty] | 30.0MW load
interrup.
| 06:06 |  | Jashore 132/33kV S/S T-1 LT Forced S/D Due to Redhot Maintanance to Auxiliary Tx. (East) | [7 empty] | 30.0MW load
interrup.
| 06:18 | 06:29 | Rampura-Ullon-2 132kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Order by
nldc
| 06:34 |  | Gollamari 132/33kV S/S Tr-1 LT Tripped showing No relay signal relays Due to 33 kv wzpdcl
cable trench burn.
| 06:34 |  | Gollamari 132/33kV S/S Tr-2 LT Forced S/D Due to Wzpdcl cable trench burn. | [7 empty] | 80.0MW load
interrup.
| 06:34 |  | Full interruption is occurring under Gollamari GIS s/s due to tripping of transformer
TR-1 and forced shutdown of transformer TR-2 caused by fire in 33 kV WZPDCL feeder
| 06:35 |  | Gollamari 132/33kV S/S Tr-1 HT Forced S/D Due to Wzpdcl cable trench burn.
| 06:35 |  | Gollamari 132/33kV S/S Tr-2 HT Forced S/D Due to Wzpdcl cable trench burn | [7 empty] | 80.0MW load
interrup.
| 06:36 |  | Rampura-Ullon-2 132kV Ckt-1 Scheduled S/D from Rampura 230/132kV end Due to Order by
NLDC
| 07:37 | 07:56 | Tongi 230/132/33kV S/S T-1 LT Scheduled S/D Due to DESCO
| 07:37 | 07:56 | Tongi 230/132/33kV S/S T-1 HT Scheduled S/D Due to DESCO
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 22-04-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 409 | 9187200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4698000 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 48 | 599086 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 324 | 7181649 | Machine Problem
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 36 | 260640 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 141 | 2825760 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 265764 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 269729 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 502200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 487440 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 48 | 528000 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 294 | 2274240 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 135 | 1111680 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1176960 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 836640 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 208217 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 271080 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 540 | 11265454.55 | FGMO Available
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3235200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2648 | 47184939.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 310575.6 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 100440 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 634080 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 37 | 862200 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 4901266 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 982727 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 54 | 878496 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 65 | 422226 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 3 | 261120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 298560 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21727 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 383891 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 137615 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 54 | 1338200 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 69 | 1070127 | Liquid fuel shortage
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 155 | 1450255 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 14547271 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 5 | 296640 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1000 | 22792727.27 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 2425.5 | 51690143.87
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 212 | 4812000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 338 | 8144400 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 300 | 7014000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 240 | 5556000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1081848 | Machine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 938400 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 29 | 809136 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 45 | 1549422 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 104 | 992160 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 164 | 4248000 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 444520 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 10 | 144480 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 34 | 552960 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 406473 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1697 | 36693799
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 16 | 266880 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13048 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 256800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1509600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 295160 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 86400 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 262080 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 122 | 2689968
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 72457 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 994000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 291000 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 153 | 3731645.46 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 100 | 2370300 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 717696 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1846080 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 99 | 2395990 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 320784 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7448000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 311 | 806000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1168 | 20993952.46
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 884 | 21963636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 25 | 336960 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 43 | 509952 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 151 | 2955168 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 650160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 50 | 139171 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1225 | 29236370 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2378 | 55791417
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 304 | 6501818 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 394272 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2429000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 29678545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5340000 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 440400 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 290 | 6938000 | Machine Problem
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4012 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2157 | 51726047.45
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 368392 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 17 | 45822 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 176201 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 140 | 3663273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 10200 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 140 | 3626972 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9352218 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 255130 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 81 | 523584 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 464352 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 318816 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 33960 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 741.54 | 35464728 | U-2 Under Maintenance
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 380256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 754251 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3739.512 | 1666.54 | 55438155
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 44 | 843055 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 91 | 648720 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 44883.84 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 570895 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 187144 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1088640 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 205 | 3383337.84
Eastern Grid Total |  |  |  |  | 17418.042 | 8060.5 | 159252802.88
Western Grid Total |  |  |  |  | 12072.195 | 6406.54 | 166338957.29
National Grid Total |  |  |  |  | 29490.237 | 14467.04 | 325591760.17
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 22-04-2026
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9626.09 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4369 | MW
i) Dhaka area |  |  | 5567.29 |  | MW | i) Khulna area |  |  |  | 1597 | MW
ii) Chattogram area |  |  | 1337.8 |  | MW | ii) Barishal area |  |  |  | 408.2 | MW
iii) Cumilla area |  |  | 1355 |  | MW | iii) Rajshahi area |  |  |  | 1527.8 | MW
iv) Mymensingh area |  |  | 890 |  | MW | iv) Rangpur area |  |  |  | 836 | MW
v) Sylhet area |  |  | 476 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13995.09 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 105 | 23:00 | 133 | Natore | 164 | 23:00
2 | AKSML | 11 | 04:00 | 68 | Hathazari | 81 | 05:00 | 134 | Nawabganj | 77.4 | 22:00
3 | Aftabnagar | 46 | 19:30 | 69 | Hatirjheel | 56 | 15:00 | 135 | Netrakona | 123 | 23:00
4 | Agargaon | 138 | 14:00 | 70 | Ishurdi | 69 | 04:00 | 136 | New | 89.2 | 11:00
5 | Agrabad | 80 | 18:30 | 71 | Jaldhaka | 59 | 23:00 | 137 | Niamatpur | 97 | 19:00
6 | Amnura | 36 | 21:00 | 72 | Jamalpur | 99 | 21:00 | 138 | Noapara | 38 | 22:00
7 | Ashuganj | 89 | 20:00 | 73 | Jashore | 168 | 22:00 | 139 | PHP | 2 | 01:00
8 | BSRM | 195 | 17:00 | 74 | Jhenaidah | 104 | 21:00 | 140 | Pabna | 119 | 22:00
9 | Bagerhat | 75 | 01:00 | 75 | Joydebpur | 176 | 18:30 | 141 | Palashbari | 126 | 22:00
10 | Bajitpur | 72 | 01:00 | 76 | Joypurhat | 85 | 22:00 | 142 | Panchagarh | 39 | 07:00
11 | Bakerganj | 13 | 22:00 | 77 | Juldah | 16 | 10:00 | 143 | Patiya | 8 | 00:00
12 | Bakulia | 87 | 19:30 | 78 | KSRM | 15 | 14:00 | 144 | Patuakhali | 76 | 22:00
13 | Banani | 64 | 13:00 | 79 | Kabirpur | 273 | 18:00 | 145 | Payra | 34 | 22:00
14 | Bangabhaban | 23 | 10:00 | 80 | Kachua | 86 | 21:00 | 146 | Postogola | 59 | 13:00
15 | Barapukuria | 58 | 19:00 | 81 | Kaliganj | 27 | 23:00 | 147 | Pubail | 28 | 22:00
16 | Barguna | 24 | 22:00 | 82 | Kallyanpur | 129 | 18:30 | 148 | Purbachal | 37 | 12:00
17 | Barishal | 114 | 22:00 | 83 | Kalurghat | 38 | 11:00 | 149 | Purbasadipur | 106 | 07:00
18 | Barishal-230 | 116 | 22:00 | 84 | Kamrangirchar | 87 | 19:30 | 150 | Rahanpur | 37 | 07:00
19 | Baroaulia | 69 | 00:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 27 | 16:00
20 | Baroirhat | 45 | 18:30 | 86 | Kasba | 31 | 23:00 | 152 | Rajbari | 71 | 22:00
21 | Bashundhara | 225 | 15:00 | 87 | Kazla | 121 | 12:00 | 153 | Rajendrapur | 122 | 10:00
22 | BashundharaCement | 12 | 00:00 | 88 | Keranigonj | 93 | 22:00 | 154 | Rajshahi | 114 | 23:00
23 | Beanibazar | 50 | 19:30 | 89 | Khagrachori | 28 | 12:00 | 155 | Rajshahi-230 | 105 | 22:00
24 | Benapole | 63 | 01:00 | 90 | Khulna | 59 | 00:00 | 156 | Ramganj | 102 | 23:00
25 | Bhaluka | 124 | 07:00 | 91 | Khulshi | 187 | 20:00 | 157 | Rampur | 46 | 00:00
26 | Bhandaria | 60 | 22:00 | 92 | Kishoreganj | 110 | 20:00 | 158 | Rangamati | 13 | 03:00
27 | Bhangura | 36 | 03:00 | 93 | Kodda | 262 | 19:00 | 159 | Rangpur | 157 | 22:00
28 | Bheramara(GK) | 62 | 23:00 | 94 | Kulaura | 44 | 18:30 | 160 | Ruppur | 4.6 | 16:00
29 | Bhulta | 189 | 20:00 | 95 | Kurigram | 50 | 19:00 | 161 | SSM | 7 | 00:00
30 | Bog-Sherpur | 88 | 07:00 | 96 | Kushtia | 160 | 22:00 | 162 | Saidpur | 94 | 20:00
31 | Bogura | 218 | 22:00 | 97 | Laksam | 22 | 03:00 | 163 | Santhia | 30 | 02:00
32 | Borhanuddin | 91 | 22:00 | 98 | Lakshmipur | 39 | 06:00 | 164 | Satkhira | 118 | 21:00
33 | Brahmanbaria | 155 | 22:00 | 99 | Lalbag | 70 | 12:00 | 165 | Satmasjid | 121 | 13:00
34 | Cantonment | 154 | 12:00 | 100 | Lalmonirhat | 40 | 08:00 | 166 | Savar | 244 | 21:00
35 | Chandina | 39 | 06:00 | 101 | MI_Cement | 18.6 | 14:00 | 167 | SevenRings | 21.21 | 17:00
36 | Chandpur | 71 | 22:00 | 102 | Madanganj | 45 | 09:00 | 168 | ShahCement | 42 | 18:00
37 | Chandraghona | 33 | 22:00 | 103 | Madaripur | 102 | 01:00 | 169 | Shahjadpur | 94 | 23:00
38 | Chapai | 89 | 22:00 | 104 | Madartek | 94 | 19:00 | 170 | Shahjibazar | 107 | 22:00
39 | Charsaidpur | 43 | 18:30 | 105 | Madunaghat | 49 | 15:00 | 171 | Shahmirpur | 56.5 | 05:00
40 | Chauddagram | 86 | 22:00 | 106 | Magura | 57 | 21:00 | 172 | Shariatpur | 69 | 01:00
41 | Chhatak | 21 | 22:00 | 107 | Mahasthangarh | 88 | 06:00 | 173 | Sherpur | 102 | 19:30
42 | Chowmuhani | 138 | 22:00 | 108 | Maijdee | 37 | 19:30 | 174 | Shikalbaha | 24 | 02:00
43 | Chuadanga | 108 | 19:30 | 109 | Manikganj | 145 | 22:00 | 175 | Shitalakhya | 94.7 | 18:00
44 | Coxsbazar | 117 | 20:00 | 110 | Maniknagar | 81 | 15:00 | 176 | Sholosohor | 48 | 09:00
45 | Cumilla(N) | 126 | 20:00 | 111 | Matarbari | 45 | 20:00 | 177 | Shyampur | 190 | 12:00
46 | Cumilla(S) | 213 | 16:00 | 112 | Matuail | 82 | 15:00 | 178 | Siddhirganj | 134 | 15:00
47 | Daganbhuiyan | 35 | 23:00 | 113 | Metrorail_Motijheel | 25 | 18:00 | 179 | Sirajganj | 150 | 21:00
48 | Daudkandi | 162 | 22:00 | 114 | Metrorail_Uttara | 8 | 20:00 | 180 | Sonargaon | 151 | 10:00
49 | DhakaUniversity | 100 | 13:00 | 115 | Millgate | 111 | 12:00 | 181 | Sreemongol | 64 | 02:00
50 | Dhamrai | 122 | 21:00 | 116 | Mirpur | 164 | 15:00 | 182 | Sreepur | 113 | 20:00
51 | Dhanmondi | 155.5 | 13:00 | 117 | Mirsorai | 61 | 11:00 | 183 | Srinagar | 61.8 | 22:00
52 | Dohazari | 85 | 00:00 | 118 | Mirzapur | 38 | 02:00 | 184 | Sunamganj | 39 | 21:00
53 | Faridpur | 199 | 21:00 | 119 | Mithapukur | 56 | 21:00 | 185 | Sylhet | 56 | 22:00
54 | Fatullah | 94 | 15:00 | 120 | Modern | N/A | N/A | 186 | Sylhet-132 | 100 | 21:00
55 | Fenchuganj | 30 | 19:30 | 121 | Mogbazar | 101.6 | 15:00 | 187 | TK | 20 | 11:00
56 | Feni | 95 | 21:00 | 122 | Mongla | 42 | 18:30 | 188 | Tangail | 162 | 20:00
57 | GPH | 9 | 23:00 | 123 | Motijheel | 56 | 13:00 | 189 | Taraganj | 21 | 06:00
58 | Ghatail | 52 | 00:00 | 124 | Muktagacha | 32 | 19:30 | 190 | Tasnim | 16 | 16:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 141 | 18:30 | 191 | Thakurgaon | 101 | 20:00
60 | Ghorashal-230 | 96 | 10:00 | 126 | Muradnagar | 57 | 22:00 | 192 | Tongi | 165 | 11:00
61 | Goalpara | 36 | 04:00 | 127 | Mymensingh | 199 | 20:00 | 193 | Ullahpara | 51 | 22:00
62 | Gollamari | 98 | 23:00 | 128 | Nabinagar | 11 | 19:00 | 194 | Ullon | 64 | 19:00
63 | Gopalganj | 88 | 19:30 | 129 | Naogaon | 145 | 23:00 | 195 | Uttara | 106 | 16:00
64 | Gulshan | 154 | 15:00 | 130 | Narail | 52 | 23:00 | 196 | UttaraNew | 61 | 19:00
65 | Halishahar | 97.5 | 11:00 | 131 | Narinda | 81 | 13:00 | 197 | Zigatola | 98 | 16:00
66 | HaripurSBU | 105 | 19:00 | 132 | Narshingdi | 161 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 22-04-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13431.38 | 2168 |  | 15697.38
1:00 | 12669.11 | 2370 |  | 15146.11
2:00 | 12367.23 | 2468 |  | 14946.23
3:00 | 12316.95 | 2420 |  | 14845.95
4:00 | 12326.91 | 2267 |  | 14695.91
5:00 | 12346.79 | 2210 |  | 14655.79
6:00 | 12338.66 | 2163 |  | 14598.66
7:00 | 12406.52 | 2098 |  | 14598.52
8:00 | 12375.08 | 2070 |  | 14538.23
9:00 | 12372.94 | 2178 |  | 14648.94
10:00 | 12769.7 | 2211 |  | 15079.7
11:00 | 13116.11 | 2233 |  | 15449.11
12:00 | 13043.75 | 2493 |  | 15648.75
13:00 | 13112.98 | 2467 |  | 15690.98
14:00 | 13127.56 | 2432 |  | 15668.56
15:00 | 13110.88 | 2495 |  | 15717.88
16:00 | 13059.1 | 2496 |  | 15667.1
17:00 | 13130.28 | 2314 |  | 15548.28
18:00 | 13383.07 | 2168 |  | 15649.07
19:00 | 14179.69 | 2264 |  | 16545.69
19:30 | 14192.01 | 2205 |  | 16496.01
20:00 | 14467.04 | 2086 |  | 16647.04
21:00 | 14217.36 | 1895 |  | 16197.36
22:00 | 14126.35 | 1218 |  | 15399.35
23:00 | 13963.33 | 1469 |  | 15498.33
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 22-04-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6584.5 | 6846.88 | 13431.38 | DAILY GENERATION CURVE
00:30 | 6471.5 | 6578.745 | 13050.245
01:00 | 6358.5 | 6310.61 | 12669.11 | 22-04-2026
01:30 | 6378 | 6140.17 | 12518.17
02:00 | 6397.5 | 5969.73 | 12367.23
02:30 | 6389 | 5953.09 | 12342.09
03:00 | 6380.5 | 5936.45 | 12316.95
03:30 | 6378.75 | 5943.18 | 12321.93
04:00 | 6377 | 5949.91 | 12326.91
04:30 | 6396.5 | 5940.35 | 12336.85
05:00 | 6416 | 5930.79 | 12346.79
05:30 | 6399.55 | 5943.175 | 12342.725
06:00 | 6383.1 | 5955.56 | 12338.66
06:30 | 6388.97 | 5983.62 | 12372.59
07:00 | 6394.84 | 6011.68 | 12406.52
07:30 | 6372.99 | 6017.81 | 12390.8
08:00 | 6351.14 | 6023.94 | 12375.08
08:30 | 6354.25 | 6019.76 | 12374.01
09:00 | 6357.36 | 6015.58 | 12372.94
09:30 | 6453.09 | 6118.23 | 12571.32
10:00 | 6548.82 | 6220.88 | 12769.7
10:30 | 6662.715 | 6280.19 | 12942.905
11:00 | 6776.61 | 6339.5 | 13116.11
11:30 | 6784.24 | 6295.69 | 13079.93
12:00 | 6791.87 | 6251.88 | 13043.75
12:30 | 6776.09 | 6302.275 | 13078.365
13:00 | 6760.31 | 6352.67 | 13112.98
13:30 | 6757.785 | 6362.485 | 13120.27
14:00 | 6755.26 | 6372.3 | 13127.56
14:30 | 6771.98 | 6347.24 | 13119.22
15:00 | 6788.7 | 6322.18 | 13110.88
15:30 | 6819.44 | 6265.55 | 13084.99
16:00 | 6850.18 | 6208.92 | 13059.1
16:30 | 6906.615 | 6188.075 | 13094.69
17:00 | 6963.05 | 6167.23 | 13130.28
17:30 | 7068.89 | 6187.785 | 13256.675
18:00 | 7174.73 | 6208.34 | 13383.07
18:30 | 7518.615 | 6262.765 | 13781.38
19:00 | 7862.5 | 6317.19 | 14179.69
19:30 | 7937.5 | 6254.51 | 14192.01
20:00 | 8060.5 | 6406.54 | 14467.04
20:30 | 7995.5 | 6346.7 | 14342.2 |  | Executive Engineer
21:00 | 7930.5 | 6286.86 | 14217.36 |  | Network Operation Division
21:30 | 7873 | 6298.855 | 14171.855
22:00 | 7815.5 | 6310.85 | 14126.35
22:30 | 7716.5 | 6328.34 | 14044.84
23:00 | 7617.5 | 6345.83 | 13963.33

## En-Curve
QF-LDC-12
Date | 22-04-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3450 | 1462.5 | 918 | 0 | 156 | 1497.88 | 30 | 4550 | 0 | 611 | 742 | 0 | 0 | 14 | 2168 | DAILY ENERGY CURVE
00:30 | 3455.5 | 1466 | 918 | 0 | 157 | 1303.745 | 30 | 4565 | 0 | 536.5 | 605.5 | 0 | 0 | 13 | 2269 | 22-04-2026
01:00 | 3461 | 1469.5 | 918 | 0 | 158 | 1109.61 | 30 | 4580 | 0 | 462 | 469 | 0 | 0 | 12 | 2370
01:30 | 3463 | 1483 | 918.5 | 0 | 159 | 937.17 | 30 | 4583.5 | 0 | 461.5 | 472.5 | 0 | 0 | 10 | 2419 | Energy Generated | 325.5918 |  | MKWHr
02:00 | 3465 | 1496.5 | 919 | 0 | 160 | 764.73 | 30 | 4587 | 0 | 461 | 476 | 0 | 0 | 8 | 2468 | Energy not Served | 52.653 |  | MKWHr
02:30 | 3469.5 | 1486 | 913.5 | 0 | 160 | 762.59 | 30 | 4593 | 0 | 461 | 456 | 0 | 0 | 10.5 | 2444 | Total Energy Requirement | 378.2448 |  | MKWHr
03:00 | 3474 | 1475.5 | 908 | 0 | 160 | 760.45 | 30 | 4599 | 0 | 461 | 436 | 0 | 0 | 13 | 2420
03:30 | 3479 | 1483.25 | 908 | 0 | 160 | 760.68 | 30 | 4602.5 | 0 | 461 | 424 | 0 | 0 | 13.5 | 2343.5
04:00 | 3484 | 1491 | 908 | 0 | 160 | 760.91 | 30 | 4606 | 0 | 461 | 412 | 0 | 0 | 14 | 2267
04:30 | 3491.5 | 1502 | 908 | 0 | 160 | 761.35 | 30 | 4607.5 | 0 | 449 | 414 | 0 | 0 | 13.5 | 2238.5
05:00 | 3499 | 1513 | 908 | 0 | 160 | 761.79 | 30 | 4609 | 0 | 437 | 416 | 0 | 0 | 13 | 2210
05:30 | 3512.5 | 1520 | 908 | 0 | 159 | 762.76 | 30 | 4608 | 6.465 | 412.5 | 414 | 0 | 0 | 9.5 | 2186.5
06:00 | 3526 | 1527 | 908 | 0 | 158 | 763.73 | 30 | 4607 | 12.93 | 388 | 412 | 0 | 0 | 6 | 2163
06:30 | 3518 | 1516 | 908 | 0 | 157 | 759.58 | 30 | 4607.5 | 58.51 | 388.5 | 425.5 | 0 | 0 | 4 | 2130.5
07:00 | 3510 | 1505 | 908 | 0 | 156 | 755.43 | 30 | 4608 | 104.09 | 389 | 439 | 0 | 0 | 2 | 2098
07:30 | 3476 | 1487 | 915.5 | 0 | 158 | 752.045 | 30 | 4602.5 | 159.255 | 360.5 | 449 | 0 | 0 | 1 | 2084
08:00 | 3442 | 1469 | 923 | 0 | 160 | 748.66 | 30 | 4597 | 214.42 | 332 | 459 | 0 | 0 | 0 | 2070
08:30 | 3430.5 | 1418.25 | 922.5 | 0 | 167 | 750.38 | 35 | 4573 | 256.88 | 331.5 | 486 | 0 | 0 | 3 | 2124
09:00 | 3419 | 1367.5 | 922 | 0 | 174 | 752.1 | 40 | 4549 | 299.34 | 331 | 513 | 0 | 0 | 6 | 2178
09:30 | 3445.5 | 1435 | 922.5 | 0 | 177 | 756.6 | 40 | 4549.5 | 393.72 | 331 | 510.5 | 0 | 0 | 10 | 2194.5
10:00 | 3472 | 1502.5 | 923 | 0 | 180 | 761.1 | 40 | 4550 | 488.1 | 331 | 508 | 0 | 0 | 14 | 2211
10:30 | 3476.5 | 1558.75 | 922.5 | 0 | 184 | 756.1 | 40 | 4554.5 | 565.055 | 330.5 | 539 | 0 | 0 | 16 | 2222
11:00 | 3481 | 1615 | 922 | 0 | 188 | 751.1 | 40 | 4559 | 642.01 | 330 | 570 | 0 | 0 | 18 | 2233
11:30 | 3489 | 1639 | 922.5 | 0 | 190 | 758.325 | 40 | 4557.5 | 579.605 | 333 | 552 | 0 | 0 | 19 | 2363
12:00 | 3497 | 1663 | 923 | 0 | 192 | 765.55 | 40 | 4556 | 517.2 | 336 | 534 | 0 | 0 | 20 | 2493
12:30 | 3504 | 1579.5 | 922.5 | 0 | 194 | 769.71 | 40 | 4546.5 | 604.905 | 348.5 | 547.25 | 0 | 0 | 21.5 | 2480
13:00 | 3511 | 1496 | 922 | 0 | 196 | 773.87 | 40 | 4537 | 692.61 | 361 | 560.5 | 0 | 0 | 23 | 2467
13:30 | 3468.5 | 1541 | 922 | 0 | 203 | 770.435 | 40 | 4561.5 | 646.335 | 377.5 | 562 | 0 | 0 | 28 | 2449.5
14:00 | 3426 | 1586 | 922 | 0 | 210 | 767 | 40 | 4586 | 600.06 | 394 | 563.5 | 0 | 0 | 33 | 2432
14:30 | 3412 | 1616.5 | 922 | 0 | 210 | 763.015 | 40 | 4620 | 529.205 | 392 | 581 | 0 | 0 | 33.5 | 2463.5
15:00 | 3398 | 1647 | 922 | 0 | 210 | 759.03 | 40 | 4654 | 458.35 | 390 | 598.5 | 0 | 0 | 34 | 2495
15:30 | 3401 | 1601.5 | 922.5 | 0 | 211 | 752.685 | 40 | 4629.5 | 386.055 | 394.5 | 714.25 | 0 | 0 | 32 | 2495.5
16:00 | 3404 | 1556 | 923 | 0 | 212 | 746.34 | 40 | 4605 | 313.76 | 399 | 830 | 0 | 0 | 30 | 2496
16:30 | 3404 | 1584 | 923 | 0 | 196 | 743.05 | 40 | 4604.5 | 220.64 | 433 | 922 | 0 | 0 | 24.5 | 2405
17:00 | 3404 | 1612 | 923 | 0 | 180 | 739.76 | 40 | 4604 | 127.52 | 467 | 1014 | 0 | 0 | 19 | 2314
17:30 | 3376.5 | 1558.5 | 922.5 | 0 | 188 | 744.27 | 40 | 4593 | 72.155 | 583.5 | 1164.75 | 0 | 0 | 13.5 | 2241
18:00 | 3349 | 1505 | 922 | 0 | 196 | 748.78 | 40 | 4582 | 16.79 | 700 | 1315.5 | 0 | 0 | 8 | 2168
18:30 | 3497 | 1575 | 903.5 | 0 | 191 | 747.485 | 38 | 4596 | 8.395 | 743 | 1474.5 | 0 | 0 | 7.5 | 2216
19:00 | 3645 | 1645 | 885 | 0 | 186 | 746.19 | 36 | 4610 | 0 | 786 | 1633.5 | 0 | 0 | 7 | 2264
19:30 | 3538 | 1569 | 834 | 0 | 184 | 737.51 | 36 | 4677 | 0 | 798 | 1782.5 | 30 | 0 | 6 | 2205
20:00 | 3668 | 1657 | 884 | 0 | 164 | 741.54 | 37 | 4675 | 0 | 798 | 1787.5 | 50 | 0 | 5 | 2086
20:30 | 3620 | 1617.5 | 835 | 0 | 168 | 740.2 | 38 | 4671 | 0 | 792.5 | 1781 | 75.5 | 0 | 3.5 | 1990.5
21:00 | 3572 | 1578 | 786 | 0 | 172 | 738.86 | 39 | 4667 | 0 | 787 | 1774.5 | 101 | 0 | 2 | 1895
21:30 | 3641.5 | 1570.5 | 835 | 0 | 177 | 740.855 | 39.5 | 4647 | 0 | 739.5 | 1729.5 | 50.5 | 0 | 1 | 1556.5
22:00 | 3711 | 1563 | 884 | 0 | 182 | 742.85 | 40 | 4627 | 0 | 692 | 1684.5 | 0 | 0 | 0 | 1218
22:30 | 3720.5 | 1615 | 884 | 0 | 185 | 756.34 | 40 | 4605.5 | 0 | 683 | 1554 | 0 | 0 | 1.5 | 1343.5
23:00 | 3730 | 1667 | 884 | 0 | 188 | 769.83 | 40 | 4584 | 0 | 674 | 1423.5 | 0 | 0 | 3 | 1469
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 22-04-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 02:00 | 367 | 15:00 | Madunaghat | 395 | 02:00 | 389 | 11:00
Amtali | 408 | 01:00 | 405 | 11:00 | Meghnaghat | 384 | 02:00 | 371 | 15:00
Ashuganj | 406 | 7:00 | 387 | 12:00 | Payra | 410 | 02:00 | 407 | 12:00
Bhulta | 398 | 05:00 | 377 | 15:00 | Rahanpur | 409 | 15:00 | 398 | 23:00
Bibiana | 403 | 23:00 | 393 | 14:00 | Rampal | 401 | 02:00 | 392 | 23:00
BIPTC | 398 | 06:00 | 387 | 15:00
Bogura | 403 | 09:00 | 388 | 23:00
Gopalganj | 395 | 02:00 | 386 | 15:00
Kaliakoir | 379 | 03:00 | 362 | 15:00
Korerhat | 399 | 19:00 | 387 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 228 | 02:00 | 216 | 15:00 | Jhenaidah | 230 | 02:00 | 217 | 22:00
AKSML | 234 | 18:30 | 225.6 | 15:00 | Kachua | 227 | 23:00 | 220 | 11:00
Aminbazar | 229 | 06:00 | 217 | 12:00 | Kaliakoir | 231 | 02:00 | 219 | 15:00
Ashuganj | 231 | 19:00 | 221 | 12:00 | Keranigonj | 226 | 02:00 | 214 | 15:00
Ashuganj-400 | 231 | 19:00 | 221 | 12:00 | Khulna(S) | 230 | 02:00 | 220 | 22:00
Baghabari | 233 | 01:00 | 227 | 21:00 | Korerhat | 228 | 19:30 | 220 | 12:00
Barapukuria | 224 | 15:00 | 210 | 23:00 | Madunaghat | 233 | 18:00 | 227 | 15:00
Barapukuria-230 | 224 | 15:00 | 210 | 23:00 | Madunaghat-400 | 233 | 19:00 | 228 | 13:00
Barishal | 226 | 02:00 | 220 | 22:00 | Maniknagar | 224 | 02:00 | 210 | 15:00
Bheramara | 232 | 02:00 | 222 | 22:00 | Meghnaghat | 232 | 04:00 | 220 | 11:00
Bhulta | 225 | 02:00 | 212 | 15:00 | Meghnaghat-400 | 226 | 02:00 | 216 | 15:00
Bibiana | 235 | 02:00 | 227 | 14:00 | Mirsorai | 235 | 19:30 | 225 | 11:00
BIPTC | 235 | 02:00 | 222 | 22:00 | Naogaon | 223 | 15:00 | 202 | 23:00
Bogura | 233 | 01:00 | 225 | 23:00 | Purbasadipur | 226 | 09:00 | 209 | 23:00
Bogura-400 | 233 | 09:00 | 224 | 23:00 | Rajshahi | 230 | 09:00 | 218 | 22:00
Borhanuddin | 230 | 02:00 | 227 | 15:00 | Rampal | 229 | 02:00 | 221 | 23:00
BSRM | 228 | 19:00 | 220 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 224 | 02:00 | 222 | 00:00 | Rampura | 224 | 03:00 | 209 | 15:00
Cumilla(N) | 225 | 02:00 | 218 | 15:00 | Shikalbaha | 231 | 17:00 | 227 | 06:00
Faridpur | 222 | 02:00 | 214 | 22:00 | Shyampur | 225 | 02:00 | 214 | 15:00
Fenchuganj | 238 | 19:00 | 233 | 15:00 | Siddhirganj | 225 | 05:00 | 214 | 11:00
Feni | 227 | 19:00 | 220 | 12:00 | Sirajgonj | 239 | 01:00 | 235 | 00:00
Ghorashal | 230 | 01:00 | 220 | 09:00 | Sreepur | 228 | 08:00 | 221 | 15:00
Ghorashal-230 | 225 | 03:00 | 211 | 15:00 | Tongi | 225 | 04:00 | 210 | 15:00
Gopalganj | 222 | 02:00 | 216 | 22:00
GPH | 232 | 19:00 | 225 | 11:00
Haripur | 225 | 02:00 | 213 | 15:00
Hasnabad | 225 | 07:00 | 215 | 12:00
Hathazari | 232 | 19:00 | 225 | 11:00
Ishurdi | 235 | 10:00 | 225 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 05:00 | 124 | 15:00 | Madunaghat | 136 | 18:00 | 132 | 11:00
Agargaon | 134 | 03:00 | 124 | 15:00 | Magura | 134 | 01:00 | 125 | 22:00
Agrabad | 135 | 19:00 | 130 | 11:00 | Mahasthangarh | 131 | 01:00 | 125 | 06:00
AKS | 132 | 18:00 | 128 | 10:00 | Maijdee | 126 | 02:00 | 122 | 11:00
Aminbazar | 130 | 06:00 | 122 | 12:00 | Manikganj | 126 | 02:00 | 116 | 12:00
Amnura | 135 | 19:00 | 125 | 23:00 | Maniknagar | 131 | 02:00 | 121 | 13:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 128 | 16:00 | 117 | 08:00
Ashuganj-230 | 140 | 08:00 | 134 | 13:00 | Matuail | 130.5 | 02:00 | 123 | 15:00
Bagerhat | 131 | 02:00 | 120 | 22:00 | Metrorail_Motijheel | 131 | 02:00 | 121 | 13:00
Bajitpur | 136 | 22:00 | 128 | 15:00 | Metrorail_Uttara | 130 | 03:00 | 119 | 16:00
Bakerganj | 132 | 01:00 | 127 | 22:00 | Millgate | 131 | 02:00 | 121 | 15:00
Bakulia | 139 | 23:00 | 131 | 15:00 | Mirpur | 129 | 04:00 | 121 | 15:00
Banani | 137 | 04:00 | 124 | 15:00 | Mirzapur | 133 | 20:00 | 125 | 15:00
Bangabhaban | 132 | 07:00 | 120 | 15:00 | Mithapukur | 132 | 12:00 | 122 | 23:00
Barapukuria | 134 | 15:00 | 123 | 23:00 | MI_Cement | 135 | 04:00 | 124 | 16:00
Barguna | 131 | 02:00 | 125 | 22:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 19:00 | 126 | 22:00 | Mogbazar | 136 | 08:00 | 126 | 15:00
Barishal-230 | 132 | 02:00 | 126 | 22:00 | Mongla | 131 | 02:00 | 121 | 22:00
Baroaulia | 135 | 00:00 | 130 | 11:00 | Motijheel | 132 | 07:00 | 120 | 15:00
Baroirhat | 129 | 03:00 | 126 | 11:00 | Muktagacha | 126 | 20:00 | 117 | 01:00
Bashundhara | 136 | 04:00 | 120 | 15:00 | Munshiganj | 129 | 05:00 | 122 | 10:00
BashundharaCement | 130 | 07:00 | 124 | 10:00 | Muradnagar | 128 | 02:00 | 123 | 10:00
Beanibazar | 134 | 00:00 | 127 | 15:00 | Mymensingh | 130 | 08:00 | 117 | 04:00
Benapole | 132 | 03:00 | 120 | 22:00 | Nabinagar | 133 | 01:00 | 126 | 14:00
Bhaluka | 137 | 22:00 | 130 | 18:30 | Naogaon | 134 | 01:00 | 121 | 23:00
Bhandaria | 129 | 16:00 | 118 | 22:00 | Narail | 136 | 09:00 | 126 | 22:00
Bhangura | 132 | 02:00 | 128 | 22:00 | Narinda | 131 | 02:00 | 121 | 13:00
Bheramara | 135 | 13:00 | 130 | 22:00 | Narshingdi | 135 | 02:00 | 116 | 12:00
Bheramara(GK) | 134 | 02:00 | 129 | 22:00 | Natore | 132 | 09:00 | 125 | 22:00
Bhulta | 123 | 21:00 | 119 | 15:00 | Nawabganj | 136 | 07:00 | 127 | 10:00
Bog-Sherpur | 132 | 01:00 | 126 | 23:00 | Netrakona | 130 | 01:00 | 123 | 18:00
Bogura | 134 | 15:00 | 128 | 22:00 | New | 136 | 02:00 | 121 | 15:00
Bogura-230 | 134 | 01:00 | 129 | 07:00 | Niamatpur | 135 | 15:00 | 125 | 23:00
Brahmanbaria | 135 | 02:00 | 128 | 12:00 | Noapara | 134 | 02:00 | 123 | 22:00
Cantonment | 134 | 03:00 | 124 | 15:00 | Pabna | 133 | 09:00 | 126 | 22:00
Chandina | 130 | 02:00 | 126 | 11:00 | Palashbari | 129 | 09:00 | 118 | 23:00
Chandpur | 131 | 23:00 | 124 | 15:00 | Panchagarh | 137 | 15:00 | 128 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 136 | 19:00 | 132 | 11:00 | Patiya | 136 | 19:00 | 131 | 11:00
Chapai | 133 | 01:00 | 127 | 22:00 | Patuakhali | 131 | 01:00 | 128 | 22:00
Charsaidpur | 130 | 02:00 | 123 | 10:00 | Payra | 134 | 01:00 | 131 | 22:00
Chauddagram | 127 | 08:00 | 124 | 11:00 | PHP | 129 | 18:00 | 125 | 11:00
Chhatak | 134 | 23:00 | 127 | 12:00 | Postogola | 136 | 08:00 | 128 | 05:00
Chowmuhani | 126 | 19:00 | 123 | 10:00 | Pubail | 136 | 19:00 | 126 | 15:00
Chuadanga | 133 | 02:00 | 124 | 22:00 | Purbachal | 136 | 03:00 | 120 | 15:00
Coxsbazar | 125 | 18:30 | 117 | 08:00 | Purbasadipur | 132 | 12:00 | 122 | 07:00
Cumilla(N) | 129 | 02:00 | 125 | 15:00 | Rahanpur | 135 | 15:00 | 129 | 23:00
Cumilla(S) | 129 | 01:00 | 115 | 15:00 | Rahanpur-400 | 136 | 15:00 | 130 | 23:00
Daganbhuiyan | 127 | 19:00 | 123 | 12:00 | Rahim | 131 | 04:00 | 124 | 11:00
Daudkandi | 127 | 05:00 | 122 | 10:00 | Rajbari | 127 | 02:00 | 122 | 22:00
DhakaUniversity | 137 | 03:00 | 125 | 15:00 | Rajendrapur | 139 | 22:00 | 127 | 10:00
Dhamrai | 133 | 04:00 | 127 | 12:00 | Rajshahi | 130 | 09:00 | 123 | 23:00
Dhanmondi | 137 | 03:00 | 124 | 15:00 | Rajshahi-230 | 132 | 09:00 | 125 | 22:00
Dohazari | 133 | 18:30 | 128 | 11:00 | Ramganj | 127 | 18:00 | 121 | 13:00
Faridpur | 129 | 02:00 | 124 | 22:00 | Rampur | 135 | 19:00 | 129 | 11:00
Fatullah | 136 | 04:00 | 121 | 12:00 | Rampura | 136 | 02:00 | 125 | 15:00
Fenchuganj | 136 | 21:00 | 132 | 12:00 | Rangamati | 135 | 19:00 | 130 | 12:00
Feni | 127 | 22:00 | 123 | 11:00 | Rangpur | 133 | 12:00 | 123 | 23:00
Feni-230 | 127 | 02:00 | 124 | 10:00 | Ruppur | 137 | 13:00 | 129 | 22:00
Ghatail | 128 | 20:00 | 118 | 18:30 | Saidpur | 132 | 15:00 | 122 | 23:00
Ghorashal | 137 | 19:00 | 128 | 15:00 | Santhia | 134 | 09:00 | 128 | 22:00
Goalpara | 135 | 02:00 | 126 | 22:00 | Satkhira | 133 | 02:00 | 122 | 22:00
Gollamari | 135 | 02:00 | 127 | 22:00 | Satmasjid | 133 | 02:00 | 124 | 12:00
Gopalganj | 132 | 03:00 | 128 | 22:00 | Savar | 129 | 19:00 | 120 | 15:00
Gopalganj-400 | 132 | 02:00 | 129 | 11:00 | SevenRings | 137 | 19:30 | 129 | 13:00
Gulshan | 137 | 05:00 | 124 | 15:00 | ShahCement | 130 | 02:00 | 123 | 10:00
Halishahar | 136 | 19:00 | 129 | 11:00 | Shahjadpur | 132 | 00:00 | 130 | 22:00
Haripur | 131 | 02:00 | 114 | 15:00 | Shahjibazar | 133 | 00:00 | 130 | 11:00
HaripurSBU | 131 | 03:00 | 125 | 16:00 | Shahmirpur | 136 | 18:30 | 133 | 07:00
Hasnabad | 137 | 04:00 | 128 | 15:00 | Shariatpur | 131 | 03:00 | 127 | 13:00
Hathazari | 136 | 18:00 | 132 | 11:00 | Sherpur | 123 | 20:00 | 108 | 00:00
Hatirjheel | 137 | 04:00 | 125 | 15:00 | Shikalbaha | 126 | 18:30 | 122 | 00:00
Ishurdi | 137 | 13:00 | 131 | 22:00 | Shikalbaha-230 | 137 | 02:00 | 134 | 00:00
Jaldhaka | 131 | 15:00 | 120 | 23:00 | Shitalakhya | 135 | 04:00 | 124 | 16:00
Jamalpur | 127 | 20:00 | 113 | 12:00 | Sholosohor | 135 | 18:30 | 131 | 11:00
Jashore | 133 | 02:00 | 122 | 22:00 | Shyampur | 128 | 19:00 | 120 | 12:00
Jhenaidah | 137 | 09:00 | 121 | 23:00 | Shyampur-230 | 130 | 02:00 | 122 | 13:00
Jhenaidah-230 | 137 | 02:00 | 128 | 23:00 | Siddhirganj | 131 | 02:00 | 124 | 12:00
Joydebpur | 136 | 19:00 | 124 | 15:00 | Sirajganj | 130 | 09:00 | 124 | 07:00
Joypurhat | 130 | 01:00 | 112 | 23:00 | Sonargaon | 130 | 03:00 | 123 | 10:00
Juldah | 137 | 20:00 | 132 | 11:00 | Sreemongol | 133 | 08:00 | 129 | 11:00
Kabirpur | 137 | 19:00 | 118 | 13:00 | Sreepur | 138 | 22:00 | 131 | 10:00
Kachua | 129 | 17:00 | 124 | 15:00 | Srinagar | 136 | 03:00 | 128 | 10:00
Kaliakoir | 137 | 19:00 | 128 | 15:00 | SSM | 140 | 18:00 | 130 | 15:00
Kaliganj | 136 | 09:00 | 126 | 22:00 | Sunamganj | 133 | 00:00 | 126 | 14:00
Kallyanpur | 130 | 05:00 | 121 | 15:00 | Sylhet | 133 | 00:00 | 129 | 15:00
Kalurghat | 136 | 22:00 | 132 | 11:00 | Sylhet-132 | 134 | 00:00 | 130 | 11:00
Kamrangirchar | 137 | 05:00 | 119 | 10:00 | Tangail | 129 | 20:00 | 120 | 18:00
Kaptai | 138 | 19:00 | 135 | 1:00 | Taraganj | 131 | 12:00 | 122 | 23:00
Kasba | 128 | 03:00 | 123 | 10:00 | Tasnim | 139 | 02:00 | 117 | 19:00
Kazla | 131 | 04:00 | 121 | 13:00 | Thakurgaon | 135 | 15:00 | 127 | 07:00
Keranigonj | 137 | 04:00 | 128 | 15:00 | TK | 136 | 18:00 | 132 | 11:00
Khagrachori | 134 | 19:00 | 129 | 12:00 | Tongi | 133 | 04:00 | 123 | 15:00
Khulna | 135 | 02:00 | 126 | 22:00 | Ullahpara | 131 | 01:00 | 126 | 22:00
Khulna(S) | 136 | 02:00 | 128 | 22:00 | Ullon | 137 | 04:00 | 125 | 14:00
Khulshi | 133 | 18:30 | 128 | 10:00 | Uttara | 131 | 03:00 | 120 | 12:00
Kishoreganj | 135 | 22:00 | 128 | 10:00 | UttaraNew | 130 | 03:00 | 119 | 15:00
Kodda | 138 | 19:30 | 123 | 12:00 | Zigatola | 137 | 05:00 | 127 | 13:00
Korerhat | 132 | 19:00 | 128 | 11:00
KSRM | 135 | 19:00 | 130 | 12:00
Kulaura | 136 | 23:00 | 131 | 15:00
Kurigram | 130 | 14:00 | 116 | 22:00
Kushtia | 132 | 03:00 | 124 | 23:00
Laksam | 129 | 19:00 | 124 | 01:00
Lakshmipur | 126 | 18:30 | 122 | 15:00
Lalbag | 136 | 06:00 | 127 | 13:00
Lalmonirhat | 130 | 12:00 | 118 | 18:30
Madanganj | 130 | 07:00 | 123 | 15:00
Madaripur | 130 | 01:00 | 129 | 00:00
Madartek | 136 | 03:00 | 124 | 15:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division