## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 24-04-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-04-2026 | during | 24-04-2026 | during | 24-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 358 | 360 | 412 | 412 | 392 | 392 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 450 | 450 | 226 | 226 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 48 | 48 | 55 | 55 | 15 | 55 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 91 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 318 | 323 | 335 | 335 | 320 | 320 | Machine Problem
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 3 | 54 | 53.97 | 53.97 | 17 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 97 | 144 | 149.36 | 149.36 | 149 | 149 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 0 | 19 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 48 | 52.19 | 52.19 | 16 | 52 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 95 | 300 | 300 | 300 | 48 | 294 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 114 | 149 | 149 | 52 | 149 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 105 | 105 | 105 | 34 | 105 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 162 | 162 | 35 | 35 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 560 | 540 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 142 | 142 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2143 | 2638 | 5947.22 | 5915.22 | 2158 | 2670
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 16 | 25.5 | 25.5 | 8 | 25 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50 | 19 | 50 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 37 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 212 | 217 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 51 | 105 | 105 | 34 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 43 | 68 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 67 | 0 | 68 | 0 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 19 | 30 | 40 | 30 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 7 | 37 | 108 | 108 | 12 | 12 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.87 | 0 | 3.94 | 0 | 3.94 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 15 | 54.36 | 54.36 | 0 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 54 | 110 | 110 | 54 | 54 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 71 | 70 | 116 | 116 | 70 | 70 | Liquid fuel shortage
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 17 | 72 | 163 | 163 | 17 | 163 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 612 | 1224 | 1224 | 1224 | 1224 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 19 | 0 | 2 | 0 | 2 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 935 | 1000 | 935 | 935 | 935 | 935 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2113.87 | 2401 | 3747.8 | 3822.86 | 2745.94 | 3049
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 194 | 177 | 221.25 | 221.25 | 210 | 210 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 351 | 356 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 300 | 320 | 342.01 | 342.01 | 342.01 | 342.01 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 220 | 215 | 393 | 393 | 230 | 230 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 140 | 18 | 150 | 20 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 30 | 30 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 96 | 163 | 163 | 100 | 100 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 58 | 104 | 200 | 200 | 17 | 80 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 204 | 150 | 84 | 76 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 18 | 113 | 113 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 70 | 115 | 115 | 17 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 44 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1612 | 1746 | 2632.44 | 2686.44 | 1628.02 | 1802.02
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-04-2026 | during | 24-04-2026 | during | 24-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 11 | 11 | 157.5 | 157.5 | 20 | 20 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 79 | 67 | 70 | 70 | 70 | 70 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 10 | 10 | 10 | 10 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 41.46 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 159.46 | 116 | 362 | 314 | 165 | 129
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 151 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 100 | 100 | 100 | 100 | 100 | 100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 81 | 81 | 81 | 81 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 17 | 17 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 336 | 324 | 350 | 350 | 350 | 350 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1207 | 1180 | 1282 | 1282 | 1204 | 1204
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 884 | 656 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 29 | 30 | 30 | 28 | 28 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 32 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 201 | 179 | 410 | 410 | 210 | 210 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 95 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 200 | 200 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1217 | 1221 | 1234.2 | 1234.2 | 1194 | 1194 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2597 | 2317 | 3584.2 | 3494.2 | 2587.1 | 2497.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 253 | 304 | 250 | 300 | 250 | 300 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 89 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 114 | 110 | 130 | 130 | 110 | 110 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1244 | 1200 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 35 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 290 | 290 | 307 | 307 | 290 | 290 | Bad quality coal
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.68 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2154.68 | 2230 | 2412 | 2461 | 2148 | 2215
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 54.5 | 0 | 58 | 0 | 58 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 140 | 180 | 214 | 214 | 140 | 140 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 196 | 213 | 220 | 220 | 200 | 200 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 170 | 220 | 220 | 150 | 150 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 30 | 30 | 0 | 25 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 82 | 85 | 85 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 113 | 35 | 113 | 113 | 0 | 50 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 30 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.01 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 762.78 | 758.43 | 748 | 748 | 748 | 748 | U-2 Under maint.
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 47.68 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 103 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2015.97 | 1936.43 | 2497.69 | 2272.99 | 1908.49 | 1878.79
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Tripped
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 92 | 113 | 113 | 35 | 113 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.8 | 0 | 6.8 | 0 | 6.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 0 | 70 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 155 | 0 | 180.56 | 0 | 180.56 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 191.8 | 162 | 459.36 | 242 | 252.36 | 183
System Total |  |  |  |  | 28823.2 | 29270.237 | 14194.78 | 14726.43 | 22924.71 | 22490.71 | 14796.91 | 15627.91
Forecast Scenario (24-04-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13300 |  | 1910 |  | 15300
|  |  |  | 1:00 | 12750 |  | 1996 |  | 14840
|  |  |  | 2:00 | 12600 |  | 1967 |  | 14660
|  |  |  | 3:00 | 12600 |  | 1834 |  | 14520
|  |  |  | 4:00 | 12600 |  | 1662 |  | 14340
|  |  |  | 5:00 | 12750 |  | 1060 |  | 13860
|  |  |  | 6:00 | 12600 |  | 1136 |  | 13790
|  |  |  | 7:00 | 12600 |  | 1041 |  | 13690
|  |  |  | 8:00 | 12750 |  | 1041 |  | 13840
|  |  |  | 9:00 | 12950 |  | 965 |  | 13960
|  |  |  | 10:00 | 13500 |  | 506 |  | 14030
|  |  |  | 11:00 | 13900 |  | 287 |  | 14200
|  |  |  | 12:00 | 14200 |  | 554 |  | 14780
|  |  |  | 13:00 | 14200 |  | 764 |  | 15000
|  |  |  | 14:00 | 13750 |  | 965 |  | 14760
|  |  |  | 15:00 | 13450 |  | 1117 |  | 14620
|  |  |  | 16:00 | 13300 |  | 1070 |  | 14420
|  |  |  | 17:00 | 13200 |  | 1012 |  | 14260
|  |  |  | 18:00 | 13300 |  | 955 |  | 14300
|  |  |  | 18:30 | 13900 |  | 955 |  | 14900
|  |  |  | 19:00 | 14200 |  | 1242 |  | 15500
|  |  |  | 19:30 | 14200 |  | 1394 |  | 15660
|  |  |  | 20:00 | 14500 |  | 1385 |  | 15950
|  |  |  | 21:00 | 14700 |  | 1146 |  | 15900
|  |  |  | 22:00 | 14660 |  | 1280 |  | 16000
|  |  |  | 23:00 | 14000 |  | 1815 |  | 15900
Probable Maximum Temperature: |  |  | 36.00°C
Probable Maximum Demand at Day Peak: |  |  | 14780.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 1146
Probable Maximum Demand at Evening Peak: |  |  | 15950.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14700.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 322.36 MKWHr. |  | 163 | 98 | 124 | 193 | 51 | 227 | 31 | 169 | 91 | 1146
*** This report is generated digitally from Operation Information System (OIS) at 08:18 hrs on 24-04-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 23-04-2026 | [28 empty] | Date: | 23-04-2026 | [28 empty] | Date: | 23-04-2026 | [28 empty] | Date: | 23-04-2026 | [28 empty] | Date: | 23-04-2026 | [17 empty] | Date: | 23-04-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [17 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 17 | 25 | 47 | 130 | 31 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 142 | 21 | 22 | 0 | 500 | 70 | 16 | 11 | 0 | 2 | 68 | 51 | 18 | 0 | 0 | 0 | 40 | 55 | 20 | 935 | 54 | 0 | 19 | 8 | 34 | 218 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 230 | 340 | 300 | 51 | 0 | 209 | 0 | 34 | 98 | 44 | 0 | 20 | 0 | 192 | 0 | 0 | 31 | 295 | 0 | 358 | 42 | 30 | 157 | 0 | 17 | 0 | 81 | 30 | 100 | 0 | 100 | 0 | 58 | 9 | 17 | 0 | 0 | 8 | 7031 | 884 | 164 | 0 | 24 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1198 | 0 | 0 | 0 | 768 | 0 | 0 | 0 | 35 | 35 | 0 | 74 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 110 | 220 | 0 | 254 | 1244 | 17 | 6230 | 13261 | 77.4
01:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 17 | 47 | 32 | 15 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 142 | 21 | 22 | 0 | 500 | 69 | 16 | 12 | 0 | 2 | 0 | 50 | 18 | 0 | 0 | 0 | 40 | 66 | 19 | 935 | 17 | 0 | 19 | 8 | 34 | 220 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 230 | 340 | 320 | 51 | 0 | 205 | 0 | 0 | 98 | 17 | 0 | 20 | 0 | 190 | 0 | 0 | 31 | 300 | 0 | 359 | 42 | 30 | 158 | 0 | 17 | 0 | 81 | 30 | 100 | 0 | 100 | 0 | 9 | 56 | 17 | 0 | 0 | 12 | 6737 | 884 | 175 | 0 | 18 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1212 | 0 | 0 | 0 | 765.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 140 | 0 | 0 | 8 | 140 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 110 | 220 | 0 | 253 | 1244 | 17 | 5999.49 | 12736.49 | 77.9
02:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 17 | 47 | 32 | 15 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 142 | 21 | 22 | 0 | 550 | 70 | 16 | 12 | 0 | 0 | 0 | 50 | 18 | 0 | 0 | 0 | 40 | 60 | 27 | 935 | 17 | 0 | 19 | 8 | 34 | 219 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 230 | 340 | 320 | 51 | 0 | 198 | 0 | 0 | 98 | 17 | 0 | 20 | 0 | 190 | 0 | 0 | 31 | 300 | 0 | 359 | 42 | 30 | 159 | 0 | 17 | 0 | 81 | 30 | 100 | 0 | 100 | 0 | 9 | 56 | 19 | 0 | 0 | 12 | 6795 | 696 | 175 | 0 | 18 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 0 | 0 | 0 | 765.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 140 | 0 | 0 | 9 | 150 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 110 | 220 | 0 | 253 | 1244 | 17 | 5726.2 | 12521.2 | 77.38
03:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 17 | 47 | 32 | 15 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 142 | 22 | 22 | 0 | 555 | 70 | 16 | 12 | 0 | 0 | 0 | 50 | 18 | 0 | 0 | 0 | 40 | 55 | 28 | 935 | 17 | 0 | 19 | 8 | 34 | 219 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 230 | 340 | 345 | 51 | 0 | 187 | 0 | 0 | 97 | 17 | 0 | 20 | 0 | 180 | 0 | 0 | 31 | 305 | 0 | 359 | 42 | 30 | 161 | 0 | 17 | 0 | 81 | 30 | 101 | 0 | 100 | 0 | 9 | 56 | 19 | 0 | 0 | 0 | 6795 | 697 | 175 | 0 | 18 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1216 | 0 | 0 | 0 | 763.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 140 | 0 | 0 | 10 | 160 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 110 | 220 | 0 | 253 | 1244 | 17 | 5802.81 | 12597.81 | 77.37
04:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 17 | 47 | 32 | 15 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 142 | 23 | 22 | 0 | 570 | 70 | 16 | 12 | 0 | 4 | 0 | 50 | 0 | 0 | 0 | 0 | 40 | 54 | 22 | 935 | 17 | 0 | 19 | 8 | 34 | 218 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 230 | 340 | 345 | 51 | 0 | 184 | 0 | 0 | 98 | 17 | 0 | 20 | 0 | 180 | 0 | 0 | 31 | 305 | 0 | 359 | 42 | 30 | 161 | 0 | 17 | 0 | 81 | 30 | 99 | 0 | 100 | 0 | 9 | 56 | 20 | 0 | 0 | 0 | 6786 | 743 | 187 | 0 | 18 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1092 | 0 | 0 | 0 | 753.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 140 | 0 | 0 | 19 | 160 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 110 | 220 | 0 | 254 | 1244 | 17 | 5736.81 | 12522.81 | 77.36
05:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 17 | 47 | 32 | 15 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 142 | 23 | 22 | 0 | 580 | 69 | 16 | 12 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 40 | 54 | 22 | 935 | 17 | 0 | 19 | 8 | 34 | 219 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 230 | 340 | 345 | 51 | 0 | 180 | 0 | 0 | 98 | 17 | 0 | 20 | 0 | 176 | 0 | 0 | 32 | 305 | 0 | 359 | 42 | 30 | 161 | 0 | 17 | 0 | 81 | 30 | 99 | 0 | 100 | 0 | 9 | 58 | 20 | 0 | 0 | 0 | 6776 | 884 | 190 | 0 | 18 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1182 | 0 | 0 | 0 | 752.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 86 | 170 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 110 | 220 | 0 | 254 | 1182 | 17 | 5960.72 | 12736.72 | 77.35
06:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 17 | 47 | 32 | 15 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 1 | 142 | 22 | 22 | 0 | 580 | 70 | 16 | 12 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0.07 | 40 | 55 | 26 | 935 | 17 | 0 | 19 | 0 | 34 | 217 | 0 | 0 | 0 | 612 | 1 | 20 | 0 | 215 | 340 | 305 | 51 | 0 | 180 | 0 | 0 | 97 | 17 | 0 | 20 | 0 | 166 | 0 | 2 | 32 | 300 | 0 | 359 | 42 | 30 | 161 | 1 | 17 | 0 | 81 | 30 | 100 | 0 | 100 | 0 | 9 | 58 | 20 | 0 | 0.7 | 0 | 6708.77 | 884 | 205 | 0 | 18 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 2.63 | 1191 | 0 | 0 | 0 | 756.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.27 | 0 | 0 | 0 | 1.14 | 140 | 0 | 0 | 122 | 170 | 0 | 414 | 0 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.02 | 16 | 290 | 116 | 220 | 0 | 254 | 1030 | 17 | 5885.18 | 12593.95 | 77.34
07:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 17 | 47 | 32 | 15 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 5 | 142 | 22 | 22 | 0 | 530 | 70 | 16 | 12 | 0 | 2 | 0 | 50 | 0 | 0 | 0 | 0.78 | 40 | 55 | 30 | 935 | 17 | 0 | 19 | 2 | 34 | 218 | 0 | 0 | 0 | 612 | 4 | 20 | 0 | 215 | 340 | 300 | 51 | 0 | 190 | 0 | 0 | 98 | 17 | 0 | 20 | 0 | 168 | 0 | 15 | 30 | 300 | 0 | 359 | 42 | 30 | 157 | 1 | 17 | 0 | 81 | 30 | 100 | 0 | 100 | 0 | 9 | 58 | 20 | 0.1 | 2.8 | 0 | 6676.68 | 884 | 205 | 0 | 18 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 18.72 | 1176 | 0 | 0 | 0 | 769.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.41 | 18 | 0 | 0 | 8.9 | 140 | 0 | 0 | 154 | 150 | 0 | 414 | 0 | 0.71 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.3 | 10 | 0.11 | 16 | 290 | 110 | 220 | 0 | 254 | 1000 | 17 | 5919.35 | 12596.03 | 77.33
08:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 17 | 47 | 32 | 15 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 13 | 142 | 22 | 22 | 0 | 480 | 70 | 16 | 12 | 0 | 1 | 0 | 50 | 0 | 0 | 0 | 1.73 | 38 | 55 | 8 | 935 | 17 | 0 | 19 | 8 | 34 | 217 | 0 | 0 | 0 | 612 | 10 | 20 | 0 | 215 | 356 | 300 | 51 | 0 | 201 | 0 | 0 | 98 | 17 | 0 | 20 | 0 | 180 | 0 | 33 | 30 | 305 | 0 | 360 | 42 | 30 | 146 | 2 | 17 | 0 | 81 | 30 | 102 | 0 | 100 | 0 | 9 | 58 | 18 | 0.5 | 12.28 | 0 | 6647.51 | 884 | 206 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 42.93 | 1224 | 0 | 0 | 0 | 762.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.3 | 31 | 0 | 0 | 16.46 | 140 | 0 | 0 | 193 | 150 | 0 | 380 | 0 | 1.81 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 1.6 | 38 | 0.24 | 16 | 290 | 110 | 180 | 0 | 254 | 1050 | 17 | 6053.7 | 12701.21 | 77.32
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 26 | 47 | 32 | 15 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 17 | 326 | 0 | 0 | 12 | 142 | 21 | 22 | 0 | 530 | 69 | 16 | 12 | 0 | 1 | 0 | 50 | 0 | 0 | 0 | 2.04 | 39 | 55 | 2 | 935 | 17 | 0 | 19 | 8 | 34 | 216 | 0 | 0 | 0 | 612 | 16 | 20 | 0 | 215 | 356 | 300 | 51 | 0 | 203 | 0 | 0 | 96 | 17 | 0 | 20 | 0 | 184 | 0 | 49 | 30 | 305 | 0 | 360 | 42 | 30 | 156 | 4 | 17 | 0 | 81 | 30 | 101 | 0 | 100 | 0 | 9 | 58 | 11 | 0.8 | 26.48 | 0 | 6754.32 | 884 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 1212 | 0 | 0 | 0 | 763.43 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 29.87 | 51 | 0 | 0 | 18.28 | 140 | 0 | 0 | 180 | 150 | 0 | 380 | 0 | 1.31 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 2.3 | 68 | 0.28 | 16 | 290 | 110 | 180 | 0 | 254 | 1124 | 17 | 6181.47 | 12935.79 | 77.31
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 0 | 0 | 0 | 34 | 97 | 45 | 32 | 17 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 23 | 142 | 20 | 22 | 0 | 545 | 70 | 16 | 12 | 0 | 6 | 0 | 43 | 0 | 0 | 0 | 3.28 | 39 | 55 | 2 | 935 | 17 | 0 | 19 | 8 | 34 | 214 | 0 | 0 | 0 | 612 | 13 | 20 | 0 | 215 | 356 | 300 | 51 | 0 | 201 | 0 | 16 | 96 | 17 | 0 | 20 | 0 | 184 | 0 | 63 | 30 | 305 | 0 | 334 | 42 | 30 | 159 | 7 | 17 | 0 | 81 | 30 | 99 | 0 | 100 | 2 | 9 | 78 | 11 | 1.1 | 29.52 | 0 | 6985.9 | 885 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 1170 | 0 | 0 | 0 | 761.64 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 48.89 | 82 | 0 | 0 | 28.04 | 140 | 0 | 0 | 180 | 150 | 0 | 414 | 0 | 1.53 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 3.2 | 94 | 0.57 | 16 | 290 | 110 | 220 | 0 | 254 | 1210 | 17 | 6476.87 | 13462.77 | 77.31
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 5 | 34 | 97 | 95 | 48 | 17 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 324 | 94 | 0 | 30 | 142 | 20 | 22 | 0 | 530 | 57 | 16 | 12 | 0 | 11 | 0 | 43 | 0 | 0 | 0 | 2.45 | 40 | 55 | 3 | 935 | 17 | 0 | 19 | 8 | 34 | 215 | 0 | 0 | 0 | 612 | 19 | 20 | 0 | 220 | 356 | 300 | 51 | 0 | 198 | 0 | 17 | 96 | 17 | 7 | 20 | 0 | 194 | 0 | 51 | 30 | 310 | 0 | 336 | 42 | 30 | 156 | 11 | 17 | 0 | 81 | 30 | 100 | 0 | 100 | 17 | 9 | 79 | 11 | 2 | 36.6 | 0 | 7171.05 | 884 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 93 | 1208 | 0 | 0 | 0 | 761.54 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 53.27 | 100 | 0 | 0 | 55.49 | 140 | 0 | 0 | 194 | 150 | 0 | 414 | 0 | 4.8 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 6.2 | 177 | 0.36 | 16 | 290 | 110 | 220 | 0 | 254 | 1240 | 17 | 6777.66 | 13948.71 | 77.3
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 3 | 17 | 34 | 97 | 95 | 48 | 35 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 318 | 91 | 0 | 31 | 142 | 0 | 22 | 0 | 560 | 71 | 16 | 7 | 0 | 19 | 0 | 43 | 0 | 0 | 0 | 3.87 | 40 | 55 | 3 | 935 | 17 | 0 | 19 | 8 | 34 | 212 | 0 | 0 | 0 | 612 | 19 | 20 | 0 | 220 | 351 | 300 | 51 | 0 | 194 | 0 | 17 | 96 | 58 | 8 | 19 | 0 | 204 | 0 | 44 | 30 | 305 | 0 | 336 | 42 | 30 | 155 | 11 | 17 | 0 | 81 | 30 | 100 | 0 | 100 | 17 | 9 | 79 | 11 | 2 | 41.46 | 0 | 7235.33 | 884 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 95 | 1217 | 0 | 0 | 0 | 762.78 | 0 | 0 | 0 | 30 | 113 | 0 | 0 | 0 | 0 | 54.5 | 103 | 0 | 0 | 47.68 | 140 | 0 | 0 | 196 | 150 | 0 | 414 | 0 | 5.01 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 6.8 | 155 | 0.68 | 16 | 290 | 114 | 220 | 0 | 253 | 1244 | 17 | 6959.45 | 14194.78 | 77.3
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 17.5 | 17 | 38 | 95 | 95 | 48 | 35 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 320 | 92 | 0 | 30 | 142 | 20 | 21 | 0 | 530 | 70 | 16 | 7 | 0 | 12 | 0 | 50 | 0 | 0 | 0 | 1.94 | 40 | 55 | 7 | 935 | 17 | 0 | 19 | 8 | 34 | 214 | 0 | 0 | 0 | 612 | 18 | 20 | 0 | 215 | 354 | 300 | 51 | 0 | 195 | 0 | 17 | 94 | 105 | 9 | 19 | 0 | 188 | 0 | 63 | 30 | 305 | 0 | 326 | 42 | 30 | 154 | 11 | 17 | 0 | 81 | 30 | 100 | 0 | 98 | 17 | 2 | 37 | 11 | 1.3 | 46.4 | 0 | 7244.14 | 884 | 195 | 0 | 8 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 93 | 1208 | 0 | 0 | 0 | 760.48 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 0 | 0 | 52.32 | 98 | 0 | 0 | 38.83 | 140 | 0 | 0 | 194 | 150 | 0 | 414 | 0 | 4.94 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 6.3 | 179 | 0.68 | 16 | 290 | 114 | 180 | 0 | 253 | 1244 | 17 | 6937.55 | 14181.69 | 77.29
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 17.5 | 17 | 56 | 30 | 45 | 46 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 317 | 90 | 0 | 25 | 35 | 19 | 21 | 0 | 560 | 69 | 16 | 16 | 0 | 16 | 0 | 50 | 0 | 0 | 0 | 2.31 | 40 | 62 | 3 | 935 | 17 | 0 | 19 | 8 | 34 | 213 | 0 | 0 | 0 | 612 | 16 | 20 | 0 | 215 | 351 | 300 | 51 | 0 | 196 | 0 | 16 | 93 | 84 | 9 | 19 | 0 | 174 | 0 | 46 | 30 | 305 | 0 | 350 | 41 | 30 | 153 | 9 | 17 | 0 | 80 | 30 | 100 | 0 | 100 | 17 | 9 | 74 | 11 | 1.7 | 39.66 | 0 | 7028.17 | 884 | 190 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 1185 | 0 | 0 | 0 | 765.5 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 0 | 0 | 46.85 | 85 | 0 | 0 | 48.58 | 140 | 0 | 0 | 175 | 150 | 0 | 414 | 0 | 4.37 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 5.7 | 100 | 0.29 | 16 | 290 | 114 | 220 | 0 | 254 | 1244 | 17 | 6616.29 | 13644.46 | 77.29
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 17.5 | 17 | 51 | 15 | 45 | 46 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 317 | 89 | 0 | 18 | 35 | 0 | 21 | 0 | 530 | 70 | 16 | 20 | 0 | 15 | 0 | 50 | 0 | 0 | 0 | 2.13 | 40 | 54 | 2 | 935 | 17 | 0 | 19 | 8 | 34 | 212 | 0 | 0 | 0 | 612 | 12 | 20 | 0 | 215 | 351 | 320 | 51 | 0 | 192 | 0 | 17 | 93 | 17 | 8 | 19 | 0 | 168 | 0 | 25 | 29 | 310 | 0 | 350 | 42 | 30 | 152 | 7 | 17 | 0 | 77 | 30 | 100 | 0 | 100 | 17 | 9 | 74 | 10 | 1.2 | 25.33 | 0 | 6864.16 | 885 | 183 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 1120 | 0 | 0 | 0 | 770.81 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 10 | 0 | 35.17 | 70 | 0 | 0 | 31.1 | 140 | 0 | 0 | 180 | 150 | 0 | 414 | 0 | 3.03 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 4.1 | 90 | 0.23 | 16 | 290 | 122 | 220 | 0 | 303 | 1244 | 20 | 6544.44 | 13408.6 | 77.28
16:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 17 | 51 | 21 | 45 | 46 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 0 | 317 | 89 | 0 | 14 | 35 | 15 | 21 | 0 | 545 | 58 | 16 | 24 | 0 | 8 | 0 | 50 | 0 | 0 | 0 | 0 | 40 | 49 | 2 | 935 | 17 | 0 | 19 | 8 | 34 | 212 | 0 | 0 | 0 | 612 | 7 | 20 | 0 | 215 | 347 | 320 | 51 | 0 | 182 | 0 | 17 | 93 | 29 | 9 | 19 | 0 | 174 | 0 | 20 | 28 | 305 | 0 | 363 | 42 | 30 | 150 | 5 | 17 | 0 | 77 | 30 | 100 | 0 | 100 | 17 | 9 | 67 | 11 | 0.4 | 17.87 | 8 | 6828.27 | 885 | 183 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 1186 | 0 | 0 | 0 | 762.22 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 12 | 0 | 23.29 | 43 | 0 | 0 | 25.51 | 140 | 0 | 0 | 195 | 150 | 0 | 414 | 0 | 1.66 | 0 | 0 | 35 | 12 | 0 | 0 | 0 | 0 | 1.2 | 75 | 0.24 | 16 | 290 | 110 | 220 | 0 | 303 | 1244 | 17 | 6546.12 | 13374.39 | 77.28
17:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 17 | 52 | 34 | 45 | 15 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 17 | 317 | 91 | 0 | 6 | 35 | 19 | 21 | 0 | 530 | 69 | 16 | 24 | 0 | 4 | 0 | 52 | 0 | 0 | 0 | 0.5 | 40 | 47 | 2 | 935 | 17 | 0 | 19 | 9 | 36 | 213 | 0 | 0 | 0 | 612 | 2 | 20 | 0 | 215 | 354 | 320 | 51 | 0 | 181 | 0 | 17 | 94 | 47 | 9 | 19 | 0 | 162 | 0 | 11 | 27 | 305 | 0 | 363 | 42 | 30 | 140 | 2 | 17 | 0 | 79 | 30 | 98 | 0 | 100 | 17 | 9 | 67 | 11 | 0.2 | 6.17 | 12 | 6776.87 | 885 | 180 | 0 | 13 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 1219 | 0 | 0 | 0 | 760.86 | 0 | 0 | 0 | 35 | 35 | 0 | 6 | 13 | 0 | 11.77 | 19 | 0 | 0 | 8.28 | 140 | 0 | 0 | 208 | 150 | 0 | 414 | 0 | 0.7 | 0 | 0 | 50 | 4 | 47 | 0 | 0 | 0 | 0.9 | 32 | 0.13 | 16 | 290 | 110 | 220 | 0 | 304 | 1244 | 17 | 6450.64 | 13227.51 | 77.27
18:00 | 0 | 105 | 21 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 17 | 87 | 76 | 112 | 15 | 0 | 72 | 0 | 225 | 0 | 0 | 0 | 35 | 320 | 0 | 0 | 0 | 80 | 19 | 21 | 0 | 450 | 70 | 16 | 31 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0.02 | 38 | 54 | 2 | 935 | 35 | 0 | 24 | 25.5 | 51 | 215 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 215 | 356 | 300 | 51 | 0 | 184 | 0 | 23 | 94 | 101 | 16 | 19 | 0 | 182 | 0 | 1 | 28 | 300 | 0 | 363 | 42 | 30 | 144 | 0 | 17 | 0 | 80 | 30 | 101 | 0 | 100 | 17 | 9 | 67 | 11 | 0.9 | 0.71 | 12 | 7051.13 | 885 | 180 | 0 | 15 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1219 | 0 | 0 | 0 | 748.86 | 0 | 0 | 0 | 35 | 35 | 0 | 82 | 25 | 0 | 0.91 | 3 | 32 | 0 | 1.21 | 160 | 0 | 0 | 210 | 150 | 0 | 300 | 0 | 0.12 | 0 | 0 | 70 | 1 | 62 | 0 | 0 | 0 | 0.2 | 4 | 0.01 | 16 | 290 | 110 | 180 | 0 | 304 | 1210 | 17 | 6367.31 | 13418.44 | 77.27
19:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 30 | 17 | 113 | 127 | 294 | 15 | 25 | 108 | 0 | 225 | 0 | 0 | 0 | 35 | 320 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 530 | 69 | 16 | 33 | 0 | 0 | 50 | 68 | 0 | 0 | 0 | 0 | 37 | 55 | 2 | 1000 | 54 | 0 | 45 | 25.5 | 51 | 217 | 0 | 0 | 0 | 590 | 0 | 100 | 0 | 225 | 356 | 300 | 51 | 0 | 194 | 0 | 53 | 95 | 103 | 17 | 19 | 0 | 146 | 0 | 0 | 28 | 315 | 0 | 323 | 42 | 30 | 149 | 0 | 17 | 0 | 80 | 30 | 101 | 0 | 99 | 17 | 9 | 68 | 10 | 0 | 0 | 12 | 7798.5 | 676 | 180 | 0 | 26 | 30 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 1217 | 0 | 0 | 0 | 760.48 | 0 | 0 | 0 | 35 | 35 | 0 | 82 | 26 | 0 | 0 | 0 | 28 | 0 | 0 | 160 | 0 | 0 | 210 | 150 | 0 | 350 | 0 | 0 | 0 | 0 | 70 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 110 | 220 | 0 | 304 | 1200 | 17 | 6352.48 | 14150.98 | 77.26
19:30 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 35 | 17 | 113 | 133 | 294 | 15 | 35 | 108 | 0 | 225 | 0 | 0 | 0 | 35 | 324 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 530 | 69 | 16 | 37 | 0 | 0 | 67 | 68 | 0 | 0 | 0 | 0 | 37 | 55 | 6 | 1000 | 54 | 0 | 50 | 25.5 | 51 | 217 | 0 | 0 | 0 | 590 | 0 | 150 | 0 | 225 | 357 | 320 | 51 | 0 | 160 | 0 | 68 | 95 | 103 | 18 | 19 | 0 | 160 | 0 | 0 | 28 | 310 | 0 | 323 | 42 | 30 | 150 | 0 | 17 | 0 | 80 | 30 | 101 | 0 | 100 | 17 | 9 | 68 | 10 | 0 | 0 | 12 | 7911.5 | 648 | 180 | 0 | 32 | 50 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 1231 | 0 | 0 | 0 | 752.88 | 0 | 0 | 0 | 35 | 35 | 0 | 82 | 26 | 0 | 0 | 0 | 28 | 0 | 0 | 180 | 0 | 0 | 214 | 170 | 0 | 345 | 0 | 0 | 0 | 0 | 70 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 290 | 110 | 180 | 0 | 303 | 1200 | 17 | 6426.88 | 14338.38 | 0
20:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 54 | 17 | 113 | 143 | 294 | 49 | 35 | 108 | 0 | 225 | 0 | 0 | 0 | 35 | 320 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 495 | 70 | 16 | 36 | 0 | 0 | 67 | 68 | 0 | 0 | 0 | 0 | 37 | 55 | 12 | 1000 | 72 | 0 | 50 | 25.5 | 51 | 217 | 0 | 0 | 0 | 612 | 0 | 150 | 0 | 225 | 356 | 320 | 51 | 0 | 180 | 0 | 69 | 96 | 104 | 18 | 19 | 0 | 150 | 0 | 0 | 28 | 310 | 0 | 324 | 42 | 30 | 144 | 0 | 17 | 0 | 81 | 30 | 100 | 0 | 101 | 17 | 9 | 68 | 10 | 0 | 0 | 12 | 8012.5 | 648 | 180 | 0 | 29 | 35 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 1218 | 0 | 0 | 0 | 756.24 | 0 | 0 | 0 | 35 | 35 | 0 | 82 | 26 | 0 | 0 | 0 | 28 | 0 | 0 | 180 | 0 | 0 | 214 | 170 | 0 | 300 | 0 | 0 | 0 | 0 | 70 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 290 | 110 | 180 | 0 | 304 | 1200 | 17 | 6473.24 | 14485.74 | 77.26
21:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 54 | 17 | 114 | 144 | 300 | 48 | 35 | 108 | 0 | 225 | 0 | 0 | 0 | 35 | 323 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 540 | 70 | 16 | 37 | 0 | 0 | 67 | 68 | 15 | 0 | 0 | 0 | 37 | 54 | 19 | 1000 | 72 | 0 | 50 | 16 | 51 | 217 | 0 | 0 | 0 | 612 | 0 | 140 | 0 | 215 | 356 | 320 | 51 | 0 | 177 | 0 | 70 | 96 | 104 | 18 | 19 | 0 | 150 | 0 | 0 | 30 | 305 | 0 | 324 | 42 | 30 | 151 | 0 | 17 | 0 | 81 | 30 | 100 | 0 | 100 | 17 | 9 | 67 | 11 | 0 | 0 | 12 | 8081 | 656 | 179 | 0 | 29 | 32 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 1221 | 0 | 0 | 0 | 758.43 | 0 | 0 | 0 | 35 | 35 | 0 | 82 | 24 | 0 | 0 | 0 | 25 | 0 | 0 | 180 | 0 | 0 | 213 | 170 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 290 | 110 | 220 | 0 | 304 | 1200 | 17 | 6645.43 | 14726.43 | 77.25
22:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 36 | 17 | 139 | 143 | 300 | 49 | 35 | 108 | 0 | 225 | 0 | 0 | 0 | 35 | 325 | 0 | 0 | 0 | 100 | 20 | 21 | 0 | 530 | 69 | 16 | 37 | 0 | 0 | 67 | 68 | 18 | 0 | 0 | 0 | 39 | 55 | 19 | 1000 | 72 | 0 | 50 | 16 | 51 | 217 | 0 | 0 | 0 | 612 | 0 | 110 | 0 | 215 | 357 | 320 | 51 | 0 | 175 | 0 | 69 | 97 | 104 | 19 | 19 | 0 | 142 | 0 | 0 | 30 | 305 | 0 | 324 | 42 | 30 | 152 | 0 | 17 | 0 | 81 | 30 | 100 | 0 | 100 | 17 | 9 | 58 | 11 | 0 | 0 | 12 | 7993 | 659 | 175 | 0 | 29 | 32 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 1222 | 0 | 0 | 0 | 763.95 | 0 | 0 | 0 | 35 | 35 | 0 | 82 | 24 | 0 | 0 | 0 | 25 | 0 | 0 | 180 | 0 | 0 | 213 | 170 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 290 | 110 | 220 | 0 | 304 | 1196 | 17 | 6667.95 | 14660.95 | 77.25
23:00 | 0 | 88 | 48 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 36 | 17 | 149 | 96 | 300 | 49 | 35 | 108 | 0 | 225 | 0 | 0 | 0 | 35 | 323 | 0 | 0 | 0 | 35 | 20 | 21 | 0 | 540 | 69 | 16 | 37 | 0 | 0 | 52 | 66 | 18 | 0 | 0 | 0 | 40 | 55 | 27 | 935 | 17 | 0 | 50 | 0 | 51 | 217 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 215 | 356 | 320 | 51 | 0 | 176 | 0 | 69 | 98 | 103 | 19 | 19 | 0 | 162 | 0 | 0 | 30 | 305 | 0 | 324 | 42 | 30 | 154 | 0 | 15 | 0 | 81 | 30 | 99 | 0 | 100 | 17 | 9 | 59 | 11 | 0 | 0 | 0 | 7656 | 659 | 168 | 0 | 29 | 30 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 1222 | 0 | 0 | 0 | 757.93 | 0 | 0 | 0 | 35 | 35 | 0 | 82 | 24 | 0 | 0 | 0 | 28 | 0 | 0 | 180 | 0 | 0 | 216 | 170 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 290 | 110 | 220 | 0 | 287 | 1196 | 17 | 6641.93 | 14297.93 | 77.24
Total KWH | 0 | 1233600 | 562560 | 0 | 0 | 0 | 0 | 0 | 8740800 | 0 | 0 | 260280 | 242280 | 1401552 | 1680000 | 2646087 | 743812 | 273428 | 794880 | 0 | 5037000 | 0 | 0 | 0 | 269748 | 7756440 | 690000 | 0 | 215450 | 2750400 | 472200 | 513360 | 0 | 13053181.82 | 1654745 | 388909 | 474240 | 0 | 103200 | 361132 | 1273824 | 138665 | 0 | 0 | 22223 | 945240 | 1353200 | 348000 | 22814545.46 | 623927 | 0 | 632640 | 251802 | 973527 | 5271276 | 0 | 0 | 0 | 14612726 | 134055 | 918327 | 0 | 5386000 | 8755500 | 7624000 | 1236928 | 0 | 4684000 | 0 | 568320 | 2252774 | 1209600 | 172200 | 472520 | 0 | 4157760 | 0 | 443064 | 721424 | 7371000 | 0 | 8697000 | 996000 | 724320 | 3701536.36 | 70144 | 382656 | 0 | 1922880 | 714624 | 2378100 | 0 | 2403280 | 253080 | 234000 | 1454400 | 312960 | 10848 | 264690 | 111360 | 172320230.64 | 19643636 | 4680288 | 0 | 353280 | 443008 | 0 | 0 | 0 | 1307654 | 0 | 0 | 689760 | 28763640 | 0 | 0 | 0 | 17847273 | 0 | 0 | 0 | 408096 | 1171776 | 0 | 513309 | 167777 | 0 | 375064 | 728490 | 264573 | 0 | 336000 | 3872882 | 0 | 0 | 4003509 | 4031548 | 0 | 9641600 | 0 | 31020 | 0 | 0 | 557754 | 152363 | 668016 | 0 | 0 | 0 | 37302.6 | 997920 | 4015 | 780864 | 7004000 | 2991000 | 5294830 | 0 | 6501818 | 28948363.64 | 433200 | 153645629.24 | 325965859.88

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 23-04-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14194.78 | MW | 12:00 Hr. | Energy Generated |  |  | 325.9659 |  | MKWHr.
| Day Peak Demand |  |  | 15903.36 | MW | 12:00 Hr. | Energy Unserverd |  |  | 46.495 |  | MKWHr.
| Evening Peak Generation |  |  | 14726.43 | MW | 21:00 Hr. | Energy Demand |  |  | 372.4609 |  | MKWHr.
| Evening Peak Demand |  |  | 16895.43 | MW | 21:00 Hr. | Maximum Temperature |  |  | 37 |  | °C
| Minimum Generation of the Day |  |  | 12521.2 | MW | 02:00 Hr. | Total Gas Supplied |  |  | 948.75 |  | MMCFD
| Maximum Generation of the Day |  |  | 14726.43 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.4884 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 36.263 | 0 | 12.8586 | 0 | 0 | 0.21545 | 0 | 0 | 49.3371 | Gas | 132.4105 | Gas | 464456716.1406
| Chattogram Zone |  |  | 5.6193 | 37.4273 | 8.1266 | 0 | 0.94524 | 0.15628 | 0 | 0.1032 | 52.3779 | Coal | 108.6451 | Coal | 736250590.695
| Cumilla Zone |  |  | 30.4117 | 0 | 3.5899 | 0 | 0 | 0.44306 | 4.1578 | 0 | 38.6024 | HFO | 32.3896 | HFO | 569278530.12
| Mymensingh Zone |  |  | 0.31296 | 0 | 2.0528 | 0 | 0 | 0.27554 | 0 | 0 | 2.6413 | HSD | 5.3112 | HSD | 38268885.16
| Sylhet Zone |  |  | 29.2914 | 0 | 0 | 0 | 0 | 0.070144 | 0 | 0 | 29.3615 | Hydro | 0.94524 | Hydro | 94524
| Khulna Zone |  |  | 4.6803 | 28.7636 | 0.79629 | 1.3077 | 0 | 0.68976 | 19.6436 | 0 | 55.8813 | Solar | 4.5124 | Solar | 71697062.58
| Barishal Zone |  |  | 8.2858 | 42.4542 | 1.2141 | 0 | 0 | 0.004015 | 0 | 0 | 51.9581 | Import | 41.6487 | Import | 233443957.37
| Rajshahi Zone |  |  | 17.546 | 0 | 2.5255 | 4.0035 | 0 | 1.4706 | 17.8473 | 0 | 43.3929 | Wind | 0.1032 | Wind | 1518072
| Rangpur Zone |  |  | 0 | 0 | 1.2258 | 0 | 0 | 1.1876 | 0 | 0 | 2.4134
| Total |  |  | 132.4105 | 108.6451 | 32.3896 | 5.3112 | 0.94524 | 4.5124 | 41.6487 | 0.1032 | 325.9659
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 464456716.1406 |  | Hydro | 94524
|  |  |  | Coal | 736250590.695 |  | Solar | 71697062.58
|  |  |  | HFO | 569278530.12 |  | Import | 233443957.37
|  |  |  | HSD | 38268885.16 |  | Wind | 1518072
[5 empty] | Total: | 211,50,08,338 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.6436 | Peak Hr Flow | 656.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47686436.36 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.8473 | Peak Hr Flow | 758.43 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2093 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 4.1578 | Peak Hr Flow | 150.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2603 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 41.6487 | Peak Hr Flow | 1564.43 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 220 |  | 6037
|  |  |  | Chattogram |  | 210 |  | 1530
|  |  |  | Cumilla |  | 270 |  | 1606
|  |  |  | Mymensingh |  | 265 |  | 1184
|  |  |  | Sylhet |  | 101 |  | 617
|  |  |  | Khulna |  | 405 |  | 1989
|  |  |  | Barishal |  | 47 |  | 476
|  |  |  | Rajshahi |  | 333 |  | 1863
|  |  |  | Rangpur |  | 225 |  | 997
|  |  |  | Total |  | 2076 |  | 16299
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20 | 1 | Patenga 50MW PP (Baraka) |  |  | 50
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 50
|  |  |  | Total Unavailable Capacity |  |  |  | 370
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:04 | Jashore 132/33kV S/S T-1 HT is restored.
|  | 08:05 | Jashore 132/33kV S/S T-1 LT is restored.
| 08:05 | 08:52 | Tongi 230/132/33kV S/S T-03 LT Scheduled S/D Due to Shutdown taken by Desco
| 08:05 | 08:52 | Tongi 230/132/33kV S/S T-03 HT Scheduled S/D Due to Shutdown taken by Desco
|  | 08:08 | Rampura-Ullon-2 132kV Ckt-1 is restored.
|  | 08:38 | Gollamari 132/33kV S/S Tr-2 HT is restored.
|  | 08:39 | Gollamari 132/33kV S/S Tr-2 LT is restored.
| 08:41 | 16:25 | Chowmuhani 230/132/33kV S/S ATR-02 HT Project Work S/D Due to Fire wall painting
| 08:42 | 16:24 | Chowmuhani 230/132/33kV S/S ATR-02 LT Project Work S/D Due to Fire wall painting
| 08:50 | 18:06 | Savar 132/33kV S/S T-1 LT Scheduled S/D Due to Painting works.
| 08:50 | 18:04 | Savar 132/33kV S/S T-1 HT Scheduled S/D Due to Painting works
| 08:57 | 20:54 | Amtali 400/132kV S/S Amtali - RNPL 400 kV Ckt - 2 Project Work S/D Due to RNPL demand
| 09:02 |  | Feni 230/132kV S/S ATR-2 LT Project Work S/D Due to Painting works on going by project
| 09:02 |  | Feni 230/132kV S/S ATR-2 HT Project Work S/D Due to Painting works on going by project
| 09:43 | 10:54 | Goalpara- Khulna (C) 132kV Ckt-1 Scheduled S/D from Goalpara 132/33kV end Due to RedHot
Remove to Central end and from Khulna (C) end Due to Red Hot maintenance.
| 10:08 |  | Chowmuhani-Feni 132 kV Ckt-1 Scheduled S/D from Chowmuhani 230/132/33kV end Due to For
replacing existing panel and integrating new panel and from Daganbhuiyan 132/33kV end Due
to Replacing Panel Chowmuhuni S/S.
| 12:30 | 18:33 | Chandina 132/33kV S/S TR-2 LT Forced S/D Due to As per written aplication by Md. Sakib
Ahmmed (AE) PDB.
| 13:09 | 17:00 | Chandina-Cumilla(N) 132 kV Ckt-1 Forced S/D from Chandina 132/33kV end Due to Due to
Maintenance work at cumilla north-1 line bay.
| 13:58 | 19:41 | Joypurhat 132/33kV S/S Naogaon Ckt.-2 Scheduled S/D
| 13:58 | 19:38 | Bogura(New)-Naogaon 132 kV Ckt-1 Project Work S/D from Bogura 230/132kV end Due to RTU
commissioning ,
| 15:33 | 17:18 | Kushtia 132/33kV S/S T-3 LT Forced S/D Due to Bus Conductor Change | [7 empty] | 61.0MW load
interrup.
| 15:34 | 17:16 | Kushtia 132/33kV S/S T-3 HT Forced S/D Due to Bus Conductor change | [7 empty] | 61.0MW load
interrup.
|  | 18:33 | Chandina 132/33kV S/S TR-2 LT is restored.
|  | 19:48 | Jamalpur 132/33kV S/S T-4 HT is restored.
|  | 19:48 | Jamalpur 132/33kV S/S T-4 LT is restored.
| 01:47 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
| 03:30 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- gt
| 05:36 | 05:36 | Mirzapur 132/33kV S/S Auxiliary Transformer-01(Q1) Scheduled S/D Due to Existing LILO | [7 empty] | 30.0MW load
|  |  | Line ( Mirzapur-Tangail- kaliakair) | [7 empty] | interrup.
| 05:36 |  | Mirzapur 132/33kV S/S Transformer-01(E05) LT Scheduled S/D Due to Existing LILO Line ( | [7 empty] | 30.0MW load
|  |  | Mirzapur-Tangail- kaliakair) | [7 empty] | interrup.
| 05:42 |  | Ghorasal-Joydeb-B 132kV Ckt-1 Project Work S/D from Joydebpur 132/33kV end. and from | [7 empty] | 60.0MW load
|  |  | Pubail 132/33kV end Due to line maintenance | [7 empty] | interrup. Joydebpur
132/33kV end
| 05:47 |  | Ghorasal-Joydeb-B 132kV Ckt-2 Project Work S/D from Pubail 132/33kV end Due to line
maintenance
| 05:52 |  | Mirzapur 132/33kV S/S Transformer-01(E05) HT Scheduled S/D Due to Existing LILO Line ( | [7 empty] | 30.0MW load
|  |  | Mirzapur-Tangail- kaliakair) | [7 empty] | interrup.
| 05:59 | 05:59 | Mirzapur 132/33kV S/S Auxiliary Transformer-02(Q2) Scheduled S/D Due to Existing LILO | [7 empty] | 25.0MW load
|  |  | Line ( Mirzapur-Tangail- kaliakair) | [7 empty] | interrup.
| 05:59 |  | Mirzapur 132/33kV S/S Transformer-02(E07) LT Scheduled S/D Due to Existing LILO Line ( | [7 empty] | 25.0MW load
|  |  | Mirzapur-Tangail- kaliakair) | [7 empty] | interrup.
| 06:00 |  | Mirzapur 132/33kV S/S Mirzapur-Tangail-ckt-2B(E03) Scheduled S/D Due to Existing LILO | [7 empty] | 55.0MW load
|  |  | Line ( Mirzapur-Tangail- kaliakair) | [7 empty] | interrup.
| 06:00 |  | Minimum Generation: 12320 MW.
| 06:09 |  | Kaliakoir-Tangail 132kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to DS
Maintenance.
| 06:38 |  | Kaliakoir 400/230/132kV S/S 132kV Bus 2 Scheduled S/D Due to Bus DS Maintenance.
| 06:45 |  | Goalpara 132/33kV S/S T1 LT Scheduled S/D Due to Shutdown taken by Wzpdcl for 33kv | [7 empty] | 20.0MW load
|  |  | chandanimohol fedder redhot maintenance | [7 empty] | interrup.
| 06:45 |  | Goalpara 132/33kV S/S T-6 LT Scheduled S/D Due to Shutdown taken by Wzpdcl for 33kv | [7 empty] | 20.0MW load
|  |  | chandanimohol fedder redhot maintenance | [7 empty] | interrup.
| 06:45 |  | Goalpara 132/33kV S/S T-5 LT Scheduled S/D Due to Shutdown taken by Wzpdcl for 33kv | [7 empty] | 20.0MW load
|  |  | chandanimohol fedder redhot maintenance | [7 empty] | interrup.
| 06:48 |  | Goalpara 132/33kV S/S T1 HT Scheduled S/D Due to Shutdown taken by Wzpdcl for 33kv | [7 empty] | 20.0MW load
|  |  | chandanimohol fedder redhot maintenance | [7 empty] | interrup.
| 06:48 |  | Goalpara 132/33kV S/S T-6 HT Scheduled S/D Due to Shutdown taken by Wzpdcl for 33kv | [7 empty] | 20.0MW load
|  |  | chandanimohol fedder redhot maintenance | [7 empty] | interrup.
| 06:48 |  | Goalpara 132/33kV S/S T-5 HT Scheduled S/D Due to Shutdown taken by Wzpdcl for 33kv | [7 empty] | 20.0MW load
|  |  | chandanimohol fedder redhot maintenance | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 23-04-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 360 | 8740800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5037000 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 48 | 743812 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 690000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 323 | 7756440 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 260280 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 144 | 1680000 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 273428 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 269748 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 472200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 513360 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 48 | 562560 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 300 | 2646087 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 114 | 1401552 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1233600 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 794880 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 215450 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 242280 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 540 | 13053181.82 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 2750400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2638 | 49337058.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 16 | 251802 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 134055 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 632640 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 37 | 945240 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5271276 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 973527 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 68 | 1273824 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 67 | 361132 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 19 | 348000 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 37 | 474240 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22223 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 388909 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 15 | 138665 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 54 | 1353200 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 70 | 1654745 | Liquid fuel shortage
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 72 | 623927 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 14612726 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 103200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1000 | 22814545.46 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 2401 | 52377876.46
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 177 | 4684000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 356 | 8755500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 320 | 7624000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 215 | 5386000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1236928 | Machine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 140 | 918327 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 30 | 721424 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 96 | 2252774 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 104 | 1209600 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 150 | 4157760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 472520 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 18 | 172200 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 70 | 568320 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 443064 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1746 | 38602417
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 11 | 312960 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10848 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 67 | 1454400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 234000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 264690 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 111360 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 253080 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 116 | 2641338
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 70144 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 996000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 724320 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3701536.36 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 100 | 2378100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 714624 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1922880 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2403280 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 382656 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7371000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 324 | 8697000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1180 | 29361540.36
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 656 | 19643636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 29 | 353280 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 32 | 443008 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 179 | 4680288 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 689760 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 200 | 1307654 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1221 | 28763640 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2317 | 55881266
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 304 | 6501818 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 89 | 780864 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2991000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 28948363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5294830 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 433200 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 290 | 7004000 | Bad quality coal
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4015 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2230 | 51958090.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 375064 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 167777 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 180 | 3872882 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 213 | 4003509 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 170 | 4031548 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9641600 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 264573 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 82 | 513309 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 1171776 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 408096 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 31020 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 758.43 | 17847273 | U-2 Under Maintenance
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 336000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 728490 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1936.43 | 43392917
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 92 | 668016 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 37302.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 557754 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 152363 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 997920 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 162 | 2413355.6
Eastern Grid Total |  |  |  |  | 17418.042 | 8081 | 172320230.64
Western Grid Total |  |  |  |  | 11852.195 | 6645.43 | 153645629.24
National Grid Total |  |  |  |  | 29270.237 | 14726.43 | 325965859.88
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 23-04-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9908.16 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4314.6 | MW
i) Dhaka area |  |  | 5816.96 |  | MW | i) Khulna area |  |  |  | 1584.4 | MW
ii) Chattogram area |  |  | 1320.2 |  | MW | ii) Barishal area |  |  |  | 428.6 | MW
iii) Cumilla area |  |  | 1336 |  | MW | iii) Rajshahi area |  |  |  | 1529.6 | MW
iv) Mymensingh area |  |  | 919 |  | MW | iv) Rangpur area |  |  |  | 772 | MW
v) Sylhet area |  |  | 516 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14222.76 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 116 | 18:30 | 133 | Natore | 153 | 22:00
2 | AKSML | 13.2 | 04:00 | 68 | Hathazari | 77 | 05:00 | 134 | Nawabganj | 63.4 | 20:00
3 | Aftabnagar | 46 | 18:30 | 69 | Hatirjheel | 55 | 15:00 | 135 | Netrakona | 112 | 21:00
4 | Agargaon | 135 | 13:00 | 70 | Ishurdi | 67 | 07:00 | 136 | New | 100 | 09:00
5 | Agrabad | 74 | 15:00 | 71 | Jaldhaka | 53 | 19:00 | 137 | Niamatpur | 94 | 13:00
6 | Amnura | 38 | 08:00 | 72 | Jamalpur | 104 | 09:00 | 138 | Noapara | 34 | 05:00
7 | Ashuganj | 91 | 19:00 | 73 | Jashore | 164 | 01:00 | 139 | PHP | 3 | 08:00
8 | BSRM | 195 | 22:00 | 74 | Jhenaidah | 99 | 21:00 | 140 | Pabna | 98 | 23:00
9 | Bagerhat | 70 | 20:00 | 75 | Joydebpur | 156 | 20:00 | 141 | Palashbari | 116 | 23:00
10 | Bajitpur | 72 | 11:00 | 76 | Joypurhat | 74 | 08:00 | 142 | Panchagarh | 35 | 00:00
11 | Bakerganj | 10.1 | 13:00 | 77 | Juldah | 18 | 18:30 | 143 | Patiya | 8 | 21:00
12 | Bakulia | 90 | 22:00 | 78 | KSRM | 12 | 02:00 | 144 | Patuakhali | 56.5 | 13:00
13 | Banani | 62 | 13:00 | 79 | Kabirpur | 257 | 21:00 | 145 | Payra | 28 | 06:00
14 | Bangabhaban | 22 | 10:00 | 80 | Kachua | 82 | 12:00 | 146 | Postogola | 59 | 19:00
15 | Barapukuria | 55 | 13:00 | 81 | Kaliganj | 28 | 13:00 | 147 | Pubail | 26 | 18:30
16 | Barguna | 16 | 00:00 | 82 | Kallyanpur | 132 | 00:00 | 148 | Purbachal | 40 | 15:00
17 | Barishal | 117 | 23:00 | 83 | Kalurghat | 42 | 10:00 | 149 | Purbasadipur | 101 | 22:00
18 | Barishal-230 | 104 | 22:00 | 84 | Kamrangirchar | 87 | 19:00 | 150 | Rahanpur | 33 | 00:00
19 | Baroaulia | 66 | 12:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 25 | 23:00
20 | Baroirhat | 48 | 18:30 | 86 | Kasba | 34 | 18:30 | 152 | Rajbari | 68 | 20:00
21 | Bashundhara | 223 | 18:30 | 87 | Kazla | 126 | 13:00 | 153 | Rajendrapur | 137 | 20:00
22 | BashundharaCement | 13 | 16:00 | 88 | Keranigonj | 89 | 18:30 | 154 | Rajshahi | 129 | 23:00
23 | Beanibazar | 54 | 19:30 | 89 | Khagrachori | 28 | 19:00 | 155 | Rajshahi-230 | 97 | 11:00
24 | Benapole | 58 | 21:00 | 90 | Khulna | 92 | 12:00 | 156 | Ramganj | 92 | 18:30
25 | Bhaluka | 116 | 18:30 | 91 | Khulshi | 183 | 22:00 | 157 | Rampur | 44 | 23:00
26 | Bhandaria | 46 | 13:00 | 92 | Kishoreganj | 101 | 18:30 | 158 | Rangamati | 14 | 12:00
27 | Bhangura | 38 | 23:00 | 93 | Kodda | 313 | 21:00 | 159 | Rangpur | 124 | 21:00
28 | Bheramara(GK) | 55 | 05:00 | 94 | Kulaura | 42 | 19:00 | 160 | Ruppur | 4.8 | 15:00
29 | Bhulta | 203 | 13:00 | 95 | Kurigram | 46 | 11:00 | 161 | SSM | 11 | 00:00
30 | Bog-Sherpur | 80 | 22:00 | 96 | Kushtia | 140 | 19:00 | 162 | Saidpur | 111 | 12:00
31 | Bogura | 193 | 23:00 | 97 | Laksam | 23 | 02:00 | 163 | Santhia | 32 | 20:00
32 | Borhanuddin | 77 | 13:00 | 98 | Lakshmipur | 33 | 22:00 | 164 | Satkhira | 116 | 13:00
33 | Brahmanbaria | 121 | 21:00 | 99 | Lalbag | 75 | 13:00 | 165 | Satmasjid | 121 | 19:00
34 | Cantonment | 141 | 13:00 | 100 | Lalmonirhat | 42 | 07:00 | 166 | Savar | 238 | 20:00
35 | Chandina | 44 | 20:00 | 101 | MI_Cement | 17.8 | 10:00 | 167 | SevenRings | 21.05 | 16:00
36 | Chandpur | 68 | 21:00 | 102 | Madanganj | 47 | 20:00 | 168 | ShahCement | 46 | 17:00
37 | Chandraghona | 35 | 05:00 | 103 | Madaripur | 94 | 22:00 | 169 | Shahjadpur | 79 | 11:00
38 | Chapai | 70 | 21:00 | 104 | Madartek | 98 | 23:00 | 170 | Shahjibazar | 119 | 21:00
39 | Charsaidpur | 41 | 10:00 | 105 | Madunaghat | 52 | 18:30 | 171 | Shahmirpur | 50 | 00:00
40 | Chauddagram | 65 | 22:00 | 106 | Magura | 57 | 20:00 | 172 | Shariatpur | 74 | 22:00
41 | Chhatak | 23 | 20:00 | 107 | Mahasthangarh | 69 | 22:00 | 173 | Sherpur | 98 | 20:00
42 | Chowmuhani | 130 | 22:00 | 108 | Maijdee | 38 | 18:30 | 174 | Shikalbaha | 23 | 06:00
43 | Chuadanga | 116 | 00:00 | 109 | Manikganj | 146 | 22:00 | 175 | Shitalakhya | 92 | 13:00
44 | Coxsbazar | 121 | 11:00 | 110 | Maniknagar | 79 | 13:00 | 176 | Sholosohor | 45 | 09:00
45 | Cumilla(N) | 120 | 22:00 | 111 | Matarbari | 46 | 21:00 | 177 | Shyampur | 190 | 10:00
46 | Cumilla(S) | 198 | 12:00 | 112 | Matuail | 82 | 12:00 | 178 | Siddhirganj | 137 | 18:30
47 | Daganbhuiyan | 31 | 08:00 | 113 | Metrorail_Motijheel | 21 | 15:00 | 179 | Sirajganj | 128 | 19:00
48 | Daudkandi | 131 | 13:00 | 114 | Metrorail_Uttara | 10 | 10:00 | 180 | Sonargaon | 131 | 18:30
49 | DhakaUniversity | 98 | 13:00 | 115 | Millgate | 109 | 16:00 | 181 | Sreemongol | 56 | 21:00
50 | Dhamrai | 136 | 21:00 | 116 | Mirpur | 162 | 18:30 | 182 | Sreepur | 86 | 18:00
51 | Dhanmondi | 152 | 13:00 | 117 | Mirsorai | 59 | 03:00 | 183 | Srinagar | 61 | 20:00
52 | Dohazari | 87 | 12:00 | 118 | Mirzapur | 41 | 05:00 | 184 | Sunamganj | 43 | 20:00
53 | Faridpur | 146 | 00:00 | 119 | Mithapukur | 52 | 13:00 | 185 | Sylhet | 52 | 19:00
54 | Fatullah | 95 | 10:00 | 120 | Modern | N/A | N/A | 186 | Sylhet-132 | 103 | 19:30
55 | Fenchuganj | 43 | 22:00 | 121 | Mogbazar | 100.5 | 16:00 | 187 | TK | 23 | 18:30
56 | Feni | 109 | 18:30 | 122 | Mongla | 52 | 11:00 | 188 | Tangail | 148 | 12:00
57 | GPH | 18 | 01:00 | 123 | Motijheel | 54 | 16:00 | 189 | Taraganj | 23 | 23:00
58 | Ghatail | 60 | 19:00 | 124 | Muktagacha | 30 | 00:00 | 190 | Tasnim | 17 | 17:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 110 | 00:00 | 191 | Thakurgaon | 82 | 19:30
60 | Ghorashal-230 | 94 | 02:00 | 126 | Muradnagar | 49 | 04:00 | 192 | Tongi | 164 | 15:00
61 | Goalpara | 48 | 11:00 | 127 | Mymensingh | 179 | 19:30 | 193 | Ullahpara | 40 | 21:00
62 | Gollamari | 86 | 01:00 | 128 | Nabinagar | 13 | 18:00 | 194 | Ullon | 66 | 23:00
63 | Gopalganj | 87.2 | 22:00 | 129 | Naogaon | 139 | 06:00 | 195 | Uttara | 111 | 16:00
64 | Gulshan | 150 | 13:00 | 130 | Narail | 51 | 20:00 | 196 | UttaraNew | 64 | 23:00
65 | Halishahar | 103.5 | 09:00 | 131 | Narinda | 82 | 13:00 | 197 | Zigatola | 96 | 15:00
66 | HaripurSBU | 120 | 20:00 | 132 | Narshingdi | 185 | 18:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 23-04-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13261 | 1934 |  | 15282.03
1:00 | 12736.49 | 1971 |  | 14796.49
2:00 | 12521.2 | 1985 |  | 14595.2
3:00 | 12597.81 | 1817 |  | 14496.81
4:00 | 12522.81 | 1793 |  | 14396.81
5:00 | 12736.72 | 1589 |  | 14397.72
6:00 | 12593.95 | 1583 |  | 14248.19
7:00 | 12596.03 | 1441 |  | 14102.03
8:00 | 12701.21 | 1627 |  | 14401.43
9:00 | 12935.79 | 1641 |  | 14650.79
10:00 | 13462.77 | 1509 |  | 15039.77
11:00 | 13948.71 | 1628 |  | 15649.71
12:00 | 14194.78 | 1635 |  | 15903.36
13:00 | 14181.69 | 1646 |  | 15901.69
14:00 | 13644.46 | 2112 |  | 15851.46
15:00 | 13408.6 | 2401 |  | 15917.6
16:00 | 13374.39 | 2387 |  | 15868.39
17:00 | 13227.51 | 2352 |  | 15685.51
18:00 | 13418.44 | 2202 |  | 15719.44
19:00 | 14150.98 | 2483 |  | 16745.98
19:30 | 14338.38 | 2352 |  | 16796.38
20:00 | 14485.74 | 2249 |  | 16835.74
21:00 | 14726.43 | 2076 |  | 16895.43
22:00 | 14660.95 | 2091 |  | 16845.95
23:00 | 14297.93 | 2343 |  | 16745.93
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 23-04-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7031 | 6230 | 13261 | DAILY GENERATION CURVE
00:30 | 6884 | 6114.745 | 12998.745
01:00 | 6737 | 5999.49 | 12736.49 | 23-04-2026
01:30 | 6766 | 5862.845 | 12628.845
02:00 | 6795 | 5726.2 | 12521.2
02:30 | 6795 | 5764.505 | 12559.505
03:00 | 6795 | 5802.81 | 12597.81
03:30 | 6790.5 | 5769.81 | 12560.31
04:00 | 6786 | 5736.81 | 12522.81
04:30 | 6781 | 5848.765 | 12629.765
05:00 | 6776 | 5960.72 | 12736.72
05:30 | 6742.385 | 5922.95 | 12665.335
06:00 | 6708.77 | 5885.18 | 12593.95
06:30 | 6692.725 | 5902.265 | 12594.99
07:00 | 6676.68 | 5919.35 | 12596.03
07:30 | 6662.095 | 5986.525 | 12648.62
08:00 | 6647.51 | 6053.7 | 12701.21
08:30 | 6700.915 | 6117.585 | 12818.5
09:00 | 6754.32 | 6181.47 | 12935.79
09:30 | 6870.11 | 6329.17 | 13199.28
10:00 | 6985.9 | 6476.87 | 13462.77
10:30 | 7078.475 | 6627.265 | 13705.74
11:00 | 7171.05 | 6777.66 | 13948.71
11:30 | 7203.19 | 6868.555 | 14071.745
12:00 | 7235.33 | 6959.45 | 14194.78
12:30 | 7239.735 | 6948.5 | 14188.235
13:00 | 7244.14 | 6937.55 | 14181.69
13:30 | 7136.155 | 6776.92 | 13913.075
14:00 | 7028.17 | 6616.29 | 13644.46
14:30 | 6946.165 | 6580.365 | 13526.53
15:00 | 6864.16 | 6544.44 | 13408.6
15:30 | 6846.215 | 6545.28 | 13391.495
16:00 | 6828.27 | 6546.12 | 13374.39
16:30 | 6802.57 | 6498.38 | 13300.95
17:00 | 6776.87 | 6450.64 | 13227.51
17:30 | 6914 | 6408.975 | 13322.975
18:00 | 7051.13 | 6367.31 | 13418.44
18:30 | 7424.815 | 6359.895 | 13784.71
19:00 | 7798.5 | 6352.48 | 14150.98
19:30 | 7911.5 | 6426.88 | 14338.38
20:00 | 8012.5 | 6473.24 | 14485.74
20:30 | 8046.75 | 6559.335 | 14606.085 |  | Executive Engineer
21:00 | 8081 | 6645.43 | 14726.43 |  | Network Operation Division
21:30 | 8037 | 6656.69 | 14693.69
22:00 | 7993 | 6667.95 | 14660.95
22:30 | 7824.5 | 6654.94 | 14479.44
23:00 | 7656 | 6641.93 | 14297.93

## En-Curve
QF-LDC-12
Date | 23-04-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3742 | 1629 | 884 | 0 | 192 | 768 | 40 | 4533 | 0 | 570 | 901 | 0 | 0 | 2 | 1934 | DAILY ENERGY CURVE
00:30 | 3754 | 1631.5 | 884 | 0 | 191 | 766.745 | 40 | 4539.5 | 0 | 483.5 | 702.5 | 4 | 0 | 2 | 1952.5 | 23-04-2026
01:00 | 3766 | 1634 | 884 | 0 | 190 | 765.49 | 40 | 4546 | 0 | 397 | 504 | 8 | 0 | 2 | 1971
01:30 | 3774 | 1663.5 | 790 | 0 | 190 | 765.345 | 40 | 4515 | 0 | 397 | 484.5 | 8.5 | 0 | 1 | 1978 | Energy Generated | 325.9659 |  | MKWHr
02:00 | 3782 | 1693 | 696 | 0 | 190 | 765.2 | 40 | 4484 | 0 | 397 | 465 | 9 | 0 | 0 | 1985 | Energy not Served | 46.495 |  | MKWHr
02:30 | 3793.5 | 1700 | 696.5 | 0 | 185 | 764.505 | 40 | 4517 | 0 | 397 | 456.5 | 9.5 | 0 | 0 | 1901 | Total Energy Requirement | 372.4609 |  | MKWHr
03:00 | 3805 | 1707 | 697 | 0 | 180 | 763.81 | 40 | 4550 | 0 | 397 | 448 | 10 | 0 | 0 | 1817
03:30 | 3809 | 1712 | 720 | 0 | 180 | 758.81 | 40 | 4488.5 | 0 | 397 | 438.5 | 14.5 | 0 | 2 | 1805
04:00 | 3813 | 1717 | 743 | 0 | 180 | 753.81 | 40 | 4427 | 0 | 397 | 429 | 19 | 0 | 4 | 1793
04:30 | 3812.5 | 1722 | 813.5 | 0 | 178 | 753.265 | 40 | 4441 | 0 | 385.5 | 429.5 | 52.5 | 0 | 2 | 1691
05:00 | 3812 | 1727 | 884 | 0 | 176 | 752.72 | 40 | 4455 | 0 | 374 | 430 | 86 | 0 | 0 | 1589
05:30 | 3795 | 1726 | 884 | 0 | 171 | 754.365 | 40 | 4383.5 | 6.47 | 374 | 427 | 104 | 0 | 0 | 1586
06:00 | 3778 | 1725 | 884 | 0 | 166 | 756.01 | 40 | 4312 | 12.94 | 374 | 424 | 122 | 0 | 0 | 1583
06:30 | 3760.5 | 1700 | 884 | 0 | 167 | 762.605 | 40 | 4289.5 | 54.385 | 373 | 425 | 138 | 0 | 1 | 1512
07:00 | 3743 | 1675 | 884 | 0 | 168 | 769.2 | 40 | 4267 | 95.83 | 372 | 426 | 154 | 0 | 2 | 1441
07:30 | 3721.5 | 1616 | 884 | 0 | 174 | 765.78 | 39 | 4316 | 165.34 | 363 | 429 | 173.5 | 0 | 1.5 | 1534
08:00 | 3700 | 1557 | 884 | 0 | 180 | 762.36 | 38 | 4365 | 234.85 | 354 | 432 | 193 | 0 | 1 | 1627
08:30 | 3691 | 1583.5 | 884 | 0 | 182 | 762.895 | 38.5 | 4396 | 292.105 | 336.5 | 464.5 | 186.5 | 0 | 1 | 1634
09:00 | 3682 | 1610 | 884 | 0 | 184 | 763.43 | 39 | 4427 | 349.36 | 319 | 497 | 180 | 0 | 1 | 1641
09:30 | 3721.5 | 1638.5 | 884.5 | 0 | 184 | 762.535 | 39 | 4449 | 419.745 | 340.5 | 576.5 | 180 | 0 | 3.5 | 1575
10:00 | 3761 | 1667 | 885 | 0 | 184 | 761.64 | 39 | 4471 | 490.13 | 362 | 656 | 180 | 0 | 6 | 1509
10:30 | 3801 | 1661 | 884.5 | 0 | 189 | 761.59 | 39.5 | 4505 | 580.15 | 362 | 701 | 212.5 | 0 | 8.5 | 1568.5
11:00 | 3841 | 1655 | 884 | 0 | 194 | 761.54 | 40 | 4539 | 670.17 | 362 | 746 | 245 | 0 | 11 | 1628
11:30 | 3824.5 | 1656.5 | 884 | 0 | 199 | 762.16 | 40 | 4545 | 660.085 | 362 | 803 | 320.5 | 0 | 15 | 1631.5
12:00 | 3808 | 1658 | 884 | 0 | 204 | 762.78 | 40 | 4551 | 650 | 362 | 860 | 396 | 0 | 19 | 1635
12:30 | 3804.5 | 1634 | 884 | 0 | 196 | 761.63 | 40 | 4546.5 | 656.855 | 368.5 | 870.75 | 410 | 0 | 15.5 | 1640.5
13:00 | 3801 | 1610 | 884 | 0 | 188 | 760.48 | 40 | 4542 | 663.71 | 375 | 881.5 | 424 | 0 | 12 | 1646
13:30 | 3802 | 1641.5 | 884 | 0 | 181 | 762.99 | 40 | 4531 | 601.585 | 290 | 865.5 | 299.5 | 0 | 14 | 1879
14:00 | 3803 | 1673 | 884 | 0 | 174 | 765.5 | 40 | 4520 | 539.46 | 205 | 849.5 | 175 | 0 | 16 | 2112
14:30 | 3819.5 | 1648.5 | 884.5 | 0 | 171 | 768.155 | 40 | 4512 | 473.375 | 203 | 813.5 | 177.5 | 0 | 15.5 | 2256.5
15:00 | 3836 | 1624 | 885 | 0 | 168 | 770.81 | 40 | 4504 | 407.29 | 201 | 777.5 | 180 | 0 | 15 | 2401
15:30 | 3820 | 1635.5 | 885 | 0 | 171 | 766.515 | 40 | 4537 | 346.73 | 205.5 | 785.25 | 187.5 | 0 | 11.5 | 2394
16:00 | 3804 | 1647 | 885 | 0 | 174 | 762.22 | 40 | 4570 | 286.17 | 210 | 793 | 195 | 0 | 8 | 2387
16:30 | 3795 | 1637.5 | 885 | 0 | 168 | 761.54 | 40 | 4587 | 201.91 | 222 | 795.5 | 201.5 | 0 | 6 | 2369.5
17:00 | 3786 | 1628 | 885 | 0 | 162 | 760.86 | 40 | 4604 | 117.65 | 234 | 798 | 208 | 0 | 4 | 2352
17:30 | 3676 | 1568 | 885 | 0 | 172 | 754.86 | 39 | 4587 | 66.365 | 392.5 | 971.25 | 209 | 0 | 2 | 2277
18:00 | 3566 | 1508 | 885 | 0 | 182 | 748.86 | 38 | 4570 | 15.08 | 551 | 1144.5 | 210 | 0 | 0 | 2202
18:30 | 3590.5 | 1578 | 780.5 | 0 | 164 | 754.67 | 37.5 | 4585.5 | 7.54 | 655.5 | 1383.5 | 247.5 | 0 | 0 | 2342.5
19:00 | 3615 | 1648 | 676 | 0 | 146 | 760.48 | 37 | 4601 | 0 | 760 | 1622.5 | 285 | 0 | 0 | 2483
19:30 | 3636 | 1608 | 648 | 0 | 160 | 752.88 | 37 | 4614 | 0 | 809 | 1734.5 | 339 | 0 | 0 | 2352
20:00 | 3631 | 1574 | 648 | 0 | 150 | 756.24 | 37 | 4624 | 0 | 801 | 1815.5 | 449 | 0 | 0 | 2249
20:30 | 3692.5 | 1621 | 652 | 0 | 150 | 757.335 | 37 | 4625.5 | 0 | 798.5 | 1841.25 | 431 | 0 | 0 | 2162.5
21:00 | 3754 | 1668 | 656 | 0 | 150 | 758.43 | 37 | 4627 | 0 | 796 | 1867 | 413 | 0 | 0 | 2076
21:30 | 3750.5 | 1664 | 657.5 | 0 | 146 | 761.19 | 38 | 4625.5 | 0 | 774.5 | 1863.5 | 413 | 0 | 0 | 2083.5
22:00 | 3747 | 1660 | 659 | 0 | 142 | 763.95 | 39 | 4624 | 0 | 753 | 1860 | 413 | 0 | 0 | 2091
22:30 | 3742.5 | 1669 | 659 | 0 | 152 | 760.94 | 39.5 | 4583 | 0 | 680.5 | 1778.5 | 414.5 | 0 | 0 | 2217
23:00 | 3738 | 1678 | 659 | 0 | 162 | 757.93 | 40 | 4542 | 0 | 608 | 1697 | 416 | 0 | 0 | 2343
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 23-04-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 95 | -7 | 238 | 24 | 1594 | 484 | Ishurdi-Ghorashal Ckt-1 | Export | 2604436.36
1:00 | 83 | -9 | 226 | 26 | 1594 | 508
2:00 | 60 | 8 | 204 | 36 | 1542 | 526 |  | Import | 0
3:00 | 52 | 7 | 200 | 36 | 1466 | 496
4:00 | 56 | 2 | 212 | 40 | 1414 | 488 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 69 | -14 | 240 | 28 | 1360 | 460
6:00 | 76 | -13 | 260 | 36 | 1400 | 488 |  | Import | 0
7:00 | 87 | -14 | 300 | 22 | 1458 | 524
8:00 | 115 | -5 | 330 | 38 | 1660 | 576 | Sirajganj-Sreepur Ckt-1 | Export | 2318000
9:00 | 131 | 4 | 400 | 78 | 1772 | 632
10:00 | 140 | 10 | 450 | 114 | 1772 | 642 |  | Import | 0
11:00 | 164 | 15 | 504 | 126 | 1932 | 672
12:00 | 162 | 19 | 516 | 164 | 1924 | 696 | Sirajganj-Sreepur Ckt-2 | Export | 2334000
13:00 | 165 | 16 | 516 | 150 | 1922 | 674
14:00 | 165 | 23 | 564 | 180 | 1872 | 724 |  | Import | 0
15:00 | 150 | 20 | 540 | 164 | 1904 | 726
16:00 | 120 | 25 | 560 | 174 | 1918 | 718 | Gopalganj-Aminbazar Ckt-1 | Export | 20190000
17:00 | 130 | 20 | 540 | 174 | 1830 | 666
18:00 | 130 | 9 | 454 | 112 | 1754 | 626 |  | Import | 0
18:30 | 133 | 9 | 500 | 122 | 1680 | 582
19:00 | 75 | 13 | 350 | 80 | 1576 | 536 | Gopalganj-Aminbazar Ckt-2 | Export | 20240000
19:30 | 72 | 2 | 340 | 64 | 1646 | 536
20:00 | 78 | 6 | 366 | 100 | 1668 | 576 |  | Import | 0
21:00 | 79 | 3 | 384 | 102 | 1630 | 558
22:00 | 78 | 1 | 420 | 102 | 1656 | 520 |  | Total Export | 47686436.36
23:00 | 76 | -1 | 400 | 96 | 1650 | 532 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 23-04-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 22:00 | 365 | 12:00 | Madunaghat | 395 | 20:00 | 389 | 12:00
Amtali | 416 | 07:00 | 406 | 00:00 | Meghnaghat | 385 | 07:00 | 368 | 12:00
Ashuganj | 407 | 2:00 | 386 | 12:00 | Payra | 419 | 07:00 | 409 | 00:00
Bhulta | 398 | 05:00 | 376 | 12:00 | Rahanpur | 410 | 18:30 | 399 | 05:00
Bibiana | 402 | 07:00 | 393 | 12:00 | Rampal | 401 | 07:00 | 388 | 12:00
BIPTC | 403 | 04:00 | 390 | 15:00
Bogura | 402 | 16:00 | 389 | 07:00
Gopalganj | 397 | 07:00 | 384 | 12:00
Kaliakoir | 378 | 07:00 | 360 | 12:00
Korerhat | 396 | 00:00 | 384 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 228 | 07:00 | 214 | 12:00 | Jhenaidah | 228 | 02:00 | 219 | 12:00
AKSML | 233.2 | 18:30 | 223.9 | 12:00 | Kachua | 227 | 19:30 | 218 | 12:00
Aminbazar | 228 | 06:00 | 215 | 12:00 | Kaliakoir | 232 | 19:30 | 217 | 12:00
Ashuganj | 231 | 00:00 | 219 | 12:00 | Keranigonj | 226 | 07:00 | 212 | 12:00
Ashuganj-400 | 231 | 00:00 | 219 | 12:00 | Khulna(S) | 229 | 02:00 | 221 | 12:00
Baghabari | 234 | 19:00 | 227 | 00:00 | Korerhat | 227 | 07:00 | 221 | 13:00
Barapukuria | 225 | 18:30 | 204 | 07:00 | Madunaghat | 233 | 19:00 | 226 | 12:00
Barapukuria-230 | 225 | 18:30 | 204 | 07:00 | Madunaghat-400 | 233 | 20:00 | 228 | 12:00
Barishal | 227 | 23:00 | 221 | 12:00 | Maniknagar | 224 | 02:00 | 209 | 12:00
Bheramara | 234 | 02:00 | 223 | 12:00 | Meghnaghat | 232 | 01:00 | 220 | 12:00
Bhulta | 231 | 21:00 | 211 | 12:00 | Meghnaghat-400 | 227 | 07:00 | 215 | 12:00
Bibiana | 236 | 06:00 | 228 | 12:00 | Mirsorai | 232 | 19:00 | 224 | 12:00
BIPTC | 236 | 19:00 | 224 | 12:00 | Naogaon | 224 | 15:00 | 206 | 06:00
Bogura | 235 | 19:00 | 225 | 07:00 | Purbasadipur | 227 | 15:00 | 201 | 07:00
Bogura-400 | 233 | 15:00 | 224 | 07:00 | Rajshahi | 232 | 19:00 | 220 | 12:00
Borhanuddin | 230 | 02:00 | 227 | 11:00 | Rampal | 228 | 02:00 | 220 | 10:00
BSRM | 227 | 19:00 | 219 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 224 | 06:00 | 218 | 11:00 | Rampura | 224 | 03:00 | 208 | 13:00
Cumilla(N) | 225 | 07:00 | 215 | 12:00 | Shikalbaha | 232 | 19:00 | 224 | 11:00
Faridpur | 222 | 06:00 | 214 | 12:00 | Shyampur | 226 | 07:00 | 212 | 12:00
Fenchuganj | 238 | 00:00 | 233 | 11:00 | Siddhirganj | 223 | 00:00 | 212 | 12:00
Feni | 228 | 19:30 | 218 | 12:00 | Sirajgonj | 240 | 19:00 | 236 | 06:00
Ghorashal | 230 | 04:00 | 220 | 13:00 | Sreepur | 231 | 00:00 | 220 | 12:00
Ghorashal-230 | 225 | 02:00 | 211 | 12:00 | Tongi | 225 | 00:00 | 209 | 15:00
Gopalganj | 223 | 07:00 | 214 | 12:00
GPH | 231 | 19:00 | 223 | 12:00
Haripur | 225 | 03:00 | 212 | 12:00
Hasnabad | 225 | 22:00 | 212 | 12:00
Hathazari | 231 | 19:00 | 225 | 09:00
Ishurdi | 235 | 02:00 | 226 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 03:00 | 124 | 12:00 | Madunaghat | 135 | 18:00 | 131 | 11:00
Agargaon | 134 | 07:00 | 123 | 12:00 | Magura | 135 | 02:00 | 127 | 10:00
Agrabad | 134 | 18:00 | 128 | 12:00 | Mahasthangarh | 133 | 18:30 | 124 | 07:00
AKS | 132 | 19:00 | 127 | 12:00 | Maijdee | 127 | 19:30 | 121 | 11:00
Aminbazar | 130 | 22:00 | 120 | 12:00 | Manikganj | 125 | 07:00 | 114 | 12:00
Amnura | 137 | 19:00 | 127 | 10:00 | Maniknagar | 132 | 07:00 | 120 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 129 | 15:00 | 115 | 07:00
Ashuganj-230 | 139 | 00:00 | 133 | 15:00 | Matuail | 131 | 05:00 | 123 | 12:00
Bagerhat | 129 | 02:00 | 122 | 12:00 | Metrorail_Motijheel | 132 | 07:00 | 120 | 12:00
Bajitpur | 135 | 00:00 | 126 | 12:00 | Metrorail_Uttara | 130 | 02:00 | 118 | 12:00
Bakerganj | 133 | 19:30 | 129 | 12:00 | Millgate | 131 | 01:00 | 120 | 15:00
Bakulia | 135 | 00:00 | 131 | 11:00 | Mirpur | 130 | 22:00 | 119 | 12:00
Banani | 137 | 03:00 | 124 | 12:00 | Mirzapur | 130 | 00:00 | 121 | 12:00
Bangabhaban | 131 | 05:00 | 120 | 12:00 | Mithapukur | 131 | 18:30 | 119 | 07:00
Barapukuria | 134 | 18:30 | 120 | 07:00 | MI_Cement | 134.7 | 07:00 | 123 | 12:00
Barguna | 132 | 08:00 | 128 | 12:00 | Modern | 132 | 07:00 | 120 | 12:00
Barishal | 133 | 20:00 | 127 | 13:00 | Mogbazar | 138 | 03:00 | 126 | 12:00
Barishal-230 | 132 | 07:00 | 127 | 12:00 | Mongla | 129 | 07:00 | 121 | 12:00
Baroaulia | 134 | 02:00 | 130 | 10:00 | Motijheel | 131 | 05:00 | 120 | 12:00
Baroirhat | 129 | 18:00 | 120 | 00:00 | Muktagacha | 126 | 00:00 | 115 | 11:00
Bashundhara | 136 | 01:00 | 119 | 12:00 | Munshiganj | 128 | 06:00 | 121 | 11:00
BashundharaCement | 130 | 21:00 | 123 | 12:00 | Muradnagar | 128 | 07:00 | 120 | 12:00
Beanibazar | 132 | 07:00 | 126 | 20:00 | Mymensingh | 132 | 00:00 | 113 | 23:00
Benapole | 130 | 07:00 | 122 | 12:00 | Nabinagar | 132 | 00:00 | 123 | 12:00
Bhaluka | 136 | 01:00 | 127 | 17:00 | Naogaon | 133 | 02:00 | 122 | 06:00
Bhandaria | 128 | 05:00 | 120 | 12:00 | Narail | 133 | 07:00 | 127 | 10:00
Bhangura | 132 | 00:00 | 129 | 05:00 | Narinda | 132 | 07:00 | 120 | 12:00
Bheramara | 135 | 02:00 | 131 | 10:00 | Narshingdi | 135 | 02:00 | 116 | 13:00
Bheramara(GK) | 135 | 19:00 | 131 | 05:00 | Natore | 133 | 19:30 | 127 | 05:00
Bhulta | 124 | 04:00 | 117 | 12:00 | Nawabganj | 136 | 03:00 | 127 | 12:00
Bog-Sherpur | 133 | 16:00 | 127 | 05:00 | Netrakona | 132 | 00:00 | 121 | 17:00
Bogura | 134 | 14:00 | 127 | 07:00 | New | 131 | 00:00 | 120 | 12:00
Bogura-230 | 136 | 19:00 | 128 | 06:00 | Niamatpur | 134 | 18:30 | 127 | 06:00
Brahmanbaria | 133 | 01:00 | 127 | 12:00 | Noapara | 132 | 02:00 | 126 | 10:00
Cantonment | 133 | 03:00 | 123 | 12:00 | Pabna | 133 | 02:00 | 129 | 05:00
Chandina | 130 | 07:00 | 124 | 12:00 | Palashbari | 130 | 18:30 | 118 | 07:00
Chandpur | 131 | 19:00 | 125 | 10:00 | Panchagarh | 136 | 19:00 | 124 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 136 | 19:00 | 131 | 10:00 | Patiya | 136 | 19:00 | 129 | 12:00
Chapai | 134 | 18:30 | 128 | 06:00 | Patuakhali | 133 | 22:00 | 128 | 12:00
Charsaidpur | 129 | 04:00 | 123 | 12:00 | Payra | 137 | 07:00 | 132 | 00:00
Chauddagram | 127 | 00:00 | 122 | 12:00 | PHP | 129 | 19:30 | 124 | 12:00
Chhatak | 132 | 03:00 | 125 | 20:00 | Postogola | 137 | 06:00 | 126 | 12:00
Chowmuhani | 127 | 03:00 | 122 | 11:00 | Pubail | 136 | 19:00 | 125 | 12:00
Chuadanga | 133 | 02:00 | 124 | 10:00 | Purbachal | 137 | 02:00 | 119 | 12:00
Coxsbazar | 124 | 18:30 | 115 | 07:00 | Purbasadipur | 132 | 15:00 | 116 | 07:00
Cumilla(N) | 130 | 00:00 | 124 | 12:00 | Rahanpur | 135 | 18:30 | 131 | 05:00
Cumilla(S) | 129 | 00:00 | 118 | 12:00 | Rahanpur-400 | 136 | 18:30 | 131 | 05:00
Daganbhuiyan | 127 | 19:00 | 122 | 12:00 | Rahim | 130 | 01:00 | 123 | 13:00
Daudkandi | 127 | 04:00 | 118 | 12:00 | Rajbari | 127 | 02:00 | 121 | 12:00
DhakaUniversity | 137 | 04:00 | 125 | 12:00 | Rajendrapur | 140 | 00:00 | 128 | 13:00
Dhamrai | 133 | 23:00 | 123 | 12:00 | Rajshahi | 131 | 18:30 | 125 | 10:00
Dhanmondi | 134.5 | 23:00 | 124.5 | 13:00 | Rajshahi-230 | 133 | 19:00 | 126 | 12:00
Dohazari | 133 | 19:00 | 125 | 09:00 | Ramganj | 127 | 19:00 | 121 | 11:00
Faridpur | 130 | 19:30 | 124 | 12:00 | Rampur | 135 | 19:30 | 128 | 12:00
Fatullah | 135 | 05:00 | 120 | 12:00 | Rampura | 137 | 04:00 | 124 | 11:00
Fenchuganj | 136 | 00:00 | 132 | 12:00 | Rangamati | 135 | 19:00 | 129 | 12:00
Feni | 127 | 00:00 | 123 | 15:00 | Rangpur | 130 | 18:30 | 120 | 07:00
Feni-230 | 128 | 19:30 | 122 | 12:00 | Ruppur | 135 | 19:00 | 130 | 03:00
Ghatail | 127 | 00:00 | 114 | 12:00 | Saidpur | 131 | 19:00 | 120 | 06:00
Ghorashal | 137 | 22:00 | 128 | 12:00 | Santhia | 133 | 00:00 | 128 | 05:00
Goalpara | 135 | 02:00 | 127 | 10:00 | Satkhira | 130 | 02:00 | 123 | 10:00
Gollamari | 133 | 02:00 | 128 | 10:00 | Satmasjid | 133 | 04:00 | 124 | 15:00
Gopalganj | 132 | 07:00 | 126 | 12:00 | Savar | 130 | 22:00 | 118 | 12:00
Gopalganj-400 | 133 | 07:00 | 127 | 12:00 | SevenRings | 137 | 02:00 | 127 | 12:00
Gulshan | 136 | 04:00 | 124 | 12:00 | ShahCement | 129 | 04:00 | 123 | 12:00
Halishahar | 136 | 19:00 | 129 | 12:00 | Shahjadpur | 135 | 01:00 | 132 | 07:00
Haripur | 131 | 04:00 | 124 | 12:00 | Shahjibazar | 135 | 02:00 | 129 | 12:00
HaripurSBU | 131 | 04:00 | 124 | 12:00 | Shahmirpur | 135 | 00:00 | 131 | 02:00
Hasnabad | 136 | 07:00 | 126 | 12:00 | Shariatpur | 131 | 07:00 | 125 | 12:00
Hathazari | 136 | 21:00 | 132 | 09:00 | Sherpur | 125 | 00:00 | 108 | 23:00
Hatirjheel | 137 | 03:00 | 125 | 12:00 | Shikalbaha | 125 | 02:00 | 120 | 12:00
Ishurdi | 136 | 02:00 | 132 | 12:00 | Shikalbaha-230 | 138 | 18:30 | 132 | 11:00
Jaldhaka | 129 | 19:30 | 119 | 05:00 | Shitalakhya | 134.7 | 07:00 | 123 | 12:00
Jamalpur | 125 | 08:00 | 111 | 22:00 | Sholosohor | 135 | 19:00 | 130 | 12:00
Jashore | 131 | 07:00 | 124 | 10:00 | Shyampur | 128 | 07:00 | 121 | 10:00
Jhenaidah | 135 | 02:00 | 124 | 07:00 | Shyampur-230 | 129 | 04:00 | 120 | 12:00
Jhenaidah-230 | 136 | 02:00 | 130 | 00:00 | Siddhirganj | 131 | 04:00 | 124 | 12:00
Joydebpur | 135 | 19:00 | 123 | 12:00 | Sirajganj | 130 | 18:30 | 125 | 06:00
Joypurhat | 130 | 20:00 | 112 | 07:00 | Sonargaon | 128 | 00:00 | 122 | 12:00
Juldah | 135 | 00:00 | 130 | 12:00 | Sreemongol | 134 | 00:00 | 129 | 13:00
Kabirpur | 138 | 19:30 | 116 | 11:00 | Sreepur | 140 | 00:00 | 130 | 17:00
Kachua | 130 | 19:30 | 124 | 12:00 | Srinagar | 136 | 05:00 | 127 | 12:00
Kaliakoir | 137 | 19:30 | 126 | 12:00 | SSM | 138 | 00:00 | 134 | 13:00
Kaliganj | 134 | 00:00 | 127 | 10:00 | Sunamganj | 130 | 02:00 | 124 | 20:00
Kallyanpur | 130 | 07:00 | 120 | 14:00 | Sylhet | 133 | 00:00 | 129 | 13:00
Kalurghat | 136 | 19:00 | 131 | 09:00 | Sylhet-132 | 132 | 00:00 | 129 | 20:00
Kamrangirchar | 137 | 05:00 | 118 | 12:00 | Tangail | 127 | 00:00 | 116 | 12:00
Kaptai | 137 | 20:00 | 134 | 11:00 | Taraganj | 129 | 18:00 | 116 | 07:00
Kasba | 128 | 07:00 | 120 | 12:00 | Tasnim | 129 | 04:00 | 122 | 12:00
Kazla | 131 | 03:00 | 120 | 13:00 | Thakurgaon | 134 | 19:30 | 119 | 07:00
Keranigonj | 137 | 07:00 | 128 | 12:00 | TK | 136 | 00:00 | 131 | 11:00
Khagrachori | 134 | 19:30 | 128 | 12:00 | Tongi | 133 | 00:00 | 122 | 11:00
Khulna | 133 | 02:00 | 127 | 10:00 | Ullahpara | 132 | 01:00 | 128 | 06:00
Khulna(S) | 134 | 02:00 | 128 | 12:00 | Ullon | 137 | 07:00 | 125 | 12:00
Khulshi | 134 | 19:00 | 127 | 12:00 | Uttara | 131 | 03:00 | 117 | 15:00
Kishoreganj | 136 | 00:00 | 126 | 12:00 | UttaraNew | 130 | 02:00 | 118 | 12:00
Kodda | 138 | 19:30 | 120 | 12:00 | Zigatola | 137 | 07:00 | 127 | 12:00
Korerhat | 131 | 00:00 | 127 | 11:00
KSRM | 135 | 22:00 | 129 | 12:00
Kulaura | 135 | 00:00 | 132 | 11:00
Kurigram | 131 | 18:30 | 114 | 07:00
Kushtia | 132 | 16:00 | 128 | 10:00
Laksam | 129 | 19:30 | 124 | 12:00
Lakshmipur | 126 | 19:00 | 121 | 10:00
Lalbag | 135 | 07:00 | 127 | 12:00
Lalmonirhat | 128 | 19:00 | 116 | 07:00
Madanganj | 130 | 21:00 | 123 | 12:00
Madaripur | 131 | 07:00 | 127 | 12:00
Madartek | 136 | 02:00 | 125 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division