## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 26-04-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-04-2026 | during | 26-04-2026 | during | 26-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 186 | 344 | 412 | 412 | 392 | 392 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 32 | 55 | 55 | 15 | 55 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 320 | 280 | 335 | 335 | 320 | 320 | Machine Problem
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 33 | 53.97 | 53.97 | 17 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 144 | 149.36 | 149.36 | 149 | 149 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 26 | 23 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 20 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 50 | 52.19 | 52.19 | 16 | 52 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 64 | 146 | 300 | 300 | 48 | 294 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 88 | 149 | 149 | 52 | 149 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 105 | 105 | 34 | 105 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 126 | 162 | 162 | 35 | 35 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 560 | 500 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 330 | 255 | 718 | 718 | 350 | 350 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 108 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1660 | 2341 | 5947.22 | 5915.22 | 2282 | 2794
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 8 | 25 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 15 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50 | 19 | 50 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 39 | 38 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 218 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 51 | 105 | 105 | 34 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 45 | 54 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 67 | 0 | 68 | 0 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 22 | 5 | 25 | 30 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 18 | 37 | 108 | 108 | 12 | 12 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.42 | 0 | 3.4 | 0 | 3.4 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 17 | 54.36 | 54.36 | 0 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 55 | 110 | 110 | 54 | 54 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 116 | 116 | 70 | 70 | Liquid fuel shortage
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 17 | 90 | 163 | 163 | 17 | 163 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 612 | 1224 | 1224 | 612 | 612 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 2 | 0 | 28 | 28 | 28 | 28 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 720 | 1000 | 935 | 1000 | 935 | 935 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1807.42 | 2352 | 3748.26 | 3900.86 | 2159.4 | 2465
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 209 | 196 | 221.25 | 221.25 | 210 | 210 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 352 | 357 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 335 | 300 | 342.01 | 342.01 | 342.01 | 342.01 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 235 | 215 | 393 | 393 | 230 | 230 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 18 | 140 | 18 | 140 | 20 | 140 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 30 | 23 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 95 | 163 | 163 | 100 | 100 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 192 | 200 | 200 | 17 | 80 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 154 | 124 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 16 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 7 | 24 | 113 | 113 | 9 | 9 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 13 | 70 | 115 | 115 | 17 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1543 | 1803 | 2632.44 | 2678.44 | 1628.02 | 1792.02
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-04-2026 | during | 26-04-2026 | during | 26-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 46 | 37 | 157.5 | 157.5 | 20 | 20 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.8 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 48 | 20 | 10 | 70 | 70 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 49 | 80 | 70 | 10 | 10 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 37.81 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 160.61 | 163 | 382 | 314 | 165 | 129
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 156 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 100 | 100 | 100 | 100 | 100 | 100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 28 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 33 | 81 | 81 | 81 | 81 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 16 | 25 | 25 | 17 | 17 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 80 | 386 | 350 | 350 | 350 | 350
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 942 | 1196 | 1262 | 1262 | 1204 | 1204
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 884 | 913 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 30 | 30 | 28 | 28 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 27 | 44 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 250 | 410 | 410 | 210 | 210 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 79 | 0 | 93 | 0 | 93 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1229 | 1221 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2469 | 2428 | 3587.2 | 3494.2 | 2630.3 | 2537.3
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 254 | 454 | 250 | 300 | 250 | 300 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 6 | 16 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 125 | 130 | 130 | 130 | 110 | 110 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1204 | 1214 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 35 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 290 | 290 | 307 | 307 | 290 | 290 | Bad quality coal
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.66 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2116.66 | 2341 | 2412 | 2461 | 2148 | 2215
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 55.13 | 0 | 58 | 0 | 58 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 31 | 40 | 40 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 12 | 24 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 172 | 171 | 214 | 214 | 170 | 170 | -
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 212 | 215 | 220 | 220 | 220 | 220 | Plant is running with HSD as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 176 | 167 | 220 | 220 | 150 | 150 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 385 | 348 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 18 | 32 | 32 | 0 | 25 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 84 | 85 | 85 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 0 | 50 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 54 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.69 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 764 | 757 | 748 | 748 | 748 | 748 | U-2 Under Maintenance
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 52.82 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 101 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1934.64 | 1919 | 2537.69 | 2312.99 | 1958.49 | 1928.79
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Tripped
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 99 | 113 | 113 | 35 | 113 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7 | 0 | 6.8 | 0 | 6.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 0 | 70 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 23 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 111 | 0 | 132.72 | 0 | 132.72 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 141 | 169 | 397.52 | 228 | 204.52 | 183
System Total |  |  |  |  | 28823.2 | 29270.237 | 12774.33 | 14712 | 22906.33 | 22566.71 | 14379.73 | 15248.11
Forecast Scenario (26-04-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13447 |  | 1865 |  | 15400
|  |  |  | 1:00 | 12885 |  | 1399 |  | 14350
|  |  |  | 2:00 | 12909 |  | 708 |  | 13650
|  |  |  | 3:00 | 12802 |  | 170 |  | 12980
|  |  |  | 4:00 | 12476 |  | 138 |  | 12620
|  |  |  | 5:00 | 12388 |  | 40 |  | 12430
|  |  |  | 6:00 | 12205 |  | 91 |  | 12300
|  |  |  | 7:00 | 12338 |  | 145 |  | 12490
|  |  |  | 8:00 | 12211 |  | 275.995 |  | 12500
|  |  |  | 9:00 | 12420 |  | 553.9 |  | 13000
|  |  |  | 10:00 | 12900 |  | 668.5 |  | 13600
|  |  |  | 11:00 | 13400 |  | 859.5 |  | 14300
|  |  |  | 12:00 | 13800 |  | 1432.5 |  | 15300
|  |  |  | 13:00 | 14000 |  | 1719 |  | 15800
|  |  |  | 14:00 | 14200 |  | 1575.75 |  | 15850
|  |  |  | 15:00 | 14300 |  | 1537.55 |  | 15910
|  |  |  | 16:00 | 14200 |  | 1585.3 |  | 15860
|  |  |  | 17:00 | 14300 |  | 1317.9 |  | 15680
|  |  |  | 18:00 | 14400 |  | 1251.05 |  | 15710
|  |  |  | 18:30 | 14700 |  | 1480.25 |  | 16250
|  |  |  | 19:00 | 14900 |  | 1757.2 |  | 16740
|  |  |  | 19:30 | 14950 |  | 1757.2 |  | 16790
|  |  |  | 20:00 | 15000 |  | 1747.65 |  | 16830
|  |  |  | 21:00 | 15100 |  | 1709.45 |  | 16890
|  |  |  | 22:00 | 14700 |  | 2043.7 |  | 16840
|  |  |  | 23:00 | 14300 |  | 2330.2 |  | 16740
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 15300.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 16890.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15100.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 324.50 MKWHr. |  | 250 | 180 | 200 | 210 | 80 | 280 | 69 | 260 | 180 | 1709
*** This report is generated digitally from Operation Information System (OIS) at 09:00 hrs on 26-04-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 25-04-2026 | [28 empty] | Date: | 25-04-2026 | [28 empty] | Date: | 25-04-2026 | [28 empty] | Date: | 25-04-2026 | [28 empty] | Date: | 25-04-2026 | [17 empty] | Date: | 25-04-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 5 | 0 | 17 | 88 | 46 | 180 | 33 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 17 | 22 | 21 | 0 | 470 | 17 | 16 | 21 | 0 | 0 | 67 | 57 | 17 | 0 | 0 | 0 | 40 | 55 | 21 | 720 | 17 | 0 | 19 | 0 | 34 | 217 | 0 | 0 | 0 | 612 | 0 | 18 | 0 | 220 | 356 | 345 | 51 | 0 | 199 | 0 | 34 | 98 | 95 | 0 | 19 | 0 | 156 | 0 | 0 | 31 | 320 | 0 | 288 | 42 | 30 | 153 | 0 | 16 | 0 | 78 | 30 | 100 | 0 | 100 | 17 | 9 | 58 | 71 | 0 | 0 | 8 | 6794 | 696 | 250 | 0 | 28 | 31 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 1215 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 35 | 35 | 0 | 81 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 178 | 0 | 0 | 214 | 180 | 0 | 400 | 0 | 0 | 0 | 47 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 290 | 130 | 220 | 0 | 262 | 1244 | 17 | 6603 | 13397 | 77.12
01:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 5 | 0 | 0 | 88 | 30 | 180 | 31 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 22 | 22 | 0 | 470 | 17 | 16 | 18 | 0 | 0 | 34 | 57 | 17 | 0 | 0 | 0 | 40 | 55 | 21 | 720 | 17 | 0 | 19 | 0 | 34 | 219 | 0 | 0 | 0 | 612 | 0 | 11 | 0 | 220 | 356 | 345 | 0 | 0 | 199 | 0 | 0 | 98 | 17 | 0 | 19 | 0 | 154 | 0 | 0 | 31 | 320 | 0 | 288 | 42 | 30 | 153 | 0 | 16 | 0 | 78 | 30 | 100 | 0 | 100 | 17 | 56 | 9 | 71 | 0 | 0 | 12 | 6496 | 884 | 250 | 0 | 24 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1218 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 180 | 0 | 0 | 214 | 180 | 0 | 394 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 290 | 130 | 220 | 0 | 262 | 1244 | 17 | 6456 | 12952 | 77.11
02:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 17 | 0 | 0 | 88 | 30 | 180 | 31 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 17 | 22 | 22 | 0 | 460 | 17 | 16 | 19 | 0 | 0 | 0 | 57 | 17 | 0 | 0 | 0 | 40 | 55 | 21 | 720 | 17 | 0 | 19 | 0 | 34 | 219 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 220 | 356 | 342 | 0 | 0 | 203 | 0 | 0 | 98 | 17 | 0 | 19 | 0 | 156 | 0 | 0 | 31 | 305 | 0 | 288 | 42 | 30 | 150 | 0 | 16 | 0 | 78 | 30 | 100 | 0 | 100 | 0 | 56 | 9 | 71 | 0 | 0 | 12 | 6408 | 697 | 250 | 0 | 24 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1215 | 0 | 0 | 0 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 216 | 180 | 0 | 365 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 290 | 130 | 220 | 0 | 251 | 1244 | 17 | 6208 | 12616 | 77.11
03:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 17 | 0 | 0 | 88 | 15 | 180 | 31 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 17 | 22 | 22 | 0 | 530 | 17 | 16 | 18 | 0 | 0 | 0 | 57 | 17 | 0 | 0 | 0 | 40 | 55 | 21 | 720 | 17 | 0 | 19 | 0 | 34 | 220 | 0 | 0 | 0 | 612 | 0 | 16 | 0 | 220 | 356 | 345 | 5 | 0 | 204 | 0 | 0 | 99 | 17 | 0 | 19 | 0 | 156 | 0 | 0 | 31 | 315 | 0 | 288 | 42 | 30 | 150 | 0 | 16 | 0 | 78 | 30 | 100 | 0 | 100 | 0 | 56 | 9 | 71 | 0 | 0 | 0 | 6504 | 697 | 310 | 0 | 24 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1222 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 215 | 180 | 0 | 410 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 130 | 220 | 0 | 251 | 1244 | 17 | 6246 | 12750 | 77.1
04:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 19 | 0 | 0 | 88 | 15 | 180 | 31 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 17 | 22 | 15 | 0 | 530 | 17 | 16 | 18 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 40 | 55 | 21 | 720 | 17 | 0 | 19 | 0 | 34 | 220 | 0 | 0 | 0 | 612 | 0 | 18 | 0 | 220 | 356 | 345 | 19 | 0 | 209 | 0 | 0 | 99 | 17 | 0 | 19 | 0 | 148 | 0 | 0 | 32 | 310 | 0 | 288 | 42 | 30 | 151 | 0 | 16 | 0 | 78 | 30 | 100 | 0 | 100 | 0 | 56 | 9 | 71 | 0 | 0 | 0 | 6490 | 696 | 330 | 0 | 24 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 216 | 180 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 130 | 220 | 0 | 253 | 1244 | 17 | 6190 | 12680 | 77.1
05:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 178 | 0 | 0 | 88 | 15 | 180 | 15 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 17 | 22 | 15 | 0 | 560 | 17 | 16 | 19 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 40 | 55 | 28 | 720 | 17 | 0 | 19 | 0 | 34 | 220 | 0 | 0 | 0 | 612 | 0 | 18 | 0 | 225 | 357 | 345 | 27 | 0 | 208 | 0 | 0 | 99 | 17 | 0 | 19 | 0 | 152 | 0 | 0 | 25 | 310 | 0 | 288 | 42 | 30 | 148 | 0 | 16 | 0 | 78 | 30 | 101 | 0 | 100 | 0 | 58 | 9 | 91 | 0 | 0 | 0 | 6544 | 884 | 339 | 0 | 24 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 215 | 160 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 130 | 220 | 0 | 253 | 1244 | 17 | 6368 | 12912 | 77.09
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 210 | 0 | 0 | 44 | 15 | 180 | 15 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 1 | 17 | 22 | 15 | 0 | 530 | 17 | 16 | 18 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0.16 | 40 | 55 | 30 | 720 | 17 | 0 | 19 | 0 | 34 | 221 | 0 | 0 | 0 | 612 | 0 | 18 | 0 | 230 | 356 | 345 | 38 | 0 | 165 | 0 | 0 | 99 | 17 | 0 | 19 | 0 | 142 | 0 | 3 | 24 | 305 | 0 | 219 | 42 | 30 | 140 | 0 | 16 | 0 | 78 | 30 | 100 | 0 | 100 | 0 | 58 | 9 | 86 | 0.05 | 1.32 | 0 | 6160.53 | 884 | 342 | 0 | 24 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1220 | 0 | 0 | 0 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 1.38 | 2 | 0 | 0 | 1 | 173 | 0 | 0 | 217 | 160 | 0 | 342 | 0 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0.02 | 0 | 290 | 130 | 220 | 0 | 253 | 1244 | 17 | 6345.52 | 12506.05 | 77.09
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 274 | 0 | 0 | 34 | 15 | 180 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 5 | 17 | 22 | 15 | 0 | 530 | 17 | 16 | 19 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0.78 | 40 | 55 | 25 | 720 | 17 | 0 | 19 | 0 | 34 | 220 | 0 | 0 | 0 | 612 | 4 | 18 | 0 | 290 | 356 | 345 | 44 | 0 | 150 | 0 | 0 | 98 | 17 | 0 | 19 | 0 | 142 | 0 | 15 | 31 | 310 | 0 | 0 | 42 | 30 | 139 | 2 | 16 | 0 | 78 | 30 | 100 | 0 | 100 | 0 | 58 | 9 | 83 | 0.16 | 8.68 | 0 | 5937.62 | 885 | 315 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1222 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8.83 | 16 | 0 | 0 | 5.53 | 148 | 0 | 0 | 216 | 160 | 0 | 392 | 0 | 0.45 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.8 | 25 | 0.12 | 0 | 290 | 130 | 220 | 0 | 254 | 1244 | 17 | 6374.73 | 12312.35 | 77.08
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 296 | 0 | 0 | 34 | 15 | 64 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 327 | 0 | 0 | 12 | 17 | 22 | 15 | 0 | 560 | 17 | 16 | 19 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 40 | 55 | 2 | 720 | 17 | 0 | 0 | 0 | 34 | 216 | 0 | 0 | 0 | 612 | 7 | 18 | 0 | 285 | 356 | 342 | 44 | 0 | 153 | 0 | 0 | 30 | 17 | 0 | 20 | 0 | 154 | 0 | 33 | 31 | 320 | 0 | 0 | 42 | 30 | 143 | 5 | 17 | 0 | 78 | 30 | 100 | 0 | 100 | 0 | 58 | 9 | 47 | 0.17 | 17.05 | 0 | 5890.22 | 884 | 250 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 1226 | 0 | 0 | 0 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 21.48 | 43 | 0 | 0 | 21.01 | 158 | 0 | 0 | 215 | 170 | 0 | 414 | 0 | 1.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 20 | 0.19 | 0 | 290 | 126 | 220 | 0 | 254 | 1220 | 17 | 6404.83 | 12295.05 | 77.08
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 301 | 0 | 0 | 34 | 15 | 64 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 19 | 17 | 22 | 15 | 0 | 530 | 17 | 16 | 19 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 2.21 | 40 | 55 | 0 | 720 | 17 | 0 | 0 | 0 | 34 | 216 | 0 | 0 | 0 | 612 | 9 | 18 | 0 | 255 | 356 | 345 | 51 | 0 | 207 | 0 | 1 | 40 | 23 | 0 | 20 | 0 | 160 | 0 | 53 | 31 | 320 | 0 | 15 | 42 | 30 | 150 | 7 | 17 | 0 | 78 | 30 | 100 | 0 | 100 | 0 | 58 | 9 | 47 | 1.41 | 25.33 | 0 | 6030.95 | 884 | 250 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 1200 | 0 | 0 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 35.3 | 70 | 0 | 0 | 35.06 | 167 | 0 | 0 | 213 | 174 | 0 | 333 | 0 | 3.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1 | 3 | 0.29 | 0 | 290 | 123 | 220 | 0 | 254 | 1204 | 17 | 6336.79 | 12367.74 | 77.07
10:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 317 | 0 | 0 | 34 | 15 | 64 | 15 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 26 | 17 | 22 | 21 | 0 | 530 | 17 | 16 | 18 | 0 | 1 | 0 | 61 | 0 | 0 | 0 | 3.05 | 40 | 55 | 0 | 720 | 17 | 0 | 0 | 0 | 34 | 215 | 0 | 0 | 0 | 612 | 16 | 18 | 0 | 235 | 356 | 335 | 51 | 0 | 211 | 0 | 2 | 40 | 17 | 0 | 11 | 0 | 160 | 0 | 64 | 31 | 325 | 0 | 80 | 42 | 30 | 152 | 10 | 8 | 0 | 78 | 30 | 100 | 0 | 100 | 0 | 68 | 9 | 47 | 1.6 | 21.39 | 0 | 6087.04 | 884 | 250 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 1225 | 0 | 0 | 0 | 763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 47.57 | 87 | 0 | 0 | 29.25 | 171 | 0 | 0 | 211 | 175 | 0 | 366 | 0 | 1.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 3 | 0.61 | 0 | 290 | 125 | 220 | 0 | 254 | 1204 | 17 | 6456.44 | 12543.48 | 77.07
11:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 330 | 0 | 0 | 34 | 15 | 64 | 15 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 30 | 17 | 26 | 21 | 0 | 560 | 17 | 16 | 18 | 0 | 2 | 0 | 45 | 0 | 0 | 0 | 3.42 | 39 | 55 | 0 | 720 | 17 | 0 | 0 | 0 | 34 | 214 | 0 | 0 | 0 | 612 | 15 | 18 | 0 | 235 | 352 | 335 | 51 | 0 | 209 | 0 | 13 | 40 | 17 | 7 | 15 | 0 | 154 | 0 | 67 | 30 | 315 | 0 | 80 | 42 | 30 | 153 | 6 | 8 | 0 | 78 | 30 | 100 | 0 | 100 | 0 | 67 | 9 | 46 | 0.8 | 37.81 | 0 | 6113.03 | 884 | 250 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 1229 | 0 | 0 | 0 | 764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 55.13 | 101 | 0 | 0 | 52.82 | 172 | 0 | 0 | 212 | 176 | 0 | 385 | 0 | 4.69 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 7 | 111 | 0.66 | 6 | 290 | 125 | 220 | 0 | 254 | 1204 | 17 | 6661.3 | 12774.33 | 77.06
12:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 317 | 0 | 0 | 35 | 15 | 64 | 15 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 31 | 17 | 26 | 21 | 0 | 530 | 21 | 16 | 16 | 0 | 7 | 0 | 45 | 0 | 0 | 0 | 3.41 | 39 | 55 | 0 | 720 | 17 | 0 | 0 | 0 | 34 | 214 | 0 | 0 | 0 | 612 | 19 | 18 | 0 | 235 | 354 | 335 | 51 | 0 | 209 | 0 | 17 | 40 | 17 | 9 | 15 | 0 | 172 | 0 | 48 | 30 | 320 | 0 | 15 | 42 | 30 | 150 | 7 | 8 | 0 | 77 | 30 | 102 | 0 | 100 | 0 | 72 | 9 | 48 | 2 | 3.95 | 0 | 5913.36 | 884 | 250 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 1226 | 0 | 0 | 0 | 759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 32.64 | 104 | 0 | 0 | 55.8 | 176 | 0 | 0 | 208 | 180 | 0 | 398 | 0 | 4.88 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 7.1 | 192 | 0.67 | 16 | 290 | 125 | 220 | 0 | 254 | 1204 | 17 | 6770.09 | 12683.45 | 77.06
13:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 318 | 0 | 0 | 34 | 15 | 64 | 15 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 29 | 17 | 8 | 21 | 0 | 530 | 17 | 16 | 14 | 0 | 14 | 0 | 45 | 0 | 0 | 0 | 0 | 40 | 55 | 3 | 720 | 17 | 0 | 0 | 0 | 34 | 213 | 0 | 0 | 0 | 612 | 17 | 18 | 0 | 235 | 353 | 335 | 51 | 0 | 203 | 0 | 17 | 40 | 17 | 8 | 15 | 0 | 180 | 0 | 63 | 30 | 315 | 0 | 80 | 42 | 30 | 149 | 2 | 8 | 0 | 77 | 30 | 100 | 0 | 100 | 0 | 62 | 46 | 49 | 2 | 48.38 | 0 | 6015.38 | 884 | 250 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 1215 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 52.3 | 100 | 0 | 0 | 53.92 | 182 | 0 | 0 | 208 | 192 | 0 | 370 | 0 | 4.67 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 6.8 | 180 | 0.61 | 16 | 290 | 125 | 220 | 0 | 253 | 1206 | 17 | 6743.3 | 12758.68 | 77.05
14:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 317 | 0 | 8 | 34 | 15 | 64 | 15 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 26 | 17 | 26 | 21 | 0 | 530 | 17 | 16 | 12 | 0 | 17 | 0 | 51 | 0 | 0 | 0 | 2.8 | 40 | 54 | 2 | 720 | 17 | 0 | 0 | 0 | 34 | 213 | 0 | 0 | 0 | 612 | 16 | 18 | 0 | 230 | 356 | 345 | 51 | 0 | 202 | 0 | 17 | 40 | 17 | 8 | 15 | 0 | 190 | 0 | 58 | 28 | 315 | 0 | 92 | 42 | 30 | 152 | 0 | 0 | 0 | 53 | 30 | 100 | 0 | 100 | 0 | 54 | 46 | 45 | 1.7 | 41.64 | 0 | 6102.14 | 884 | 250 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 1232 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 44.03 | 89 | 0 | 0 | 46 | 172 | 0 | 0 | 208 | 177 | 0 | 396 | 0 | 4.14 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 6 | 155 | 0.54 | 16 | 290 | 125 | 220 | 0 | 254 | 1220 | 17 | 6711.71 | 12813.85 | 77.05
15:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 257 | 17 | 17 | 34 | 15 | 64 | 15 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 21 | 17 | 24 | 21 | 0 | 450 | 17 | 16 | 12 | 0 | 20 | 0 | 51 | 0 | 0 | 0 | 0 | 40 | 55 | 0 | 720 | 17 | 0 | 0 | 0 | 34 | 214 | 0 | 0 | 0 | 614 | 12 | 18 | 0 | 215 | 355 | 342 | 51 | 0 | 204 | 0 | 18 | 45 | 17 | 8 | 15 | 0 | 186 | 0 | 43 | 28 | 320 | 0 | 160 | 42 | 30 | 156 | 7 | 16 | 0 | 77 | 30 | 100 | 0 | 100 | 0 | 55 | 46 | 33 | 1.3 | 31.87 | 0 | 6188.17 | 884 | 250 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 1227 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 12 | 0 | 35.06 | 69 | 0 | 0 | 27 | 179 | 0 | 0 | 202 | 176 | 0 | 396 | 0 | 3.06 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 4.4 | 121 | 0.45 | 16 | 290 | 122 | 220 | 0 | 279 | 1232 | 17 | 6644.97 | 12833.14 | 77.04
16:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 273 | 17.5 | 17 | 34 | 19 | 64 | 15 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 13 | 17 | 24 | 13 | 0 | 470 | 17 | 16 | 18 | 0 | 22 | 0 | 45 | 0 | 0 | 0 | 1.32 | 40 | 55 | 0 | 780 | 17 | 0 | 0 | 0 | 34 | 214 | 0 | 0 | 0 | 612 | 7 | 18 | 0 | 215 | 356 | 340 | 51 | 0 | 207 | 0 | 20 | 30 | 17 | 8 | 12 | 0 | 174 | 0 | 25 | 20 | 320 | 0 | 186 | 42 | 30 | 155 | 5 | 16 | 0 | 77 | 30 | 100 | 0 | 100 | 0 | 50 | 46 | 33 | 0.7 | 19.93 | 0 | 6247.45 | 884 | 250 | 0 | 5 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 1230 | 0 | 0 | 0 | 761 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 12 | 0 | 20.59 | 45 | 0 | 0 | 21 | 175 | 0 | 0 | 208 | 168 | 0 | 402 | 0 | 1.86 | 0 | 0 | 35 | 12 | 55 | 0 | 0 | 0 | 2.1 | 83 | 0.26 | 16 | 290 | 122 | 220 | 0 | 305 | 1220 | 17 | 6664.81 | 12912.26 | 77.04
17:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 250 | 17.5 | 17 | 34 | 50 | 64 | 15 | 17 | 35 | 0 | 0 | 0 | 0 | 0 | 17 | 250 | 0 | 0 | 5 | 17 | 24 | 13 | 0 | 450 | 17 | 16 | 25 | 0 | 15 | 0 | 45 | 0 | 0 | 0 | 0.51 | 40 | 54 | 0 | 925 | 17 | 0 | 0 | 0 | 37 | 216 | 0 | 0 | 0 | 612 | 2 | 18 | 0 | 215 | 356 | 342 | 51 | 0 | 206 | 0 | 17 | 35 | 67 | 9 | 15 | 0 | 168 | 0 | 10 | 20 | 325 | 0 | 233 | 42 | 30 | 155 | 2 | 8 | 0 | 77 | 30 | 100 | 0 | 99 | 2 | 56 | 48 | 43 | 0.3 | 8.31 | 1 | 6469.62 | 884 | 250 | 0 | 28 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 1202 | 0 | 0 | 0 | 765 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 12 | 0 | 8.6 | 20 | 0 | 0 | 9 | 173 | 0 | 0 | 170 | 167 | 0 | 390 | 0 | 0.8 | 0 | 0 | 45 | 5 | 67 | 0 | 0 | 0 | 0.6 | 31 | 0.12 | 16 | 290 | 125 | 220 | 0 | 305 | 1210 | 17 | 6496.12 | 12965.74 | 77.03
18:00 | 0 | 54 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 263 | 36 | 17 | 34 | 127 | 146 | 15 | 35 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 250 | 0 | 0 | 1 | 25 | 17 | 13 | 0 | 400 | 17 | 16 | 38 | 0 | 2 | 14 | 53 | 4 | 0 | 0 | 0 | 40 | 54 | 7 | 830 | 35 | 0 | 22 | 1 | 51 | 216 | 0 | 0 | 0 | 612 | 0 | 50 | 0 | 230 | 356 | 300 | 51 | 0 | 170 | 0 | 18 | 50 | 191 | 17 | 15 | 0 | 118 | 0 | 1 | 21 | 315 | 0 | 395 | 42 | 30 | 139 | 0 | 16 | 0 | 78 | 30 | 101 | 0 | 99 | 17 | 58 | 48 | 43 | 0 | 0.84 | 12 | 6898.84 | 894 | 250 | 0 | 27 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 2.74 | 1217 | 0 | 0 | 0 | 765 | 0 | 0 | 0 | 50 | 50 | 0 | 74 | 15 | 0 | 1.29 | 3 | 18 | 0 | 0.6 | 165 | 0 | 0 | 150 | 161 | 0 | 371 | 0 | 0.06 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 3 | 0.02 | 23 | 290 | 125 | 180 | 0 | 305 | 1210 | 17 | 6534.71 | 13433.55 | 77.03
19:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 233 | 36 | 17 | 46 | 127 | 146 | 18 | 35 | 108 | 0 | 0 | 0 | 0 | 0 | 35 | 250 | 0 | 0 | 0 | 56 | 22 | 13 | 0 | 450 | 17 | 16 | 37 | 0 | 0 | 67 | 53 | 17 | 0 | 0 | 0 | 40 | 54 | 10 | 935 | 54 | 0 | 46 | 8 | 51 | 216 | 0 | 0 | 0 | 612 | 0 | 120 | 0 | 225 | 356 | 345 | 51 | 0 | 204 | 0 | 56 | 50 | 192 | 17 | 15 | 0 | 126 | 0 | 0 | 21 | 310 | 0 | 386 | 42 | 30 | 149 | 0 | 8 | 0 | 33 | 30 | 100 | 0 | 100 | 17 | 49 | 48 | 43 | 0 | 0 | 12 | 7365 | 867 | 250 | 0 | 32 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1202 | 0 | 0 | 0 | 766 | 0 | 31 | 0 | 54 | 50 | 0 | 84 | 18 | 0 | 0 | 0 | 22 | 0 | 0 | 168 | 0 | 0 | 150 | 164 | 0 | 340 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 290 | 125 | 220 | 0 | 445 | 1210 | 17 | 6710 | 14075 | 77.02
19:30 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 275 | 36 | 17 | 88 | 127 | 146 | 30 | 35 | 108 | 0 | 0 | 0 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 70 | 24 | 13 | 0 | 500 | 17 | 16 | 37 | 0 | 0 | 67 | 53 | 17 | 0 | 0 | 0 | 40 | 55 | 10 | 935 | 54 | 0 | 50 | 8 | 51 | 216 | 0 | 0 | 0 | 612 | 0 | 150 | 0 | 225 | 356 | 340 | 51 | 0 | 201 | 0 | 69 | 80 | 194 | 17 | 15 | 0 | 118 | 0 | 0 | 21 | 310 | 0 | 386 | 42 | 30 | 146 | 0 | 8 | 0 | 33 | 30 | 101 | 0 | 100 | 17 | 49 | 48 | 44 | 0 | 0 | 12 | 7704 | 909 | 250 | 0 | 29 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 758 | 0 | 31 | 0 | 54 | 50 | 0 | 84 | 24 | 0 | 0 | 0 | 13 | 0 | 0 | 164 | 0 | 0 | 210 | 163 | 0 | 385 | 0 | 0 | 0 | 0 | 70 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 290 | 125 | 220 | 0 | 452 | 1205 | 17 | 6892 | 14596
20:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 258 | 36 | 17 | 85 | 127 | 146 | 32 | 35 | 108 | 0 | 0 | 0 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 70 | 23 | 13 | 0 | 510 | 17 | 16 | 38 | 0 | 0 | 67 | 53 | 17 | 0 | 0 | 0 | 40 | 55 | 18 | 1000 | 54 | 0 | 50 | 8 | 51 | 217 | 0 | 0 | 0 | 612 | 0 | 150 | 0 | 215 | 356 | 342 | 51 | 0 | 201 | 0 | 69 | 95 | 192 | 18 | 16 | 0 | 116 | 0 | 0 | 22 | 310 | 0 | 387 | 42 | 30 | 151 | 0 | 16 | 0 | 33 | 30 | 101 | 0 | 100 | 17 | 49 | 48 | 39 | 0 | 0 | 12 | 7760 | 912 | 250 | 0 | 24 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1212 | 0 | 0 | 0 | 753 | 0 | 31 | 0 | 54 | 50 | 0 | 84 | 26 | 0 | 0 | 0 | 13 | 0 | 0 | 165 | 0 | 0 | 195 | 163 | 0 | 359 | 0 | 0 | 0 | 0 | 70 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 290 | 125 | 220 | 0 | 450 | 1210 | 17 | 6842 | 14602 | 77.02
21:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 255 | 33 | 17 | 88 | 144 | 146 | 32 | 35 | 126 | 0 | 0 | 0 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 108 | 23 | 20 | 0 | 500 | 17 | 16 | 37 | 0 | 0 | 67 | 54 | 17 | 0 | 0 | 0 | 38 | 55 | 22 | 1000 | 90 | 0 | 50 | 8 | 51 | 218 | 0 | 0 | 0 | 612 | 0 | 140 | 0 | 215 | 357 | 300 | 51 | 0 | 196 | 0 | 70 | 95 | 192 | 24 | 16 | 0 | 124 | 0 | 0 | 23 | 305 | 0 | 386 | 42 | 30 | 156 | 0 | 16 | 0 | 33 | 28 | 100 | 0 | 100 | 17 | 49 | 48 | 37 | 0 | 0 | 12 | 7855 | 913 | 250 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1221 | 0 | 0 | 0 | 757 | 0 | 31 | 0 | 54 | 50 | 0 | 84 | 24 | 0 | 0 | 0 | 18 | 0 | 0 | 171 | 0 | 0 | 215 | 167 | 0 | 348 | 0 | 0 | 0 | 0 | 70 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 454 | 1214 | 17 | 6857 | 14712 | 77.01
22:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 260 | 36 | 17 | 88 | 145 | 146 | 32 | 35 | 126 | 0 | 0 | 0 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 108 | 22 | 20 | 0 | 500 | 17 | 16 | 37 | 0 | 0 | 67 | 47 | 17 | 0 | 0 | 0 | 38 | 55 | 24 | 1000 | 90 | 0 | 50 | 0 | 51 | 217 | 0 | 0 | 0 | 612 | 0 | 110 | 0 | 215 | 356 | 300 | 51 | 0 | 207 | 0 | 69 | 97 | 192 | 27 | 16 | 0 | 116 | 0 | 0 | 23 | 300 | 0 | 386 | 42 | 30 | 156 | 0 | 16 | 0 | 11 | 25 | 102 | 0 | 100 | 17 | 49 | 48 | 34 | 0 | 0 | 12 | 7787 | 914 | 250 | 0 | 24 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1230 | 0 | 0 | 0 | 765 | 0 | 31 | 0 | 54 | 50 | 0 | 84 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 216 | 164 | 0 | 349 | 0 | 0 | 0 | 0 | 70 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 130 | 220 | 0 | 453 | 1215 | 17 | 6868 | 14655 | 77.01
23:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 263 | 36 | 17 | 73 | 145 | 34 | 32 | 35 | 126 | 0 | 0 | 0 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 60 | 21 | 20 | 0 | 525 | 17 | 16 | 37 | 0 | 0 | 67 | 47 | 17 | 0 | 0 | 0 | 37 | 55 | 27 | 935 | 17 | 0 | 50 | 0 | 51 | 218 | 0 | 0 | 0 | 612 | 0 | 30 | 0 | 215 | 356 | 300 | 51 | 0 | 210 | 0 | 69 | 97 | 192 | 27 | 16 | 0 | 128 | 0 | 0 | 23 | 305 | 0 | 386 | 42 | 30 | 158 | 0 | 16 | 0 | 11 | 30 | 102 | 0 | 100 | 17 | 59 | 9 | 32 | 0 | 0 | 12 | 7431 | 917 | 250 | 0 | 24 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1231 | 0 | 0 | 0 | 765 | 0 | 31 | 0 | 54 | 50 | 0 | 84 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 217 | 168 | 0 | 367 | 0 | 0 | 0 | 0 | 70 | 0 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 0 | 220 | 0 | 413 | 1215 | 17 | 6716 | 14147 | 77
Total KWH | 0 | 1113600 | 429120 | 0 | 0 | 0 | 0 | 0 | 6418800 | 0 | 5458700 | 260280 | 194400 | 1348704 | 1221120 | 2824233 | 540517 | 269774 | 875520 | 0 | 1244800 | 0 | 0 | 0 | 269225 | 7255876 | 0 | 0 | 218592 | 722400 | 528600 | 411120 | 0 | 12420909.09 | 424036 | 386400 | 566400 | 0 | 92640 | 458624 | 1191840 | 177865 | 0 | 0 | 18988 | 948180 | 1344000 | 314880 | 19083636.36 | 657382 | 0 | 432000 | 26377.2 | 968508 | 5161626 | 0 | 0 | 0 | 14634544 | 110835 | 956800 | 0 | 5657500 | 8863100 | 8068000 | 1040984 | 0 | 4856000 | 0 | 569280 | 1648450 | 1570560 | 194880 | 401860 | 0 | 3595200 | 0 | 474009 | 648944 | 7591000 | 0 | 5462000 | 995000 | 726960 | 3631909.09 | 58121 | 313104 | 0 | 1488000 | 706176 | 2368000 | 0 | 2399990 | 148680 | 1353600 | 616800 | 1190400 | 12250 | 281310 | 112800 | 159026718.74 | 20850909 | 6794784 | 0 | 332640 | 690688 | 0 | 59904 | 0 | 0 | 0 | 0 | 671040 | 29258180 | 0 | 0 | 0 | 18074330 | 0 | 162506 | 0 | 324768 | 476160 | 0 | 534544 | 379012 | 0 | 356192 | 752690 | 83525 | 0 | 346496 | 4186000 | 0 | 0 | 5139136 | 4380173 | 0 | 9325454 | 0 | 30480 | 0 | 160581 | 554748 | 161890 | 681561 | 0 | 0 | 0 | 42135.84 | 944640 | 4075 | 413952 | 7025000 | 2785000 | 5352760 | 0 | 7207272 | 29805090.91 | 434400 | 158782716.75 | 317809435.49

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 25-04-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12774.33 | MW | 11:00 Hr. | Energy Generated |  |  | 317.8094 |  | MKWHr.
| Day Peak Demand |  |  | 15000.45 | MW | 12:00 Hr. | Energy Unserverd |  |  | 52.772 |  | MKWHr.
| Evening Peak Generation |  |  | 14712 | MW | 21:00 Hr. | Energy Demand |  |  | 370.5814 |  | MKWHr.
| Evening Peak Demand |  |  | 16765 | MW | 21:00 Hr. | Maximum Temperature |  |  | 36.5 |  | °C
| Minimum Generation of the Day |  |  | 12295.05 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 925.64 |  | MMCFD
| Maximum Generation of the Day |  |  | 14712 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.2712 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.7388 | 0 | 10.0689 | 0 | 0 | 0.21859 | 0 | 0 | 44.0263 | Gas | 129.4479 | Gas | 452276859.0881
| Chattogram Zone |  |  | 5.4765 | 33.7182 | 6.6334 | 0 | 0.94818 | 0.12982 | 0 | 0.09264 | 46.9988 | Coal | 107.1743 | Coal | 728009368.0711
| Cumilla Zone |  |  | 30.5359 | 0 | 3.9405 | 0 | 0 | 0.47401 | 3.5952 | 0 | 38.5456 | HFO | 27.9432 | HFO | 484976187.96
| Mymensingh Zone |  |  | 1.1904 | 0 | 2.2319 | 0 | 0 | 0.29356 | 0 | 0 | 3.7158 | HSD | 5.199 | HSD | 20857734.4
| Sylhet Zone |  |  | 25.6821 | 0 | 0 | 0 | 0 | 0.058121 | 0 | 0 | 25.7403 | Hydro | 0.94818 | Hydro | 94818
| Khulna Zone |  |  | 6.7948 | 29.2582 | 1.0233 | 0.059904 | 0 | 0.67104 | 20.8509 | 0 | 58.6581 | Solar | 4.4837 | Solar | 71045923.698
| Barishal Zone |  |  | 8.1378 | 44.0374 | 0.84835 | 0 | 0 | 0.004075 | 0 | 0 | 53.0275 | Import | 42.5204 | Import | 234412915.35
| Rajshahi Zone |  |  | 17.8916 | 0 | 1.9605 | 5.1391 | 0 | 1.4859 | 18.0743 | 0 | 44.5515 | Wind | 0.09264 | Wind | 1362734.4
| Rangpur Zone |  |  | 0 | 0.16058 | 1.2363 | 0 | 0 | 1.1487 | 0 | 0 | 2.5456
| Total |  |  | 129.4479 | 107.1743 | 27.9432 | 5.199 | 0.94818 | 4.4837 | 42.5204 | 0.09264 | 317.8094
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 452276859.0881 |  | Hydro | 94818
|  |  |  | Coal | 728009368.0711 |  | Solar | 71045923.698
|  |  |  | HFO | 484976187.96 |  | Import | 234412915.35
|  |  |  | HSD | 20857734.4 |  | Wind | 1362734.4
[5 empty] | Total: | 199,30,36,540 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.8509 | Peak Hr Flow | 913.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 52791618.18 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 18.0743 | Peak Hr Flow | 757.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2124 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.5952 | Peak Hr Flow | 124.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2840 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 42.5204 | Peak Hr Flow | 1794.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 390 |  | 5871
|  |  |  | Chattogram |  | 220 |  | 1484
|  |  |  | Cumilla |  | 250 |  | 1576
|  |  |  | Mymensingh |  | 260 |  | 1278
|  |  |  | Sylhet |  | 0 |  | 551
|  |  |  | Khulna |  | 335 |  | 2018
|  |  |  | Barishal |  | 110 |  | 523
|  |  |  | Rajshahi |  | 240 |  | 1752
|  |  |  | Rangpur |  | 160 |  | 1010
|  |  |  | Total |  | 1965 |  | 16063
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 320
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:01 | 09:12 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to PBS bus DS redhot maintenance | [7 empty] | 18.0MW load interrup.
| 08:01 | 09:14 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to PBS bus DS redhot maintenance | [7 empty] | 18.0MW load interrup.
| 08:38 | 08:46 | Dhamrai 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Kaliakoir end.
| 08:38 | 08:46 | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Kaliakoir end bus shift
| 08:38 | 08:46 | Dhamrai 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Kaliakoir end bus shift.
| 08:38 | 08:46 | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Kaliakoir end bus shift
| 08:40 | 08:50 | Nabinagar 132/33kV S/S T-1 LT Forced S/D Due to কালিয়াকৈর গ্রিড উপকেন্দ্রে Bus Shifting | [7 empty] | 8.0MW load
|  |  | জনিত কারনে অপারেশন করা হয়। | [7 empty] | interrup.
| 08:40 | 08:50 | Nabinagar 132/33kV S/S T-1 HT Forced S/D Due to কালিয়াকৈর গ্রিড উপকেন্দ্রে Bus Shifting | [7 empty] | 8.0MW load
|  |  | জনিত কারনে অপারেশন করা হয়। | [7 empty] | interrup.
| 08:45 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- GT
|  | 08:46 | Kaliakoir 400/230/132kV S/S 132kV Bus 2 is restored.
|  | 08:51 | Ghorasal-Joydeb-B 132kV Ckt-1 is restored.
|  | 08:53 | Ghorasal-Joydeb-B 132kV Ckt-2 is restored.
| 09:00 | 17:47 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Project Work S/D Due to Aviation light replace.
|  | 09:06 | Kaliakoir-Tangail 132kV Ckt-1 is restored.
| 10:13 | 17:37 | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-2 Project Work S/D from Rangpur 132/33kV end
Due to Project work
| 10:22 | 13:12 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T LT Scheduled S/D Due to under ground cable fault
| 10:36 | 19:03 | Savar 132/33kV S/S T-2 LT Scheduled S/D Due to Painting
| 10:37 | 19:00 | Savar 132/33kV S/S T-2 HT Scheduled S/D Due to Painting
| 10:40 | 18:59 | Savar 132/33kV S/S Main Bus-I Scheduled S/D Due to Redhot maintenance
| 11:11 | 13:12 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T HT Scheduled S/D Due to 33 kv under
ground cable fault.
| 11:42 |  | Jamalpur 132/33kV S/S T-3 HT Scheduled S/D Due to Project work.
| 11:42 |  | Jamalpur 132/33kV S/S T-3 LT Scheduled S/D Due to Project work.
| 12:00 |  | Day peak generation 12679 MW
| 12:24 | 13:36 | Barishal 230/132kV S/S ATR-1 LT Scheduled S/D Due to Oil Refill Auxiliary-1 of ATR-1
| 12:24 | 13:38 | Barishal 230/132kV S/S ATR-1 HT Scheduled S/D Due to Oil Refill of Aux-1
|  | 12:33 | Baroaulia-Hathazari 132 kV Ckt-1 is restored.
|  | 12:33 | Baroaulia-Hathazari 132 kV Ckt-1 is restored.
| 12:36 |  | Khulshi-Madunaghat 132kV Ckt-2 Forced S/D from Khulshi 132/33kV end Due to as per
instruction of nldc
| 13:14 |  | Haripur 412 MW CCPP Synchronized with remarks:- ST
| 13:25 | 13:38 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Tripped from Shahjibazar 132/33kV end showing
Distance Relay relays Due to Bad Weather and from Brahmanbaria 132/33kV end showing Distance relays.
| 14:15 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- STG
|  | 14:45 | Gollamari 132/33kV S/S Tr-1 HT is restored.
| 14:58 | 20:16 | Niamatpur 132/33kV S/S 132kV Rahanpur Ckt-1 Project Work S/D Due to Commission work of RTU
| 14:59 | 20:11 | Rahanpur 400/132kV S/S Rahanpur-Niamatpur 132 KV Line Ckt-01 Scheduled S/D
|  | 15:08 | Gollamari 132/33kV S/S Tr-1 LT is restored.
|  | 17:22 | Feni 230/132kV S/S ATR-2 HT is restored.
|  | 17:22 | Feni 230/132kV S/S ATR-2 LT is restored.
| 17:48 | 19:17 | Pabna- Shahjadpur 132kV Ckt-1 Scheduled S/D from Pabna 132/33kV end.
| 21:00 |  | Evening Peak Generation is 14712 MW.
| 22:33 | 23:36 | Rangpur 132/33kV S/S Rangpur-Teesta Solar-1 Tripped showing Distance relay relays Due to
storm and thundering
|  | 00:42 | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) is restored.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 25-04-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 344 | 6418800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 1244800 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 32 | 540517 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 7255876 | Machine Problem
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 33 | 260280 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 144 | 1221120 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 269774 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 269225 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 528600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 411120 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 429120 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 146 | 2824233 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 88 | 1348704 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1113600 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 875520 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 218592 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 194400 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 500 | 12420909.09 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 255 | 5458700 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 108 | 722400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2341 | 44026290.09
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 26377.2 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 110835 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 432000 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 38 | 948180 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5161626 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 968508 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 54 | 1191840 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 67 | 458624 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 22 | 314880 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 37 | 566400 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 18988 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 386400 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 17 | 177865 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1344000 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 424036 | Liquid fuel shortage
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 90 | 657382 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 14634544 | As per Section 13.2(j) PPA, U-1 dispatch suspended
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 92640 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1000 | 19083636.36 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 2352 | 46998761.56
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 196 | 4856000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 357 | 8863100 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 300 | 8068000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 215 | 5657500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1040984 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 140 | 956800 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 648944 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 95 | 1648450 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 192 | 1570560 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 124 | 3595200 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 16 | 401860 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 24 | 194880 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 70 | 569280 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 474009 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1803 | 38545567
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 37 | 1190400 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 48 | 616800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 49 | 1353600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 281310 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 112800 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 148680 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 163 | 3715840
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 58121 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 995000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 726960 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 156 | 3631909.09 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 100 | 2368000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 28 | 706176 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 33 | 1488000 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2399990 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 313104 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7591000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 386 | 5462000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1196 | 25740260.09
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 913 | 20850909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 332640 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 59904 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 44 | 690688 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 6794784 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 671040 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1221 | 29258180 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2428 | 58658145
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 454 | 7207272 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 413952 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 2785000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1214 | 29805090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5352760 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 434400 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 290 | 7025000 | Bad quality coal
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4075 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2341 | 53027549.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 356192 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 31 | 162506 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 379012 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 171 | 4186000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 215 | 5139136 | FGMO not available
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 167 | 4380173 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 348 | 9325454 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 18 | 83525 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 84 | 534544 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 476160 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 54 | 324768 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30480 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 757 | 18074330 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 346496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 752690 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1919 | 44551466
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 160581 | Tripped
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 681561 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 42135.84 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 554748 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 161890 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 944640 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 169 | 2545555.84
Eastern Grid Total |  |  |  |  | 17418.042 | 7855 | 159026718.74
Western Grid Total |  |  |  |  | 11852.195 | 6857 | 158782716.75
National Grid Total |  |  |  |  | 29270.237 | 14712 | 317809435.49
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 25-04-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9640.04 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4458.2 | MW
i) Dhaka area |  |  | 5481.14 |  | MW | i) Khulna area |  |  |  | 1683 | MW
ii) Chattogram area |  |  | 1263.9 |  | MW | ii) Barishal area |  |  |  | 413 | MW
iii) Cumilla area |  |  | 1326 |  | MW | iii) Rajshahi area |  |  |  | 1512.2 | MW
iv) Mymensingh area |  |  | 1018 |  | MW | iv) Rangpur area |  |  |  | 850 | MW
v) Sylhet area |  |  | 551 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14098.24 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 100 | 21:00 | 133 | Natore | 147 | 22:00
2 | AKSML | 16.7 | 09:00 | 68 | Hathazari | 74 | 07:00 | 134 | Nawabganj | 80 | 19:30
3 | Aftabnagar | 44 | 00:00 | 69 | Hatirjheel | 48 | 15:00 | 135 | Netrakona | 112 | 20:00
4 | Agargaon | 126 | 13:00 | 70 | Ishurdi | 74 | 23:00 | 136 | New | 90 | 16:00
5 | Agrabad | 60 | 09:00 | 71 | Jaldhaka | 60 | 23:00 | 137 | Niamatpur | 98 | 05:00
6 | Amnura | 36 | 23:00 | 72 | Jamalpur | 91 | 22:00 | 138 | Noapara | 42 | 18:30
7 | Ashuganj | 84 | 18:30 | 73 | Jashore | 175 | 19:00 | 139 | PHP | 10 | 13:00
8 | BSRM | 199 | 17:00 | 74 | Jhenaidah | 106 | 18:00 | 140 | Pabna | 99 | 19:00
9 | Bagerhat | 77 | 18:00 | 75 | Joydebpur | 166 | 19:30 | 141 | Palashbari | 132 | 22:00
10 | Bajitpur | 79 | 22:00 | 76 | Joypurhat | 60 | 06:00 | 142 | Panchagarh | 43 | 09:00
11 | Bakerganj | 11 | 19:00 | 77 | Juldah | 18 | 14:00 | 143 | Patiya | 12 | 18:30
12 | Bakulia | 89 | 18:30 | 78 | KSRM | 12 | 11:00 | 144 | Patuakhali | 56 | 20:00
13 | Banani | 50.2 | 13:00 | 79 | Kabirpur | 272 | 19:00 | 145 | Payra | 28 | 14:00
14 | Bangabhaban | 9 | 11:00 | 80 | Kachua | 108 | 19:30 | 146 | Postogola | 59 | 01:00
15 | Barapukuria | 55 | 21:00 | 81 | Kaliganj | 27 | 21:00 | 147 | Pubail | 26 | 04:00
16 | Barguna | 20 | 12:00 | 82 | Kallyanpur | 120 | 00:00 | 148 | Purbachal | 37 | 13:00
17 | Barishal | 123 | 12:00 | 83 | Kalurghat | 38 | 09:00 | 149 | Purbasadipur | 110 | 21:00
18 | Barishal-230 | 90 | 14:00 | 84 | Kamrangirchar | 87 | 13:00 | 150 | Rahanpur | 33 | 22:00
19 | Baroaulia | 66 | 00:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 29 | 09:00
20 | Baroirhat | 50 | 23:00 | 86 | Kasba | 34 | 18:30 | 152 | Rajbari | 92 | 18:00
21 | Bashundhara | 218 | 16:00 | 87 | Kazla | 126 | 12:00 | 153 | Rajendrapur | 128 | 20:00
22 | BashundharaCement | 12 | 10:00 | 88 | Keranigonj | 95 | 20:00 | 154 | Rajshahi | 130 | 00:00
23 | Beanibazar | 58 | 21:00 | 89 | Khagrachori | 30 | 19:00 | 155 | Rajshahi-230 | 86 | 20:00
24 | Benapole | 69 | 18:30 | 90 | Khulna | 74 | 18:30 | 156 | Ramganj | 92 | 20:00
25 | Bhaluka | 114 | 20:00 | 91 | Khulshi | 178 | 19:30 | 157 | Rampur | 44 | 00:00
26 | Bhandaria | 48 | 12:00 | 92 | Kishoreganj | 112 | 21:00 | 158 | Rangamati | 13 | 06:00
27 | Bhangura | 38 | 05:00 | 93 | Kodda | 259 | 19:30 | 159 | Rangpur | 132 | 19:30
28 | Bheramara(GK) | 78 | 18:00 | 94 | Kulaura | 40 | 04:00 | 160 | Ruppur | 2.8 | 14:00
29 | Bhulta | 223 | 21:00 | 95 | Kurigram | 52 | 19:30 | 161 | SSM | 1 | 23:00
30 | Bog-Sherpur | 70 | 06:00 | 96 | Kushtia | 164 | 18:00 | 162 | Saidpur | 91 | 11:00
31 | Bogura | 179 | 19:00 | 97 | Laksam | 23 | 00:00 | 163 | Santhia | 32 | 20:00
32 | Borhanuddin | 84 | 15:00 | 98 | Lakshmipur | 26 | 19:00 | 164 | Satkhira | 123 | 18:00
33 | Brahmanbaria | 120 | 23:00 | 99 | Lalbag | 69 | 13:00 | 165 | Satmasjid | 116 | 14:00
34 | Cantonment | 120 | 13:00 | 100 | Lalmonirhat | 47 | 07:00 | 166 | Savar | 228 | 20:00
35 | Chandina | 44 | 23:00 | 101 | MI_Cement | 17.8 | 02:00 | 167 | SevenRings | 21.97 | 13:00
36 | Chandpur | 72 | 21:00 | 102 | Madanganj | 38 | 19:30 | 168 | ShahCement | 43 | 00:00
37 | Chandraghona | 32 | 06:00 | 103 | Madaripur | 118 | 18:00 | 169 | Shahjadpur | 74 | 07:00
38 | Chapai | 66 | 22:00 | 104 | Madartek | 100 | 00:00 | 170 | Shahjibazar | 122 | 18:30
39 | Charsaidpur | 41 | 10:00 | 105 | Madunaghat | 49 | 21:00 | 171 | Shahmirpur | 40 | 22:00
40 | Chauddagram | 59 | 19:30 | 106 | Magura | 73 | 18:30 | 172 | Shariatpur | 89 | 18:30
41 | Chhatak | 32 | 21:00 | 107 | Mahasthangarh | 76 | 23:00 | 173 | Sherpur | 120 | 21:00
42 | Chowmuhani | 134 | 21:00 | 108 | Maijdee | 35 | 05:00 | 174 | Shikalbaha | 27.5 | 20:00
43 | Chuadanga | 119 | 18:00 | 109 | Manikganj | 123 | 08:00 | 175 | Shitalakhya | 91.8 | 12:00
44 | Coxsbazar | 115 | 19:30 | 110 | Maniknagar | 75 | 00:00 | 176 | Sholosohor | 44 | 08:00
45 | Cumilla(N) | 115 | 23:00 | 111 | Matarbari | 44 | 04:00 | 177 | Shyampur | 178 | 13:00
46 | Cumilla(S) | 190 | 14:00 | 112 | Matuail | 82 | 16:00 | 178 | Siddhirganj | 136 | 17:00
47 | Daganbhuiyan | 30 | 03:00 | 113 | Metrorail_Motijheel | 22 | 12:00 | 179 | Sirajganj | 138 | 22:00
48 | Daudkandi | 173 | 19:30 | 114 | Metrorail_Uttara | 6 | 17:00 | 180 | Sonargaon | 163 | 19:30
49 | DhakaUniversity | 82 | 13:00 | 115 | Millgate | 107 | 12:00 | 181 | Sreemongol | 75 | 22:00
50 | Dhamrai | 130 | 20:00 | 116 | Mirpur | 176 | 16:00 | 182 | Sreepur | 113 | 19:30
51 | Dhanmondi | 134 | 13:00 | 117 | Mirsorai | 55 | 12:00 | 183 | Srinagar | 45.6 | 19:00
52 | Dohazari | 78 | 20:00 | 118 | Mirzapur | 38 | 20:00 | 184 | Sunamganj | 56 | 21:00
53 | Faridpur | 167 | 18:00 | 119 | Mithapukur | 54 | 22:00 | 185 | Sylhet | 46 | 00:00
54 | Fatullah | 96 | 16:00 | 120 | Modern | N/A | N/A | 186 | Sylhet-132 | 115 | 16:00
55 | Fenchuganj | 36 | 07:00 | 121 | Mogbazar | 86.2 | 13:00 | 187 | TK | 20 | 06:00
56 | Feni | 98 | 19:30 | 122 | Mongla | 41 | 19:00 | 188 | Tangail | 156 | 21:00
57 | GPH | 21 | 12:00 | 123 | Motijheel | 51 | 16:00 | 189 | Taraganj | 23 | 17:00
58 | Ghatail | 72 | 21:00 | 124 | Muktagacha | 28 | 00:00 | 190 | Tasnim | 14 | 15:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 112 | 21:00 | 191 | Thakurgaon | 85 | 21:00
60 | Ghorashal-230 | 83 | 22:00 | 126 | Muradnagar | 55 | 19:30 | 192 | Tongi | 140 | 13:00
61 | Goalpara | 51 | 19:30 | 127 | Mymensingh | 200 | 19:00 | 193 | Ullahpara | 39 | 19:30
62 | Gollamari | 94 | 18:30 | 128 | Nabinagar | 12 | 19:00 | 194 | Ullon | 69 | 00:00
63 | Gopalganj | 108.2 | 18:30 | 129 | Naogaon | 133 | 23:00 | 195 | Uttara | 103 | 16:00
64 | Gulshan | 124 | 13:00 | 130 | Narail | 64 | 18:30 | 196 | UttaraNew | 63 | 00:00
65 | Halishahar | 105 | 10:00 | 131 | Narinda | 78 | 13:00 | 197 | Zigatola | 92 | 13:00
66 | HaripurSBU | 140 | 19:30 | 132 | Narshingdi | 146 | 23:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 25-04-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13397 | 2438 |  | 15945
1:00 | 12952 | 2720 |  | 15794
2:00 | 12616 | 2754 |  | 15494
3:00 | 12750 | 2531 |  | 15395
4:00 | 12680 | 2502 |  | 15295
5:00 | 12912 | 2252 |  | 15265
6:00 | 12506.05 | 2192 |  | 14796.69
7:00 | 12312.35 | 1998 |  | 14400.35
8:00 | 12295.05 | 1917 |  | 14298.05
9:00 | 12367.74 | 1942 |  | 14396.74
10:00 | 12543.48 | 1920 |  | 14549.48
11:00 | 12774.33 | 2034 |  | 14900.33
12:00 | 12683.45 | 2217 |  | 15000.45
13:00 | 12758.68 | 2287 |  | 15148.6
14:00 | 12813.85 | 2090 |  | 14997.85
15:00 | 12833.14 | 2215 |  | 15148.14
16:00 | 12912.26 | 2337 |  | 15354.43
17:00 | 12965.74 | 2326 |  | 15396.41
18:00 | 13433.55 | 2030 |  | 15554.9
19:00 | 14075 | 2385 |  | 16567.33
19:30 | 14596 | 2018 |  | 16704.81
20:00 | 14602 | 1902 |  | 16589.59
21:00 | 14712 | 1965 |  | 16765
22:00 | 14655 | 1857 |  | 16596
23:00 | 14147 | 1961 |  | 16196
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 25-04-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6794 | 6603 | 13397 | DAILY GENERATION CURVE
00:30 | 6645 | 6529.5 | 13174.5
01:00 | 6496 | 6456 | 12952 | 25-04-2026
01:30 | 6452 | 6332 | 12784
02:00 | 6408 | 6208 | 12616
02:30 | 6456 | 6227 | 12683
03:00 | 6504 | 6246 | 12750
03:30 | 6497 | 6218 | 12715
04:00 | 6490 | 6190 | 12680
04:30 | 6517 | 6279 | 12796
05:00 | 6544 | 6368 | 12912
05:30 | 6352.265 | 6356.76 | 12709.025
06:00 | 6160.53 | 6345.52 | 12506.05
06:30 | 6049.075 | 6360.125 | 12409.2
07:00 | 5937.62 | 6374.73 | 12312.35
07:30 | 5913.92 | 6389.78 | 12303.7
08:00 | 5890.22 | 6404.83 | 12295.05
08:30 | 5960.585 | 6370.81 | 12331.395
09:00 | 6030.95 | 6336.79 | 12367.74
09:30 | 6058.995 | 6396.615 | 12455.61
10:00 | 6087.04 | 6456.44 | 12543.48
10:30 | 6100.035 | 6558.87 | 12658.905
11:00 | 6113.03 | 6661.3 | 12774.33
11:30 | 6013.195 | 6715.695 | 12728.89
12:00 | 5913.36 | 6770.09 | 12683.45
12:30 | 5964.37 | 6756.695 | 12721.065
13:00 | 6015.38 | 6743.3 | 12758.68
13:30 | 6058.76 | 6727.505 | 12786.265
14:00 | 6102.14 | 6711.71 | 12813.85
14:30 | 6145.155 | 6678.34 | 12823.495
15:00 | 6188.17 | 6644.97 | 12833.14
15:30 | 6217.81 | 6654.89 | 12872.7
16:00 | 6247.45 | 6664.81 | 12912.26
16:30 | 6358.535 | 6580.465 | 12939
17:00 | 6469.62 | 6496.12 | 12965.74
17:30 | 6684.23 | 6515.415 | 13199.645
18:00 | 6898.84 | 6534.71 | 13433.55
18:30 | 7131.92 | 6622.355 | 13754.275
19:00 | 7365 | 6710 | 14075
19:30 | 7704 | 6892 | 14596
20:00 | 7760 | 6842 | 14602
20:30 | 7807.5 | 6849.5 | 14657 |  | Executive Engineer
21:00 | 7855 | 6857 | 14712 |  | Network Operation Division
21:30 | 7821 | 6862.5 | 14683.5
22:00 | 7787 | 6868 | 14655
22:30 | 7609 | 6792 | 14401
23:00 | 7431 | 6716 | 14147

## En-Curve
QF-LDC-12
Date | 25-04-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3947 | 1621 | 696 | 0 | 156 | 758 | 40 | 4390 | 0 | 456 | 1029 | 304 | 0 | 0 | 2438 | DAILY ENERGY CURVE
00:30 | 3933 | 1596 | 790 | 0 | 155 | 758 | 40 | 4392 | 0 | 389.5 | 862 | 259 | 0 | 0 | 2579 | 25-04-2026
01:00 | 3919 | 1571 | 884 | 0 | 154 | 758 | 40 | 4394 | 0 | 323 | 695 | 214 | 0 | 0 | 2720
01:30 | 3898 | 1563 | 790.5 | 0 | 155 | 759.5 | 40 | 4387.5 | 0 | 294 | 681.5 | 215 | 0 | 0 | 2737 | Energy Generated | 317.8094 |  | MKWHr
02:00 | 3877 | 1555 | 697 | 0 | 156 | 761 | 40 | 4381 | 0 | 265 | 668 | 216 | 0 | 0 | 2754 | Energy not Served | 52.772 |  | MKWHr
02:30 | 3941.5 | 1597.5 | 697 | 0 | 156 | 758.5 | 40 | 4382.5 | 0 | 257 | 637.5 | 215.5 | 0 | 0 | 2642.5 | Total Energy Requirement | 370.5814 |  | MKWHr
03:00 | 4006 | 1640 | 697 | 0 | 156 | 756 | 40 | 4384 | 0 | 249 | 607 | 215 | 0 | 0 | 2531
03:30 | 4001 | 1642.5 | 696.5 | 0 | 152 | 757 | 40 | 4361.5 | 0 | 249.5 | 599.5 | 215.5 | 0 | 0 | 2516.5
04:00 | 3996 | 1645 | 696 | 0 | 148 | 758 | 40 | 4339 | 0 | 250 | 592 | 216 | 0 | 0 | 2502
04:30 | 3925 | 1745.5 | 790 | 0 | 150 | 759 | 40 | 4339 | 0 | 246.5 | 585.5 | 215.5 | 0 | 0 | 2377
05:00 | 3854 | 1846 | 884 | 0 | 152 | 760 | 40 | 4339 | 0 | 243 | 579 | 215 | 0 | 0 | 2252
05:30 | 3722 | 1804.5 | 884 | 0 | 147 | 760.5 | 40 | 4339 | 9.525 | 230 | 556.5 | 216 | 0 | 0 | 2222
06:00 | 3590 | 1763 | 884 | 0 | 142 | 761 | 40 | 4339 | 19.05 | 217 | 534 | 217 | 0 | 0 | 2192
06:30 | 3499 | 1727.5 | 884.5 | 0 | 142 | 759.5 | 40 | 4340.5 | 64.7 | 205.5 | 529.5 | 216.5 | 0 | 0 | 2095
07:00 | 3408 | 1692 | 885 | 0 | 142 | 758 | 40 | 4342 | 110.35 | 194 | 525 | 216 | 0 | 0 | 1998
07:30 | 3381 | 1714.5 | 884.5 | 0 | 148 | 759.5 | 40 | 4332 | 167.7 | 195 | 466 | 215.5 | 0 | 0 | 1957.5
08:00 | 3354 | 1737 | 884 | 0 | 154 | 761 | 40 | 4322 | 225.05 | 196 | 407 | 215 | 0 | 0 | 1917
08:30 | 3367 | 1730.5 | 884 | 0 | 157 | 759 | 40 | 4301 | 271.895 | 196.5 | 410.5 | 214 | 0 | 0 | 1929.5
09:00 | 3380 | 1724 | 884 | 0 | 160 | 757 | 40 | 4280 | 318.74 | 197 | 414 | 213 | 0 | 0 | 1942
09:30 | 3407 | 1729.5 | 884 | 0 | 160 | 760 | 40 | 4292.5 | 359.61 | 194.5 | 416 | 212 | 0 | 0.5 | 1931
10:00 | 3434 | 1735 | 884 | 0 | 160 | 763 | 40 | 4305 | 400.48 | 192 | 418 | 211 | 0 | 1 | 1920
10:30 | 3430.5 | 1756 | 884 | 0 | 157 | 763.5 | 39.5 | 4307 | 497.405 | 181.5 | 429.5 | 211.5 | 0 | 1.5 | 1977
11:00 | 3427 | 1777 | 884 | 0 | 154 | 764 | 39 | 4309 | 594.33 | 171 | 441 | 212 | 0 | 2 | 2034
11:30 | 3350 | 1756 | 884 | 0 | 163 | 761.5 | 39 | 4307.5 | 616.39 | 184 | 453 | 210 | 0 | 4.5 | 2125.5
12:00 | 3273 | 1735 | 884 | 0 | 172 | 759 | 39 | 4306 | 638.45 | 197 | 465 | 208 | 0 | 7 | 2217
12:30 | 3288 | 1725 | 884 | 0 | 176 | 759.5 | 39.5 | 4301 | 658.565 | 196.5 | 474.5 | 208 | 0 | 10.5 | 2252
13:00 | 3303 | 1715 | 884 | 0 | 180 | 760 | 40 | 4296 | 678.68 | 196 | 484 | 208 | 0 | 14 | 2287
13:30 | 3354 | 1708.5 | 884 | 0 | 185 | 760 | 40 | 4312 | 638.765 | 198 | 482.5 | 208 | 0 | 15.5 | 2188.5
14:00 | 3405 | 1702 | 884 | 0 | 190 | 760 | 40 | 4328 | 598.85 | 200 | 481 | 208 | 0 | 17 | 2090
14:30 | 3497 | 1654.5 | 884 | 0 | 188 | 757.5 | 40 | 4345 | 530.495 | 200 | 503.5 | 205 | 0 | 18.5 | 2152.5
15:00 | 3589 | 1607 | 884 | 0 | 186 | 755 | 40 | 4362 | 462.14 | 200 | 526 | 202 | 0 | 20 | 2215
15:30 | 3596.5 | 1619 | 884 | 0 | 180 | 758 | 40 | 4399.5 | 381.45 | 197.5 | 590.75 | 205 | 0 | 21 | 2276
16:00 | 3604 | 1631 | 884 | 0 | 174 | 761 | 40 | 4437 | 300.76 | 195 | 655.5 | 208 | 0 | 22 | 2337
16:30 | 3627.5 | 1609.5 | 884 | 0 | 171 | 763 | 40 | 4490.5 | 211.5 | 214 | 720.5 | 189 | 0 | 18.5 | 2331.5
17:00 | 3651 | 1588 | 884 | 0 | 168 | 765 | 40 | 4544 | 122.24 | 233 | 785.5 | 170 | 0 | 15 | 2326
17:30 | 3686 | 1541 | 889 | 0 | 143 | 765 | 40 | 4504 | 67.895 | 352 | 1043.25 | 160 | 0 | 8.5 | 2178
18:00 | 3721 | 1494 | 894 | 0 | 118 | 765 | 40 | 4464 | 13.55 | 471 | 1301 | 150 | 0 | 2 | 2030
18:30 | 3722.5 | 1504 | 880.5 | 0 | 122 | 765.5 | 40 | 4579 | 6.775 | 560 | 1423 | 150 | 0 | 1 | 2207.5
19:00 | 3724 | 1514 | 867 | 0 | 126 | 766 | 40 | 4694 | 0 | 649 | 1545 | 150 | 0 | 0 | 2385
19:30 | 3877 | 1605 | 909 | 0 | 118 | 758 | 40 | 4718 | 0 | 684 | 1677 | 210 | 0 | 0 | 2018
20:00 | 3831 | 1619 | 912 | 0 | 116 | 753 | 40 | 4774 | 0 | 685 | 1677 | 195 | 0 | 0 | 1902
20:30 | 3812.5 | 1618 | 912.5 | 0 | 120 | 755 | 39 | 4782.5 | 0 | 718.5 | 1694 | 205 | 0 | 0 | 1933.5
21:00 | 3794 | 1617 | 913 | 0 | 124 | 757 | 38 | 4791 | 0 | 752 | 1711 | 215 | 0 | 0 | 1965
21:30 | 3791 | 1606.5 | 913.5 | 0 | 120 | 761 | 38 | 4795.5 | 0 | 750 | 1692.5 | 215.5 | 0 | 0 | 1911
22:00 | 3788 | 1596 | 914 | 0 | 116 | 765 | 38 | 4800 | 0 | 748 | 1674 | 216 | 0 | 0 | 1857
22:30 | 3745.5 | 1614.5 | 915.5 | 0 | 122 | 765 | 37.5 | 4748 | 0 | 720 | 1516.5 | 216.5 | 0 | 0 | 1909
23:00 | 3703 | 1633 | 917 | 0 | 128 | 765 | 37 | 4696 | 0 | 692 | 1359 | 217 | 0 | 0 | 1961
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 25-04-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 00:00 | 371 | 12:00 | Madunaghat | 399 | 01:00 | 392 | 13:00
Amtali | 409 | 02:00 | 402 | 13:00 | Meghnaghat | 388 | 04:00 | 375 | 12:00
Ashuganj | 412 | 4:00 | 392 | 12:00 | Payra | 410 | 02:00 | 405 | 12:00
Bhulta | 402 | 04:00 | 382 | 12:00 | Rahanpur | 410 | 00:00 | 397 | 05:00
Bibiana | 404 | 03:00 | 393 | 08:00 | Rampal | 401 | 00:00 | 389 | 13:00
BIPTC | 403 | 03:00 | 389 | 16:00
Bogura | 404 | 23:00 | 388 | 05:00
Gopalganj | 396 | 00:00 | 329 | 23:00
Kaliakoir | 383 | 03:00 | 367 | 12:00
Korerhat | 402 | 00:00 | 391 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 04:00 | 219 | 12:00 | Jhenaidah | 228 | 00:00 | 216 | 12:00
AKSML | 234 | 19:00 | 227 | 13:00 | Kachua | 229 | 19:00 | 221 | 12:00
Aminbazar | 230 | 06:00 | 220 | 12:00 | Kaliakoir | 234 | 00:00 | 222 | 12:00
Ashuganj | 231 | 00:00 | 223 | 13:00 | Keranigonj | 230 | 04:00 | 217 | 12:00
Ashuganj-400 | 232 | 4:00 | 220 | 12:00 | Khulna(S) | 229 | 00:00 | 218 | 18:00
Baghabari | 234 | 00:00 | 227 | 06:00 | Korerhat | 228 | 00:00 | 222 | 16:00
Barapukuria | 232 | 23:00 | 206 | 04:00 | Madunaghat | 236 | 01:00 | 230 | 06:00
Barapukuria-230 | 232 | 23:00 | 210 | 4:00 | Madunaghat-400 | 235 | 00:00 | 230 | 12:00
Barishal | 227 | 02:00 | 219 | 12:00 | Maniknagar | 227 | 03:00 | 212 | 12:00
Bheramara | 232 | 00:00 | 221 | 11:00 | Meghnaghat | 233 | 02:00 | 223 | 14:00
Bhulta | 228 | 04:00 | 215 | 12:00 | Meghnaghat-400 | 230 | 04:00 | 218 | 12:00
Bibiana | 235 | 05:00 | 229 | 07:00 | Mirsorai | 233 | 19:00 | 227 | 13:00
BIPTC | 234 | 00:00 | 221 | 11:00 | Naogaon | 218 | 15:00 | 207 | 06:00
Bogura | 236 | 23:00 | 225 | 06:00 | Purbasadipur | 232 | 23:00 | 207 | 04:00
Bogura-400 | 235 | 23:00 | 223 | 05:00 | Rajshahi | 230 | 00:00 | 221 | 06:00
Borhanuddin | 230 | 02:00 | 224 | 22:00 | Rampal | 228 | 00:00 | 219 | 13:00
BSRM | 229 | 00:00 | 223 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 227 | 16:00 | 222 | 10:00 | Rampura | 228 | 04:00 | 212 | 12:00
Cumilla(N) | 227 | 02:00 | 219 | 12:00 | Shikalbaha | 233 | 00:00 | 228 | 13:00
Faridpur | 223 | 02:00 | 213 | 12:00 | Shyampur | 229 | 04:00 | 216 | 13:00
Fenchuganj | 238 | 00:00 | 233 | 18:30 | Siddhirganj | 228 | 00:00 | 215 | 12:00
Feni | 229 | 00:00 | 222 | 13:00 | Sirajgonj | 239 | 00:00 | 230 | 16:00
Ghorashal | 230 | 00:00 | 220 | 11:00 | Sreepur | 229 | 00:00 | 220 | 11:00
Ghorashal-230 | 229 | 04:00 | 215 | 12:00 | Tongi | 230 | 04:00 | 216 | 13:00
Gopalganj | 222 | 02:00 | 215 | 12:00
GPH | 233 | 01:00 | 227 | 13:00
Haripur | 229 | 04:00 | 215 | 12:00
Hasnabad | 229 | 07:00 | 216 | 12:00
Hathazari | 233 | 00:00 | 228 | 11:00
Ishurdi | 234 | 00:00 | 224 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 04:00 | 127 | 12:00 | Madunaghat | 137 | 01:00 | 133 | 13:00
Agargaon | 136 | 04:00 | 127 | 12:00 | Magura | 134 | 04:00 | 123 | 18:00
Agrabad | 135 | 00:00 | 131 | 13:00 | Mahasthangarh | 134 | 23:00 | 122 | 06:00
AKS | 133 | 00:00 | 129 | 13:00 | Maijdee | 127 | 00:00 | 123 | 10:00
Aminbazar | 130 | 06:00 | 123 | 13:00 | Manikganj | 130 | 06:00 | 119 | 16:00
Amnura | 136 | 00:00 | 126 | 06:00 | Maniknagar | 133 | 02:00 | 122 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 131 | 01:00 | 119 | 03:00
Ashuganj-230 | 139 | 06:00 | 135 | 11:00 | Matuail | 132.5 | 06:00 | 124 | 13:00
Bagerhat | 129 | 00:00 | 118 | 18:00 | Metrorail_Motijheel | 133 | 02:00 | 122 | 12:00
Bajitpur | 133 | 01:00 | 128 | 11:00 | Metrorail_Uttara | 128 | 00:00 | 122 | 12:00
Bakerganj | 131 | 00:00 | 127 | 13:00 | Millgate | 134 | 03:00 | 123 | 16:00
Bakulia | 136 | 00:00 | 132 | 04:00 | Mirpur | 130 | 05:00 | 121 | 14:00
Banani | 138 | 03:00 | 127 | 12:00 | Mirzapur | 132 | 00:00 | 125 | 15:00
Bangabhaban | 134 | 03:00 | 122 | 12:00 | Mithapukur | 140 | 00:00 | 119 | 05:00
Barapukuria | 139 | 23:00 | 121 | 04:00 | MI_Cement | 137 | 01:00 | 127 | 12:00
Barguna | 132 | 02:00 | 126 | 13:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 00:00 | 125 | 12:00 | Mogbazar | 139 | 03:00 | 130 | 11:00
Barishal-230 | 132 | 02:00 | 125 | 13:00 | Mongla | 130 | 01:00 | 118 | 18:00
Baroaulia | 136 | 00:00 | 128 | 20:00 | Motijheel | 134 | 03:00 | 122 | 12:00
Baroirhat | 131 | 00:00 | 127 | 12:00 | Muktagacha | 133 | 13:00 | 124 | 21:00
Bashundhara | 138 | 04:00 | 124 | 12:00 | Munshiganj | 130 | 00:00 | 122 | 12:00
BashundharaCement | 132 | 00:00 | 123 | 12:00 | Muradnagar | 129 | 00:00 | 121 | 20:00
Beanibazar | 133 | 14:00 | 123 | 21:00 | Mymensingh | 133 | 11:00 | 119 | 20:00
Benapole | 129 | 02:00 | 118 | 18:00 | Nabinagar | 136 | 05:00 | 128 | 08:00
Bhaluka | 132 | 00:00 | 127 | 08:00 | Naogaon | 134 | 00:00 | 121 | 06:00
Bhandaria | 128 | 01:00 | 120 | 12:00 | Narail | 134 | 00:00 | 119 | 18:30
Bhangura | 133 | 00:00 | 127 | 05:00 | Narinda | 133 | 2:00 | 122 | 12:00
Bheramara | 136 | 00:00 | 131 | 10:00 | Narshingdi | 135 | 04:00 | 118 | 13:00
Bheramara(GK) | 136 | 00:00 | 131 | 11:00 | Natore | 133 | 00:00 | 125 | 06:00
Bhulta | 127 | 06:00 | 118 | 12:00 | Nawabganj | 139 | 04:00 | 131 | 12:00
Bog-Sherpur | 134 | 00:00 | 126 | 06:00 | Netrakona | 130 | 12:00 | 118 | 20:00
Bogura | 136 | 00:00 | 127 | 05:00 | New | 134 | 00:00 | 124 | 15:00
Bogura-230 | 136 | 00:00 | 127 | 05:00 | Niamatpur | 132 | 23:00 | 128 | 04:00
Brahmanbaria | 134 | 07:00 | 126 | 21:00 | Noapara | 131 | 00:00 | 119 | 18:30
Cantonment | 136 | 06:00 | 126 | 13:00 | Pabna | 134 | 00:00 | 128 | 06:00
Chandina | 131 | 00:00 | 126 | 12:00 | Palashbari | 139 | 00:00 | 118 | 04:00
Chandpur | 134 | 19:00 | 126 | 05:00 | Panchagarh | 139 | 00:00 | 124 | 06:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 136 | 00:00 | 133 | 13:00 | Patiya | 137 | 01:00 | 131 | 07:00
Chapai | 133 | 20:00 | 128 | 05:00 | Patuakhali | 130 | 00:00 | 127 | 13:00
Charsaidpur | 132 | 02:00 | 123 | 12:00 | Payra | 135 | 02:00 | 131 | 12:00
Chauddagram | 129 | 01:00 | 125 | 11:00 | PHP | 130 | 00:00 | 126 | 13:00
Chhatak | 131 | 13:00 | 123 | 21:00 | Postogola | 139 | 03:00 | 129 | 14:00
Chowmuhani | 127 | 00:00 | 123 | 14:00 | Pubail | 138 | 04:00 | 128 | 11:00
Chuadanga | 131 | 03:00 | 119 | 18:00 | Purbachal | 138 | 03:00 | 123 | 16:00
Coxsbazar | 127 | 01:00 | 120 | 06:00 | Purbasadipur | 135 | 23:00 | 119 | 04:00
Cumilla(N) | 131 | 00:00 | 126 | 12:00 | Rahanpur | 135 | 00:00 | 131 | 03:00
Cumilla(S) | 130 | 00:00 | 121 | 13:00 | Rahanpur-400 | 135 | 00:00 | 131 | 05:00
Daganbhuiyan | 128 | 00:00 | 124 | 13:00 | Rahim | 133 | 03:00 | 124 | 12:00
Daudkandi | 127 | 00:00 | 119 | 19:30 | Rajbari | 128 | 02:00 | 120 | 18:00
DhakaUniversity | 138 | 03:00 | 127 | 12:00 | Rajendrapur | 134 | 00:00 | 126 | 08:00
Dhamrai | 136 | 06:00 | 128 | 14:00 | Rajshahi | 130 | 00:00 | 124 | 11:00
Dhanmondi | 138 | 05:00 | 127.5 | 12:00 | Rajshahi-230 | 132 | 00:00 | 122 | 06:00
Dohazari | 133 | 00:00 | 128 | 05:00 | Ramganj | 130 | 19:00 | 122 | 14:00
Faridpur | 129 | 02:00 | 124 | 12:00 | Rampur | 135 | 21:00 | 131 | 09:00
Fatullah | 138 | 04:00 | 122 | 13:00 | Rampura | 138 | 04:00 | 127 | 12:00
Fenchuganj | 136 | 14:00 | 131 | 21:00 | Rangamati | 135 | 00:00 | 133 | 05:00
Feni | 129 | 02:00 | 122 | 07:00 | Rangpur | 138 | 23:00 | 120 | 06:00
Feni-230 | 129 | 01:00 | 124 | 13:00 | Ruppur | 136 | 00:00 | 131 | 06:00
Ghatail | 130 | 06:00 | 123 | 02:00 | Saidpur | 137 | 23:00 | 123 | 01:00
Ghorashal | 138 | 00:00 | 131 | 09:00 | Santhia | 134 | 00:00 | 130 | 10:00
Goalpara | 134 | 00:00 | 127 | 20:00 | Satkhira | 131 | 00:00 | 119 | 18:00
Gollamari | 134 | 00:00 | 127 | 18:00 | Satmasjid | 135 | 02:00 | 125 | 13:00
Gopalganj | 132 | 00:00 | 125 | 18:30 | Savar | 129 | 18:30 | 120 | 13:00
Gopalganj-400 | 132 | 00:00 | 128 | 12:00 | SevenRings | 138 | 06:00 | 130 | 12:00
Gulshan | 137 | 04:00 | 127 | 12:00 | ShahCement | 132 | 02:00 | 123 | 12:00
Halishahar | 137 | 01:00 | 131 | 13:00 | Shahjadpur | 136 | 00:00 | 133 | 06:00
Haripur | 134 | 04:00 | 124 | 12:00 | Shahjibazar | 135 | 14:00 | 123 | 22:00
HaripurSBU | 132 | 00:00 | 124 | 12:00 | Shahmirpur | 136 | 00:00 | 133 | 10:00
Hasnabad | 138 | 00:00 | 129 | 13:00 | Shariatpur | 131 | 02:00 | 125 | 13:00
Hathazari | 137 | 18:30 | 134 | 10:00 | Sherpur | 135 | 11:00 | 115 | 02:00
Hatirjheel | 138 | 04:00 | 128 | 13:00 | Shikalbaha | 127 | 02:00 | 122 | 10:00
Ishurdi | 137 | 00:00 | 132 | 06:00 | Shikalbaha-230 | 138 | 00:00 | 133 | 13:00
Jaldhaka | 134 | 23:00 | 116 | 05:00 | Shitalakhya | 137 | 01:00 | 127 | 12:00
Jamalpur | 135 | 11:00 | 117 | 04:00 | Sholosohor | 136 | 00:00 | 133 | 09:00
Jashore | 130 | 01:00 | 120 | 18:00 | Shyampur | 130 | 01:00 | 122 | 13:00
Jhenaidah | 135 | 00:00 | 121 | 18:00 | Shyampur-230 | 132 | 04:00 | 123 | 13:00
Jhenaidah-230 | 136 | 02:00 | 127 | 18:00 | Siddhirganj | 133 | 06:00 | 124 | 14:00
Joydebpur | 135 | 18:00 | 125 | 14:00 | Sirajganj | 130 | 00:00 | 123 | 06:00
Joypurhat | 132 | 00:00 | 120 | 06:00 | Sonargaon | 131 | 00:00 | 123 | 12:00
Juldah | 136 | 00:00 | 132 | 14:00 | Sreemongol | 134 | 14:00 | 125 | 21:00
Kabirpur | 136 | 22:00 | 120 | 16:00 | Sreepur | 136 | 00:00 | 129 | 15:00
Kachua | 131 | 19:00 | 126 | 10:00 | Srinagar | 139 | 05:00 | 131 | 12:00
Kaliakoir | 138 | 02:00 | 130 | 12:00 | SSM | 140 | 00:00 | 138 | 10:00
Kaliganj | 133 | 00:00 | 125 | 18:00 | Sunamganj | 130 | 13:00 | 121 | 21:00
Kallyanpur | 130 | 03:00 | 122 | 13:00 | Sylhet | 133 | 14:00 | 127 | 21:00
Kalurghat | 137 | 19:00 | 134 | 05:00 | Sylhet-132 | 132 | 14:00 | 127 | 20:00
Kamrangirchar | 139 | 07:00 | 120 | 12:00 | Tangail | 130 | 18:30 | 123 | 15:00
Kaptai | N/A | N/A | N/A | N/A | Taraganj | 138 | 23:00 | 118 | 03:00
Kasba | 129 | 00:00 | 120 | 20:00 | Tasnim | 132 | 02:00 | 123 | 12:00
Kazla | 133 | 04:00 | 122 | 13:00 | Thakurgaon | 138 | 23:00 | 120 | 04:00
Keranigonj | 140 | 04:00 | 131 | 12:00 | TK | 136 | 00:00 | 131 | 10:00
Khagrachori | 135 | 01:00 | 131 | 13:00 | Tongi | 137 | 04:00 | 127 | 13:00
Khulna | 134 | 00:00 | 124 | 18:00 | Ullahpara | 132 | 00:00 | 125 | 06:00
Khulna(S) | 135 | 00:00 | 126 | 18:00 | Ullon | 138 | 04:00 | 127 | 12:00
Khulshi | 134 | 00:00 | 130 | 13:00 | Uttara | 134 | 03:00 | 122 | 16:00
Kishoreganj | 131 | 00:00 | 125 | 08:00 | UttaraNew | 128 | 00:00 | 122 | 12:00
Kodda | 137 | 22:00 | 125 | 12:00 | Zigatola | 139 | 03:00 | 130 | 13:00
Korerhat | 133 | 00:00 | 127 | 16:00
KSRM | 135 | 00:00 | 131 | 11:00
Kulaura | 135 | 14:00 | 130 | 21:00
Kurigram | 138 | 23:00 | 120 | 11:00
Kushtia | 132 | 00:00 | 125 | 18:00
Laksam | 131 | 19:00 | 125 | 14:00
Lakshmipur | 127 | 00:00 | 123 | 13:00
Lalbag | 139 | 03:00 | 130 | 12:00
Lalmonirhat | 132 | 09:00 | 117 | 06:00
Madanganj | 132 | 05:00 | 123 | 12:00
Madaripur | 132 | 00:00 | 128 | 12:00
Madartek | 137 | 03:00 | 127 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division