## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-01-02 | Wednesday
|  | Date (day): | 2019-01-02 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10890 | MW |  |  | (b) At Evening Peak Hour : |  | 12487 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-01-01 | 2019-01-02 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit #1 Under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 88 | 0 | 0 |  | 170 | Under maint.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 380 | 300 | 350 | 350
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 35 | 40 | 40 | 38 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 87 | 103 | 100 | 100
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 370 | 300 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 360 | 307 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 330 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 |  |  | Reserve
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 1 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 180 | 125 | 140 | 200 |  |  | FGMO
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 135 | 146 | 200 | 200
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
21 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 56 | 102 | 102
22 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 48 | 47 | 48 |  | 3 | Engoine problem
23 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 18 | 54 | 54 | 54
24 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
25 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
26 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 36 | 36 | 36 |  | 19 | Engine problem
27 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 8 | 47 | 8 | 46 |  | 62 | Engine problem
28 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 57 | 58 | 58 |  | 22 | Engine problem
29 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
30 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 43 | 42 | 43 | 43 |  | 9 | Engine problem
32 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
33 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 190 | 0 | 300
34 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 0 | 79 | 130 | 130 |  | 19 | Engine problem
| Dhaka area Total |  |  |  |  | 6034 | 5798 | 2159 | 2552 | 3822 | 4421 | 298 | 534
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 140 | 120 | 150 | 30 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.5 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 48 | 50 | 50
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 70 | 70 |  | 160 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 100 | 150 | 150 |  |  | FGMO
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 24 | 50 | 50 | 50 |  | 11
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 72 | 72
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 22 | 68 | 68
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 20 | 90 | 90 |  | 10 | Engine problem
50 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 30 | 92 | 100 | 100
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 20 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 14 | 35 | 20 | 20
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 13 | 90 | 100 |  |  | Engine problem
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 409.5 | 605 | 947 | 967 | 210 | 446
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 120 | 120 | 120 | 120 | 9 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 135 | 80 | 120 | 120 | 14 |  | Gas shortage
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 193 | 195 | 221 | 221 |  |  | FGMO
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 260 | 260 |  | 100 | ST Under maint.
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 323 | 290 | 360 | 360 |  |  | FGMO
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 40 | 40 | 40 |  | 5 | Engine problem
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 30 | 30 | 30 | 25 |  | Gas shortage
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas Shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 45 | 45 | 51 | 51 | 6
62 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 100 | 150 | 150
63 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 85 | 10 | 85 | 85
64 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 40
65 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100 |  | 63 | FGMO & STG under maint.
66 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 0 | 68 | 180 | 180
67 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
68 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 90 | 118 | 82 | 112
69 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 12 | 25 | 0 | 33
70 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
71 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 17 | 22 | 22 | 22
72 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1230 | 1286 | 1919 | 2222 | 424 | 168
73 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 162 | 169 | 210 | 170 | 33 |  | Gas shortage
74 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
75 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 64 | 79 | 79 |  | 16 | Engine problem.
76 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.1 | 0 | 2 | 0
77 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 7 | 100 | 100 | 200
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 191.1 | 355 | 413 | 471 | 33 | 16
78 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 26 | 26 | 57 | 57
79 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 54 | 63 | 63
80 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 10 | 100 | 163 | 163
81 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 146 | 214 | 230 | 230 |  |  | FGMO
82 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 2 | 53 | 51 | 51
83 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 0 | 21 | 21 | 21 |  | 23 | Engine problem
84 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
85 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 56 | 66 | 66 |  |  | FGMO
86 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 20 | 10 | 86 | 86
87 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 47 | 49 | 50 | 50
88 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 118 | 78 | 78 | 140
89 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
90 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 25 | 25 | 50 | 50
91 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 25 | 0 | 25
92 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 300 | 341 | 341 |  |  | FGMO
| Bibiyana-3 285MW |  | Gas | PDB | 285 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
93 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 9 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 793 | 1031 | 1297 | 1384 | 0 | 23
94 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 529 | 669 | 538 | 685
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
95 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 115 | 115
96 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 0 | 40
97 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
98 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 34 | 0 | 80
99 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 360 | 300 | 410 | 410
100 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
102 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 70 | 105 | 105
| Khulna Area Total |  |  |  |  | 2223 | 2209 | 897 | 1153 | 1308 | 1621 | 0 | 0
103 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
104 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
105 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 16 | 23 | 25 | 25 |  | 8 | Engine problem
106 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 189 | 190 | 194 | 194
107 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 50 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 255 | 326 | 424 | 454 | 0 | 8
108 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage.
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 100 | 80 | 100 |  | 0
109 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 8 | 0 | 50
110 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40
111 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 50 | 50
112 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 50 | 50
113 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 50 | 50
114 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
115 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 186 | 178 | 220 | 220 |  |  | FGMO
116 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 141 | 141 | 0 | 0 | 0 | 0 | 141 |  | Gas shortage.
117 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 0 | 0 | 0 | 0 | 282 |  | Gas shortage.
118 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 0 | 35
119 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
120 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 5 | 5 | 5 | 5 |  | 5 | Engine problem
121 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
122 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 34 | 43 | 43 |  |  | Engine problem
123 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 65 | 90 | 100
| Rajshahi Area Total |  |  |  |  | 1556 | 1546 | 226 | 512 | 621 | 776 | 704 | 5
124 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint.
125 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 139 | 139 | 139 | 139 | 135 |  | Coal shortage
126 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 17
127 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 15 | 0 | 15
| Rangpur Area Total |  |  |  |  | 564 | 484 | 139 | 171 | 139 | 171 | 220 | 85
| Total |  |  |  |  | 17685 | 17142 | 6299.6 | 7991 | 10890 | 12487 | 1889 | 1285
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5940.1184 | 7535 | 10268.5709 | 11774.4394
A. |  | 2019-01-01 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 7991 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 4350 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 7991 | MW
3 | Day peak Generation : |  |  | 6299.6 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7535 | MW
4 | Evening peak Generation : |  |  | 7991 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 143.0383 | MKWHr | By Solar | 0.147 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 115.511 | MKWHr |  | By Oil: | 8.3317 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.8569 | MKWHr |  | By Hydro: | 0.951 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1889 | MW | Dhaka | 2642 | 2642 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1285 | MW | Chittagong | 847 | 847 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3174 | MW | Khulna | 965 | 965 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1018.24 | MMCFD |  |  | Rajshahi | 799 | 799 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 83979336.842 | ii) Oil : | Taka | 59688613.37 | Comilla | 668 | 668 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 15819312.89 | Total | Taka | 159487263.102 | Mymensingh | 574 | 574 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 3.8825 | MKWHr. | Sylhet | 308 | 308 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -610 | MW at | 19:00 | hrs | Barisal | 194 | 194 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -610 | MW at | 18:30 | hrs | Rangpur | 538 | 538 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 27.7° C |  |  | Total | 7535 | 7535 |  | 0
B. |  | 2019-01-02 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 25.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12487 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6600 | MW
4 | Reserve(Generation end) |  |  |  | 4187 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 148.5694 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4674 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 12.192 | MKWHr. | ii) HVDC Flow at Peak Time |  | 669 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0486 | MKWHr. | iii) Maximum HVDC Flow : |  | 671 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.47 |  | (b) Today: | 98.39 |  | (c) Rule Curve: |  | 102.81
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-01-01
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 0 | 220 | 0 | 0 | 350 | 306 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 150 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 30 | 33 | 0 | 0 | 40 | 0 | 0 | 100 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 80 | 80 | 0 | 250 | 184 | 8 | 100 | 10 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 74 | 168 | 0 | 0 | 0 | 10 | 10 | 2 | 0 | 0 | 138 | 40 | 5 | 2 | 50 | 0 | 5 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 349 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 12 | 0 | 0 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 68 | 140 | 0 | 0 | 0 | 0 | 161 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3578 | 1406 | 4984 | 3233 | 349 | 1073 | 7 | 208 | 40 | 0 | 74 | 0 | 0 | 98.48
2:00 | 35 | 0 | 0 | 0 | 220 | 0 | 0 | 352 | 305 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 120 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 30 | 33 | 0 | 0 | 40 | 0 | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 80 | 80 | 0 | 250 | 187 | 8 | 100 | 10 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 68 | 168 | 0 | 0 | 0 | 10 | 10 | 2 | 0 | 0 | 146 | 40 | 5 | 2 | 50 | 0 | 5 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 348 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 68 | 140 | 0 | 0 | 0 | 0 | 139 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3454 | 1190 | 4644 | 2947 | 348 | 1026 | 7 | 208 | 40 | 0 | 68 | 0 | 0 | 98.48
3:00 | 35 | 0 | 0 | 0 | 220 | 0 | 0 | 345 | 277 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 120 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 30 | 33 | 0 | 0 | 40 | 0 | 0 | 100 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 80 | 80 | 0 | 250 | 155 | 8 | 100 | 10 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 64 | 170 | 0 | 0 | 0 | 10 | 10 | 2 | 0 | 0 | 138 | 40 | 5 | 2 | 50 | 0 | 5 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 348 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 67 | 140 | 0 | 0 | 0 | 0 | 136 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3351 | 1136 | 4487 | 2828 | 348 | 993 | 7 | 207 | 40 | 0 | 64 | 0 | 0 | 98.48
4:00 | 35 | 0 | 0 | 0 | 220 | 0 | 0 | 345 | 276 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 120 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 30 | 33 | 0 | 0 | 40 | 0 | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 80 | 80 | 0 | 250 | 161 | 8 | 100 | 10 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 60 | 139 | 0 | 0 | 0 | 10 | 10 | 2 | 0 | 0 | 146 | 40 | 5 | 2 | 50 | 0 | 5 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 348 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 136 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3330 | 1069 | 4399 | 2807 | 348 | 998 | 7 | 139 | 40 | 0 | 60 | 0 | 0 | 98.47
5:00 | 35 | 0 | 0 | 0 | 220 | 0 | 0 | 350 | 276 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 120 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 30 | 33 | 0 | 0 | 40 | 0 | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 80 | 80 | 0 | 220 | 168 | 8 | 100 | 10 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 60 | 134 | 0 | 0 | 0 | 10 | 10 | 2 | 0 | 0 | 147 | 40 | 5 | 2 | 50 | 0 | 5 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 348 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 139 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3278 | 1072 | 4350 | 2788 | 348 | 968 | 7 | 139 | 40 | 0 | 60 | 0 | 0 | 98.47
6:00 | 35 | 0 | 0 | 0 | 250 | 0 | 0 | 370 | 336 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 120 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 30 | 33 | 0 | 0 | 42 | 0 | 0 | 100 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 80 | 80 | 0 | 250 | 168 | 8 | 100 | 10 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 66 | 136 | 0 | 0 | 0 | 10 | 10 | 2 | 0 | 0 | 152 | 40 | 5 | 2 | 50 | 0 | 5 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 348 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 146 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3529 | 1139 | 4668 | 2942 | 348 | 1124 | 7 | 139 | 42 | 0 | 66 | 0 | 0 | 98.47
7:00 | 35 | 0 | 0 | 0 | 250 | 0 | 0 | 367 | 336 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 167 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 0 | 0 | 40 | 0 | 0 | 100 | 0 | 0 | 0 | 145 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 80 | 80 | 0 | 250 | 202 | 8 | 100 | 35 | 5 | 5 | 5 | 5 | 0 | 0 | 20 | 0 | 0 | 15 | 66 | 135 | 0 | 22 | 0 | 10 | 10 | 2 | 0 | 0 | 143 | 40 | 5 | 2 | 50 | 0 | 5 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1.6 | 10 | 0 | 0 | 0 |  | 348 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 156 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 3741.6 | 1176 | 4917.6 | 3182 | 348 | 1123 | 18 | 139 | 40 | 0 | 66 | 1.6 | 0 | 98.46
8:00 | 35 | 0 | 0 | 0 | 280 | 0 | 0 | 370 | 336 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 180 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 145 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 22 | 21 | 0 | 80 | 80 | 0 | 257 | 205 | 8 | 100 | 36 | 5 | 5 | 5 | 40 | 0 | 0 | 20 | 8 | 0 | 15 | 76 | 169 | 0 | 22 | 0.5 | 10 | 10 | 2 | 0 | 0 | 148 | 40 | 20 | 30 | 70 | 0 | 25 | 0 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7.52 | 30 | 0 | 0 | 0 |  | 530 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 186 | 0 | 13 | 0 | 0 | 0 | 0 | 0 |  | 4072.02 | 1456 | 5528.02 | 3455 | 530 | 1230 | 50 | 139 | 40 | 0 | 76 | 8.02 | 0 | 98.46
9:00 | 35 | 0 | 0 | 0 | 320 | 12 | 0 | 360 | 337 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 150 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 39 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 2 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 145 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 0 | 100 | 100 | 0 | 287 | 186 | 8 | 100 | 40 | 30 | 5 | 30 | 40 | 0 | 0 | 22 | 8 | 8 | 15 | 80 | 167 | 0 | 22 | 1.3 | 10 | 10 | 2 | 0 | 0 | 141 | 56 | 20 | 48 | 68 | 0 | 25 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 13.45 | 30 | 0 | 0 | 0 |  | 532 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 190 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 5 | 5 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 188 | 0 | 52 | 0 | 0 | 0 | 0 | 0 |  | 4297.75 | 1597 | 5894.75 | 3554 | 532 | 1358 | 177 | 139 | 40 | 0 | 80 | 14.75 | 0 | 98.46
10:00 | 35 | 0 | 0 | 0 | 320 | 13 | 0 | 345 | 371 | 0 | 0 | 390 | 0 | 0 | 0 | 0 | 120 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 24 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 145 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 0 | 100 | 100 | 0 | 287 | 177 | 8 | 100 | 40 | 30 | 5 | 45 | 40 | 0 | 0 | 22 | 8 | 8 | 13 | 84 | 165 | 0 | 22 | 1.8 | 10 | 10 | 2 | 0 | 10 | 141 | 51 | 20 | 48 | 67 | 0 | 24 | 0 | 280 | 0 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 17.8 | 30 | 0 | 0 | 0 |  | 531 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 179 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 5 | 5 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 180 | 0 | 52 | 0 | 0 | 0 | 0 | 0 |  | 4299.6 | 1514 | 5813.6 | 3435 | 531 | 1394 | 171 | 139 | 40 | 0 | 84 | 19.6 | 0 | 98.46
11:00 | 35 | 0 | 0 | 0 | 340 | 13 | 0 | 360 | 362 | 0 | 0 | 390 | 0 | 0 | 0 | 0 | 120 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 18 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 37 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 140 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 0 | 120 | 120 | 0 | 323 | 193 | 8 | 100 | 40 | 30 | 5 | 45 | 40 | 0 | 0 | 22 | 8 | 8 | 17 | 88 | 162 | 0 | 20 | 2.1 | 10 | 20 | 2 | 0 | 10 | 150 | 55 | 20 | 48 | 87 | 0 | 24 | 0 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 19.11 | 30 | 0 | 0 | 0 |  | 531 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 186 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 5 | 5 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 179 | 0 | 50 | 0 | 0 | 0 | 0 | 0 |  | 4469.21 | 1509 | 5978.21 | 3618 | 531 | 1401 | 140 | 139 | 40 | 0 | 88 | 21.21 | 0 | 98.45
12:00 | 35 | 0 | 0 | 0 | 380 | 87 | 0 | 370 | 360 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 135 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 18 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 43 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 140 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 0 | 120 | 135 | 0 | 323 | 193 | 8 | 100 | 40 | 30 | 5 | 45 | 85 | 0 | 0 | 19 | 8 | 12 | 17 | 90 | 162 | 0 | 20 | 2.1 | 26 | 20 | 2 | 0 | 10 | 146 | 61 | 20 | 47 | 118 | 0 | 25 | 0 | 310 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 19.5 | 30 | 0 | 0 | 0 |  | 529 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 189 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 5 | 5 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 186 | 0 | 50 | 0 | 0 | 0 | 0 | 0 |  | 4782.6 | 1517 | 6299.6 | 3773 | 529 | 1561 | 146 | 139 | 40 | 0 | 90 | 21.6 | 0 | 98.45
13:00 | 35 | 0 | 0 | 0 | 330 | 102 | 15 | 350 | 336 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 195 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 18 | 0 | 0 | 22 | 25 | 32 | 33 | 33 | 8 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 140 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 18 | 0 | 120 | 100 | 0 | 294 | 172 | 8 | 100 | 40 | 30 | 5 | 45 | 85 | 0 | 0 | 22 | 8 | 25 | 0 | 92 | 161 | 0 | 20 | 2 | 26 | 20 | 50 | 21 | 10 | 140 | 52 | 50 | 47 | 123 | 0 | 25 | 8 | 250 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 18.4 | 70 | 0 | 0 | 0 |  | 528 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 152 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 5 | 5 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 177 | 0 | 50 | 0 | 0 | 0 | 0 | 0 |  | 4764.4 | 1550 | 6314.4 | 3626 | 528 | 1648 | 218 | 139 | 40 | 3 | 92 | 20.4 | 0 | 98.45
14:00 | 35 | 7 | 0 | 0 | 320 | 102 | 35 | 300 | 306 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 130 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 18 | 0 | 0 | 22 | 25 | 32 | 33 | 33 | 8 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 100 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 18 | 0 | 120 | 80 | 0 | 268 | 171 | 8 | 102 | 40 | 30 | 5 | 45 | 40 | 0 | 0 | 22 | 8 | 25 | 22 | 94 | 161 | 0 | 22 | 1.6 | 26 | 32 | 50 | 21 | 10 | 215 | 50 | 50 | 48 | 97 | 0 | 25 | 9 | 250 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 16.3 | 70 | 0 | 0 | 0 |  | 531 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 188 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 5 | 5 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 137 | 0 | 50 | 0 | 0 | 0 | 0 | 0 |  | 4555.9 | 1513 | 6068.9 | 3470 | 531 | 1538 | 235 | 139 | 40 | 4 | 94 | 17.9 | 0 | 98.45
15:00 | 35 | 0 | 0 | 0 | 330 | 99 | 35 | 300 | 303 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 140 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 18 | 0 | 0 | 22 | 25 | 32 | 33 | 33 | 8 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 100 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 0 | 120 | 80 | 0 | 268 | 186 | 8 | 96 | 40 | 30 | 5 | 45 | 40 | 0 | 0 | 22 | 8 | 25 | 22 | 94 | 161 | 0 | 22 | 1.2 | 26 | 32 | 50 | 21 | 20 | 209 | 40 | 50 | 48 | 97 | 0 | 25 | 9 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 12.2 | 70 | 0 | 0 | 0 |  | 531 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 40 | 162 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 5 | 5 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 134 | 0 | 50 | 0 | 0 | 0 | 0 | 0 |  | 4564.4 | 1483 | 6047.4 | 3447 | 531 | 1553 | 224 | 139 | 40 | 6 | 94 | 13.4 | 0 | 98.44
16:00 | 35 | 0 | 0 | 0 | 250 | 101 | 35 | 300 | 306 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 140 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 18 | 0 | 0 | 22 | 25 | 32 | 33 | 33 | 8 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 100 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 0 | 120 | 80 | 0 | 268 | 227 | 8 | 100 | 40 | 30 | 5 | 45 | 40 | 0 | 0 | 22 | 8 | 25 | 20 | 92 | 162 | 0 | 22 | 0.5 | 25 | 32 | 52 | 21 | 60 | 212 | 54 | 50 | 46 | 100 | 0 | 25 | 9 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 6.9 | 70 | 0 | 0 | 0 |  | 531 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 40 | 187 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 5 | 5 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 134 | 0 | 51 | 0 | 0 | 0 | 0 | 0 |  | 4562.4 | 1441 | 6003.4 | 3425 | 531 | 1571 | 192 | 139 | 40 | 6 | 92 | 7.4 | 0 | 98.44
17:00 | 35 | 0 | 0 | 0 | 250 | 103 | 35 | 270 | 303 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 140 | 0 | 80 | 0 | 0 | 7 | 0 | 0 | 9 | 0 | 6 | 18 | 36 | 17 | 22 | 25 | 32 | 33 | 33 | 32 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 100 | 0 | 0 | 42 | 0 | 0 | 8 | 78 | 0 | 22 | 27 | 0 | 120 | 80 | 0 | 268 | 185 | 8 | 100 | 40 | 30 | 5 | 45 | 10 | 0 | 0 | 22 | 8 | 25 | 20 | 96 | 207 | 0 | 22 | 0 | 26 | 54 | 53 | 21 | 100 | 209 | 40 | 10 | 45 | 100 | 0 | 24 | 9 | 310 | 24 | 8 | 0 | 37 | 0 | 0 | 7 | 0 | 0 | 0.67 | 0 | 5 | 6 | 0 |  | 589 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 23 | 24 | 40 | 145 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 6 | 0 | 0 | 8 | 9 | 22 | 5 | 5 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 134 | 0 | 50 | 0 | 0 | 0 | 0 | 0 |  | 4632.67 | 1525 | 6157.67 | 3304 | 589 | 1559 | 362 | 139 | 40 | 68 | 96 | 0.67 | 0 | 98.44
18:00 | 35 | 18 | 0 | 0 | 300 | 103 | 35 | 270 | 307 | 0 | 0 | 330 | 0 | 0 | 0 | 25 | 120 | 0 | 120 | 0 | 0 | 58 | 0 | 0 | 47 | 0 | 24 | 54 | 54 | 36 | 22 | 25 | 18 | 33 | 33 | 42 | 0 | 40 | 0 | 0 | 120 | 25 | 0 | 0 | 100 | 0 | 0 | 50 | 25 | 68 | 60 | 92 | 46 | 22 | 37 | 0 | 120 | 80 | 0 | 268 | 185 | 8 | 100 | 40 | 30 | 5 | 45 | 10 | 8 | 0 | 22 | 8 | 25 | 22 | 118 | 183 | 19 | 22 | 0 | 26 | 54 | 53 | 21 | 100 | 208 | 52 | 10 | 49 | 78 | 0 | 25 | 9 | 260 | 25 | 11 | 0 | 160 | 0 | 0 | 103 | 0 | 43 | 0 | 77 | 67 | 62 | 0 |  | 669 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 40 | 36 | 40 | 190 | 18 | 16 | 0 | 100 | 0 | 25 | 0 | 51 | 50 | 8 | 0 | 10 | 31 | 22 | 5 | 11 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 137 | 0 | 50 | 0 | 0 | 0 | 0 | 53 |  | 5605 | 2001 | 7606 | 3503 | 669 | 1532 | 1321 | 139 | 40 | 284 | 118 | 0 | 0 | 98.44
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 88 | 0 | 0 | 300 | 103 | 35 | 300 | 307 | 0 | 0 | 330 | 0 | 0 | 1 | 30 | 146 | 0 | 125 | 0 | 0 | 56 | 0 | 0 | 47 | 0 | 48 | 54 | 55 | 36 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 40 | 0 | 0 | 140 | 25 | 0 | 0 | 100 | 0 | 0 | 50 | 0 | 22 | 20 | 13 | 48 | 20 | 35 | 0 | 120 | 80 | 0 | 290 | 195 | 8 | 100 | 40 | 30 | 5 | 45 | 10 | 0 | 0 | 22 | 8 | 25 | 22 | 118 | 169 | 64 | 22 | 0 | 26 | 54 | 53 | 21 | 100 | 214 | 56 | 10 | 49 | 78 | 0 | 25 | 9 | 300 | 25 | 11 | 0 | 190 | 0 | 0 | 100 | 0 | 79 | 0 | 92 | 68 | 100 | 0 |  | 669 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 40 | 34 | 40 | 190 | 23 | 16 | 0 | 100 | 0 | 8 | 0 | 65 | 50 | 8 | 0 | 34 | 31 | 22 | 5 | 11 | 0 | 0 | 139 | 17 | 15 | 0 | 0 | 178 | 0 | 97 | 0 | 0 | 0 | 0 | 70 |  | 5829 | 2162 | 7991 | 3735 | 669 | 1622 | 1436 | 139 | 40 | 232 | 118 | 0 | 0 | 98.43
19:30 | 35 | 90 | 0 | 0 | 350 | 103 | 35 | 300 | 309 | 0 | 0 | 360 | 0 | 0 | 16 | 30 | 172 | 0 | 150 | 0 | 0 | 32 | 0 | 0 | 47 | 0 | 47 | 54 | 55 | 36 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 41 | 0 | 0 | 150 | 25 | 0 | 0 | 100 | 0 | 0 | 50 | 0 | 17 | 20 | 13 | 50 | 22 | 33 | 0 | 120 | 80 | 0 | 268 | 185 | 8 | 100 | 40 | 30 | 5 | 45 | 10 | 0 | 0 | 22 | 8 | 25 | 22 | 118 | 159 | 80 | 22 | 0 | 25 | 54 | 53 | 21 | 100 | 210 | 47 | 10 | 49 | 80 | 0 | 24 | 9 | 300 | 25 | 11 | 0 | 12 | 0 | 0 | 30 | 0 | 79 | 0 | 92 | 70 | 100 | 0 |  | 671 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 40 | 39 | 40 | 181 | 25 | 16 | 0 | 80 | 0 | 8 | 0 | 60 | 50 | 8 | 0 | 34 | 31 | 22 | 5 | 11 | 0 | 0 | 139 | 17 | 15 | 0 | 0 | 173 | 0 | 95 | 0 | 0 | 0 | 0 | 73 |  | 5677 | 2183 | 7860 | 3812 | 671 | 1651 | 1201 | 139 | 41 | 227 | 118 | 0 | 0 | 0
20:00 | 35 | 90 | 0 | 0 | 380 | 103 | 35 | 363 | 357 | 0 | 0 | 360 | 0 | 0 | 0 | 30 | 178 | 0 | 150 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 47 | 54 | 18 | 0 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 41 | 0 | 0 | 150 | 25 | 0 | 0 | 100 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 50 | 22 | 31 | 0 | 120 | 80 | 0 | 268 | 185 | 8 | 100 | 40 | 30 | 5 | 45 | 10 | 0 | 0 | 22 | 8 | 25 | 22 | 118 | 159 | 80 | 22 | 0 | 25 | 54 | 53 | 21 | 100 | 209 | 56 | 10 | 49 | 80 | 0 | 25 | 9 | 310 | 25 | 11 | 0 | 12 | 0 | 0 | 7 | 0 | 72 | 0 | 92 | 70 | 50 | 0 |  | 670 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 40 | 190 | 22 | 16 | 0 | 80 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 43 | 31 | 22 | 5 | 11 | 0 | 0 | 139 | 17 | 15 | 0 | 0 | 175 | 0 | 95 | 0 | 0 | 0 | 0 | 70 |  | 5540 | 2181 | 7721 | 4000 | 670 | 1705 | 915 | 139 | 41 | 133 | 118 | 0 | 0 | 98.43
21:00 | 35 | 105 | 0 | 0 | 380 | 103 | 35 | 438 | 368 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 180 | 0 | 148 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 41 | 0 | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 50 | 22 | 41 | 0 | 120 | 80 | 0 | 268 | 184 | 8 | 100 | 40 | 30 | 5 | 45 | 10 | 0 | 0 | 22 | 8 | 25 | 22 | 110 | 159 | 80 | 22 | 0 | 25 | 54 | 50 | 21 | 100 | 210 | 47 | 10 | 49 | 80 | 0 | 25 | 9 | 310 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 38 | 0 | 92 | 40 | 0 | 0 |  | 670 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 40 | 168 | 25 | 16 | 0 | 90 | 0 | 0 | 0 | 12 | 50 | 0 | 0 | 43 | 23 | 22 | 5 | 11 | 0 | 0 | 139 | 0 | 13 | 0 | 0 | 170 | 0 | 95 | 0 | 0 | 0 | 0 | 70 |  | 5385 | 2091 | 7476 | 4054 | 670 | 1726 | 669 | 139 | 41 | 67 | 110 | 0 | 0 | 98.42
22:00 | 35 | 23 | 0 | 0 | 300 | 103 | 35 | 440 | 365 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 150 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 33 | 33 | 8 | 0 | 41 | 0 | 0 | 150 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 0 | 120 | 80 | 0 | 268 | 184 | 8 | 100 | 40 | 30 | 5 | 7 | 10 | 0 | 0 | 22 | 8 | 25 | 22 | 98 | 148 | 80 | 22 | 0 | 25 | 54 | 5 | 21 | 100 | 205 | 56 | 10 | 49 | 80 | 0 | 25 | 0 | 300 | 17 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 92 | 30 | 0 | 0 |  | 669 | 0 | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 185 | 24 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 43 | 0 | 22 | 5 | 11 | 0 | 0 | 139 | 0 | 13 | 0 | 0 | 174 | 0 | 95 | 0 | 0 | 0 | 0 | 0 |  | 4801 | 1956 | 6757 | 3832 | 669 | 1619 | 346 | 139 | 41 | 13 | 98 | 0 | 0 | 98.42
23:00 | 35 | 0 | 0 | 0 | 300 | 52 | 0 | 440 | 325 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 150 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 0 | 0 | 40 | 0 | 0 | 150 | 0 | 0 | 0 | 110 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 0 | 120 | 80 | 0 | 272 | 185 | 8 | 96 | 40 | 30 | 5 | 7 | 10 | 0 | 0 | 22 | 8 | 8 | 22 | 90 | 149 | 51 | 22 | 0 | 10 | 32 | 5 | 5 | 100 | 210 | 56 | 10 | 49 | 80 | 0 | 6 | 0 | 300 | 23 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 20 | 0 | 0 | 0 |  | 668 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 23 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 5 | 0 | 0 | 139 | 0 | 13 | 0 | 0 | 179 | 0 | 53 | 0 | 0 | 0 | 0 | 0 |  | 4425 | 1755 | 6180 | 3732 | 668 | 1396 | 102 | 139 | 40 | 13 | 90 | 0 | 0 | 98.41
24:00 | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 380 | 327 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 150 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 33 | 33 | 0 | 0 | 40 | 0 | 0 | 150 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 41 | 0 | 120 | 80 | 0 | 268 | 193 | 8 | 101 | 40 | 55 | 5 | 7 | 10 | 0 | 0 | 0 | 8 | 8 | 22 | 80 | 166 | 0 | 0 | 0 | 10 | 32 | 5 | 5 | 100 | 216 | 40 | 10 | 5 | 78 | 0 | 5 | 0 | 290 | 23 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 463 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 21 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 5 | 0 | 0 | 140 | 0 | 12 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4172 | 1504 | 5676 | 3672 | 463 | 1262 | 7 | 140 | 40 | 12 | 80 | 0 | 0 | 98.41
KWH | 740000 | 414000 | 0 | 0 | 6902303 | 1197045 | 388864 | 8657920 | 7747000 | 0 | 0 | 8807875 | 0 | 0 | 12216 | 111777 | 3640270 | 0 | 3536000 | 0 | 0 | 185040 | 0 | 0 | 179721 | 0 | 207840 | 444960 | 176605 | 106000 | 198792 | 600000 | 744660 | 791945 | 822100 | 416868 | 0 | 951000 | 0 | 0 | 2900000 | 89460 | 0 | 0 | 2614907 | 0 | 0 | 533280 | 28800 | 123193 | 89040 | 192000 | 234240 | 380448 | 577920 | 0 | 2523225 | 2073726 | 0 | 6631500 | 4436000 | 200727 | 414000 | 707760 | 592320 | 120000 | 664893 | 512940 | 6032 | 0 | 360324 | 135360 | 303200 | 441510 | 2048640 | 3770280 | 408960 | 358308 | 12950 | 412000 | 659788 | 507600 | 220000 | 1066238 | 4016000 | 1136000 | 509760 | 767160 | 1830860 | 0 | 424100 | 78120 | 7728000 | 258720 | 220992 | 0 | 474218 | 0 | 0 | 412800 | 0 | 243360 | 134055 | 885120 | 295200 | 279300 | 0 |  | 12192000 | 0 | 8490816 | 0 | 0 | 0 | 0 | 0 | 136800 | 103168 | 433125 | 4421310 | 392700 | 64320 | 0 | 784000 | 0 | 35624 | 0 | 184064 | 224580 | 18399 | 0 | 379680 | 222191 | 334080 | 79776 | 158076 | 0 | 421527 | 3435400 | 40000 | 72000 | 0 | 0 | 4054964 | 0 | 1051803 | 0 | 0 | 0 | 0 | 281760 |  | 105026135 | 38012163 | 143038298 | 81542064 | 12192000 | 33968921 | 7379869 | 3856927 | 951000 | 951872 | 2048640 | 147005 | 0
Fuel Cost | 636400 | 356040 | 0 | 0 | 4417473.92 | 969606.45 | 365532.16 | 5281331.2 | 4725670 | 0 | 0 | 5901276.25 | 0 | 0 | 81602.88 | 682957.47 | 2366175.5 | 0 | 3924960 | 0 | 0 | 1219413.6 | 0 | 0 | 1076528.79 | 0 | 1386292.8 | 3172564.8 | 1103781.25 | 664620 | 149094 | 450000 | 0 | 0 | 0 | 3943571.28 | 0 | 0 | 0 | 0 | 3190000 | 847186.2 | 0 | 0 | 3007143.05 | 0 | 0 | 4687531.2 | 310176 | 1198667.89 | 551157.6 | 1240320 | 1531929.6 | 323380.8 | 0 | 0 | 2296134.75 | 1887090.66 | 0 | 4575735 | 3105200 | 138501.63 | 397440 | 474199.2 | 509395.2 | 110400 | 545212.26 | 487293 | 65386.88 | 0 | 277449.48 | 101520 | 233464 | 331132.5 | 14012697.6 | 2827710 | 3758342.4 | 275897.16 | 0 | 428480 | 686179.52 | 487296 | 198000 | 831665.64 | 2811200 | 1295040 | 545443.2 | 843876 | 2087180.4 | 0 | 394413 | 72651.6 | 4945920 | 194040 | 167953.92 | 0 | 3442822.68 | 0 | 0 | 2951520 | 0 | 0 | 0 | 0 | 2757168 | 2608662 | 0 |  | 62179200 | 0 | 5688846.72 | 0 | 0 | 0 | 0 | 0 | 1540368 | 1215319.04 | 3413025 | 3050703.9 | 388773 | 475968 | 0 | 823200 | 0 | 407894.8 | 0 | 1649213.44 | 1942617 | 163751.1 | 0 | 3766425.6 | 2615188.07 | 367488 | 74989.44 | 119663.532 | 0 | 2558668.89 | 13260644 | 1289200 | 1927440 | 0 | 0 | 2838474.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 123922098.37 | 111757062.332 | 235679160.702 | 61075934.012 | 62179200 | 22903402.83 | 47469759.25 | 15819312.89 | 0 | 12218854.12 | 14012697.6 | 0 | 0
Yesterday Day Peak | 35 | 0 | 0 | 0 | 380 | 87 | 0 | 370 | 360 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 135 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 18 | 0 | 0 | 0 | 25 | 32 | 33 | 33 | 43 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 140 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 0 | 120 | 135 | 0 | 323 | 193 | 8 | 100 | 40 | 30 | 5 | 45 | 85 | 0 | 0 | 19 | 8 | 12 | 17 | 90 | 162 | 0 | 20 | 2.1 | 26 | 20 | 2 | 0 | 10 | 146 | 61 | 20 | 47 | 118 | 0 | 25 | 0 | 310 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 19.5 | 30 | 0 | 0 | 0 |  | 529 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 189 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 5 | 5 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 186 | 0 | 50 | 0 | 0 | 0 | 0 | 0 |  | 6299.6 | DayPeak
Yesterday Evening Peak | 35 | 88 | 0 | 0 | 300 | 103 | 35 | 300 | 307 | 0 | 0 | 330 | 0 | 0 | 1 | 30 | 146 | 0 | 125 | 0 | 0 | 56 | 0 | 0 | 47 | 0 | 48 | 54 | 55 | 36 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 40 | 0 | 0 | 140 | 25 | 0 | 0 | 100 | 0 | 0 | 50 | 0 | 22 | 20 | 13 | 48 | 20 | 35 | 0 | 120 | 80 | 0 | 290 | 195 | 8 | 100 | 40 | 30 | 5 | 45 | 10 | 0 | 0 | 22 | 8 | 25 | 22 | 118 | 169 | 64 | 22 | 0 | 26 | 54 | 53 | 21 | 100 | 214 | 56 | 10 | 49 | 78 | 0 | 25 | 9 | 300 | 25 | 11 | 0 | 190 | 0 | 0 | 100 | 0 | 79 | 0 | 92 | 68 | 100 | 0 |  | 669 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 40 | 34 | 40 | 190 | 23 | 16 | 0 | 100 | 0 | 8 | 0 | 65 | 50 | 8 | 0 | 34 | 31 | 22 | 5 | 11 | 0 | 0 | 139 | 17 | 15 | 0 | 0 | 178 | 0 | 97 | 0 | 0 | 0 | 0 | 70 |  | 7991 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 0 | 350 | 100 | 40 | 412 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 200 | 0 | 200 | 100 | 100 | 102 | 149 | 100 | 46 | 0 | 48 | 54 | 55 | 36 | 22 | 25 | 33 | 33 | 33 | 43 | 0 | 40 | 30 | 0 | 150 | 25 | 0 | 0 | 150 | 0 | 0 | 50 | 72 | 68 | 90 | 100 | 50 | 22 | 20 | 0 | 120 | 120 | 260 | 360 | 221 | 8 | 100 | 40 | 30 | 5 | 51 | 85 | 40 | 52 | 22 | 11 | 33 | 22 | 112 | 170 | 79 | 22 | 0 | 57 | 63 | 51 | 21 | 163 | 230 | 66 | 86 | 50 | 140 | 20 | 50 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 130 | 0 | 100 | 180 | 150 | 0 |  | 685 | 46 | 410 | 0 | 115 | 0 | 0 | 0 | 40 | 80 | 40 | 194 | 25 | 110 | 30 | 100 | 0 | 50 | 40 | 100 | 50 | 50 | 50 | 43 | 35 | 22 | 5 | 11 | 0 | 0 | 139 | 17 | 15 | 0 | 0 | 220 | 0 | 95 | 100 | 0 | 0 | 0 | 105
Forecast for Day | 35 | 0 | 0 | 0 | 350 | 100 | 40 | 412 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 200 | 0 | 140 | 100 | 100 | 102 | 149 | 100 | 8 | 0 | 47 | 54 | 55 | 36 | 22 | 25 | 33 | 33 | 33 | 43 | 0 | 40 | 30 | 0 | 120 | 25 | 0 | 0 | 150 | 0 | 0 | 50 | 72 | 68 | 90 | 90 | 50 | 22 | 20 | 0 | 120 | 120 | 260 | 360 | 221 | 8 | 100 | 40 | 30 | 5 | 51 | 85 | 0 | 52 | 22 | 11 | 0 | 22 | 82 | 210 | 79 | 22 | 2 | 57 | 63 | 51 | 21 | 163 | 230 | 66 | 86 | 50 | 78 | 20 | 50 | 10 | 341 | 0 | 11 | 0 | 0 | 300 | 0 | 100 | 0 | 130 | 20 | 100 | 180 | 150 | 0 |  | 538 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 194 | 25 | 110 | 0 | 80 | 0 | 0 | 0 | 90 | 50 | 50 | 50 | 43 | 0 | 22 | 5 | 11 | 0 | 0 | 139 |  | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 0 | 0 | 0 | 105
Generation at 08:00(Today) | 35 | 0 | 0 | 0 | 300 | 12 | 20 | 370 | 305 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 150 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 18 | 0 | 0 | 22 | 25 | 21 | 33 | 33 | 0 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 130 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 0 | 120 | 120 | 0 | 272 | 199 | 8 | 100 | 40 | 30 | 5 | 25 | 20 | 0 | 0 | 22 | 8 | 0 | 22 | 78 | 222 | 7 | 22 | 0.5 | 10 | 32 | 5 | 21 | 100 | 158 | 57 | 20 | 49 | 78 | 0 | 25 | 0 | 320 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7.8 | 30 | 0 | 0 | 0 | 0 | 446 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 193 | 17 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 5 | 5 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 163 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 4350 | 5:00
| Highest Generation |  | 7991 | 19:00
| Day Peak Generation |  | 6299.6 | 12:00
| Evening Peak Generation |  | 7991 | 19:00
| HVDC Max Flow |  | 671 | 19:30
| HVDC EvPeak Flow |  | 669 | 19:00
| Load factor L.F |  | 74.58%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-01-02
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2019-01-01 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6299.6 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 4674 | MW
Evening Peak Generation : |  | 7991 | MW Hour : | 19:00 | Available Max Generation : |  | 12487 | MW
E.P. Demand (at gen end) : |  | 7991 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8300 | MW
Maximum Generation : |  | 7991 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4187 | MW
Total Gen. (MKWH) : |  | 143.0383 | System Load Factor : | 74.58% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -610 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-01-02
Actual : | 98.39 | Ft.(MSL) , | Rule curve : | 102.81 | Ft.( MSL )
Gas Consumed : | Total = | 1018.24 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 83979336.842
|  | Coal : | 15819312.89 | Oil : | 59688613.37 | Total : | 159487263.102
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2928.7986 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 988.5648 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 884.4047 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 798.6668 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 722.0014 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 582.6109 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 335.2756 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 150.2583 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 449.293 |  |  | 0 | 0%
Total | 0 |  | 7839.8741 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 8) Raozan # 01
| Nil |  |  | 2) Khulna ST 110 MW |  | 9) Sirajganj Unit-1,3,4
|  |  |  | 3) Ghorasal Unit-1,3,5 |  | 10) Ashuganj #3
4) Tongi GT
5) Haripur GT-1,2
6) Siddhirganj ST 210 MW
7) Bhagabari 71 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Joydevpur-Kodda 132 kV Ckt-1 was under shut down from 10:30 to 10:42 for A/M.
b) Joydevpur-Kodda 132 kV Ckt-2 was under shut down from 10:45 to 12:45 for A/M.
c) Cumilla(N)-Ashuganj 230 kV Ckt-2 was under shut down from 08:28 to 17:25 for A/M.
d) Mymensingh-Kishoreganj 132 kV Ckt-1 was under shut down from 09:20 to 13:44 for A/M.
e) Bibiyana 400/230 kV T1 transformer was under shut down from 09:51 to 14:15 for A/M.
f) Srimongal-Fenchuganj 132 kV Ckt-2 was under shut down from 09:20 to 15:30 for A/M.
g) Barapukuria-Saidpur 132 kV Ckt-2 was shut down at 09:25 for D/W.
h) Khulna(C )-Noapara 132 kV Ckt-1 was under shut down from 10:14 to 11:59 due to problem
with alignment of line earthling rod at Khulna(C ) end.
i) Magura 132/33 kV T1 & T2 transformers tripped at 09:28 from 33 kV sides showing O/C |  |  |  | About 20 MW Power interruption occurred under Magura S/S
& E/F and were switched on at 09:36. |  |  |  | area from 09:28 to 09:36.
j) Bheramara HVDC, 20DO2A-Q51 E/S was shut down from 10:38 to 17:24 for replacing motor.
k) Haripur-Norshingdi-Bhulta 132 kV Ckt was shut under shut down from 10:35 to 14:03 for D/W.
l) Ghorasal Unit-3 was synchronized at 17:45 for test purpose and tripped at 14:15.
Again synchronized at 17:45.
m) Baghabari 100 MW synchronized at 17:22.
n) Chandraghona-Madunaghat 132 kV Ckt-2 was shut down at 07:47(02/01/2019) for A/M.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-01-01 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 35 | 740000 | #2 under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 88 | 414000
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 6902303 | Frequency control
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 35 | 388864 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 103 | 1197045
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 300 | 8657920 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 0 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 307 | 7747000 | Frequency control
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 330 | 8807875 | Frequency control
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 1 | 12216 | Engine problem
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 30 | 111777 | Low demand
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 198792
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 125 | 3536000 | FGMO
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 146 | 3640270 | Frequency control
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 56 | 185040 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 48 | 207840
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 444960
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 176605
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 36 | 106000 | Engine problem
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 47 | 179721 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1344660 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 791945
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 822100
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 42 | 416868 | Engine problem
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 190 | 474218 | Low demand
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 79 | 243360 | Low demand
| Dhaka area Total |  |  |  | 5798 | 2552 | 47747379
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 140 | 2900000 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 89460
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 134055
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 48 | 234240
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 951000 | Low water lavel
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 100 | 2614907 | FGMO
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 50 | 533280
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 0 | 28800 | Reserve
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 22 | 123193 | Low demand
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 20 | 89040 | Low demand
| Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 92 | 885120 | Engine problem
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 380448
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 35 | 577920
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 13 | 192000 | Low demand
| Chattogram area Total |  |  |  | 1681 | 605 | 9733463
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 120 | 2523225
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 2073726 | Gas shortage
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 195 | 4436000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Reserve
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 290 | 6631500 | FGMO
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 40 | 707760 | Engine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 30 | 592320 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 45 | 664893
| Midland 150MW |  | IPP | 23*7.015 | 150 | 100 | 279300 | Low demand
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 10 | 512940 | High voltage
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 6032 | Reserve
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 414000 | ST Under maint.
| Chandpur Desh 200MW |  | IPP | 0 | 200 | 68 | 295200 | Low demand
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 360324
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 135360 | Engine problem
** | Tripura |  | Imported power | 0 | 160 | 118 | 2048640
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 25 | 303200 | Engine problem
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 441510
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1286 | 22746657
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 169 | 3770280 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 358308
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 64 | 408960 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 12950
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 100 | 412800 | Low demand
| Mymensingh Area Total |  |  |  | 522 | 355 | 4963298
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 26 | 412000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 54 | 659788
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 100 | 1066238 | Frequency control
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 214 | 4016000 | FGMO
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 507600
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 21 | 220000 | Engine problem
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 220992
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 56 | 1136000 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 10 | 509760 | High voltage
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 49 | 767160
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 78 | 1830860
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 25 | 424100 | High voltage
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 25 | 258720
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 300 | 7728000 | FGMO
| Bibiyana-3 285MW |  | PDB | 285 MW | 0 | 0 | 0 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 9 | 78120
| Sylhet Area Total |  |  |  | 1549 | 1031 | 19835338
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 669 | 12192000
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 40 | 136800
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 34 | 103168
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 300 | 8490816 | Frequency control
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 433125
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 70 | 281760 | Low demand
| Khulna Area Total |  |  |  | 2209 | 1153 | 21637669
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 16 | 64320 | Low demand
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 23 | 392700
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 190 | 4421310 | FGMO
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 1051803
| Barisal Area Total |  |  |  | 462 | 326 | 5930133
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 100 | 784000
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 8 | 35624 | Low demand
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 224580
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 18399 | Low demand
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 178 | 4054964 | FGMO
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 141 | 0 | 0 | Gas shortage
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 0 | 0 | Gas shortage
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 31 | 222191
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 334080
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 5 | 79776 | Engine problem
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 158076
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 34 | 379680 | Low demand
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 65 | 184064 | Low demand
| Rajshahi Area Total |  |  |  | 1546 | 512 | 6475434
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 421527 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 139 | 3435400
122 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 40000
123 | Saidpur GT |  | PDB | 1*20 | 20 | 15 | 72000
| Rangpur Area Total |  |  |  | 484 | 171 | 3968927
| Total |  |  |  | 17142 | 7991 | 143038298
| Eastern Grid Total |  |  |  | 12441 | 5829 | 105026135
| Western Grid Total |  |  |  | 4701 | 2162 | 38012163
| National Grid Total |  |  |  | 17142 | 7991 | 143038298
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-01-01 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 5039 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2496 | MW
i) Dhaka area |  |  | 2642 | MW | i) Khulna area |  |  | 965 | MW
ii) Chittagong area |  |  | 847 | MW | ii) Rajshahi area |  |  | 799 | MW
iii) Comilla area |  |  | 668 | MW | iii) Barisal area |  |  | 194 | MW
iv) Mymensingh area |  |  | 574 | MW | iv) Rangpur area |  |  | 538 | MW
v) Sylhet area |  |  | 308 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 7535 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 86 | 1800 | Netrokona | 64 | 1830 | Goalpara | 30 | 1830
Munsiganj | 70 | 1930 | Jamalpur | 87 | 1830 | Central s/s | 54 | 1830
Sonargaon | 36 | 1830 | Sherpur | 66 | 1800 | Noapara | 76 | 2000
Shyampur | 120 | 1200 | Srimongal | 23 | 1800 | Jessore | 101 | 1830
Bhulta | 137 | 1200 | Shahjibazar | 79 | 1900 | Jhenida | 73 | 1830
Madanganj | 132 | 800 | Fenchuganj | 27 | 1830 | Bottail | 92 | 1830
Shitalakhya | 66 | 1200 | Kulawara | 26 | 1800 | G.K Project | 35 | 1830
Rahim steel | 12 | 1700 | Sylhet | 87 | 2000 | Faridpur | 118 | 1830
Matuail | 62 | 1200 | Chatak | 18 | 1800 | Madaripur | 92 | 2000
Ghorasal | 57 | 1930 | Sunamganj | 24 | 1800 | Gopalganj | 57 | 1830
Narsingdi | 98 | 1930 | Biani Bazar | 27 | 1800 | Bagerhat | 63 | 1830
Haripur (SBU) | 86 | 1930 | Comilla (S) | 120 | 1830 | Mongla | 14 | 100
Ullon | 45 | 1800 | Comilla(N) | 68 | 1930 | Satkhira | 66 | 1830
Hasnabad | 122 | 1800 | Chandpur | 72 | 1830 | Gallamari | 26 | 1830
Magbazar | 85 | 1200 | Feni | 85 | 1830 | Magura | 34 | 1800
Maniknagar | 64 | 1800 | Chowmuhani | 120 | 1930 | Chuadanga | 57 | 1830
Bangabhaban | 19 | 1100 | Ashuganj | 36 | 1830 | Barisal | 82 | 1830
Narinda | 54 | 1700 | Daudkandi | 82 | 1930 | Patuakhali | 60 | 1830
Dhanmondi | 65 | 1400 | B.Baria | 84 | 1930 | Bhandaria | 38 | 1930
Lalbag | 63 | 1300 | Ramganj | 24 | 1800 | Ishurdi | 38 | 1830
Madartek | 32 | 1800 | Madunaghat | 40.5 | 2000 | Ruppur Paromanobik | 1 | 100
Mirpur | 79 | 1800 | Hathazari | 63 | 1800 | Natore | 84 | 1830
Kalyanpur | 57 | 1800 | Khulshi | 148 | 1300 | Bogra | 167 | 1830
Gulshan | 72 | 1800 | Halishahar | 90 | 1830 | Noagaon | 81 | 1830
Uttara | 34 | 1800 | Baraulia | 137 | 1200 | Rajshahi | 89 | 1900
Uttara(New) | 4 | 1800 | Sikalbaha | 36 | 1800 | C.Nawabganj | 47 | 2000
Kamrangirchar | 58 | 1800 | Dohazari | 60 | 1830 | Amnura | 30 | 1830
Savar | 94 | 1830 | Cox'sbazar | 62 | 1930 | Pabna | 72 | 1900
Bhasantec | 76 | 1800 | Chandraghona | 19 | 1830 | Shahjadpur | 63 | 1830
Agargaon | 33 | 1830 | Kaptai | 3.5 | 1800 | Serajganj | 64 | 1830
Satmosjid | 44 | 1830 | A. Khaer Stl. | 14 | 100 | Niyamatpur | 41 | 1900
Tongi | ui | 1830 | Bakulia | 64 | 1800 | Joypurhat | 39 | 1930
Kabirpur | 11 | 1830 | Julda | 19 | 1000 | Rangpur | 94 | 1900
Basundhara | 80 | 1830 | TK chemical | 5.2 | 900 | Lalmonirhat | 71 | 1800
Manikganj | 64 | 1930 | Modern Steel | 12 | 1400 | Saidpur | 100 | 1830
Joydevpur | 179 | 1800 | Shahmirpur | 20 | 1830 | Purbasadipur | 77 | 1930
New Tongi | 81 | 1500 | Khagrachhari | 14 | 1900 | Thakurgaon | 59 | 1830
Korda | 173 | 1100 | Matarbari | 19 | 1830 | Palashbari | 83 | 1830
Dhamrai | 30 | 1800 | Baroiar Hat | 18 | 1800 | Barapukuria | 37 | 1830
Tangail | 123 | 1900 | Rangamati | 8 | 1800 | Panchagar | 32 | 1830
Mymensing | 178 | 1830 | Abul Khair 230 | 162 | 1100
Kishorganj | 68 | 1830 | BSRM | 100 | 500
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-01-01
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 419 | 4:00 | 410 | 12:00 | Kaliakoir | 414 | 4:00 | 402 | 12:00
Bheramara | 405 | 2:00 | 396 | 10:00 | Bhulta | 406 | 4:00 | 395 | 12:00
Ashuganj(N) | 404 | 3:00 | 395 | 12:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 240 | 18:00 | 238 | 1:00 | Hathazari | 226 | 18:00 | 217 | 12:00
Ishurdi | 240 | 2:00 | 230 | 18:00 | Megnaghat | 238 | 1:00 | 231 | 12:00
Ashuganj | 245 | 4:00 | 236 | 21:00 | Fenchuganj | 247 | 17:00 | 242 | 11:00
Serajganj | 236 | 3:00 | 222 | 12:00 | Siddhirganj | 238 | 4:00 | 230 | 11:00
Baghabari | 233 | 3:00 | 224 | 19:00 | Maniknagar | 234 | 1:00 | 228 | 15:00
Barapukuria | 235 | 1:00 | 225 | 18:00 | Old Airport | 236 | 2:00 | 228 | 12:00
Bogra | 233 | 3:00 | 219 | 18:00 | Barisal | 237 | 4:00 | 225 | 20:00
Khulna South | 243 | 4:00 | 224 | 18:00 | AKSML | 225 | 18:30 | 216 | 11:00
Rampura | 231 | 1:00 | 228 | 10:00 | BSRM | 229 | 18:30 | 218 | 11:00
Haripur | 233 | 7:00 | 228 | 11:00 | Bibiyana | 245 | 18:30 | 239 | 12:00
Hasnabad | 235 | 1:00 | 228 | 21:00 | Bhulta | 235 | 2:00 | 228 | 12:00
Aminbazar | 237 | 2:00 | 229 | 12:00 | Ashuganj (S) | 242 | 3:00 | 237 | 12:00
Tongi | 232 | 4:00 | 225 | 11:00 | Kaliakoir | 239 | 4:00 | 230 | 12:00
Comilla (N) | 242 | 7:00 | 235 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 137 | 100 | 134 | 1200 | Ramganj | 136 | 700 | 134 | 1800
Munsiganj | 139 | 1800 | 134 | 1200 | Madanhat | 136 | 1800 | 128 | 1200
Megnaghat | 138 | 100 | 136 | 1200 | Hathazari | 135 | 1800 | 128 | 1100
Shyampur | 133 | 100 | 130 | 1400 | Khulshi | 133 | 1800 | 124 | 1100
Bhulta | 139 | 300 | 133 | 1200 | Halishahar | 138 | 1900 | 127 | 1200
Madanganj | 140 | 1800 | 132 | 900 | Baraulia | 135 | 1830 | 125 | 1200
Shitalakhya | 143 | 1900 | 132 | 900 | Sikalbaha | 135 | 1830 | 127 | 1100
Rahim steal | 138 | 700 | 135 | 1300 | Dohazari | 135 | 1800 | 136 | 1000
Matuail | 138 | 400 | 133 | 1200 | Cox'sbazar | 130 | 2100 | 121 | 1200
Ghorasal | 144 | 700 | 138 | 1200 | Chandraghona | 136 | 1830 | 127 | 1200
Narsinghdi | 140 | 1300 | 134 | 600 | Kaptai | 135 | 1800 | 129 | 1000
Haripur (SBU) | 137 | 400 | 133 | 700 | A. Khaer Stl. | 132 | 100 | 125 | 1200
Ullon | 135 | 300 | 129 | 1200 | Bakulia | 134 | 1900 | 124 | 1200
Hasnabad | 136 | 200 | 132 | 1000 | Julda | 135 | 1800 | 126 | 1100
Magbazar | 136 | 400 | 129 | 1200 | TK Chemical | 136 | 1830 | 127 | 1000
Maniknagar | 137 | 300 | 134 | 1200 | Modern Steel | 134 | 1800 | 125 | 1200
Bangabhaban | 141 | 1830 | 134 | 1200 | Shahmirpur | 134 | 1800 | 125 | 1100
Narinda | 135 | 400 | 129 | 1200 | Khagrachhari | 135 | 1830 | 126 | 1100
Dhanmondi | 135 | 300 | 129 | 1200 | Matarbari | 130 | 1800 | 123 | 1200
Lalbag | 141 | 1830 | 134 | 1200 | Baroiar Hat | 136 | 700 | 129 | 1200
Madartek | 135 | 400 | 129 | 1200 | Rangamati | 135 | 1800 | 127 | 1100
Mirpur | 134 | 500 | 128 | 1200 | Goalpara | 139 | 200 | 126 | 800
Kalyanpur | 137 | 200 | 132 | 1200 | Central s/s | 136 | 100 | 127 | 800
Gulshan | 133 | 200 | 128 | 1200 | Noapara | 136 | 100 | 125 | 800
Uttara | 137 | 500 | 130 | 1200 | Jessore | 132 | 100 | 122 | 800
Uttara(New) | 135 | 200 | 129 | 1200 | Jhenida | 136 | 200 | 123 | 1800
Kamrangirchar | 138 | 300 | 134 | 1200 | Bottail | 139 | 400 | 130 | 1830
Savar | 134 | 200 | 128 | 1200 | G.K.Project | 142 | 200 | 138 | 1800
Bhasantec | 138 | 200 | 132 | 1200 | Faridpur | 137 | 500 | 127 | 2000
Agargaon | 138 | 200 | 133 | 1200 | Madaripur | 138 | 400 | 127 | 2000
Satmosjid | 138 | 300 | 133 | 1200 | Gopalganj | 136 | 300 | 123 | 1930
Tongi | 139 | 400 | 132 | 1500 | Bagerhat | 132 | 300 | 124 | 1800
Kabirpur | 135 | 100 | 131 | 1200 | Mongla | 135 | 200 | 127 | 1800
Basundhara | 131 | 200 | 125 | 1400 | Satkhira | 137 | 200 | 126 | 1800
Manikganj | 140 | 400 | 136 | 1100 | Gallamari | 139 | 300 | 128 | 1800
Joydevpur | 142 | 1830 | 135 | 1600 | Magura | 137 | 200 | 121 | 1800
New Tongi | 139 | 100 | 132 | 1200 | Chuadanga | 134 | 200 | 120 | 1800
Kodda | 140 | 1830 | 134 | 2100 | Barisal | 139 | 600 | 130 | 2000
Dhamrai | 136 | 200 | 131 | 1200 | Patuakhali | 136 | 200 | 128 | 2000
Tangail | 138 | 700 | 135 | 800 | Bhandaria | 135 | 100 | 127 | 2000
Mymensing | 137 | 300 | 131 | 1200 | Ishurdi | 142 | 400 | 134 | 1830
Kishorganj | 138 | 300 | 135 | 1300 | Ruppur Paromanobik | 140 | 100 | 136 | 1830
Netrokona | 137 | 300 | 132 | 1100 | Natore | 139 | 400 | 130 | 1200
Jamalpur | 137 | 1800 | 126 | 1200 | Bogra | 138 | 100 | 128 | 1830
Sherpur | 138 | 1830 | 123 | 1300 | Noagaon | 135 | 100 | 126 | 1800
Srimongal | 143 | 500 | 140 | 1800 | Rajshahi | 136 | 200 | 126 | 1200
Shahjibazar | 141 | 1500 | 139 | 100 | C.Nawabganj | 130 | 100 | 124 | 1200
Fenchuganj | 140 | 300 | 137 | 1000 | Amnura | 134 | 300 | 124 | 1100
Khulawara | 139 | 100 | 136 | 1200 | Pabna | 137 | 200 | 130 | 1100
Sylhet | 138 | 1600 | 137 | 100 | Shahjadpur | 143 | 100 | 137 | 1930
Chatak | 138 | 100 | 136 | 1100 | Serajganj | 138 | 100 | 130 | 1830
Sunamganj | 138 | 200 | 135 | 1000 | Niyamatpur | 136 | 300 | 124 | 1800
Biani Bazar | 139 | 600 | 136 | 1100 | Joypurhat | 138 | 100 | 126 | 1800
Cumilla(s) | 132 | 2300 | 127 | 1800 | Rangpur | 132 | 500 | 116 | 1800
Cumilla(n) | 143 | 700 | 140 | 100 | Lalmonirhat | 130 | 300 | 110 | 1800
Chandpur | 140 | 100 | 137 | 1600 | Saidpur | 132 | 400 | 118 | 1830
Feni | 135 | 2100 | 131 | 1200 | Purbasadipur | 135 | 200 | 114 | 1830
Chowmuhani | 133 | 2300 | 131 | 1500 | Thakurgaon | 130 | 100 | 107 | 1900
Ashuganj | 144 | 2300 | 142 | 800 | Palashbari | 134 | 100 | 118 | 1800
Daudkandi | 139 | 700 | 134 | 1200 | Barapukuria | 135 | 100 | 125 | 1800
B.Baria | 141 | 800 | 137 | 2000 | Panchagar | 130 | 400 | 100 | 1830

## L-Curve
Date | 2019-01-01
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 340 | 4172 | 1504 | 5676 |  |  |  | QF-LDC-12
0:30 | 295 | 3875 | 1455 | 5330 | Date: | 2019-01-01
1:00 | 250 | 3578 | 1406 | 4984
1:30 | 280 | 3516 | 1298 | 4814
2:00 | 310 | 3454 | 1190 | 4644
2:30 | 305 | 3402.5 | 1163 | 4565.5 | [5 empty] | Gen. at Eve. Peak | 7991 | 7991 MW (19:00 )
3:00 | 300 | 3351 | 1136 | 4487 | [6 empty] | 19:00
3:30 | 320 | 3340.5 | 1102.5 | 4443 | [5 empty] | Gen. at Day Peak | 6299.6 | 6299.6 MW (12:00 )
4:00 | 340 | 3330 | 1069 | 4399 | [6 empty] | 12:00
4:30 | 340 | 3304 | 1070.5 | 4374.5 | [5 empty] | Highest Generation | 7991
5:00 | 340 | 3278 | 1072 | 4350 | [6 empty] | 19:00
5:30 | 340 | 3403.5 | 1105.5 | 4509
6:00 | 340 | 3529 | 1139 | 4668
6:30 | 355 | 3635.3 | 1157.5 | 4792.8
7:00 | 370 | 3741.6 | 1176 | 4917.6
7:30 | 390 | 3906.81 | 1316 | 5222.81
8:00 | 410 | 4072.02 | 1456 | 5528.02
8:30 | 320 | 4184.885 | 1526.5 | 5711.385
9:00 | 230 | 4297.75 | 1597 | 5894.75
9:30 | 210 | 4298.675 | 1555.5 | 5854.175
10:00 | 190 | 4299.6 | 1514 | 5813.6
10:30 | 200 | 4384.405 | 1511.5 | 5895.905
11:00 | 210 | 4469.21 | 1509 | 5978.21
11:30 | 260 | 4625.905 | 1513 | 6138.905
12:00 | 310 | 4782.6 | 1517 | 6299.6
12:30 | 345 | 4773.5 | 1533.5 | 6307
13:00 | 380 | 4764.4 | 1550 | 6314.4
13:30 | 325 | 4660.15 | 1531.5 | 6191.65
14:00 | 270 | 4555.9 | 1513 | 6068.9
14:30 | 235 | 4560.15 | 1498 | 6058.15
15:00 | 200 | 4564.4 | 1483 | 6047.4
15:30 | 210 | 4563.4 | 1462 | 6025.4
16:00 | 220 | 4562.4 | 1441 | 6003.4
16:30 | 250 | 4597.535 | 1483 | 6080.535
17:00 | 280 | 4632.67 | 1525 | 6157.67
17:30 | 425 | 5118.835 | 1763 | 6881.835
18:00 | 570 | 5605 | 2001 | 7606
18:30 | 590 | 5717 | 2081.5 | 7798.5
19:00 | 610 | 5829 | 2162 | 7991
19:30 | 600 | 5677 | 2183 | 7860
20:00 | 520 | 5540 | 2181 | 7721 |  |  |  | Executive Engineer
20:30 | 460 | 5462.5 | 2136 | 7598.5 |  |  |  | Network Operation Division
21:00 | 400 | 5385 | 2091 | 7476
21:30 | 350 | 5093 | 2023.5 | 7116.5
22:00 | 300 | 4801 | 1956 | 6757 |  |  |  |  | Page 6 of 7
22:30 | 250 | 4613 | 1855.5 | 6468.5
23:00 | 200 | 4425 | 1755 | 6180
23:30 | 270 | 4298.5 | 1629.5 | 5928
24:00 | 340 | 4172 | 1504 | 5676
7991 MW (19:00 )
6299.6 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-01-01 |  | Energy | 143038298
[10 empty] | 2019-01-01 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3672 | 463 | 1262 | 7 | 140 | 40 | 12 | 0 | 80
0:30 | 3452.5 | 406 | 1167.5 | 7 | 174 | 40 | 6 | 0 | 77 | Date: | 2019-01-01
1:00 | 3233 | 349 | 1073 | 7 | 208 | 40 | 0 | 0 | 74
1:30 | 3090 | 348.5 | 1049.5 | 7 | 208 | 40 | 0 | 0 | 71 | [7 empty] | Total Energy | 143.0383 | Total Energy Gen 143.038 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 143.038 MKWHr
2:00 | 2947 | 348 | 1026 | 7 | 208 | 40 | 0 | 0 | 68 | [7 empty] | Energy not Served | 0
2:30 | 2887.5 | 348 | 1009.5 | 7 | 207.5 | 40 | 0 | 0 | 66 | [7 empty] | Energy Requirement | 143.0383
3:00 | 2828 | 348 | 993 | 7 | 207 | 40 | 0 | 0 | 64
3:30 | 2817.5 | 348 | 995.5 | 7 | 173 | 40 | 0 | 0 | 62 | [6 empty] | Shortage
4:00 | 2807 | 348 | 998 | 7 | 139 | 40 | 0 | 0 | 60
4:30 | 2797.5 | 348 | 983 | 7 | 139 | 40 | 0 | 0 | 60
5:00 | 2788 | 348 | 968 | 7 | 139 | 40 | 0 | 0 | 60
5:30 | 2865 | 348 | 1046 | 7 | 139 | 41 | 0 | 0 | 63
6:00 | 2942 | 348 | 1124 | 7 | 139 | 42 | 0 | 0 | 66
6:30 | 3062 | 348 | 1123.5 | 12.5 | 139 | 41 | 0 | 0 | 66 |  |  |  |  | Coal
7:00 | 3182 | 348 | 1123 | 18 | 139 | 40 | 0 | 0 | 66
7:30 | 3318.5 | 439 | 1176.5 | 34 | 139 | 40 | 0 | 0 | 71 |  |  |  | Oil |  |  |  | ,
8:00 | 3455 | 530 | 1230 | 50 | 139 | 40 | 0 | 0 | 76
8:30 | 3504.5 | 531 | 1294 | 113.5 | 139 | 40 | 0 | 0 | 78
9:00 | 3554 | 532 | 1358 | 177 | 139 | 40 | 0 | 0 | 80
9:30 | 3494.5 | 531.5 | 1376 | 174 | 139 | 40 | 0 | 0 | 82
10:00 | 3435 | 531 | 1394 | 171 | 139 | 40 | 0 | 0 | 84
10:30 | 3526.5 | 531 | 1397.5 | 155.5 | 139 | 40 | 0 | 0 | 86
11:00 | 3618 | 531 | 1401 | 140 | 139 | 40 | 0 | 0 | 88
11:30 | 3695.5 | 530 | 1481 | 143 | 139 | 40 | 0 | 0 | 89
12:00 | 3773 | 529 | 1561 | 146 | 139 | 40 | 0 | 0 | 90
12:30 | 3699.5 | 528.5 | 1604.5 | 182 | 139 | 40 | 1.5 | 0 | 91
13:00 | 3626 | 528 | 1648 | 218 | 139 | 40 | 3 | 0 | 92
13:30 | 3626 | 528 | 1648 | 218 | 139 | 40 | 3 | 0 | 92
14:00 | 3626 | 528 | 1648 | 218 | 139 | 40 | 3 | 0 | 92
14:30 | 3536.5 | 529.5 | 1600.5 | 221 | 139 | 40 | 4.5 | 0 | 93
15:00 | 3447 | 531 | 1553 | 224 | 139 | 40 | 6 | 0 | 94
15:30 | 3436 | 531 | 1562 | 208 | 139 | 40 | 6 | 0 | 93
16:00 | 3425 | 531 | 1571 | 192 | 139 | 40 | 6 | 0 | 92
16:30 | 3364.5 | 560 | 1565 | 277 | 139 | 40 | 37 | 0 | 94
17:00 | 3304 | 589 | 1559 | 362 | 139 | 40 | 68 | 0 | 96
17:30 | 3403.5 | 629 | 1545.5 | 841.5 | 139 | 40 | 176 | 0 | 107
18:00 | 3503 | 669 | 1532 | 1321 | 139 | 40 | 284 | 0 | 118
18:30 | 3619 | 669 | 1577 | 1378.5 | 139 | 40 | 258 | 0 | 118
19:00 | 3735 | 669 | 1622 | 1436 | 139 | 40 | 232 | 0 | 118
19:30 | 3812 | 671 | 1651 | 1201 | 139 | 41 | 227 | 0 | 118
20:00 | 4000 | 670 | 1705 | 915 | 139 | 41 | 133 | 0 | 118
20:30 | 4027 | 670 | 1715.5 | 792 | 139 | 41 | 100 | 0 | 114
21:00 | 4054 | 670 | 1726 | 669 | 139 | 41 | 67 | 0 | 110
21:30 | 3943 | 669.5 | 1672.5 | 507.5 | 139 | 41 | 40 | 0 | 104
22:00 | 3832 | 669 | 1619 | 346 | 139 | 41 | 13 | 0 | 98
22:30 | 3782 | 668.5 | 1507.5 | 224 | 139 | 40.5 | 13 | 0 | 94
23:00 | 3732 | 668 | 1396 | 102 | 139 | 40 | 13 | 0 | 90
23:30 | 3702 | 565.5 | 1329 | 54.5 | 139.5 | 40 | 12.5 | 0 | 85 | Max Temp. in Dhaka |  | 27.7° C
24:00 | 3672 | 463 | 1262 | 7 | 140 | 40 | 12 | 0 | 80
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 143.038 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 143.038 MKWHr
Note on W13: Author:

## Generation
2019-01-01
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 40 | 40 | 40 | 40 | 40 | 42 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 41 | 41 | 41 | 41 | 40 | 40 | 951000
2 | Kaptai Unit-4 & 5
3 | Chattogram ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 140 | 150 | 150 | 150 | 150 | 150 | 150 | 2900000
5 | Raozan 25 MW (RPCL) | [16 empty] | 0 | 25 |  | 25 | 25 | 25 | 0 | 0 |  |  | 89460
| Teknaf Solartech 20MW | [5 empty] | 0 | 1.6 | 7.52 | 13.45 | 17.8 | 19.11 | 19.5 | 18.4 | 16.3 | 12.2 | 6.9 | 0.67 | 0 | [8 empty] | 134055
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 130 | 80 | 84 | 80 | 80 | 80 | 145 | 145 | 145 | 145 | 140 | 140 | 140 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 110 | 130 | 2614907
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | [16 empty] | 0 | 68 |  | 22 | 17 | 0 |  |  |  |  | 123193
12 | Hathazari peaking | [16 empty] | 0 | 25 |  | 0 | [6 empty] | 28800
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [16 empty] | 0 | 8 |  | 0 | [6 empty] | 6032
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 170 | 165 | 140 | 140 | 140 | 140 | 140 | 165 | 165 | 155 | 165 | 180 | 130 | 128 | 128 | 138 | 80 | 120 |  | 125 | 150 | 150 | 148 | 80 | 105 | 105 | 3536000
17 | Siddhirganj CCPP-335 MW | 150 | 120 | 120 | 120 | 120 | 120 | 167 | 180 | 150 | 120 | 120 | 135 | 195 | 130 | 140 | 140 | 140 | 120 |  | 146 | 172 | 178 | 180 | 150 | 150 | 150 | 3640270
18 | Summit Gazipur -2 | [15 empty] | 0 | 37 | 160 |  | 190 | 12 | 12 | 0 | 0 |  |  | 474218
19 | Ashuganj 195MW Modular | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal ST: Unit-1,2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 740000
21 | Ghorasal GT: Unit-3 | [13 empty] | 7 | 0 |  | 0 | 18 |  | 88 | 90 | 90 | 105 | 23 |  |  | 414000
22 | Ghorasal GT: Unit-4 | 0
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 220 | 220 | 220 | 220 | 220 | 250 | 250 | 280 | 320 | 320 | 340 | 380 | 330 | 320 | 330 | 250 | 250 | 300 |  | 300 | 350 | 380 | 380 | 300 | 300 | 300 | 6902303
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2523225
30 | Ashuganj ST: Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 120 | 135 | 100 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2073726
32 | Ashuganj Engines TSK | 10 | 10 | 10 | 10 | 10 | 10 | 35 | 36 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 707760
33 | Ashuganj CCPP 225 MW | 184 | 187 | 155 | 161 | 168 | 168 | 202 | 205 | 186 | 177 | 193 | 193 | 172 | 171 | 186 | 227 | 185 | 185 |  | 195 | 185 | 185 | 184 | 184 | 185 | 193 | 4436000
34 | Ashuganj CCPP(South) | 250 | 250 | 250 | 250 | 220 | 250 | 250 | 257 | 287 | 287 | 323 | 323 | 294 | 268 | 268 | 268 | 268 | 268 |  | 290 | 268 | 268 | 268 | 268 | 272 | 268 | 6631500
Ashuganj CCPP(North)
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 55 | 592320
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 102 | 96 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 96 | 101 | 414000
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 350 | 352 | 345 | 345 | 350 | 370 | 367 | 370 | 360 | 345 | 360 | 370 | 350 | 300 | 300 | 300 | 270 | 270 |  | 300 | 300 | 363 | 438 | 440 | 440 | 380 | 8657920
40 | Meghnaghat CCPP 450MW | 380 | 340 | 340 | 340 | 320 | 380 | 380 | 380 | 410 | 390 | 390 | 420 | 450 | 400 | 370 | 330 | 330 | 330 |  | 330 | 360 | 360 | 360 | 360 | 360 | 360 | 8807875
41 | Haripur Power CCPP 360MW | 306 | 305 | 277 | 276 | 276 | 336 | 336 | 336 | 337 | 371 | 362 | 360 | 336 | 306 | 303 | 306 | 303 | 307 |  | 307 | 309 | 357 | 368 | 365 | 325 | 327 | 7747000
42 | Mymensingh RPCL 210MW | 168 | 168 | 170 | 139 | 134 | 136 | 135 | 169 | 167 | 165 | 162 | 162 | 161 | 161 | 161 | 162 | 207 | 183 |  | 169 | 159 | 159 | 159 | 148 | 149 | 166 | 3770280
43 | Haripur NEPC 110MW
44 | Fenchugonj CCPP-1 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 26 | 26 | 26 | 26 | 25 | 26 | 26 |  | 26 | 25 | 25 | 25 | 25 | 10 | 10 | 412000
45 | Fenchugonj CCPP-2 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 20 | 20 | 32 | 32 | 32 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 32 | 32 | 659788
46 | Shajibazar 330 MW | 138 | 146 | 138 | 146 | 147 | 152 | 143 | 148 | 141 | 141 | 150 | 146 | 140 | 215 | 209 | 212 | 209 | 208 |  | 214 | 210 | 209 | 210 | 205 | 210 | 216 | 4016000
47 | Shahjibazar GT: Unit- 8, 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 56 | 51 | 55 | 61 | 52 | 50 | 40 | 54 | 40 | 52 |  | 56 | 47 | 56 | 47 | 56 | 56 | 40 | 1136000
48 | Shahjibazar 86MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 20 | 20 | 20 | 20 | 50 | 50 | 50 | 50 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 509760
49 | Shahjibazar (EPL) 50MW | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 30 | 48 | 48 | 48 | 47 | 47 | 48 | 48 | 46 | 45 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 5 | 767160
50 | Sylhet GT 150 MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 70 | 68 | 67 | 87 | 118 | 123 | 97 | 97 | 100 | 100 | 78 |  | 78 | 80 | 80 | 80 | 80 | 80 | 78 | 1830860
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 25 | 25 | 24 | 24 | 25 | 25 | 25 | 25 | 25 | 24 | 25 |  | 25 | 24 | 25 | 25 | 25 | 6 | 5 | 424100
53 | Sylhet (Desh) 10MW | [12 empty] | 8 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 0 | 0 |  | 78120
54 | Hobiganj 11MW | [7 empty] | 11 | 11 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 220992
55 | Fenchugonj (Barakatullah) 51MW | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 50 | 50 | 50 | 52 | 53 | 53 |  | 53 | 53 | 53 | 50 | 5 | 5 | 5 | 507600
56 | Shahjahanulla 25 MW | [12 empty] | 24 | 24 | 24 | 24 | 24 | 25 |  | 25 | 25 | 25 | 25 | 17 | 23 | 23 | 258720
57 | Summit Bibiana- 2 | 310 | 305 | 300 | 305 | 295 | 320 | 300 | 300 | 280 | 280 | 300 | 310 | 250 | 250 | 300 | 300 | 310 | 260 |  | 300 | 300 | 310 | 310 | 300 | 300 | 290 | 7728000
58 | Southern 55MW | [15 empty] | 0 | 17 | 36 |  | 36 | 36 | 0 |  |  |  |  | 106000
59 | Sikalbaha (Energis) | [6 empty] | 1 | 13 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 42 | 50 |  | 50 | 50 | 40 | 40 | 40 | 24 | 0 | 533280
60 | Barabkunda (Regent) | [7 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 380448
61 | Narshingdi (Doreen) | [12 empty] | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 0 | 0 | 198792
62 | Tangail (Doreen) 22MW | [5 empty] | 0 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 358308
63 | Tripura | 74 | 68 | 64 | 60 | 60 | 66 | 66 | 76 | 80 | 84 | 88 | 90 | 92 | 94 | 94 | 92 | 96 | 118 |  | 118 | 118 | 118 | 110 | 98 | 90 | 80 | 2048640
64 | Malancha, Ctg. EPZ (United) | 9 | 9 | 9 | 9 | 9 | 20 | 39 | 21 | 15 | 12 | 11 | 14 | 18 | 18 | 12 | 17 | 27 | 37 |  | 35 | 33 | 31 | 41 | 40 | 40 | 41 | 577920
65 | Feni (Doreen) 22MW | [6 empty] | 20 | 20 | 22 | 22 | 22 | 19 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 360324
66 | Feni, Mohipal (Doreen) | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 135360
67 | Jangalia (Summit) 33MW | [8 empty] | 8 | 8 | 8 | 12 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 303200
68 | Summit Cumilla 25MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 13 | 17 | 17 | 0 | 22 | 22 | 20 | 20 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 441510
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 18 |  | 32 | 32 | 32 | 32 | 32 | 32 | 33 | 744660
71 | Summit Maona | 30 | 30 | 30 | 30 | 30 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 791945
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 822100
73 | Ghorashal (Regent) | [7 empty] | 0 | 12 | 13 | 13 | 87 | 102 | 102 | 99 | 101 | 103 | 103 |  | 103 | 103 | 103 | 103 | 103 | 52 | 0 | 1197045
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla)
78 | Gazipur (RPCL) | [8 empty] | 2 | 24 | 37 | 43 | 8 | 8 | 8 | 8 | 32 | 42 |  | 42 | 42 | 42 | 42 | 8 | 0 | 0 | 416868
79 | Kodda 149MW
80 | Jamalpur 95MW | [17 empty] | 19 |  | 64 | 80 | 80 | 80 | 80 | 51 | 0 | 408960
81 | Lakdhanvi 52 MW
82 | Madanganj 102MW | [19 empty] | 1 | 16 | 0 |  |  |  |  | 12216
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 40 | 40 | 40 | 40 | 85 | 85 | 40 | 40 | 40 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 512940
85 | Keraniganj (Powerpac) 100MW
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL)
88 | Ghorashal 78MW (MAX) | [12 empty] | 15 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 0 |  | 388864
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | [15 empty] | 0 | 8 | 60 |  | 20 | 20 | 0 |  |  |  |  | 89040
92 | Fenchuganj (EPL) 44MW | [11 empty] | 0 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 5 | 5 | 220000
93 | Ashuganj (Midland) 51MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 7 | 7 | 7 | 664893
94 | Gagnagar (Orion) |  | 0 | [13 empty] | 0 | 7 | 58 |  | 56 | 32 | 7 | 7 | 0 | 0 |  | 185040
95 | Patenga 50MW | [16 empty] | 0 | 46 |  | 48 | 50 | 50 | 50 | 0 |  |  | 234240
96 | Chattogram ECPV 108 MW | [15 empty] | 0 | 78 | 92 |  | 13 | 13 | 0 |  |  |  |  | 192000
97 | Katpotti 51 MW | [12 empty] | 0 | 17 | 6 | 6 | 6 | 24 |  | 48 | 47 | 47 | 0 | 0 |  |  | 207840
98 | Bosila 108MW | [8 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 47 |  | 47 | 47 | 0 |  |  |  |  | 179721
99 | Madanganj-55 MW | [16 empty] | 0 | 25 |  | 30 | 30 | 30 | 0 | 0 |  |  | 111777
100 | Northern 55 MW | [15 empty] | 0 | 36 | 54 |  | 55 | 55 | 18 | 0 | 0 |  |  | 176605
101 | Kushiara 163 MW CCPP GT | [8 empty] | 0 | 10 | 10 | 10 | 10 | 10 | 20 | 60 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1066238
102 | Sarishabari (Solar) | [6 empty] | 0 | 0.5 | 1.3 | 1.8 | 2.1 | 2.1 | 2 | 1.6 | 1.2 | 0.5 | 0 | [9 empty] | 12950
103 | Banco Energy 54MW | [7 empty] | 0 | 39 | 54 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 54 |  | 54 | 54 | 54 | 54 | 0 | 0 |  | 444960
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 103 |  | 100 | 30 | 7 | 7 | 7 | 7 | 7 | 412800
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | [17 empty] | 43 |  | 79 | 79 | 72 | 38 | 0 | 0 |  | 243360
115 | Juldah 100 MW Unit-3 | [6 empty] | 10 | 30 | 30 | 30 | 30 | 30 | 70 | 70 | 70 | 70 | 0 | 77 |  | 92 | 92 | 92 | 92 | 92 | 20 | 0 | 885120
116 | Chandpur Desh 200MW | [15 empty] | 0 | 5 | 67 |  | 68 | 70 | 70 | 40 | 30 | 0 |  | 295200
117 | Midland 150MW | [15 empty] | 0 | 6 | 62 |  | 100 | 100 | 50 | 0 | 0 |  |  | 279300
118 | Bibiyana-3 285MW
120 | Eastern Zone Total | 3578 | 3454 | 3351 | 3330 | 3278 | 3529 | 3741.6 | 4072.02 | 4297.75 | 4299.6 | 4469.21 | 4782.6 | 4764.4 | 4555.9 | 4564.4 | 4562.4 | 4632.67 | 5605 | 0 | 5829 | 5677 | 5540 | 5385 | 4801 | 4433 | 4172 | 105026135
121
122 | o
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | [16 empty] | 0
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | [15 empty] | 0 | 23 | 40 |  | 40 | 40 | 20 | 19 | 0 |  |  | 136800
Khulna CCPP 225MW
129 | Labon Chora 105 MW | [16 empty] | 0 | 53 |  | 70 | 73 | 70 | 70 | 0 |  |  | 281760
130
131
132
133
| Summit Barisal 110 MW | [16 empty] | 0 | 16 |  | 16 | 16 | 16 | 16 | 0 |  |  | 64320
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 13 | 52 | 52 | 50 | 50 | 50 | 50 | 50 | 51 | 50 | 50 |  | 97 | 95 | 95 | 95 | 95 | 53 | 0 | 1051803
| Bhola CCPP 194MW | 190 | 165 | 165 | 165 | 165 | 165 | 192 | 193 | 190 | 179 | 186 | 189 | 152 | 188 | 162 | 187 | 145 | 190 |  | 190 | 181 | 190 | 168 | 185 | 187 | 192 | 4421310
140 | Bhola (Venture) 33MW | 12 | 14 | 14 | 15 | 15 | 15 | 15 | 18 | 17 | 17 | 16 | 16 | 16 | 9 | 6 | 13 | 14 | 18 |  | 23 | 25 | 22 | 25 | 24 | 23 | 21 | 392700
141 | Bangla Trak Noapara
142 | Noapara (KZA) 40MW | [7 empty] | 0 | 24 | 8 | 8 | 8 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 0 |  | 433125
143 | Gopalganj Peaking | [11 empty] | 0 | 3 | 4 | 6 | 6 | 24 | 36 |  | 34 | 39 | 0 |  |  |  |  | 103168
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 349 | 348 | 348 | 348 | 348 | 348 | 348 | 530 | 532 | 531 | 531 | 529 | 528 | 531 | 531 | 531 | 589 | 669 |  | 669 | 671 | 670 | 670 | 669 | 668 | 463 | 12192000
147 | Bheramara 360 MW | 350 | 300 | 250 | 250 | 250 | 310 | 310 | 350 | 380 | 360 | 360 | 360 | 370 | 340 | 340 | 300 | 300 | 300 |  | 300 | 350 | 420 | 410 | 440 | 400 | 400 | 8490816
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2 | 68 | 68 | 67 | 0 | [22 empty] | 421527
152 | Barapukuria Unit-3 | 140 | 140 | 140 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 |  | 139 | 139 | 139 | 139 | 139 | 139 | 140 | 3435400
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW | 117 | 0 | [14 empty] | 0 | 100 |  | 100 | 80 | 80 | 90 | 90 | 80 | 80 | 784000
| Baghabari Peaking 50MW | [16 empty] | 0 | 25 |  | 8 | 8 | 0 |  |  |  |  | 35624
157 | Sirajgonj Unit-1 225MW (Gas)
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 161 | 139 | 136 | 136 | 139 | 146 | 156 | 186 | 188 | 180 | 179 | 186 | 177 | 137 | 134 | 134 | 134 | 137 |  | 178 | 173 | 175 | 170 | 174 | 179 | 183 | 4054964
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas)
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking
162 | Bogra (GBB) | 3 | 0 | [5 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 3 | 3 | 334080
163 | Bogra (EPL) | [7 empty] | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 79776
164 | Ullapara (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 158076
165 | Amnura 50MW | [15 empty] | 0 | 6 | 50 |  | 50 | 50 | 50 | 50 | 6 | 0 |  | 224580
166 | Katakhali (Northern) | [16 empty] | 0 | 8 |  | 8 | 8 | 0 |  |  |  |  | 18399
167 | Katakhali Peaking
168 | Santahar Peaking | [15 empty] | 0 | 9 | 31 |  | 31 | 31 | 31 | 23 | 0 | 0 |  | 222191
169 | Rajlanka 52 MW | [7 empty] | 0 | 43 | 16 | 8 | 8 | 43 | 43 | 43 | 8 | 8 | 10 |  | 34 | 34 | 43 | 43 | 43 | 0 |  | 379680
170 | Chapainawabganj-100 MW | [15 empty] | 0 | 12 | 51 |  | 65 | 60 | 50 | 12 | 0 | 0 |  | 184064
171
172
173 | Rangpur GT | [19 empty] | 17 | 17 | 17 | 0 | 0 |  |  | 40000
175 | Saidpur GT | [19 empty] | 15 | 15 | 15 | 13 | 13 | 13 | 12 | 72000
176
177
178
178 | Western Zone Total | 1406 | 1190 | 1136 | 1069 | 1072 | 1139 | 1176 | 1456 | 1597 | 1514 | 1509 | 1517 | 1550 | 1513 | 1483 | 1441 | 1525 | 2001 |  | 2162 | 2183 | 2181 | 2091 | 1956 | 1755 | 1504 | 38012163