## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 27-04-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-04-2026 | during | 27-04-2026 | during | 27-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 373 | 412 | 412 | 412 | 392 | 392 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 0 | 55 | 55 | 15 | 55 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 320 | 335 | 335 | 335 | 300 | 300 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 0 | 53.97 | 53.97 | 17 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 15 | 149.36 | 149.36 | 15 | 149 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 20 | 33 | 33 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 14 | 14 | 14 | 14 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 8 | 52.19 | 52.19 | 16 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 97 | 0 | 300 | 300 | 48 | 294 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 35 | 149 | 149 | 52 | 149 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 2 | 105 | 105 | 35 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 162 | 162 | 35 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 19 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 450 | 400 | 584 | 584 | 500 | 500 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 277 | 296 | 718 | 718 | 330 | 330 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 0 | 160 | 160 | 17 | 70 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1771 | 1697 | 5939.22 | 5907.22 | 1892 | 2663
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 0 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 0 | 50 | 50 | 19 | 50 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 37 | 35 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 213 | 224 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 18 | 0 | 105 | 105 | 34 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 14 | 0 | 56 | 64 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 0 | 68 | 0 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 18 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 18 | 37 | 108 | 108 | 12 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.48 | 0 | 3.4 | 0 | 3.4 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 0 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 0 | 110 | 110 | 54 | 54 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 17 | 0 | 163 | 163 | 17 | 54 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 840 | 1224 | 1224 | 1224 | 1224 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 30 | 0 | 46 | 46 | 46 | 46 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 935 | 800 | 935 | 935 | 935 | 935 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2565.48 | 2022 | 3774.26 | 3843.86 | 2799.4 | 3005
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 210 | 202 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 354 | 357 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 300 | 345 | 342.01 | 342.01 | 342.01 | 342.01 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 215 | 300 | 393 | 393 | 230 | 230 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 18 | 0 | 18 | 150 | 18 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 22 | 0 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 102 | 163 | 163 | 100 | 100 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 125 | 0 | 200 | 200 | 17 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 122 | 48 | 84 | 80 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 8 | 17.75 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 0 | 114 | 114 | 0 | 0 | Liquid fuel shortage
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 0 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 23 | 0 | 115 | 115 | 17 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 66 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1601 | 1413 | 2625.69 | 2690.44 | 1621.27 | 1906.27
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-04-2026 | during | 27-04-2026 | during | 27-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 12 | 9 | 157.5 | 157.5 | 31 | 31 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.7 | 0 | 1.82 | 0 | 1.82 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 46 | 65 | 70 | 70 | 70 | 70 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 9 | 10 | 10 | 10 | 10 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 25.47 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 142.17 | 95 | 361.82 | 314 | 175.82 | 140
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 30 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 0 | 0 | 30 | 30 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 153 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 101 | 100 | 100 | 100 | 100 | 100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Tripped
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 53 | 81 | 83 | 83 | 50 | 50 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 17 | 17 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 380 | 392 | 380 | 380 | 380 | 380 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1202 | 1208 | 1264 | 1264 | 1173 | 1173
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 923 | 923 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 30 | 30 | 30 | 30 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 125 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 224 | 190 | 410 | 410 | 250 | 250 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 81 | 0 | 95 | 0 | 95 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1214 | 842 | 1234.2 | 1234.2 | 1194 | 1194 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2567 | 1955 | 3589.2 | 3494.2 | 2616.1 | 2521.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 253 | 300 | 250 | 300 | 250 | 300 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 0 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 0 | 65 | 130 | 130 | 110 | 110 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1200 | 850 | 1244 | 1244 | 1184 | 1184 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 0 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 290 | 171 | 307 | 307 | 290 | 290 | Bad quality coal
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.64 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1996.64 | 1606 | 2412 | 2461 | 2088 | 2137
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 51.31 | 0 | 58 | 0 | 58 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 199 | 130 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 206 | 0 | 220 | 220 | 0 | 0 | Liquid fuel shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 160 | 140 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 391 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 21 | 21 | 0 | 25 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 84 | 84 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 50 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.01 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 761.66 | 764.91 | 748 | 748 | 748 | 748 | U-2 Under Maintenance
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 52.86 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 71 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1897.84 | 1448.91 | 2481.84 | 2256.99 | 1807.26 | 1777.41
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Tripped
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 35 | 113 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 0.2 | 0 | 0 | 0 | 0 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 0 | 70 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 2 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 4 | 0 | 100.25 | 0 | 100.25 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 6.2 | 34 | 356.25 | 228 | 163.25 | 183
System Total |  |  |  |  | 28823.2 | 29270.237 | 13749.33 | 11478.91 | 22804.28 | 22459.71 | 14336.1 | 15505.78
Forecast Scenario (27-04-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11900 |  | 0 |  | 11900
|  |  |  | 1:00 | 11700 |  | 0 |  | 11700
|  |  |  | 2:00 | 11200 |  | 0 |  | 11200
|  |  |  | 3:00 | 10600 |  | 0 |  | 10600
|  |  |  | 4:00 | 9500 |  | 0 |  | 9500
|  |  |  | 5:00 | 8400 |  | 0 |  | 8400
|  |  |  | 6:00 | 7400 |  | 0 |  | 7400
|  |  |  | 7:00 | 7500 |  | 0 |  | 7500
|  |  |  | 8:00 | 8100 |  | 0 |  | 8100
|  |  |  | 9:00 | 9000 |  | 0 |  | 9000
|  |  |  | 10:00 | 9700 |  | 0 |  | 9700
|  |  |  | 11:00 | 10800 |  | 0 |  | 10800
|  |  |  | 12:00 | 12000 |  | 0 |  | 12000
|  |  |  | 13:00 | 13000 |  | 0 |  | 13000
|  |  |  | 14:00 | 13500 |  | 0 |  | 13500
|  |  |  | 15:00 | 13600 |  | 0 |  | 13600
|  |  |  | 16:00 | 13300 |  | 0 |  | 13300
|  |  |  | 17:00 | 13000 |  | 0 |  | 13000
|  |  |  | 18:00 | 13100 |  | 0 |  | 13100
|  |  |  | 18:30 | 13900 |  | 0 |  | 13900
|  |  |  | 19:00 | 14200 |  | 0 |  | 14200
|  |  |  | 19:30 | 14250 |  | 0 |  | 14250
|  |  |  | 20:00 | 14500 |  | 0 |  | 14500
|  |  |  | 21:00 | 14450 |  | 0 |  | 14450
|  |  |  | 22:00 | 14400 |  | 0 |  | 14400
|  |  |  | 23:00 | 14200 |  | 0 |  | 14200
Probable Maximum Temperature: |  |  | 34.0°C
Probable Maximum Demand at Day Peak: |  |  | 12000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14500.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14500.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 312.48 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:03 hrs on 27-04-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 26-04-2026 | [28 empty] | Date: | 26-04-2026 | [28 empty] | Date: | 26-04-2026 | [28 empty] | Date: | 26-04-2026 | [28 empty] | Date: | 26-04-2026 | [17 empty] | Date: | 26-04-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [17 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 257 | 18 | 17 | 55 | 145 | 32 | 32 | 35 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 21 | 21 | 0 | 500 | 17 | 16 | 34 | 0 | 0 | 67 | 47 | 17 | 0 | 0 | 0 | 38 | 55 | 27 | 935 | 17 | 0 | 19 | 0 | 34 | 218 | 0 | 0 | 0 | 612 | 0 | 18 | 0 | 215 | 356 | 300 | 51 | 0 | 211 | 0 | 64 | 98 | 66 | 0 | 17 | 0 | 126 | 0 | 0 | 23 | 305 | 0 | 386 | 42 | 30 | 158 | 0 | 16 | 0 | 11 | 30 | 100 | 0 | 100 | 17 | 59 | 9 | 31 | 0 | 0 | 12 | 6966 | 922 | 250 | 0 | 24 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1225 | 0 | 0 | 0 | 768 | 0 | 31 | 0 | 35 | 35 | 0 | 84 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 217 | 174 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 0 | 220 | 0 | 330 | 1220 | 17 | 6481 | 13447 | 77
01:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 241 | 0 | 0 | 36 | 96 | 32 | 32 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 21 | 20 | 0 | 500 | 17 | 16 | 22 | 0 | 0 | 0 | 47 | 17 | 0 | 0 | 0 | 40 | 42 | 23 | 935 | 17 | 0 | 19 | 0 | 34 | 220 | 0 | 0 | 0 | 817 | 0 | 18 | 0 | 215 | 356 | 300 | 51 | 0 | 210 | 0 | 0 | 98 | 17 | 0 | 17 | 0 | 116 | 0 | 0 | 23 | 305 | 0 | 386 | 42 | 30 | 154 | 0 | 16 | 0 | 11 | 30 | 100 | 0 | 100 | 17 | 59 | 9 | 31 | 0 | 0 | 0 | 6645 | 922 | 250 | 0 | 24 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1221 | 0 | 0 | 0 | 759 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 218 | 162 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 30 | 220 | 0 | 253 | 1244 | 17 | 6240 | 12885 | 76.99
02:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 253 | 0 | 0 | 35 | 48 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 21 | 20 | 0 | 500 | 17 | 16 | 18 | 0 | 4 | 0 | 47 | 0 | 0 | 0 | 0 | 40 | 55 | 28 | 935 | 17 | 0 | 19 | 0 | 34 | 219 | 0 | 0 | 0 | 912 | 0 | 18 | 0 | 215 | 356 | 300 | 51 | 0 | 192 | 0 | 0 | 98 | 17 | 0 | 19 | 0 | 118 | 0 | 0 | 23 | 300 | 0 | 386 | 42 | 30 | 152 | 0 | 16 | 0 | 11 | 30 | 100 | 0 | 100 | 17 | 59 | 9 | 31 | 0 | 0 | 0 | 6660 | 923 | 250 | 0 | 24 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1221 | 0 | 0 | 0 | 765 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 219 | 160 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 65 | 220 | 0 | 251 | 1244 | 17 | 6249 | 12909 | 76.99
03:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 239 | 0 | 0 | 34 | 15 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 21 | 20 | 0 | 450 | 17 | 16 | 19 | 0 | 20 | 0 | 47 | 0 | 0 | 0 | 0 | 40 | 54 | 28 | 935 | 17 | 0 | 19 | 0 | 34 | 219 | 0 | 0 | 0 | 994 | 0 | 18 | 0 | 215 | 357 | 300 | 51 | 0 | 178 | 0 | 0 | 99 | 17 | 0 | 19 | 0 | 108 | 0 | 0 | 23 | 305 | 0 | 383 | 42 | 30 | 149 | 0 | 16 | 0 | 11 | 0 | 100 | 0 | 100 | 0 | 59 | 9 | 31 | 0 | 0 | 0 | 6584 | 923 | 250 | 0 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1217 | 0 | 0 | 0 | 764 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 219 | 156 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 290 | 65 | 220 | 0 | 253 | 1244 | 17 | 6218 | 12802 | 76.98
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 260 | 0 | 0 | 34 | 15 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 21 | 20 | 0 | 400 | 0 | 0 | 18 | 0 | 3 | 0 | 47 | 0 | 0 | 0 | 0 | 40 | 34 | 17 | 935 | 0 | 0 | 19 | 0 | 34 | 220 | 0 | 0 | 0 | 1012 | 0 | 0 | 0 | 315 | 356 | 300 | 51 | 0 | 193 | 0 | 0 | 97 | 0 | 0 | 19 | 0 | 110 | 0 | 0 | 23 | 305 | 0 | 324 | 42 | 30 | 150 | 0 | 0 | 0 | 11 | 0 | 101 | 0 | 100 | 0 | 59 | 9 | 31 | 0 | 0 | 0 | 6377 | 923 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1215 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 219 | 156 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 65 | 220 | 0 | 251 | 1244 | 0 | 6099 | 12476 | 76.98
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 262 | 0 | 0 | 34 | 15 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 21 | 20 | 0 | 450 | 0 | 0 | 19 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 14 | 825 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 1050 | 0 | 0 | 0 | 265 | 356 | 300 | 51 | 0 | 180 | 0 | 0 | 98 | 0 | 0 | 19 | 0 | 102 | 0 | 0 | 23 | 310 | 0 | 324 | 42 | 30 | 157 | 0 | 0 | 0 | 11 | 0 | 100 | 0 | 100 | 0 | 59 | 9 | 31 | 0 | 0 | 0 | 6242 | 923 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1223 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 220 | 165 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 65 | 220 | 0 | 252 | 1244 | 0 | 6146 | 12388 | 76.98
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 260 | 0 | 0 | 36 | 15 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 21 | 20 | 0 | 450 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 40 | 0 | 16 | 860 | 0 | 0 | 19 | 0 | 0 | 221 | 0 | 0 | 0 | 1050 | 1 | 0 | 0 | 265 | 356 | 300 | 51 | 0 | 183 | 0 | 0 | 98 | 0 | 0 | 19 | 0 | 120 | 0 | 2 | 8 | 305 | 0 | 324 | 42 | 30 | 151 | 0 | 10 | 0 | 11 | 0 | 100 | 0 | 100 | 0 | 59 | 9 | 31 | 0.01 | 0.91 | 0 | 6257.96 | 923 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1160 | 0 | 0 | 0 | 767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0 | 0 | 0 | 0.84 | 162 | 0 | 0 | 140 | 157 | 0 | 356 | 0 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 290 | 65 | 180 | 0 | 253 | 1244 | 0 | 5949.39 | 12207.35 | 76.97
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 251 | 0 | 0 | 34 | 15 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 5 | 0 | 19 | 20 | 0 | 450 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 40 | 1 | 9 | 895 | 0 | 0 | 19 | 0 | 4 | 221 | 0 | 0 | 0 | 1117 | 3 | 0 | 0 | 250 | 357 | 300 | 51 | 0 | 177 | 0 | 0 | 99 | 0 | 0 | 14 | 0 | 110 | 0 | 12 | 8 | 310 | 0 | 324 | 42 | 30 | 154 | 0 | 17 | 0 | 11 | 0 | 100 | 0 | 100 | 0 | 59 | 9 | 27 | 0.3 | 3.36 | 0 | 6369.06 | 923 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 1148 | 0 | 0 | 0 | 765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.57 | 6 | 0 | 0 | 5.15 | 166 | 0 | 0 | 140 | 162 | 0 | 341 | 0 | 0.44 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 6 | 0.16 | 0 | 290 | 65 | 180 | 0 | 253 | 1244 | 0 | 5971.32 | 12340.38 | 76.96
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 257 | 0 | 0 | 35 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 8 | 0 | 19 | 20 | 0 | 400 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 | 40 | 17 | 6 | 920 | 0 | 0 | 19 | 0 | 17 | 219 | 0 | 0 | 0 | 1069 | 8 | 0 | 0 | 215 | 356 | 300 | 51 | 0 | 195 | 0 | 0 | 98 | 0 | 0 | 19 | 0 | 106 | 0 | 38 | 8 | 305 | 0 | 324 | 42 | 30 | 149 | 0 | 17 | 0 | 11 | 0 | 101 | 0 | 100 | 0 | 59 | 9 | 27 | 0.6 | 10.78 | 0 | 6320.34 | 923 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 1093 | 0 | 0 | 0 | 767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.11 | 31 | 0 | 0 | 22.57 | 158 | 0 | 0 | 140 | 153 | 0 | 349 | 0 | 1.81 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 0.16 | 0 | 290 | 65 | 180 | 0 | 253 | 1150 | 0 | 5894.65 | 12214.99 | 76.96
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 262 | 0 | 0 | 35 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 19 | 0 | 20 | 20 | 0 | 420 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.92 | 40 | 17 | 0 | 925 | 0 | 0 | 19 | 0 | 17 | 216 | 0 | 0 | 0 | 1062 | 15 | 0 | 0 | 215 | 357 | 300 | 51 | 0 | 202 | 0 | 1 | 40 | 0 | 0 | 19 | 0 | 108 | 0 | 43 | 8 | 315 | 0 | 324 | 42 | 30 | 160 | 0 | 17 | 0 | 11 | 0 | 101 | 0 | 100 | 0 | 59 | 9 | 26 | 1.3 | 27.44 | 0 | 6375.66 | 923 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 1116 | 0 | 0 | 0 | 765.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.21 | 65 | 0 | 0 | 17.03 | 171 | 0 | 0 | 140 | 170 | 0 | 366 | 0 | 1.73 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 72 | 0.24 | 0 | 290 | 65 | 180 | 0 | 253 | 1120 | 0 | 6047.75 | 12423.41 | 76.96
10:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 251 | 1 | 0 | 35 | 15 | 48 | 15 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 26 | 14 | 20 | 14 | 0 | 400 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.12 | 39 | 17 | 10 | 925 | 17 | 0 | 22 | 0 | 17 | 216 | 0 | 0 | 0 | 1130 | 17 | 18 | 0 | 215 | 356 | 300 | 51 | 0 | 193 | 0 | 16 | 40 | 26 | 0 | 19 | 0 | 114 | 0 | 55 | 15 | 325 | 0 | 351 | 42 | 30 | 159 | 5 | 17 | 0 | 11 | 0 | 101 | 0 | 100 | 0 | 68 | 19 | 11 | 1.8 | 44.08 | 0 | 6704 | 923 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 1151 | 0 | 0 | 0 | 765.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.1 | 83 | 0 | 0 | 48.12 | 173 | 0 | 0 | 170 | 190 | 0 | 400 | 0 | 4.22 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 144 | 0.59 | 6 | 290 | 0 | 180 | 0 | 253 | 1150 | 17 | 6272.2 | 12976.2 | 76.94
11:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 261 | 17 | 0 | 35 | 15 | 96 | 15 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 23 | 17 | 20 | 14 | 0 | 400 | 0 | 0 | 18 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1.78 | 38 | 17 | 10 | 935 | 17 | 0 | 19 | 0 | 17 | 216 | 0 | 0 | 0 | 1224 | 19 | 18 | 0 | 215 | 356 | 300 | 51 | 0 | 203 | 0 | 17 | 50 | 37 | 6 | 19 | 0 | 114 | 0 | 65 | 15 | 315 | 0 | 372 | 42 | 30 | 149 | 3 | 17 | 0 | 51 | 0 | 99 | 0 | 100 | 0 | 58 | 46 | 12 | 1.7 | 50.47 | 0 | 7015.95 | 923 | 233 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 69.7 | 1216 | 0 | 0 | 0 | 754.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.73 | 96 | 0 | 0 | 57.25 | 172 | 0 | 0 | 194 | 201 | 0 | 408 | 0 | 4.99 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 7 | 0.29 | 16 | 290 | 0 | 220 | 0 | 253 | 1200 | 17 | 6478.07 | 13494.02 | 76.93
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 277 | 17 | 0 | 35 | 15 | 97 | 15 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 19 | 17 | 20 | 14 | 0 | 450 | 0 | 0 | 18 | 0 | 30 | 0 | 14 | 0 | 0 | 0 | 3.48 | 37 | 17 | 2 | 935 | 17 | 0 | 19 | 0 | 18 | 213 | 0 | 0 | 0 | 1224 | 18 | 18 | 0 | 215 | 354 | 300 | 51 | 0 | 210 | 0 | 23 | 50 | 125 | 9 | 19 | 17 | 122 | 0 | 66 | 22 | 315 | 0 | 380 | 42 | 30 | 155 | 9 | 17 | 0 | 53 | 0 | 101 | 0 | 100 | 0 | 58 | 46 | 12 | 0.7 | 25.47 | 0 | 7281.65 | 923 | 224 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 0 | 81 | 1214 | 0 | 0 | 0 | 761.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.31 | 71 | 0 | 0 | 52.86 | 199 | 0 | 0 | 206 | 160 | 0 | 391 | 0 | 5.01 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.2 | 4 | 0.64 | 16 | 290 | 0 | 220 | 0 | 253 | 1200 | 17 | 6467.68 | 13749.33 | 76.92
13:00 | 0 | 30 | 8 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 247 | 17 | 0 | 35 | 15 | 97 | 15 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 31 | 17 | 20 | 14 | 0 | 430 | 1 | 0 | 19 | 0 | 32 | 0 | 16 | 0 | 0 | 0 | 3.52 | 35 | 21 | 3 | 935 | 17 | 0 | 19 | 0 | 34 | 215 | 0 | 0 | 0 | 1224 | 18 | 18 | 8 | 215 | 356 | 300 | 51 | 0 | 183 | 0 | 17 | 50 | 160 | 8 | 19 | 17 | 126 | 0 | 55 | 22 | 320 | 0 | 381 | 42 | 30 | 157 | 6 | 17 | 0 | 53 | 0 | 101 | 0 | 100 | 0 | 57 | 46 | 12 | 1.1 | 7.64 | 0 | 7253.26 | 923 | 215 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 79 | 1215 | 0 | 0 | 0 | 763.1 | 0 | 0 | 0 | 50 | 13 | 0 | 0 | 0 | 0 | 42.17 | 58 | 0 | 0 | 6.05 | 190 | 0 | 0 | 210 | 160 | 0 | 330 | 0 | 0.74 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0.4 | 2 | 0.45 | 16 | 290 | 0 | 220 | 0 | 253 | 1225 | 17 | 6493.91 | 13747.17 | 76.9
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 267 | 0 | 0 | 35 | 15 | 48 | 15 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 3 | 17 | 21 | 14 | 0 | 350 | 13 | 0 | 18 | 0 | 39 | 0 | 40 | 0 | 0 | 0 | 2.56 | 35 | 47 | 0 | 935 | 17 | 0 | 19 | 0 | 48 | 214 | 0 | 0 | 0 | 1224 | 15 | 18 | 0 | 215 | 356 | 280 | 51 | 0 | 187 | 0 | 17 | 50 | 64 | 9 | 19 | 17 | 134 | 0 | 51 | 26 | 315 | 0 | 362 | 42 | 30 | 144 | 5 | 17 | 0 | 52 | 0 | 100 | 0 | 100 | 0 | 58 | 46 | 11 | 2 | 25.51 | 0 | 6907.07 | 923 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 1225 | 0 | 0 | 0 | 762.59 | 0 | 0 | 0 | 109 | 70 | 0 | 0 | 0 | 0 | 20.28 | 38 | 0 | 0 | 39.05 | 150 | 0 | 0 | 123 | 140 | 0 | 340 | 0 | 4.08 | 0 | 0 | 35 | 0 | 88 | 0 | 0 | 0 | 0.9 | 1 | 0.55 | 16 | 290 | 0 | 220 | 0 | 253 | 1244 | 17 | 6393.45 | 13300.52 | 76.88
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 240 | 0 | 0 | 35 | 15 | 48 | 15 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 16 | 17 | 21 | 14 | 0 | 350 | 45 | 0 | 18 | 0 | 40 | 0 | 35 | 0 | 0 | 0 | 2.12 | 35 | 54 | 0 | 935 | 17 | 0 | 19 | 0 | 101 | 217 | 0 | 0 | 0 | 1224 | 11 | 18 | 0 | 240 | 356 | 250 | 51 | 0 | 177 | 0 | 17 | 50 | 17 | 8 | 19 | 17 | 140 | 0 | 42 | 30 | 320 | 0 | 394 | 42 | 30 | 147 | 4 | 17 | 0 | 63 | 0 | 100 | 0 | 100 | 7 | 49 | 48 | 8 | 0 | 24.72 | 0 | 7069.84 | 923 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 1222 | 0 | 0 | 0 | 766.76 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 12.28 | 17 | 0 | 0 | 8.65 | 150 | 0 | 0 | 123 | 140 | 0 | 321 | 0 | 1.02 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0.5 | 1 | 0.23 | 16 | 290 | 0 | 180 | 0 | 284 | 1230 | 17 | 6042.44 | 13112.28 | 76.86
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 297 | 0 | 4 | 35 | 15 | 48 | 15 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 1 | 17 | 11 | 0 | 0 | 360 | 17 | 0 | 18 | 0 | 39 | 0 | 35 | 0 | 0 | 0 | 1.41 | 35 | 50 | 0 | 935 | 0 | 0 | 19 | 0 | 51 | 215 | 0 | 0 | 0 | 1145 | 6 | 18 | 0 | 225 | 356 | 270 | 51 | 0 | 196 | 0 | 17 | 50 | 17 | 8 | 19 | 0 | 140 | 0 | 26 | 30 | 310 | 0 | 367 | 42 | 30 | 143 | 2 | 17 | 0 | 63 | 0 | 100 | 0 | 100 | 25 | 8 | 24 | 8 | 0 | 0 | 0 | 6762.41 | 922 | 198 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 1171 | 0 | 0 | 0 | 698.35 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2 | 0 | 0 | 2.31 | 1 | 0 | 0 | 1.22 | 130 | 0 | 0 | 123 | 140 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.9 | 1 | 0.13 | 0 | 266 | 0 | 180 | 0 | 304 | 1182 | 0 | 5698.11 | 12460.52 | 76.84
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 215 | 0 | 17 | 35 | 15 | 0 | 15 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 310 | 13 | 0 | 21 | 0 | 43 | 0 | 35 | 0 | 0 | 0 | 0.43 | 35 | 47 | 2 | 850 | 0 | 0 | 19 | 0 | 17 | 189 | 0 | 0 | 0 | 875 | 2 | 18 | 0 | 225 | 330 | 250 | 10 | 0 | 192 | 0 | 0 | 50 | 0 | 0 | 10 | 0 | 110 | 0 | 11 | 30 | 310 | 0 | 300 | 42 | 30 | 135 | 0 | 17 | 0 | 23 | 0 | 90 | 0 | 100 | 17 | 8 | 8 | 8 | 0 | 1.36 | 0 | 5767.79 | 922 | 194 | 0 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 894 | 0 | 0 | 0 | 571.1 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 123 | 140 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 8 | 0.1 | 0 | 174 | 0 | 180 | 0 | 270 | 1040 | 0 | 5004.9 | 10772.69 | 76.82
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 380 | 0 | 0 | 33 | 0 | 23 | 0 | 36 | 0 | 0 | 0 | 0 | 35 | 0 | 2 | 720 | 0 | 0 | 50 | 1 | 0 | 188 | 0 | 0 | 0 | 619 | 0 | 0 | 0 | 225 | 310 | 220 | 0 | 0 | 157 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 118 | 0 | 0 | 23 | 265 | 0 | 309 | 42 | 18 | 125 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 100 | 0 | 0 | 0 | 8 | 0 | 0.15 | 0 | 4839.15 | 873 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 765 | 0 | 0 | 0 | 422.54 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7 | 0 | 0 | 1.68 | 7 | 0 | 0 | 3.21 | 130 | 0 | 0 | 90 | 140 | 0 | 337 | 0 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 5 | 0.01 | 0 | 140 | 0 | 180 | 0 | 241 | 740 | 0 | 4235.52 | 9074.67 | 76.8
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 0 | 222 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 20 | 6 | 0 | 350 | 0 | 0 | 38 | 0 | 16 | 62 | 46 | 0 | 0 | 0 | 0 | 35 | 0 | 4 | 800 | 0 | 0 | 50 | 8 | 0 | 217 | 0 | 0 | 0 | 830 | 0 | 0 | 0 | 250 | 357 | 300 | 10 | 0 | 184 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 300 | 0 | 389 | 42 | 30 | 147 | 0 | 0 | 0 | 63 | 0 | 100 | 0 | 100 | 0 | 5 | 24 | 8 | 0 | 0 | 1 | 5970 | 922 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 898 | 0 | 0 | 0 | 567.97 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 140 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 180 | 0 | 244 | 780 | 0 | 4628.87 | 10598.87 | 76.78
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416 | 0 | 234 | 0 | 0 | 17 | 0 | 0 | 0 | 35 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 20 | 10 | 0 | 350 | 0 | 0 | 38 | 0 | 3 | 68 | 39 | 0 | 0 | 0 | 0 | 35 | 0 | 4 | 800 | 0 | 0 | 50 | 8 | 0 | 218 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 250 | 357 | 300 | 51 | 0 | 192 | 0 | 0 | 101 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 300 | 0 | 392 | 30 | 30 | 148 | 0 | 0 | 0 | 63 | 0 | 100 | 0 | 100 | 0 | 24 | 45 | 8 | 0 | 0 | 12 | 6163 | 923 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 902 | 0 | 0 | 0 | 630.52 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 140 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 65 | 180 | 0 | 301 | 840 | 0 | 4897.42 | 11060.42 | 76.78
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 249 | 0 | 4 | 17 | 0 | 0 | 0 | 35 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 20 | 14 | 0 | 350 | 0 | 0 | 37 | 0 | 2 | 68 | 46 | 0 | 0 | 0 | 0 | 35 | 0 | 3 | 800 | 0 | 0 | 50 | 0 | 0 | 216 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 250 | 358 | 345 | 51 | 0 | 199 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 310 | 0 | 392 | 30 | 30 | 152 | 0 | 0 | 0 | 63 | 0 | 100 | 0 | 100 | 0 | 24 | 45 | 8 | 0 | 0 | 12 | 6244 | 923 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 827 | 0 | 0 | 0 | 642.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 65 | 220 | 0 | 300 | 850 | 0 | 4918.47 | 11162.47 | 76.76
21:00 | 0 | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 296 | 0 | 17 | 35 | 15 | 0 | 0 | 35 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 20 | 14 | 0 | 400 | 0 | 0 | 37 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 18 | 800 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 300 | 357 | 345 | 51 | 0 | 202 | 0 | 0 | 102 | 0 | 0 | 8 | 0 | 48 | 0 | 0 | 0 | 305 | 0 | 392 | 30 | 30 | 153 | 0 | 17 | 0 | 81 | 0 | 100 | 0 | 100 | 0 | 9 | 65 | 9 | 0 | 0 | 12 | 6435 | 923 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 842 | 0 | 0 | 0 | 764.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 65 | 220 | 0 | 300 | 850 | 0 | 5043.91 | 11478.91 | 76.75
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 299 | 0 | 17 | 51 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 18.5 | 14 | 0 | 420 | 0 | 0 | 31 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 26 | 800 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1032 | 0 | 0 | 0 | 225 | 357 | 345 | 51 | 0 | 180 | 0 | 0 | 102 | 0 | 0 | 8 | 0 | 72 | 0 | 0 | 0 | 315 | 0 | 392 | 30 | 30 | 161 | 0 | 17 | 0 | 63 | 0 | 100 | 0 | 100 | 0 | 9 | 56 | 8 | 0 | 0 | 12 | 6431.5 | 923 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 982 | 0 | 0 | 0 | 765.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 65 | 220 | 0 | 304 | 900 | 0 | 5283.88 | 11715.38 | 76.74
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 273 | 0 | 17 | 54 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 18.5 | 14 | 0 | 400 | 0 | 0 | 12 | 0 | 5 | 67 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 28 | 800 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1130 | 0 | 0 | 0 | 215 | 357 | 345 | 51 | 0 | 170 | 0 | 0 | 103 | 0 | 0 | 8 | 0 | 76 | 0 | 0 | 0 | 310 | 0 | 392 | 30 | 30 | 157 | 0 | 17 | 0 | 63 | 0 | 101 | 0 | 100 | 0 | 9 | 56 | 8 | 0 | 0 | 12 | 6411.5 | 923 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1125 | 0 | 0 | 0 | 755.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 140 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 65 | 220 | 0 | 315 | 1060 | 0 | 5587.81 | 11999.31 | 76.73
Total KWH | 0 | 413760 | 199680 | 0 | 0 | 0 | 0 | 0 | 8823600 | 0 | 6308400 | 58680 | 113040 | 920880 | 492000 | 623509 | 350696 | 195506 | 563040 | 0 | 0 | 0 | 0 | 0 | 35910 | 7025667 | 0 | 0 | 155599 | 199200 | 448200 | 346320 | 0 | 9836818.18 | 155564 | 50182 | 524160 | 0 | 313440 | 411895 | 483552 | 21423 | 0 | 0 | 20027 | 894600 | 550330 | 267840 | 21192727.27 | 155564 | 0 | 513120 | 15829.2 | 567054 | 5067068 | 0 | 0 | 0 | 24398179 | 125550 | 234181 | 8865 | 5706000 | 8840500 | 7334000 | 1156284 | 0 | 4726000 | 0 | 168000 | 1810908 | 518400 | 59640 | 337110 | 71820 | 2453760 | 0 | 414418 | 374976 | 7463000 | 0 | 8855000 | 924000 | 709800 | 3601800 | 36185 | 300864 | 0 | 839040 | 79392 | 2284000 | 0 | 2403030 | 132840 | 999600 | 664800 | 379200 | 9350 | 231000 | 52800 | 157019172.65 | 22024000 | 5491872 | 0 | 94560 | 83328 | 0 | 884020 | 0 | 0 | 0 | 0 | 542160 | 26385460 | 0 | 0 | 0 | 16880422 | 0 | 0 | 0 | 110784 | 154464 | 0 | 67968 | 51743 | 0 | 269056 | 484420 | 0 | 0 | 290256 | 3769909 | 0 | 0 | 3285155 | 3955180 | 0 | 8776800 | 0 | 25440 | 0 | 0 | 55642 | 21392 | 314505 | 0 | 0 | 0 | 4621.44 | 252720 | 3925 | 153504 | 6284000 | 887000 | 5164310 | 0 | 6472727 | 27387636.36 | 163200 | 140792179.8 | 297811352.45

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 26-04-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13749.33 | MW | 12:00 Hr. | Energy Generated |  |  | 297.8114 |  | MKWHr.
| Day Peak Demand |  |  | 14283.33 | MW | 12:00 Hr. | Energy Unserverd |  |  | 9.776 |  | MKWHr.
| Evening Peak Generation |  |  | 11478.91 | MW | 21:00 Hr. | Energy Demand |  |  | 307.5874 |  | MKWHr.
| Evening Peak Demand |  |  | 11478.91 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34 |  | °C
| Minimum Generation of the Day |  |  | 10598.87 | MW | 19:00 Hr. | Total Gas Supplied |  |  | 866.53 |  | MMCFD
| Maximum Generation of the Day |  |  | 13749.33 | MW | 12:00 Hr. | Production Cost per KWHr |  |  | 5.699 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.789 | 0 | 4.1659 | 0 | 0 | 0.1556 | 0 | 0 | 37.1105 | Gas | 123.9278 | Gas | 428672845.8506
| Chattogram Zone |  |  | 5.3349 | 45.5909 | 3.4487 | 0 | 0.8946 | 0.14558 | 0 | 0.31344 | 55.7281 | Coal | 112.1207 | Coal | 760694134.2319
| Cumilla Zone |  |  | 29.9197 | 0 | 1.427 | 0 | 0 | 0.41442 | 2.4538 | 0 | 34.2149 | HFO | 12.1413 | HFO | 208043367.38
| Mymensingh Zone |  |  | 0.3792 | 0 | 1.85 | 0 | 0 | 0.24035 | 0 | 0 | 2.4696 | HSD | 4.1692 | HSD | 30645181.5
| Sylhet Zone |  |  | 27.4599 | 0 | 0 | 0 | 0 | 0.036185 | 0 | 0 | 27.4961 | Hydro | 0.8946 | Hydro | 89460
| Khulna Zone |  |  | 5.4919 | 26.3855 | 0.17789 | 0.88402 | 0 | 0.54216 | 22.024 | 0 | 55.5054 | Solar | 2.8861 | Solar | 44063143.708
| Barishal Zone |  |  | 6.0513 | 40.1444 | 0.3167 | 0 | 0 | 0.003925 | 0 | 0 | 46.5163 | Import | 41.3582 | Import | 220395165.58
| Rajshahi Zone |  |  | 16.5019 | 0 | 0.38496 | 3.2852 | 0 | 1.0692 | 16.8804 | 0 | 38.1216 | Wind | 0.31344 | Wind | 4610702.4
| Rangpur Zone |  |  | 0 | 0 | 0.37015 | 0 | 0 | 0.27873 | 0 | 0 | 0.64888
| Total |  |  | 123.9278 | 112.1207 | 12.1413 | 4.1692 | 0.8946 | 2.8861 | 41.3582 | 0.31344 | 297.8114
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 428672845.8506 |  | Hydro | 89460
|  |  |  | Coal | 760694134.2319 |  | Solar | 44063143.708
|  |  |  | HFO | 208043367.38 |  | Import | 220395165.58
|  |  |  | HSD | 30645181.5 |  | Wind | 4610702.4
[5 empty] | Total: | 169,72,14,000 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.024 | Peak Hr Flow | 923.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 43580127.27 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 16.8804 | Peak Hr Flow | 764.91 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 969 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.4538 | Peak Hr Flow | 48.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2747 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 41.3582 | Peak Hr Flow | 1735.91 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4599
|  |  |  | Chattogram |  | 0 |  | 1094
|  |  |  | Cumilla |  | 0 |  | 466
|  |  |  | Mymensingh |  | 0 |  | 807
|  |  |  | Sylhet |  | 0 |  | 251
|  |  |  | Khulna |  | 0 |  | 1661
|  |  |  | Barishal |  | 0 |  | 448
|  |  |  | Rajshahi |  | 0 |  | 1182
|  |  |  | Rangpur |  | 0 |  | 638
|  |  |  | Total |  | 0 |  | 11146
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20 | 1 | Patenga 50MW PP (Baraka) |  |  | 50
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 50
|  |  |  | Total Unavailable Capacity |  |  |  | 370
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:45 | 20:40 | Nabinagar 132/33kV S/S T-1 LT Project Work S/D Due to clamp connector replacement due to
red hot maintenance
| 08:45 | 20:40 | Nabinagar 132/33kV S/S T-1 HT Project Work S/D Due to clamp connector replacement due to
red hot maintenance
| 08:50 | 17:22 | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-2 Project Work S/D from Rangpur 132/33kV
end.
| 09:07 | 16:46 | Khulna (C) S/S TR-1 425T LT Project Work S/D Due to Due to x-former painting work.
| 09:08 | 16:45 | Khulna (C) S/S TR-1 425T HT Project Work S/D Due to Due to x-former painting work
| 10:20 | 17:30 | Niamatpur 132/33kV S/S 132kV Rahanpur Ckt-1 Forced S/D Due to Extra sound at inside of
rahanpur ckt 1 Y phase breaker.
| 10:30 | 14:45 | Savar 132/33kV S/S T-1 LT Scheduled S/D
| 10:32 | 14:45 | Savar 132/33kV S/S T-2 HT Scheduled S/D
| 10:54 | 12:21 | Barapukuria-Rangpur 132 kV Ckt-2 Tripped from Barapukuria 230/132/33kV end showing Simens
siprotec relays Due to Zone 01Trip
| 11:13 | 17:32 | Rahanpur 400/132kV S/S Rahanpur-Niamatpur 132 KV Line Ckt-01 Forced S/D
| 12:00 |  | Day Peak Generation: 13745 MW.
| 12:55 | 13:04 | Baghabari-Shahjadpur 132 kV Ckt-1 Tripped from Shahjadpur 132/33kV end showing N/A relays
Due to N/A
| 13:55 | 16:17 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Scheduled S/D Due to 33 kv Prib feeder source | [7 empty] | 35.0MW load
|  |  | side red hot | [7 empty] | interrup.
| 13:56 | 16:16 | Mahasthangarh 132/33kV S/S 416T MTR 2 HT Scheduled S/D Due to 33 kv Prib feeder source | [7 empty] | 35.0MW load
|  |  | side red hot | [7 empty] | interrup.
| 14:14 | 14:28 | Jaldhaka-Saidpur 132kV Ckt-2 Tripped from Saidpur 132/33kV end showing Distance relay,
zone -2 relays.
| 14:35 | 15:25 | Sunamganj 132/33kV S/S Tr-1 HT Forced S/D Due to Shutdown due to PDB Busbar maintenance
| 16:00 | 16:24 | Tangail 132/33kV S/S Kaliakair-1 Tripped showing REL 316*4 relays Due to Main Protection
Operated Distance-Trip
| 16:41 |  | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) HT Tripped showing DIFFERENTIAL PROTECTION
P632 relays Due to Not Finding
| 16:41 |  | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) LT Tripped showing DIFFERENTIAL PROTECTION
P632 relays Due to Not Finding
| 17:03 | 20:56 | Aminbazar 400/230/132kV S/S 230/132kv Tr-02 LT Tripped showing Diff (R, Y, B) ph
trip General trip relays Due to 33KV Auxiliary Bus Ph to Ph short
| 17:14 | 18:44 | Keraniganj-Nawabganj 132kV Ckt-1 Tripped from Keranigonj 230/132/33kV end showing 86.1
relays Due to 50/67N earth fault trip & Zone-1 trip and from Nawabganj 132/33kV end
showing DISTANCE PROTECTION RELAY P443, LOCK OUT RELAY 1 & 2, BUSBAR PROTECTION. relays
Due to Extreme strom, DISTANCE TRIP Z-1,
| 17:14 |  | Keranigonj 230/132/33kV S/S 132 kV Hasnabad Ckt. 1 Tripped showing 86.1 relays Due to
SOTF & Zone -1 trip
| 17:15 | 19:01 | Madanganj 132/33kV S/S GT-2 HT Tripped showing R,Y, B phase trip General trip O/C and | [7 empty] | 10.0MW load
|  |  | earth fault trip relays Due to Heavy Storm and rain | [7 empty] | interrup.
| 17:15 | 19:13 | Madanganj 132/33kV S/S GT-2 LT Tripped showing Phase instants fault relays Due to Heavy | [7 empty] | 10.0MW load
|  |  | Storm and rain | [7 empty] | interrup.
| 17:19 | 18:20 | Postogola 132/33kV S/S GT-1 LT Tripped showing RET670 relays Due to GT-1 tripped due to | [7 empty] | 46.0MW load
|  |  | over flux 46 | [7 empty] | interrup.
| 17:19 | 21:21 | Postogola 132/33kV S/S GT-2 HT Tripped showing RET670 relays Due to GT-2 tripped due to
over flux
| 17:24 | 17:56 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing Gen. Trip,Non Dir OC DMT Trip relays
Due to Shaistaganj Feeder Over Curent Earth Fault.
| 17:25 | 17:56 | Shahjibazar 132/33kV S/S TR-04 LT Tripped showing Trip Relay-1, General Trip, Y&B PH
Trip, Non Dir OC relays Due to Habiganj Bypass Feeder Over Current Earth.
| 17:26 | 18:46 | Keranigonj 230/132/33kV S/S 132 kV Lalbagh Ckt. 3 Tripped showing 86.1 relays Due to SOTF | [7 empty] | 66.0MW load
|  |  | & Zone-1 trip | [7 empty] | interrup.
| 18:01 | 18:43 | Kasba 132/33kV S/S Muradnagar-Kasba Ckt-1 Tripped showing Distance(F21) relays Due to Bad
weather
| 18:09 |  | Sirajgonj 225MW CCPP Unit-2 ST Shutdown with remarks:- As per NLDC request to shutdown
the plant
| 18:09 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- ST
| 18:17 |  | Sirajgonj 225MW CCPP Unit-2 GT Shutdown with remarks:- As per NLDC request to shutdown
the plant (XEN, Fahad Mahmud)
| 18:17 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- GT
| 18:47 | 19:41 | Cumilla(S)-Kachua 132 kV Ckt-1 Tripped from Cumilla(S) 132/33kV end showing REL670 relays | [7 empty] | 7.0MW load
|  |  | Due to B-ph, zone1, SOTF, | [7 empty] | interrup.
Cumilla(S) 132/33kV
end
| 20:02 | 22:15 | Chandpur 132/33kV S/S 412T (T-2) LT Forced S/D Due to Maintainance
| 20:02 | 22:15 | Chandpur 132/33kV S/S 422T(T-5) LT Forced S/D Due to Maintainace
| 20:08 | 21:29 | Madunaghat 132/33kV S/S TR-1(507T) LT Tripped showing REL 615 relays Due to Due to 33 kv | [7 empty] | 29.0MW load
|  |  | feeder fault | [7 empty] | interrup.
| 20:12 | 21:08 | Bhangura 132/33kV S/S Tr-2(413T) LT Forced S/D Due to red hot 33 kv side
| 20:12 | 21:07 | Bhangura 132/33kV S/S Tr-2(413T) HT Forced S/D Due to red hot 33 kv side
| 20:35 | 22:11 | Patiya 132/33kV S/S BUS I Forced S/D Due to Pbs 33 kv fedeer load side redhot | [7 empty] | 12.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 21:00 |  | Evening Peak Generation is 11478 MW.
| 21:16 | 22:14 | Chandpur 132/33kV S/S 422T(T-5) HT Scheduled S/D Due to Maintainace Work at 33kv Side
| 21:16 | 22:14 | Chandpur 132/33kV S/S 412T (T-2) HT Scheduled S/D Due to Maintainace Work at 33kv Side | [7 empty] | 5.0MW load
interrup.
| 21:55 | 23:21 | Daudkandi 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Red hot maintenance by PBS-3
at 33 kV switchyard
| 21:56 | 23:20 | Daudkandi 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Red hot maintenance by PBS-3
at 33 kV switchyard
| 22:35 | 23:42 | Narshingdi 132/33kV S/S T-4 HT Scheduled S/D Due to Redhot maintenance
| 22:35 | 23:43 | Narshingdi 132/33kV S/S T-4 LT Scheduled S/D Due to Redhot maintenance
| 23:00 | 23:39 | Chandina 132/33kV S/S TR-3 LT Forced S/D Due to For Pbs fedder R phase DS red hot problem
| 23:09 | 23:22 | Shahjibazar 132/33kV S/S TR-04 LT Tripped showing General Trip, Y PH Trip, B PH Trip, Non
Dir EF relays Due to Madhabpur-1 feeder fault
| 00:06 | 00:53 | Bhangura 132/33kV S/S Tr-1(403T) LT Forced S/D Due to 33 kv bua red hot remove
| 00:08 | 00:51 | Bhangura 132/33kV S/S Tr-1(403T) HT Forced S/D Due to 33 kv bua red hot remove
| 01:40 | 02:47 | Purbasadipur-Saidpur 132kV Ckt-1 Tripped from Saidpur 132/33kV end showing 1) Distance
Relay, C 2) Auto Reclose fail relays. and from Purbasadipur 230/132/33kV end showing
Siprotech,siemens relays Due to Thundering
| 03:30 | 04:10 | Sirajganj-Ullahpara 132KV Ckt-1 Tripped from Sirajganj 132/33kV end showing Quadramho
SHPM 101-(21) Power Swing (B Ph) relays.
| 04:02 | 07:10 | Bogura 230/132kV S/S Confidance UN-2 Tripped showing Over voltage trip relays Due to
stormy weather
| 04:12 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Forced S/D Due to Reduce system
voltage
| 04:12 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 Forced S/D Due to Reduce system
voltage
| 04:56 |  | Jamalpur-Mymensingh 132kV Ckt-1 Forced S/D from Jamalpur 132/33kV end Due to open due to
over voltage
| 05:08 |  | Rajendrapur 132/33kV S/S MTR-3 LT Tripped showing REF630 relays Due to 81 trip | [7 empty] | 15.0MW load
interrup.
| 05:08 |  | Rajendrapur 132/33kV S/S MTR-1 LT Tripped showing REF 630 relays Due to 81 trip | [7 empty] | 20.0MW load
interrup.
| 05:08 |  | Rajendrapur 132/33kV S/S MTR-2 LT Tripped showing REF 630 relays Due to 81 trip | [7 empty] | 15.0MW load
interrup.
| 05:10 |  | Mirzapur 132/33kV S/S Mirzapur-Tangail-ckt-2A(E04) Tripped showing Bay contro Protection | [7 empty] | 34.0MW load
|  |  | Unit -FB CPU relays Due to Storm and rain system Over Voltage | [7 empty] | interrup.
| 05:11 | 07:28 | Bhaluka-Mymensingh 132 kV Ckt-1 Tripped from Bhaluka 132/33kV end showing Distance Relay
relays Due to O ver voltage Trip
| 05:11 | 07:28 | Bhaluka-Mymensingh 132 kV Ckt-2 Tripped from Bhaluka 132/33kV end showing Distance relay
relays Due to Over voltage Trip
| 05:11 |  | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Tripped showing Distance PROTN RLY relays Due to
Over voltage trip
| 05:11 |  | Bhaluka 132/33kV S/S BR Powergen Ckt- 02 Tripped showing Distance PROTN RLY relays Due to
Over voltage Trip
| 05:12 |  | Mymensingh RPCL-Tangail 132kV Ckt-1 Tripped from Muktagacha 132/33kV end showing O/V
relay relays Due to Over voltage and from Muktagacha 132/33kV end showing O/V relays Due
to Over voltage
| 05:12 | 06:36 | Mymensingh RPCL-Tangail 132kV Ckt-2 Tripped from Muktagacha 132/33kV end showing O/V
relays Due to Over voltage
| 05:12 | 06:36 | Muktagacha 132/33kV S/S RPCL-2 Tripped showing O/v relay relays Due to O/v
| 05:20 |  | Jamalpur United (20MW)-Jamalpur 132kV Ckt-1 Forced S/D from Jamalpur 132/33kV end Due to
Open due to over voltage
| 05:38 | 07:22 | Kabirpur -Tongi 132kV Ckt-2 Tripped from Tongi 230/132/33kV end showing
Y,B-Phase OV/DTT AR BLOCKED SYNCH NOT OK relays.
| 06:00 |  | Minimum Generation: 7332 MW
| 06:02 |  | Sreepur 230/132/33kV S/S 230/132 kV T-2 HT Tripped showing 86.1 86.2 relays Due to Over | [7 empty] | 5.0MW load
|  |  | Voltage | [7 empty] | interrup.
| 06:02 |  | Sreepur 230/132/33kV S/S 230/132 kV T-1 HT Tripped showing 86.1 and 86.2 relays Due to
Over Voltage
| 06:03 | 07:15 | Bakulia 132/33kV S/S T-2 (412T) LT Forced S/D Due to 33KV side Y-phase terminal point
emergency Hot Spot maintenance work.
| 06:03 |  | Mirpur-Uttara 3PH 132kV Ckt-1 Tripped from Mirpur 132/33kV end showing Line
Differential/Distance relay.( Siemens, siprotec 7DL87) relays Due to Over Voltage.
| 06:05 |  | Mirpur-Uttara 3PH 132kV Ckt-1 Forced S/D from Mirpur 132/33kV end Due to Fault
rectification.
| 06:08 | 06:33 | Shahjibazar 132/33kV S/S SPCL 86 MW Tripped showing P341 operated relays Due to Heavy
Rain with Thundering
| 06:12 |  | Aminbazar-Kallyanpur 132kV Ckt-2 Tripped from Aminbazar 400/230/132kV end showing
Overvoltage Protection relays Due to Over Voltage
| 06:34 |  | Jhenaidah 132/33kV S/S Transformer T-1 LT Forced S/D | [7 empty] | 15.0MW load
interrup.
| 06:34 |  | Jhenaidah 132/33kV S/S Transformer T-1 HT Forced S/D Due to Redhot maintenance | [7 empty] | 15.0MW load
interrup.
| 06:37 |  | Muktagacha 132/33kV S/S T-1(404T) HT Tripped showing 0/v relay relays Due to
24-overexitation
| 06:37 |  | Muktagacha 132/33kV S/S T-2(414T) HT Tripped showing Over excitation relays Due to Over
voltage
| 06:37 |  | Muktagacha 132/33kV S/S T-3(424T) HT Tripped showing Over excitation relays Due to Over
voltage
| 06:42 | 06:46 | Jamalpur-Mymensingh 132kV Ckt-2 Forced S/D from Jamalpur 132/33kV end Due to Open due to
over voltage
| 06:50 | 06:55 | Jamalpur 132/33kV S/S T-4 HT Tripped showing Lockout relays Due to Over voltage
| 06:50 | 06:55 | Jamalpur 132/33kV S/S T-4 LT Tripped showing Lockout relays Due to Over voltage
| 07:04 |  | Jamalpur 132/33kV S/S T-4 HT Tripped showing Lockout relays Due to Over voltage
| 07:04 |  | Jamalpur 132/33kV S/S T-4 LT Tripped showing Lockout relays Due to Over voltage
| 07:12 |  | Halishahar-Khulshi 132kV Ckt-1 Project Work S/D from Halishahar 132/33kV end Due to Line
parameters check
| 07:15 |  | Joypurhat 132/33kV S/S Transformer T-1 (407 T) LT Forced S/D Due to Due to 33kv bus side | [7 empty] | 7.0MW load
|  |  | loop jumper maintenence.(Baliatoir feeder). | [7 empty] | interrup.
| 07:16 |  | Joypurhat 132/33kV S/S Transformer T-1 (407 T) HT Forced S/D Due to Due to 33kv bus side | [7 empty] | 7.0MW load
|  |  | loop jumper maintenence.(Baliatoir feeder). | [7 empty] | interrup.
| 07:16 |  | Joypurhat 132/33kV S/S Transformer T-2 (417 T) LT Forced S/D Due to Due to 33kv bus side
loop jumper maintenence.(Baliatoir feeder).
| 07:17 |  | Bakulia 132/33kV S/S T-1 (402T) LT Forced S/D Due to Hot Spot Maintenance work.
| 07:17 |  | Joypurhat 132/33kV S/S Transformer T-2 (417 T) HT Forced S/D Due to Due to 33kv bus side
loop jumper maintenence.(Baliatoir feeder).
| 07:17 |  | Bakulia 132/33kV S/S T-1 (402T) LT Forced S/D Due to Hot Spot Maintenance work.
| 07:27 |  | Bhaluka 132/33kV S/S Sreepur Ckt- 01 Tripped showing Busbar bay unit relays Due to CB
open by NLDC
| 07:27 |  | Bhaluka 132/33kV S/S Sreepur Ckt- 02 Tripped showing Busbar bay unit relays Due to CB
Open by NLDC
|  | 07:28 | Bhaluka-Mymensingh 132 kV Ckt-2 is restored.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 26-04-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 412 | 8823600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 350696 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7025667 | Machine Problem
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 58680 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 15 | 492000 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 195506 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 35910 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 448200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 346320 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 199680 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 623509 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 35 | 920880 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 2 | 413760 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 563040 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 155599 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 113040 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 9836818.18 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 296 | 6308400 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 199200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1697 | 37110505.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 15829.2 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 125550 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 513120 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 35 | 894600 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 224 | 5067068 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 567054 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 483552 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 411895 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 18 | 267840 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 37 | 524160 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20027 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 50182 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 21423 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 550330 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 155564 | Liquid fuel shortage
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 155564 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 840 | 24398179 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 313440 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 800 | 21192727.27 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 2022 | 55728104.47
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 202 | 4726000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 357 | 8840500 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 345 | 7334000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 300 | 5706000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 8865 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1156284 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 234181 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 374976 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 102 | 1810908 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 518400 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 48 | 2453760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 8 | 337110 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 71820 | Liquid fuel shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 59640 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 168000 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 414418 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1413 | 34214862
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 9 | 379200 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9350 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 65 | 664800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 999600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 231000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 52800 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 132840 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 95 | 2469590
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 36185 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 924000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 709800 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 153 | 3601800 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 100 | 2284000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 79392 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 839040 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2403030 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 300864 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7463000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 392 | 8855000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1208 | 27496111
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 923 | 22024000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 94560 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 884020 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 83328 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 190 | 5491872 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 542160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 842 | 26385460 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1955 | 55505400
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 300 | 6472727 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 153504 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 65 | 887000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 850 | 27387636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5164310 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 163200 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 171 | 6284000 | Bad quality coal
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3925 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1606 | 46516302.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 269056 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 51743 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 130 | 3769909 | -
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 3285155 | Plant is running with HSD as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 140 | 3955180 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 8776800 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Liquid fuel shortage
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 67968 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 154464 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 110784 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 25440 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 764.91 | 16880422 | U-2 Under Maintenance
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 290256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 484420 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1448.91 | 38121597
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Tripped
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 314505 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 4621.44 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 55642 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 21392 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 252720 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 34 | 648880.44
Eastern Grid Total |  |  |  |  | 17418.042 | 6435 | 157019172.65
Western Grid Total |  |  |  |  | 11852.195 | 5043.91 | 140792179.8
National Grid Total |  |  |  |  | 29270.237 | 11478.91 | 297811352.45
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 26-04-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7216.88 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3929 | MW
i) Dhaka area |  |  | 4599.18 |  | MW | i) Khulna area |  |  |  | 1661 | MW
ii) Chattogram area |  |  | 1093.7 |  | MW | ii) Barishal area |  |  |  | 448 | MW
iii) Cumilla area |  |  | 466 |  | MW | iii) Rajshahi area |  |  |  | 1182 | MW
iv) Mymensingh area |  |  | 807 |  | MW | iv) Rangpur area |  |  |  | 638 | MW
v) Sylhet area |  |  | 251 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11145.88 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 100 | 02:00 | 133 | Natore | 160 | 03:00
2 | AKSML | 13 | 19:00 | 68 | Hathazari | 96 | 19:00 | 134 | Nawabganj | 57.4 | 02:00
3 | Aftabnagar | 42 | 00:00 | 69 | Hatirjheel | 52 | 13:00 | 135 | Netrakona | 94 | 21:00
4 | Agargaon | 130 | 13:00 | 70 | Ishurdi | 80 | 15:00 | 136 | New | 86 | 14:00
5 | Agrabad | 78 | 12:00 | 71 | Jaldhaka | 60 | 19:00 | 137 | Niamatpur | 83 | 07:00
6 | Amnura | 38 | 00:00 | 72 | Jamalpur | 87 | 12:00 | 138 | Noapara | 49 | 19:00
7 | Ashuganj | 87 | 01:00 | 73 | Jashore | 157 | 00:00 | 139 | PHP | 10 | 11:00
8 | BSRM | 196 | 02:00 | 74 | Jhenaidah | 113 | 02:00 | 140 | Pabna | 102 | 03:00
9 | Bagerhat | 92 | 18:30 | 75 | Joydebpur | 136 | 00:00 | 141 | Palashbari | 68 | 19:30
10 | Bajitpur | 75 | 00:00 | 76 | Joypurhat | 60 | 08:00 | 142 | Panchagarh | 53 | 00:00
11 | Bakerganj | 13 | 02:00 | 77 | Juldah | 15 | 13:00 | 143 | Patiya | 12 | 23:00
12 | Bakulia | 104 | 18:30 | 78 | KSRM | 11 | 01:00 | 144 | Patuakhali | 74 | 20:00
13 | Banani | 60 | 13:00 | 79 | Kabirpur | 257 | 20:00 | 145 | Payra | 34 | 02:00
14 | Bangabhaban | 22 | 10:00 | 80 | Kachua | 97 | 03:00 | 146 | Postogola | 60 | 00:00
15 | Barapukuria | 55 | 19:30 | 81 | Kaliganj | 27 | 21:00 | 147 | Pubail | 29 | 02:00
16 | Barguna | 22 | 02:00 | 82 | Kallyanpur | 132 | 00:00 | 148 | Purbachal | 35 | 13:00
17 | Barishal | 115 | 19:00 | 83 | Kalurghat | 45 | 16:00 | 149 | Purbasadipur | 90 | 19:00
18 | Barishal-230 | 110 | 18:30 | 84 | Kamrangirchar | 84 | 13:00 | 150 | Rahanpur | 32 | 00:00
19 | Baroaulia | 64 | 00:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 36 | 10:00
20 | Baroirhat | 60 | 18:30 | 86 | Kasba | 37 | 03:00 | 152 | Rajbari | 93.5 | 03:00
21 | Bashundhara | 217 | 13:00 | 87 | Kazla | 106 | 16:00 | 153 | Rajendrapur | 115 | 06:00
22 | BashundharaCement | 12 | 00:00 | 88 | Keranigonj | 87 | 15:00 | 154 | Rajshahi | 138 | 01:00
23 | Beanibazar | 46 | 00:00 | 89 | Khagrachori | 36 | 19:00 | 155 | Rajshahi-230 | 82 | 02:00
24 | Benapole | 72 | 23:00 | 90 | Khulna | 77 | 02:00 | 156 | Ramganj | 108 | 18:00
25 | Bhaluka | 126 | 10:00 | 91 | Khulshi | 189 | 19:00 | 157 | Rampur | 44 | 18:30
26 | Bhandaria | 60 | 19:30 | 92 | Kishoreganj | 100 | 01:00 | 158 | Rangamati | 17 | 19:00
27 | Bhangura | 44 | 09:00 | 93 | Kodda | 269 | 06:00 | 159 | Rangpur | 102 | 19:30
28 | Bheramara(GK) | 70 | 03:00 | 94 | Kulaura | 36 | 00:00 | 160 | Ruppur | 4 | 10:00
29 | Bhulta | 209 | 08:00 | 95 | Kurigram | 47 | 19:00 | 161 | SSM | 1 | 00:00
30 | Bog-Sherpur | 70 | 12:00 | 96 | Kushtia | 153 | 02:00 | 162 | Saidpur | 81 | 19:00
31 | Bogura | 155 | 04:00 | 97 | Laksam | 22 | 04:00 | 163 | Santhia | 38 | 03:00
32 | Borhanuddin | 95 | 19:00 | 98 | Lakshmipur | 31 | 18:30 | 164 | Satkhira | 138 | 02:00
33 | Brahmanbaria | 120 | 17:00 | 99 | Lalbag | 67 | 13:00 | 165 | Satmasjid | 107 | 00:00
34 | Cantonment | 114 | 13:00 | 100 | Lalmonirhat | 40 | 19:00 | 166 | Savar | 204 | 21:00
35 | Chandina | 45 | 06:00 | 101 | MI_Cement | 16.9 | 13:00 | 167 | SevenRings | 14.71 | 01:00
36 | Chandpur | 81 | 16:00 | 102 | Madanganj | 41 | 22:00 | 168 | ShahCement | 43 | 15:00
37 | Chandraghona | 40 | 18:00 | 103 | Madaripur | 119 | 03:00 | 169 | Shahjadpur | 90 | 13:00
38 | Chapai | 73 | 02:00 | 104 | Madartek | 94 | 00:00 | 170 | Shahjibazar | 111 | 02:00
39 | Charsaidpur | 41 | 10:00 | 105 | Madunaghat | 58 | 18:30 | 171 | Shahmirpur | 53 | 03:00
40 | Chauddagram | 90 | 03:00 | 106 | Magura | 67 | 03:00 | 172 | Shariatpur | 87 | 04:00
41 | Chhatak | 29 | 02:00 | 107 | Mahasthangarh | 55 | 11:00 | 173 | Sherpur | 100 | 00:00
42 | Chowmuhani | 174 | 18:30 | 108 | Maijdee | 50 | 19:00 | 174 | Shikalbaha | 30 | 10:00
43 | Chuadanga | 120 | 02:00 | 109 | Manikganj | 131 | 02:00 | 175 | Shitalakhya | 90.3 | 15:00
44 | Coxsbazar | 155 | 20:00 | 110 | Maniknagar | 75 | 14:00 | 176 | Sholosohor | 50 | 16:00
45 | Cumilla(N) | 123 | 03:00 | 111 | Matarbari | 58 | 19:30 | 177 | Shyampur | 178 | 15:00
46 | Cumilla(S) | 194 | 15:00 | 112 | Matuail | 81 | 16:00 | 178 | Siddhirganj | 137 | 15:00
47 | Daganbhuiyan | 38 | 19:00 | 113 | Metrorail_Motijheel | 33 | 12:00 | 179 | Sirajganj | 134 | 00:00
48 | Daudkandi | 150 | 03:00 | 114 | Metrorail_Uttara | 5 | 11:00 | 180 | Sonargaon | 168 | 04:00
49 | DhakaUniversity | 96 | 13:00 | 115 | Millgate | 105 | 12:00 | 181 | Sreemongol | 67 | 02:00
50 | Dhamrai | 130 | 16:00 | 116 | Mirpur | 162 | 00:00 | 182 | Sreepur | 114 | 16:00
51 | Dhanmondi | 147.3 | 13:00 | 117 | Mirsorai | 48 | 03:00 | 183 | Srinagar | 53.6 | 02:00
52 | Dohazari | 113 | 18:30 | 118 | Mirzapur | 55 | 01:00 | 184 | Sunamganj | 38 | 16:00
53 | Faridpur | 181 | 02:00 | 119 | Mithapukur | 41 | 21:00 | 185 | Sylhet | 37 | 13:00
54 | Fatullah | 98 | 15:00 | 120 | Modern | N/A | N/A | 186 | Sylhet-132 | 99 | 17:00
55 | Fenchuganj | 38 | 02:00 | 121 | Mogbazar | 93.3 | 13:00 | 187 | TK | 26 | 18:30
56 | Feni | 117 | 16:00 | 122 | Mongla | 46 | 11:00 | 188 | Tangail | 202 | 01:00
57 | GPH | 83 | 08:00 | 123 | Motijheel | 53 | 13:00 | 189 | Taraganj | 13 | 18:00
58 | Ghatail | 70 | 21:00 | 124 | Muktagacha | 29 | 14:00 | 190 | Tasnim | 32 | 15:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 105 | 13:00 | 191 | Thakurgaon | 61 | 19:30
60 | Ghorashal-230 | 107 | 07:00 | 126 | Muradnagar | 46 | 03:00 | 192 | Tongi | 160 | 12:00
61 | Goalpara | 48 | 02:00 | 127 | Mymensingh | 157 | 00:00 | 193 | Ullahpara | 47 | 07:00
62 | Gollamari | 104 | 22:00 | 128 | Nabinagar | 24 | 22:00 | 194 | Ullon | 65 | 00:00
63 | Gopalganj | 104.8 | 20:00 | 129 | Naogaon | 132 | 02:00 | 195 | Uttara | 96 | 12:00
64 | Gulshan | 138 | 14:00 | 130 | Narail | 63 | 18:30 | 196 | UttaraNew | 61 | 00:00
65 | Halishahar | 108 | 18:30 | 131 | Narinda | 80 | 13:00 | 197 | Zigatola | 90 | 00:00
66 | HaripurSBU | 140 | 23:00 | 132 | Narshingdi | 172 | 07:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 26-04-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13447 | 1865 |  | 15395.93
1:00 | 12885 | 1399 |  | 14347
2:00 | 12909 | 708 |  | 13649
3:00 | 12802 | 170 |  | 12980
4:00 | 12476 | 138 |  | 12620
5:00 | 12388 | 40 |  | 12430
6:00 | 12207.35 | 91 |  | 12302.35
7:00 | 12340.38 | 145 |  | 12492.38
8:00 | 12214.99 | 209 |  | 12432.99
9:00 | 12423.41 | 334 |  | 12772.41
10:00 | 12976.2 | 416 |  | 13411.2
11:00 | 13494.02 | 459 |  | 13974.02
12:00 | 13749.33 | 511 |  | 14283.33
13:00 | 13747.17 | 932 |  | 14721.17
14:00 | 13300.52 | 1006 |  | 14351.52
15:00 | 13112.28 | 755 |  | 13901.28
16:00 | 12460.52 | 231 |  | 12701.52
17:00 | 10772.69 | 142 |  | 10920.69
18:00 | 9074.67 | 66 |  | 9143.67
19:00 | 10598.87 | 98 |  | 10700.87
19:30 | 11060.42 | 0 |  | 11060.42
20:00 | 11162.47 | 0 |  | 11162.47
21:00 | 11478.91 | 0 |  | 11478.91
22:00 | 11715.38 | 30 |  | 11746.38
23:00 | 11999.31 | 31 |  | 12031.31
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 26-04-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 177 | 10 | 670 | 186 | 1900 | 544 | Ishurdi-Ghorashal Ckt-1 | Export | 2979127.27
1:00 | 153 | 2 | 580 | 132 | 1800 | 516
2:00 | 138 | -6 | 460 | 72 | 1720 | 472 |  | Import | 0
3:00 | 126 | -12 | 480 | 92 | 1636 | 434
4:00 | 134 | -7 | 524 | 130 | 1624 | 428 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 142 | -4 | 536 | 122 | 1684 | 442
6:00 | 130 | -7 | 488 | 110 | 1588 | 438 |  | Import | 0
7:00 | 119 | -7 | 470 | 126 | 1536 | 424
8:00 | 142 | 4 | 520 | 152 | 1624 | 512 | Sirajganj-Sreepur Ckt-1 | Export | 2845000
9:00 | 165 | 12 | 568 | 164 | 1700 | 550
10:00 | 179 | 19 | 630 | 190 | 1730 | 554 |  | Import | 0
11:00 | 171 | 23 | 600 | 192 | 1754 | 618
12:00 | 165 | 27 | 620 | 232 | 1744 | 674 | Sirajganj-Sreepur Ckt-2 | Export | 2866000
13:00 | 163 | 23 | 580 | 200 | 1714 | 654
14:00 | 186 | 32 | 660 | 232 | 1750 | 676 |  | Import | 0
15:00 | 146 | 11 | 590 | 188 | 1674 | 498
16:00 | 179 | 28 | 650 | 212 | 1670 | 592 | Gopalganj-Aminbazar Ckt-1 | Export | 17420000
17:00 | 163 | 5 | 410 | 56 | 1266 | 410
18:00 | 67 | -36 | 250 | 20 | 810 | 272 |  | Import | 0
18:30 | 68 | -34 | 230 | 58 | 782 | 304
19:00 | 26 | -29 | 150 | 80 | 690 | 266 | Gopalganj-Aminbazar Ckt-2 | Export | 17470000
19:30 | 24 | -25 | 160 | 96 | 688 | 316
20:00 | 32 | -21 | 220 | 104 | 680 | 316 |  | Import | 0
21:00 | 43 | -20 | 260 | 122 | 666 | 312
22:00 | 63 | -16 | 320 | 134 | 906 | 330 |  | Total Export | 43580127.27
23:00 | 66 | -10 | 330 | 138 | 1170 | 322 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 26-04-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6966 | 6481 | 13447 | DAILY GENERATION CURVE
00:30 | 6805.5 | 6360.5 | 13166
01:00 | 6645 | 6240 | 12885 | 26-04-2026
01:30 | 6652.5 | 6244.5 | 12897
02:00 | 6660 | 6249 | 12909
02:30 | 6622 | 6233.5 | 12855.5
03:00 | 6584 | 6218 | 12802
03:30 | 6480.5 | 6158.5 | 12639
04:00 | 6377 | 6099 | 12476
04:30 | 6309.5 | 6122.5 | 12432
05:00 | 6242 | 6146 | 12388
05:30 | 6249.98 | 6047.695 | 12297.675
06:00 | 6257.96 | 5949.39 | 12207.35
06:30 | 6313.51 | 5960.355 | 12273.865
07:00 | 6369.06 | 5971.32 | 12340.38
07:30 | 6344.7 | 5932.985 | 12277.685
08:00 | 6320.34 | 5894.65 | 12214.99
08:30 | 6348 | 5971.2 | 12319.2
09:00 | 6375.66 | 6047.75 | 12423.41
09:30 | 6539.83 | 6159.975 | 12699.805
10:00 | 6704 | 6272.2 | 12976.2
10:30 | 6859.975 | 6375.135 | 13235.11
11:00 | 7015.95 | 6478.07 | 13494.02
11:30 | 7148.8 | 6472.875 | 13621.675
12:00 | 7281.65 | 6467.68 | 13749.33
12:30 | 7267.455 | 6480.795 | 13748.25
13:00 | 7253.26 | 6493.91 | 13747.17
13:30 | 7080.165 | 6443.68 | 13523.845
14:00 | 6907.07 | 6393.45 | 13300.52
14:30 | 6988.455 | 6217.945 | 13206.4
15:00 | 7069.84 | 6042.44 | 13112.28
15:30 | 6916.125 | 5870.275 | 12786.4
16:00 | 6762.41 | 5698.11 | 12460.52
16:30 | 6265.1 | 5351.505 | 11616.605
17:00 | 5767.79 | 5004.9 | 10772.69
17:30 | 5303.47 | 4620.21 | 9923.68
18:00 | 4839.15 | 4235.52 | 9074.67
18:30 | 5404.575 | 4432.195 | 9836.77
19:00 | 5970 | 4628.87 | 10598.87
19:30 | 6163 | 4897.42 | 11060.42
20:00 | 6244 | 4918.47 | 11162.47
20:30 | 6339.5 | 4981.19 | 11320.69 |  | Executive Engineer
21:00 | 6435 | 5043.91 | 11478.91 |  | Network Operation Division
21:30 | 6433.25 | 5163.895 | 11597.145
22:00 | 6431.5 | 5283.88 | 11715.38
22:30 | 6421.5 | 5435.845 | 11857.345
23:00 | 6411.5 | 5587.81 | 11999.31

## En-Curve
QF-LDC-12
Date | 26-04-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3705 | 1604 | 922 | 0 | 126 | 768 | 38 | 4612 | 0 | 535 | 920 | 217 | 0 | 0 | 1865 | DAILY ENERGY CURVE
00:30 | 3685 | 1591.5 | 922 | 0 | 121 | 763.5 | 39 | 4686 | 0 | 436.5 | 704 | 217.5 | 0 | 0 | 1632 | 26-04-2026
01:00 | 3665 | 1579 | 922 | 0 | 116 | 759 | 40 | 4760 | 0 | 338 | 488 | 218 | 0 | 0 | 1399
01:30 | 3673.5 | 1585 | 922.5 | 0 | 117 | 762 | 40 | 4806.5 | 0 | 312 | 458 | 218.5 | 0 | 2 | 1053.5 | Energy Generated | 297.8114 |  | MKWHr
02:00 | 3682 | 1591 | 923 | 0 | 118 | 765 | 40 | 4853 | 0 | 286 | 428 | 219 | 0 | 4 | 708 | Energy not Served | 9.776 |  | MKWHr
02:30 | 3643.5 | 1560 | 923 | 0 | 113 | 764.5 | 40 | 4893 | 0 | 268.5 | 419 | 219 | 0 | 12 | 439 | Total Energy Requirement | 307.5874 |  | MKWHr
03:00 | 3605 | 1529 | 923 | 0 | 108 | 764 | 40 | 4933 | 0 | 251 | 410 | 219 | 0 | 20 | 170
03:30 | 3630 | 1501.5 | 923 | 0 | 109 | 760 | 40 | 4940 | 0 | 180.5 | 324.5 | 219 | 0 | 11.5 | 154
04:00 | 3655 | 1474 | 923 | 0 | 110 | 756 | 40 | 4947 | 0 | 110 | 239 | 219 | 0 | 3 | 138
04:30 | 3674 | 1504.5 | 923 | 0 | 106 | 758 | 40 | 4915.5 | 0 | 90.5 | 199.5 | 219.5 | 0 | 1.5 | 89
05:00 | 3693 | 1535 | 923 | 0 | 102 | 760 | 40 | 4884 | 0 | 71 | 160 | 220 | 0 | 0 | 40
05:30 | 3674 | 1514.5 | 923 | 0 | 111 | 763.5 | 40 | 4870.5 | 3.175 | 59.5 | 158.5 | 180 | 0 | 0 | 65.5
06:00 | 3655 | 1494 | 923 | 0 | 120 | 767 | 40 | 4857 | 6.35 | 48 | 157 | 140 | 0 | 0 | 91
06:30 | 3645 | 1490 | 923 | 0 | 115 | 766 | 40 | 4902 | 38.365 | 48 | 166.5 | 140 | 0 | 0 | 118
07:00 | 3635 | 1486 | 923 | 0 | 110 | 765 | 40 | 4947 | 70.38 | 48 | 176 | 140 | 0 | 0 | 145
07:30 | 3606 | 1460 | 923 | 0 | 108 | 766 | 40 | 4861 | 135.685 | 48 | 190 | 140 | 0 | 0 | 177
08:00 | 3577 | 1434 | 923 | 0 | 106 | 767 | 40 | 4775 | 200.99 | 48 | 204 | 140 | 0 | 0 | 209
08:30 | 3591.5 | 1454.5 | 923 | 0 | 107 | 766.27 | 40 | 4770.5 | 273.93 | 48 | 204.5 | 140 | 0 | 0 | 271.5
09:00 | 3606 | 1475 | 923 | 0 | 108 | 765.54 | 40 | 4766 | 346.87 | 48 | 205 | 140 | 0 | 0 | 334
09:30 | 3613 | 1466 | 923 | 0 | 111 | 765.355 | 39.5 | 4832.5 | 427.95 | 58.5 | 308 | 155 | 0 | 0 | 375
10:00 | 3620 | 1457 | 923 | 0 | 114 | 765.17 | 39 | 4899 | 509.03 | 69 | 411 | 170 | 0 | 0 | 416
10:30 | 3663 | 1492 | 923 | 0 | 114 | 759.64 | 38.5 | 5008.5 | 479.47 | 70.5 | 455.5 | 229.5 | 0 | 1.5 | 437.5
11:00 | 3706 | 1527 | 923 | 0 | 114 | 754.11 | 38 | 5118 | 449.91 | 72 | 500 | 289 | 0 | 3 | 459
11:30 | 3690 | 1560 | 923 | 0 | 118 | 757.885 | 37.5 | 5117 | 429.79 | 95 | 567 | 310 | 0 | 16.5 | 485
12:00 | 3674 | 1593 | 923 | 0 | 122 | 761.66 | 37 | 5116 | 409.67 | 118 | 634 | 331 | 0 | 30 | 511
12:30 | 3625.5 | 1576 | 923 | 0 | 124 | 762.38 | 36 | 5129 | 360.37 | 113 | 725 | 343 | 0 | 31 | 721.5
13:00 | 3577 | 1559 | 923 | 0 | 126 | 763.1 | 35 | 5142 | 311.07 | 108 | 816 | 355 | 0 | 32 | 932
13:30 | 3484.5 | 1514.5 | 923 | 0 | 130 | 762.845 | 35 | 5156.5 | 299 | 115.5 | 828.5 | 239 | 0 | 35.5 | 969
14:00 | 3392 | 1470 | 923 | 0 | 134 | 762.59 | 35 | 5171 | 286.93 | 123 | 841 | 123 | 0 | 39 | 1006
14:30 | 3442.5 | 1446 | 923 | 0 | 137 | 764.675 | 35 | 5178 | 231.225 | 122.5 | 764 | 123 | 0 | 39.5 | 880.5
15:00 | 3493 | 1422 | 923 | 0 | 140 | 766.76 | 35 | 5185 | 175.52 | 122 | 687 | 123 | 0 | 40 | 755
15:30 | 3479.5 | 1436.5 | 922.5 | 0 | 140 | 732.555 | 35 | 5094 | 115.245 | 129.6 | 539 | 123 | 0 | 39.5 | 493
16:00 | 3466 | 1451 | 922 | 0 | 140 | 698.35 | 35 | 5003 | 54.97 | 137.2 | 391 | 123 | 0 | 39 | 231
16:30 | 3329.5 | 1337.5 | 922 | 0 | 125 | 634.725 | 35 | 4553 | 47.43 | 146.95 | 321.5 | 123 | 0 | 41 | 186.5
17:00 | 3193 | 1224 | 922 | 0 | 110 | 571.1 | 35 | 4103 | 39.89 | 156.7 | 252 | 123 | 0 | 43 | 142
17:30 | 3062 | 1205.5 | 897.5 | 0 | 114 | 496.82 | 35 | 3664 | 29.16 | 112.2 | 168 | 106.5 | 0 | 33 | 104
18:00 | 2931 | 1187 | 873 | 0 | 118 | 422.54 | 35 | 3225 | 18.43 | 67.7 | 84 | 90 | 0 | 23 | 66
18:30 | 3256 | 1244.5 | 897.5 | 0 | 71 | 495.255 | 35 | 3486.5 | 9.215 | 92.3 | 185 | 45 | 0 | 19.5 | 82
19:00 | 3581 | 1302 | 922 | 0 | 24 | 567.97 | 35 | 3748 | 0 | 116.9 | 286 | 0 | 0 | 16 | 98
19:30 | 3700 | 1360 | 923 | 0 | 32 | 630.52 | 35 | 3884 | 0 | 115.9 | 377 | 0 | 0 | 3 | 0
20:00 | 3820 | 1432 | 923 | 0 | 30 | 642.47 | 35 | 3794 | 0 | 114 | 370 | 0 | 0 | 2 | 0
20:30 | 3848.5 | 1507.5 | 923 | 0 | 39 | 703.69 | 35 | 3798.5 | 0 | 103.5 | 361 | 0 | 0 | 1 | 0
21:00 | 3877 | 1583 | 923 | 0 | 48 | 764.91 | 35 | 3803 | 0 | 93 | 352 | 0 | 0 | 0 | 0
21:30 | 3826.5 | 1597.75 | 923 | 0 | 60 | 765.395 | 35 | 4037.5 | 0 | 88 | 264 | 0 | 0 | 0 | 15
22:00 | 3776 | 1612.5 | 923 | 0 | 72 | 765.88 | 35 | 4272 | 0 | 83 | 176 | 0 | 0 | 0 | 30
22:30 | 3731 | 1586 | 923 | 0 | 74 | 760.845 | 35 | 4487 | 0 | 90 | 168 | 0 | 0 | 2.5 | 30.5
23:00 | 3686 | 1559.5 | 923 | 0 | 76 | 755.81 | 35 | 4702 | 0 | 97 | 160 | 0 | 0 | 5 | 31
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 26-04-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 398 | 17:00 | 365 | 14:00 | Madunaghat | 398 | 21:00 | 385 | 12:00
Amtali | 413 | 18:00 | 403 | 03:00 | Meghnaghat | 396 | 18:00 | 370 | 12:00
Ashuganj | 409 | 00:00 | 391 | 11:00 | Payra | 414 | 18:00 | 406 | 03:00
Bhulta | 409 | 18:00 | 372 | 12:00 | Rahanpur | 414 | 17:00 | 399 | 12:00
Bibiana | 411 | 18:00 | 390 | 12:00 | Rampal | 404 | 17:00 | 389 | 15:00
BIPTC | 402 | 08:00 | 391 | 00:00
Bogura | 409 | 00:00 | 391 | 11:00
Gopalganj | 404 | 18:00 | 383 | 12:00
Kaliakoir | 390 | 18:00 | 357 | 12:00
Korerhat | 403 | 21:00 | 382 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 240 | 18:00 | 214 | 12:00 | Jhenaidah | 229 | 17:00 | 215 | 03:00
AKSML | 234 | 21:00 | 221 | 11:00 | Kachua | 233 | 20:00 | 215 | 16:00
Aminbazar | 242 | 17:00 | 214 | 14:00 | Kaliakoir | 242 | 18:00 | 217 | 12:00
Ashuganj | 238 | 18:00 | 217 | 12:00 | Keranigonj | 239 | 18:00 | 212 | 12:00
Ashuganj-400 | 238 | 18:00 | 217 | 12:00 | Khulna(S) | 230 | 17:00 | 217 | 22:00
Baghabari | 238 | 17:00 | 227 | 12:00 | Korerhat | 230 | 19:30 | 217 | 11:00
Barapukuria | 237 | 01:00 | 213 | 19:00 | Madunaghat | 233 | 21:00 | 223 | 11:00
Barapukuria-230 | 237 | 01:00 | 213 | 19:00 | Madunaghat-400 | 234 | 21:00 | 224 | 11:00
Barishal | 228 | 18:00 | 217 | 15:00 | Maniknagar | 232 | 18:00 | 208 | 12:00
Bheramara | 234 | 17:00 | 222 | 19:00 | Meghnaghat | 242 | 18:00 | 218 | 12:00
Bhulta | 235 | 18:00 | 209 | 12:00 | Meghnaghat-400 | 237 | 18:00 | 213 | 12:00
Bibiana | 239 | 18:00 | 226 | 12:00 | Mirsorai | 233 | 20:00 | 222 | 16:00
BIPTC | 237 | 17:00 | 222 | 20:00 | Naogaon | 225 | 16:00 | 212 | 12:00
Bogura | 241 | 00:00 | 228 | 11:00 | Purbasadipur | 238 | 14:00 | 211 | 19:00
Bogura-400 | 238 | 00:00 | 228 | 11:00 | Rajshahi | 235 | 17:00 | 219 | 22:00
Borhanuddin | 231 | 18:00 | 223 | 03:00 | Rampal | 231 | 17:00 | 218 | 22:00
BSRM | 230 | 19:30 | 217 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 228 | 23:00 | 215 | 16:00 | Rampura | 235 | 18:00 | 206 | 12:00
Cumilla(N) | 231 | 19:00 | 215 | 12:00 | Shikalbaha | 231 | 00:00 | 223 | 07:00
Faridpur | 227 | 18:00 | 213 | 03:00 | Shyampur | 237 | 18:00 | 211 | 12:00
Fenchuganj | 244 | 18:00 | 232 | 02:00 | Siddhirganj | 237 | 18:00 | 210 | 12:00
Feni | 231 | 19:30 | 214 | 16:00 | Sirajgonj | 243 | 17:00 | 234 | 12:00
Ghorashal | 245 | 18:00 | 212 | 14:00 | Sreepur | 235 | 17:00 | 216 | 12:00
Ghorashal-230 | 236 | 18:00 | 209 | 12:00 | Tongi | 237 | 17:00 | 212 | 12:00
Gopalganj | 226 | 18:00 | 213 | 12:00
GPH | 232 | 21:00 | 220 | 11:00
Haripur | 236 | 18:00 | 210 | 12:00
Hasnabad | 236 | 18:00 | 212 | 13:00
Hathazari | 232 | 21:00 | 221 | 11:00
Ishurdi | 237 | 17:00 | 225 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 18:00 | 124 | 12:00 | Madunaghat | 135 | 00:00 | 129 | 10:00
Agargaon | 137 | 18:00 | 124 | 12:00 | Magura | 135 | 18:00 | 124 | 03:00
Agrabad | 134 | 00:00 | 126 | 05:00 | Mahasthangarh | 139 | 00:00 | 129 | 11:00
AKS | 132 | 00:00 | 125 | 10:00 | Maijdee | 132 | 20:00 | 119 | 04:00
Aminbazar | 135 | 17:00 | 120 | 12:00 | Manikganj | 135 | 18:00 | 112 | 12:00
Amnura | 136 | 03:00 | 127 | 02:00 | Maniknagar | 139 | 18:00 | 119 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 135 | 09:00 | 109 | 04:00
Ashuganj-230 | 145 | 18:00 | 132 | 12:00 | Matuail | 139 | 18:00 | 121 | 12:00
Bagerhat | 128 | 11:00 | 115 | 22:00 | Metrorail_Motijheel | 135 | 19:00 | 119 | 12:00
Bajitpur | 137 | 17:00 | 125 | 12:00 | Metrorail_Uttara | 134 | 18:00 | 118 | 12:00
Bakerganj | 133 | 18:00 | 126 | 06:00 | Millgate | 138 | 18:00 | 120 | 12:00
Bakulia | 134 | 21:00 | 126 | 05:00 | Mirpur | 135 | 18:00 | 119 | 12:00
Banani | 139 | 18:00 | 123 | 12:00 | Mirzapur | 139 | 17:00 | 119 | 12:00
Bangabhaban | 138 | 18:00 | 119 | 12:00 | Mithapukur | 140 | 00:00 | 126 | 19:00
Barapukuria | 140 | 00:00 | 123 | 19:00 | MI_Cement | 145 | 18:00 | 122 | 12:00
Barguna | 138 | 19:00 | 125 | 04:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 132 | 18:00 | 125 | 05:00 | Mogbazar | 140 | 18:00 | 125 | 12:00
Barishal-230 | 132 | 18:00 | 126 | 03:00 | Mongla | 128 | 17:00 | 116 | 23:00
Baroaulia | 135 | 21:00 | 127 | 11:00 | Motijheel | 138 | 18:00 | 119 | 12:00
Baroirhat | 134 | 21:00 | 124 | 10:00 | Muktagacha | 140 | 17:00 | 119 | 23:00
Bashundhara | 139 | 18:00 | 119 | 12:00 | Munshiganj | 137 | 18:00 | 119 | 12:00
BashundharaCement | 136 | 18:30 | 120 | 08:00 | Muradnagar | 136 | 18:00 | 118 | 11:00
Beanibazar | 136 | 18:00 | 126 | 12:00 | Mymensingh | 139 | 17:00 | 117 | 23:00
Benapole | 129 | 18:00 | 117 | 23:00 | Nabinagar | 142 | 17:00 | 121 | 12:00
Bhaluka | 141 | 17:00 | 123 | 12:00 | Naogaon | 138 | 00:00 | 126 | 07:00
Bhandaria | 129 | 00:00 | 119 | 23:00 | Narail | 134 | 17:00 | 123 | 22:00
Bhangura | 138 | 17:00 | 128 | 12:00 | Narinda | 139 | 18:00 | 119 | 12:00
Bheramara | 138 | 17:00 | 131 | 03:00 | Narshingdi | 141 | 18:00 | 117 | 10:00
Bheramara(GK) | 137 | 17:00 | 131 | 21:00 | Natore | 136 | 17:00 | 127 | 12:00
Bhulta | 133 | 18:00 | 116 | 12:00 | Nawabganj | 147 | 18:00 | 126 | 12:00
Bog-Sherpur | 139 | 17:00 | 128 | 11:00 | Netrakona | 135 | 17:00 | 120 | 12:00
Bogura | 139 | 00:00 | 130 | 11:00 | New | 139 | 18:00 | 120 | 12:00
Bogura-230 | 141 | 00:00 | 131 | 11:00 | Niamatpur | 136 | 15:00 | 128 | 10:00
Brahmanbaria | 141 | 18:00 | 121 | 16:00 | Noapara | 132 | 17:00 | 121 | 21:00
Cantonment | 137 | 18:00 | 123 | 12:00 | Pabna | 137 | 17:00 | 129 | 03:00
Chandina | 136 | 19:00 | 122 | 11:00 | Palashbari | 139 | 00:00 | 124 | 19:00
Chandpur | 133 | 20:00 | 120 | 05:00 | Panchagarh | 142 | 14:00 | 123 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 137 | 21:00 | 129 | 08:00 | Patiya | 134 | 00:00 | 126 | 08:00
Chapai | 135 | 15:00 | 130 | 10:00 | Patuakhali | 133 | 18:00 | 127 | 02:00
Charsaidpur | 139 | 18:00 | 120 | 12:00 | Payra | 135 | 18:00 | 131 | 02:00
Chauddagram | 134 | 19:00 | 120 | 11:00 | PHP | 133 | 19:30 | 123 | 05:00
Chhatak | 138 | 18:00 | 125 | 02:00 | Postogola | 149 | 18:00 | 126 | 12:00
Chowmuhani | 131 | 19:30 | 120 | 05:00 | Pubail | 142 | 17:00 | 123 | 12:00
Chuadanga | 133 | 17:00 | 120 | 03:00 | Purbachal | 139 | 18:00 | 118 | 12:00
Coxsbazar | 124 | 00:00 | 110 | 06:00 | Purbasadipur | 138 | 14:00 | 121 | 19:00
Cumilla(N) | 135 | 18:00 | 123 | 11:00 | Rahanpur | 137 | 00:00 | 132 | 11:00
Cumilla(S) | 137 | 19:00 | 122 | 11:00 | Rahanpur-400 | 137 | 15:00 | 131 | 12:00
Daganbhuiyan | 133 | 19:30 | 121 | 04:00 | Rahim | 139 | 18:00 | 121 | 12:00
Daudkandi | 137 | 18:00 | 116 | 11:00 | Rajbari | 130 | 18:00 | 119 | 03:00
DhakaUniversity | 140 | 18:00 | 124 | 12:00 | Rajendrapur | 143 | 17:00 | 126 | 10:00
Dhamrai | 160 | 09:00 | 121 | 12:00 | Rajshahi | 134 | 17:00 | 125 | 12:00
Dhanmondi | 140 | 18:00 | 124 | 12:00 | Rajshahi-230 | 135 | 17:00 | 126 | 12:00
Dohazari | 133 | 00:00 | 121 | 08:00 | Ramganj | 131 | 19:30 | 116 | 16:00
Faridpur | 134 | 18:00 | 123 | 02:00 | Rampur | 134 | 00:00 | 126 | 08:00
Fatullah | 144 | 18:00 | 120 | 12:00 | Rampura | 139 | 18:00 | 124 | 12:00
Fenchuganj | 140 | 18:00 | 131 | 02:00 | Rangamati | 137 | 21:00 | 127 | 11:00
Feni | 132 | 20:00 | 120 | 11:00 | Rangpur | 140 | 00:00 | 124 | 19:00
Feni-230 | 133 | 19:30 | 121 | 11:00 | Ruppur | 138 | 17:00 | 131 | 13:00
Ghatail | 140 | 17:00 | 118 | 12:00 | Saidpur | 139 | 00:00 | 122 | 19:00
Ghorashal | 143 | 18:00 | 126 | 13:00 | Santhia | 139 | 17:00 | 130 | 13:00
Goalpara | 135 | 17:00 | 123 | 00:00 | Satkhira | 130 | 17:00 | 117 | 22:00
Gollamari | 134 | 17:00 | 124 | 03:00 | Satmasjid | 137 | 18:00 | 124 | 12:00
Gopalganj | 133 | 18:00 | 124 | 15:00 | Savar | 134 | 18:00 | 117 | 14:00
Gopalganj-400 | 134 | 00:00 | 127 | 03:00 | SevenRings | 143 | 18:00 | 126 | 12:00
Gulshan | 139 | 18:00 | 124 | 12:00 | ShahCement | 139 | 18:00 | 120 | 12:00
Halishahar | 135 | 00:00 | 126 | 12:00 | Shahjadpur | 141 | 17:00 | 131 | 12:00
Haripur | 139 | 18:00 | 121 | 12:00 | Shahjibazar | 140 | 18:00 | 123 | 16:00
HaripurSBU | 135 | 19:00 | 126 | 11:00 | Shahmirpur | 135 | 00:00 | 128 | 05:00
Hasnabad | 145 | 18:00 | 126 | 12:00 | Shariatpur | 134 | 18:30 | 123 | 04:00
Hathazari | 135 | 00:00 | 130 | 08:00 | Sherpur | 141 | 01:00 | 114 | 23:00
Hatirjheel | 135 | 06:00 | 124 | 12:00 | Shikalbaha | 125 | 00:00 | 118 | 07:00
Ishurdi | 139 | 17:00 | 132 | 03:00 | Shikalbaha-230 | 135 | 00:00 | 129 | 08:00
Jaldhaka | 139 | 01:00 | 119 | 19:00 | Shitalakhya | 145 | 18:00 | 122 | 12:00
Jamalpur | 140 | 01:00 | 120 | 19:00 | Sholosohor | 135 | 00:00 | 128 | 11:00
Jashore | 131 | 17:00 | 120 | 22:00 | Shyampur | 137 | 18:00 | 120 | 11:00
Jhenaidah | 137 | 18:00 | 124 | 02:00 | Shyampur-230 | 138 | 18:00 | 118 | 12:00
Jhenaidah-230 | 137 | 18:00 | 126 | 03:00 | Siddhirganj | 139 | 18:00 | 121 | 12:00
Joydebpur | 141 | 17:00 | 120 | 12:00 | Sirajganj | 139 | 17:00 | 126 | 12:00
Joypurhat | 137 | 00:00 | 125 | 11:00 | Sonargaon | 140 | 18:00 | 119 | 12:00
Juldah | 135 | 00:00 | 127 | 07:00 | Sreemongol | 139 | 18:00 | 125 | 02:00
Kabirpur | 141 | 17:00 | 115 | 12:00 | Sreepur | 140 | 17:00 | 126 | 12:00
Kachua | 133 | 20:00 | 122 | 03:00 | Srinagar | 148 | 18:00 | 126 | 12:00
Kaliakoir | 143 | 17:00 | 124 | 12:00 | SSM | 139 | 00:00 | 130 | 12:00
Kaliganj | 136 | 17:00 | 30 | 12:00 | Sunamganj | 135 | 18:00 | 124 | 02:00
Kallyanpur | 135 | 18:00 | 120 | 12:00 | Sylhet | 137 | 18:00 | 13 | 22:00
Kalurghat | 136 | 21:00 | 129 | 11:00 | Sylhet-132 | 136 | 18:00 | 129 | 12:00
Kamrangirchar | 147 | 18:00 | 117 | 12:00 | Tangail | 139 | 17:00 | 117 | 12:00
Kaptai | N/A | N/A | N/A | N/A | Taraganj | 138 | 00:00 | 26 | 19:30
Kasba | 136 | 18:00 | 118 | 11:00 | Tasnim | 140 | 18:00 | 119 | 12:00
Kazla | 138 | 18:00 | 119 | 13:00 | Thakurgaon | 141 | 14:00 | 121 | 19:00
Keranigonj | 147 | 18:00 | 127 | 12:00 | TK | 136 | 21:00 | 129 | 10:00
Khagrachori | 137 | 21:00 | 125 | 11:00 | Tongi | 143 | 17:00 | 124 | 12:00
Khulna | 133 | 17:00 | 123 | 22:00 | Ullahpara | 139 | 17:00 | 128 | 11:00
Khulna(S) | 134 | 17:00 | 124 | 23:00 | Ullon | 144 | 17:00 | 123 | 12:00
Khulshi | 133 | 00:00 | 125 | 10:00 | Uttara | 137 | 18:00 | 117 | 12:00
Kishoreganj | 137 | 17:00 | 123 | 12:00 | UttaraNew | 134 | 18:00 | 118 | 12:00
Kodda | 142 | 17:00 | 118 | 12:00 | Zigatola | 147 | 18:00 | 127 | 12:00
Korerhat | 135 | 19:30 | 126 | 09:00
KSRM | 134 | 00:00 | 127 | 11:00
Kulaura | 139 | 18:00 | 130 | 02:00
Kurigram | 137 | 00:00 | 120 | 18:30
Kushtia | 136 | 17:00 | 128 | 22:00
Laksam | 134 | 20:00 | 121 | 04:00
Lakshmipur | 131 | 19:30 | 118 | 05:00
Lalbag | 139 | 17:00 | 128 | 13:00
Lalmonirhat | 134 | 02:00 | 120 | 18:30
Madanganj | 139 | 18:00 | 121 | 12:00
Madaripur | 135 | 18:00 | 125 | 03:00
Madartek | 138 | 18:00 | 123 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division