## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID BANGLADESH PLC
SYSTEM OPERATION DATA
Month: March 2026
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2026-03-01 |  | 2026-02-01 |  | 2025-03-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 14856.09 | 2026-03-11 | 12935.25 | 2026-02-18 | 15336.92 | 2025-03-15 | 16794 | 2025-07-23
|  |  | 21:00 Hr. |  | 19:00 Hr. |  | 21:00 Hr. |  | 21:00 Hr.
2 | Minimum Generation (MW) | 5964.82 | 2026-03-22 | 5563 | 2026-02-13 | 8360.79 | 2025-03-08 | - | -
|  |  | 06:00 Hr. |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 14856.09 | 2026-03-11 | 12935.25 | 2026-02-18 | 15336.92 | 2025-03-15 | 16794 | 2025-07-23
|  |  | 21:00 Hr. |  | 19:00 Hr. |  | 21:00 Hr. |  | 21:00 Hr.
4 | Maximum Day Peak Generation (MW) | 13333.42 | 2026-03-11 | 12121.94 | 2026-02-26 | 13926.95 | 2025-03-27 | 14965.88 | 2025-09-30
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 Hr.
5 | Maximum Evening Peak Demand (MW) Estimated | 14960.09 | 2026-03-11 | 13001.25 | 2026-02-18 | 14658 | 2025-03-15 | 17200 | 2024-04-29
|  |  | 21:00 Hr. |  | 19:00 Hr. |  | 21:00 Hr. |  | 21:00
6 | Average Generation (MW) at Evening Peak | 12524.5352 |  | 11551.6225 |  | 13455.0287 |  | - | -
7 | Average Generation (MW) at Day Peak | 11174.6671 |  | 11052.9771 |  | 12259.0329 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 924 | 2026-03-30 | 980 | 2026-02-20 | 936 | 2025-03-01 | 980 | 2026-02-20
|  |  | 17:00 |  | 0:30 |  | 2:00 |  | 0:30
9 | Maximum Power Import from Tripura, India (MW) | 187 | 2026-03-11 | 148 | 2026-02-26 | 173 | 2025-03-19 | 194 | 12/06/19
|  |  | 14:00 |  | 14:00 |  | 21:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 100 | 2026-03-11 | 87 | 2026-02-17 | 113 | 45732 | 4395 | 04/10/2022
|  |  | 21:00 Hr. |  | 19:30 Hr. |  | 19:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 14856.09 | 2026-03-11 | 12494.9 | 2026-02-17 | 14425 | 45732 | 14965 | 2024-05-16
|  |  | 21:00 Hr. |  | 19:00 Hr. |  | 19:00 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 10 | 2026-03-03 | 24 | 2026-02-01 | 0 | 45719 | - | -
|  |  | 19:30 Hr. |  | 19:00 Hr. |  | 19:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 12957.59 | 2026-03-03 | 11875.1 | 2026-02-01 | 12195 | 45719 | - | -
|  |  | 19:30 Hr. |  | 19:00 Hr. |  | 19:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 369 | 2026-03-16 | 368 | 2026-02-03 | 175 | 45736 | - | -
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 11578 | 2026-03-16 | 11069.32 | 2026-02-03 | 12899 | 45736 | - | -
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 90 | 2026-03-09 | 10 | 2026-02-23 | 0 | 45717 | - | -
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 12641.8 | 2026-03-09 | 11549.55 | 2026-02-23 | 11795 | 45719 | - | -
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 9 |  | 9 |  | 4 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 11 |  | 10 |  | 13 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 885.5136 |  | 630.2766 |  | 1723.1429 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 14.9241 |  | 16.944 |  | 135.2017 |  | - | -
22 | Net Generation of BPDB (MKWH) | 870.5895 |  | 613.3326 |  | 1587.9412 |  | - | -
23 | Net Generation of IPP (MKWH) | 2322.2578 |  | 1851.6463 |  | 2881.8044 |  | - | -
23b | Net Generation by Generation Companies | 3481.2826 |  | 3033.6017 |  | 2640.4845
24 | Net Generation of REB (MKWH) | 49.7992 |  | 44.2268 |  | 154.781 |  | - | -
25 | Net Generation of Rental Power Plant (MKWH) | 54.0965 |  | 63.8482 |  | 239.0099 |  | - | -
26 | Total Net Generation (MKHWh) (Excluding Import) | 6778.0256 |  | 5606.6557 |  | 7504.021 |  | - | -
27 | Energy Generation by Gas (MKWH) | 3548.1844 |  | 3025.2502 |  | 4228.5203 |  | - | -
28 | Energy Generation by Diesel (MKWH) | 0 |  | 0.08545 |  | 432.8368 |  | - | -
29 | Energy Generation by Furnace Oil (MKWH) | 438.8774 |  | 262.9201 |  | 708.9829 |  | - | -
30 | Energy Generation by Hydro (MKWH) | 56.2631 |  | 36.7922 |  | 0.74082 |  | - | -
31 | Energy Generation by Solar (MKWH) | 120.8884 |  | 116.9977 |  | 142.698 |  | 149.04 | 2026-04-25
31b | Energy Generation by Wind (MKWH) | 3.7781 |  | 5.9448 |  | 0 |  | - | -
32 | Energy Generation by Coal (MKWH) | 2624.9585 |  | 2175.6092 |  | 2125.4439 |  | 3144.92 | 2025-08-25
33 | Enegry Import from India (MKWH) | 1524.069 |  | 1291.3548 |  | 1468.4092 |  | - | -
34 | Monthly Load Factor (%) | 75.2472 |  | 79.5509 |  | 79.8168 |  | 86.52 | 2026-09-25

## QF-LDC-22
QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: March 2026
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 14856.09 | 2026-03-11 | 21:00 Hr.
Generation Period
| Dhaka | MW | 5463.1
| Chattogram | MW | 1376
| Cumilla | MW | 1355
| Mymensingh | MW | 1192
| Sylhet | MW | 560
a) | Total supply in East zone | MW | 9946.1
| Khulna | MW | 1662
| Barisal | MW | 414.48
| Rajshahi | MW | 1459
| Rangpur | MW | 823
b) | Total supply in West zone | MW | 4358.48
c) | Total supply in both zone ( a+b) | MW | 14304.58
Ref: | 27.21.0000.603.16.087.20.971 | Date: 16/04/2026
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month: March 2026
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Maximum power Export through EWI/ NO-1
| a) Ishurdi end | AMPS | 622 | 2026-03-15 | 22:00
|  | MW | 258
| b) Ghorashal end | AMPS | 62 | 23/03/2026 | 7:00
|  | MW | 14
18 | Maximum power Import through EWI/ NO-1 |  |  | -
| a) Ishurdi end | AMPS | 102 | 23/03/2026 | 7:00
|  | MW | 36
| b) Ghorashal end | AMPS | 618 | 2026-03-15 | 22:00
|  | MW | 233
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ishurdi end | MWh | 4049.67 | 2026-03-16 | N/A
| b) Ghorashal end | MWh | 650 | 2026-03-28
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ishurdi end | MWh | 65.23 | 2026-03-28 |  | 86326110.5 |  | 83736327.18
| b) Ghorashal end | MWh | 3855.54 | 2026-03-16 | N/A | 5983345.552 |  | 5803845.19
21 | Total Energy Export through EWI/ NO-1
| a) Ishurdi end | MWh | 92309.45
| b) Ghorashal end | MWh | 39.63 |  |  | 39626.9097 | 38472.7279
22 | Total Energy Import through EWI/ NO-1 | [5 empty] | 31781.8187
| a) Ishurdi end | MWh | 70.25
| b) Ghorashal end | MWh | 89540.17
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Maximum power Export through EWI/ NO-2
| a) Sirajganj end | AMPS | 1780 | 2026-03-12
|  | MW | 690
| b) Sreepur end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
25 | Maximum power Import through EWI/ NO-2 |  | - | -
| a) Serajganj end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
| b) Sreepur | AMPS | - | - | -
|  | MW | -
26 | Daily Maximum Energy Export through EWI/NO-2
| a) Serajganj end | MWh | 7193 | 2026-03-12
| b) Sreepur | MWh | 0
27 | Daily Maximum Energy Import through EWI/ NO-2
| a)Serajganj end | MWh | 0 | - | -
| b) Sreepur | MWh | - | - | -
28 | Total Energy Export through EWI/ NO-2
| a)Serajganj end | MWh | 341331.2 | - | -
| b) Sreepur | MWh | 0 | - | -
29 | Total Energy Import through EWI/ NO-2
| a)Serajganj end | MWh | 0 | - | -
| b) Sreepur | MWh | 330858.9 | - | -
30 | Transmission loss of EWI/ NO-2 | % | 3.07 | - | -
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2946 | 2026-03-15 | 21:00
|  | MW | 1944
| b) Aminbazar end | AMPS | 0
|  | MW | 0
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | 0
|  | MW | 0
| b) Aminbazar end | AMPS | 2935 | 2026-03-15 | 21:00
|  | MW | 1943
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 39720 | 2026-03-15 | N/A
| a) Aminbazar end | MWh | 0
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0 | - | N/A
| a) Aminbazar end | MWh | 39677 | 2026-03-15
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 875520
| b) Aminbazar end (ckt-1 ) | MWh | 0
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0
| b) Aminbazar end (ckt-2 ) | MWh | 874185
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.152
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: March 2026
| Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Jamalpur 132/33kV | T-2 | 2026-03-03 17:47 | 2026-03-03 18:17 | 0.020833 | T | Over current A-phase trip Micom p632 ,p132 132 side | 45 | 22.5 | Power interruption
Jamalpur 132/33kV | T-2 | 2026-03-28 16:13 | 2026-03-28 21:37 | 0.225 | T | O/C, E/F, R-Y phase N/A | 30 | 162 | Power interruption
Kabirpur 132/33kV | XFR, T-I | 2026-03-31 09:53 | 2026-03-31 10:16 | 0.015972 | T | 33 kV baroibari feeder CT and CB blast Micom P-127 | 67 | 25.6833 | Power interruption
Savar 132/33kV | T-3 | 2026-03-17 05:43 | 2026-03-17 07:20 | 0.067361 | T | Frequency Protection Trip LV Backup protection Relay | 0 | 0 | No interruption
Savar 132/33kV | T-4 | 2026-03-17 05:43 | 2026-03-17 07:24 | 0.070139 | T | Under Frequency Tripping LV Backup Protection Relay | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2026-03-13 19:25 | 2026-03-13 21:40 | 0.09375 | T | Over current FBCPU | 34 | 76.5 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2026-03-17 06:06 | 2026-03-17 06:24 | 0.0125 | T | Main1 | 32 | 9.6 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2026-03-17 06:06 | 2026-03-17 06:24 | 0.0125 | T | Main1 | 44 | 13.2 | Power interruption
Tongi 230/132/33kV | 230 kV Bus-2 | 2026-03-20 21:10 | 2026-03-20 21:25 | 0.010417 | T | 230 kv bus 2, B phase PT Blast High impedance, phase R T, Supervison relay | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-2 | 2026-03-19 21:05 | 2026-03-20 00:41 | 0.15 | E/O | Red hot at 33 kV bus DS of TR-2 | 24 | 86.4 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2026-03-27 20:17 | 2026-03-27 22:42 | 0.10069 | E/O | RedHot Maintenance of TR-02 ,Y phase 33kV incoming Bus DS . | 40 | 96.6667 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2026-03-31 09:58 | 2026-03-31 09:58 | 0 | E/O | 33 kV boroibari feeder bus DS loop connecting work | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-2 HT | 2026-03-19 21:06 | 2026-03-20 00:38 | 0.14722 | E/O | Red hot at 33 kV Bus DS of TR -2 | 24 | 84.8 | Power interruption
Kabirpur 132/33kV | XFR, T-2 HT | 2026-03-27 20:17 | 2026-03-27 22:41 | 0.1 | E/O | RedHot Maintenance of TR-02 Y phase 33kV incoming Bus DS. | 40 | 96 | Power interruption
|  |  | Total : | 1899-12-31 00:38 |  | Unserved Energy: |  | 673.35
Dhaka (South) Grid Circle :
Hasnabad 132/33kV | 132/33kV 404 T-1 | 2026-03-13 20:45 | 2026-03-13 21:24 | 0.027083 | T | 33kV feeder trip Over current and eart fault | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 414 T-2 | 2026-03-13 20:45 | 2026-03-13 21:24 | 0.027083 | T | 33kV feeder trip Over current and eart fault | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 424 T-5 | 2026-03-13 20:45 | 2026-03-13 21:24 | 0.027083 | T | 33 kv feeder fault Over current and eart fault | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 404 T-1 | 2026-03-14 02:26 | 2026-03-14 02:41 | 0.010417 | T | Pangoan Cb to mid d/s detached from the system. Master Trip relay | 27 | 6.75 | Power interruption
Hasnabad 132/33kV | 132/33kV 424 T-5 | 2026-03-14 02:26 | 2026-03-14 02:41 | 0.010417 | T | 33kv pangoan CB to mid D/s loop detached from the system. Trip relay | 27 | 6.75 | Power interruption
Hasnabad 132/33kV | 132/33kV 404 T-1 | 2026-03-20 11:20 | 2026-03-20 11:36 | 0.011111 | T | 33kv pangaon and Nawabganj-2 feeder fault E/F, O/C and 33kv master trip OPDG | 15 | 4 | Power interruption
Hasnabad 132/33kV | 132/33kV 424 T-5 | 2026-03-20 11:20 | 2026-03-20 11:36 | 0.011111 | T | 33kv pangaon and Nawabganj-2 feeder fault Over current and Earth Fault | 15 | 4 | Power interruption
Hasnabad 132/33kV | 33kv Main Bus | 2026-03-20 11:20 | 2026-03-20 11:36 | 0.011111 | T | 33kv pangaon and Nawabganj-2 feeder fault Over current and Earth fault | 30 | 8 | Power interruption
Narshingdi 132/33kV | T-2 | 2026-03-13 19:55 | 2026-03-13 20:25 | 0.020833 | T | Thundaring RET670 | 30 | 15 | Power interruption
Narshingdi 132/33kV | T-2 | 2026-03-20 11:26 | 2026-03-20 12:06 | 0.027778 | T | Inter trip REF 630 | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-2 | 2026-03-25 19:25 | 2026-03-25 19:42 | 0.011806 | T | Due to 33 kv PBS Feeders fault Overcurrent protection relay P142 | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-2 | 2026-03-02 16:25 | 2026-03-02 18:30 | 0.086806 | T | 33 kv narsingdi feeder CB flashing and auxiliary 2 b phase loop out and all the fuses are burn out due to rain. MVAJ | 70 | 145.8333 | Power interruption
Sonargaon 132/33kV | Tr-1 | 2026-03-02 16:30 | 2026-03-02 18:31 | 0.084028 | T | 33 kv Barpa, langalband feeder flushing due to rain and auxiliary 1 r phase loop out and lay off to bus, fuses burn out. MVAJ | 60 | 121 | Power interruption
Sonargaon 132/33kV | Tr-1 | 2026-03-13 20:15 | 2026-03-13 23:03 | 0.11667 | T | Auxiliary transformer flashing due to bad weather DIR O/C | 41 | 114.8 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2026-03-13 20:21 | 2026-03-13 21:58 | 0.067361 | T | Auxiliary transformer flashing due to bad weather O/C | 16 | 25.8667 | Power interruption
Sonargaon 132/33kV | Tr-1 | 2026-03-17 05:45 | 2026-03-17 07:17 | 0.063889 | T | Under frequency Trip Under frequency | 60 | 92 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2026-03-17 05:45 | 2026-03-17 07:17 | 0.063889 | T | Under frequency Under frequency | 57 | 87.4 | Power interruption
Sonargaon 132/33kV | Tr-1 | 2026-03-18 19:42 | 2026-03-19 03:31 | 0.32569 | T | DUE TO BAD WEATHER. T-1 auxiliary TRANSFORMER droup out fuse burst. TRIP RELAY(MVAJM-25) | 4 | 31.2667 | Power interruption
Bhulta 400/230kV | 400kV Bus-1 | 2026-03-19 15:02 | 2026-03-19 21:42 | 0.27778 | E/O | Due to Emeregency maint.work | 0 | 0 | No interruption
Madanganj 132/33kV | GT-1 | 2026-03-18 22:00 | 2026-03-18 22:22 | 0.015278 | E/O | Neutral grounding bushing flashing maintenance | 12 | 4.4 | Power interruption | 0:22
Madanganj 132/33kV | BUS Coupler | 2026-03-22 14:46 | 2026-03-22 21:50 | 0.29444 | E/O | Redhot maintenance | 0 | 0 | No interruption | 0:08
Munshiganj 132/33kV | Transformer-1 | 2026-03-18 21:10 | 2026-03-18 22:08 | 0.040278 | E/O | T1 & T2 both sides incoming trip at 08:20 for 33kv bus-coupler insulator flashing. Now T1 x-former is shut down from 09:10 for maintenance by PBS. | 40 | 38.6667 | Power interruption | 3:49
Munshiganj 132/33kV | Transformer-2 | 2026-03-18 21:10 | 2026-03-18 22:08 | 0.040278 | E/O | T1 & T2 both sides incoming trip at 08:20 for 33kv bus-coupler insulator flashing. Now T2 x-former is shut down from 09:10 for maintenance by PBS. | 40 | 38.6667 | Power interruption | 0:10
Narshingdi 132/33kV | T-3 | 2026-03-29 12:01 | 2026-03-29 13:39 | 0.068056 | E/O | নরসিংদী ১৩২/৩৩কেভি গ্রিডের T-3 ট্রান্সফরমারের ১৩২কেভি বাস-০১ ডিএস রিমোটে অপারেশন হয় না | 0 | 0 | No interruption | 2:02
Nawabganj 132/33kV | TR-2 | 2026-03-25 23:39 | 2026-03-26 00:22 | 0.029861 | E/O | 33 kv Incomer -2 shutdown for redhot maintenance on R phase. | 15 | 10.75 | Power interruption | 0:13
Nawabganj 132/33kV | 33kV Bus Section-1 | 2026-03-26 00:26 | 2026-03-26 02:05 | 0.06875 | E/O | 33 kv Incomer -1 & Bus-01 shutdown for redhot maintenance on R & Y phase. | 10 | 16.5 | Power interruption | 0:13
Nawabganj 132/33kV | TR-2 | 2026-03-30 08:33 | 2026-03-30 09:55 | 0.056944 | E/O | 33 kV incomer-02 shutdown for redhot maintenance. | 0 | 0 | No interruption | 0:12
|  |  | Total : | 1899-12-31 21:30 |  | Unserved Energy: |  | 771.65 |  | 1:09
Chattogram Grid Circle :
Bakulia 132/33kV | T-3 (422T) | 2026-03-17 05:00 | 2026-03-17 06:28 | 0.061111 | T | Micom | 12 | 17.6 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2026-03-10 12:28 | 2026-03-10 12:48 | 0.013889 | T | Lockout Relay K862 trip | 28 | 9.3333 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2026-03-10 15:42 | 2026-03-10 15:55 | 0.0090278 | T | Lockout Relay K862 trip | 24 | 5.2 | Power interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2026-03-20 17:56 | 2026-03-20 20:02 | 0.0875 | T | Fault by bpdb REF615,RET650,RET 670 | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2026-03-14 19:39 | 2026-03-16 14:50 | 1899-12-31 19:11 | T | 132/33 KV, 44.1/63 MVA Tr-1 LT side cable blust. | 0 | 0 | No interruption
Halishahar 132/33kV | 415T(TR-2) | 2026-03-08 14:45 | 2026-03-08 15:48 | 0.04375 | E/O | Due to emergency maintenance work at t-2 secondary B-phase Isolator contact. | 0 | 0 | No interruption
Rampur 230/132/33 | TR 02 (417T) | 2026-03-15 00:15 | 2026-03-15 10:40 | 0.43403 | E/O | high temperature at 33kv side B-phase | 0 | 0 | No interruption
Sholosohor 132/33kV | TRAFO-02 | 2026-03-02 14:26 | 2026-03-02 14:34 | 0.0055556 | E/O | To remove bird nest from 33kV gantry which is directly above the auxiliary Transformer-02. | 10 | 1.3333 | Power interruption
Halishahar 132/33kV | 405T(TR-1) | 2026-03-08 16:05 | 2026-03-08 16:53 | 0.033333 | E/O | Due to 33Kv side CT unbalanced problem to B phase CT Protection core Short. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 11:42 |  | Unserved Energy: |  | 33.4667
Cumilla Grid Circle :
Brahmanbaria 132/33kV | 402T | 2026-03-25 17:38 | 2026-03-25 18:20 | 0.029167 | T | O/C &E/F | 40 | 28 | Power interruption
Brahmanbaria 132/33kV | Aux. Tr-2 (PGCB) | 2026-03-25 17:38 | 2026-03-25 18:22 | 0.030556 | T | O/C | 1.2 | 0.88 | Power interruption
Cumilla(S) 132/33kV | TR-3 | 2026-03-06 08:19 | 2026-03-06 08:47 | 0.019444 | T | RET 650 ,REF615 | 33 | 15.4 | Power interruption
Cumilla(S) 132/33kV | TR-3 | 2026-03-18 19:47 | 2026-03-18 20:11 | 0.016667 | T | 33KV PDB Fedder fult REF615 | 54 | 21.6 | Power interruption
Daudkandi 132/33kV | Transformer-3 | 2026-03-26 07:40 | 2026-03-26 08:07 | 0.01875 | T | Flashing at 33KV switchyard near to Palli Bidyut Feeder-10 breaker. Overcurrent relay | 20 | 9 | Power interruption
Shahjibazar 132/33kV | TR-04 | 2026-03-02 19:22 | 2026-03-02 19:38 | 0.011111 | T | Madhabpur-02 Feeder tripped OC/EF Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2026-03-04 13:11 | 2026-03-04 13:19 | 0.0055556 | T | Habiganj Bypass & Shaistaganj Feeder OC/EF Fault. Trip Relay-1 | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2026-03-17 02:50 | 2026-03-17 03:30 | 0.027778 | T | Shaistagang Feeder OC/EF Fault. Lock out | 55 | 36.6667 | Power interruption
Shahjibazar 132/33kV | TR-02 | 2026-03-20 16:16 | 2026-03-20 16:37 | 0.014583 | T | Madhabpur-3 Feeder OC/EF fault. Non | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2026-03-30 14:32 | 2026-03-30 14:37 | 0.0034722 | T | Chunarughat Feeder Tripped of PBS OC/EF Protection Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2026-03-30 21:45 | 2026-03-30 21:56 | 0.0076389 | T | Chunarughat feeder Trip Under PBS. Lockout | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-2 | 2026-03-13 05:18 | 2026-03-13 05:23 | 0.0034722 | T | 33 kV Bus fault. Over current | 2 | 0.16667 | Power interruption
Sylhet (South) | Trafo-1 | 2026-03-17 05:42 | 2026-03-17 07:27 | 0.072917 | T | Under Frequency Bay Control Protection Unit 7SJ85 | 7 | 12.25 | Power interruption
Sylhet (South) | Trafo-2 | 2026-03-17 05:42 | 2026-03-17 07:27 | 0.072917 | T | Under Frequency Bay Control Protection Unit 7SJ85 | 8 | 14 | Power interruption
Shahjibazar 132/33kV | TR-02 HT | 2026-03-17 02:50 | 2026-03-17 03:09 | 0.013194 | T | Shaistaganj Feeder OC/EF Fault. | 55 | 17.4167 | Power interruption
Sreemongol 132/33kV | 132/33kv T-3 HT | 2026-03-11 07:45 | 2026-03-11 08:22 | 0.025694 | T | 33kv Tr-3 circuit breaker is burst | 45 | 27.75 | Power interruption
Chandina 132/33kV | TR-2 | 2026-03-11 11:45 | 2026-03-13 14:02 | 1900-01-01 02:17 | E/O | For isolator changing work by PDB. Clearance by Md. Motiur Rahman (SAE) PDB. | 0 | 0 | No interruption
Chandina 132/33kV | TR-3 | 2026-03-18 21:13 | 2026-03-18 22:31 | 0.054167 | E/O | Auxiliary TR-2 Post Insulator Red Hot problem for Raining . | 0 | 0 | No interruption
Chandpur 132/33kV | 402T (T-01) | 2026-03-02 13:00 | 2026-03-02 13:00 | 0 | E/O | Loadshare | 0 | 0 | No interruption
Chowmuhani 230/132/33kV |  | 2026-03-14 09:45 | 2026-03-14 12:15 | 0.10417 | E/O | 33kv T-3 Bus S/D | 20 | 50 | Power interruption
Daganbhuiyan 132/33kV | Transformer-1 | 2026-03-14 09:32 | 2026-03-14 15:34 | 0.25139 | E/O | 33KV side Red hot work by Pbs | 11 | 66.3667 | Power interruption
Sreemongol 132/33kV | 132/33kv T-1AB | 2026-03-13 05:23 | 2026-03-13 09:10 | 0.15764 | E/O | 33 kV Bus fault removing work. | 5 | 18.9167 | Power interruption
Sunamganj 132/33kV | Tr-2 | 2026-03-29 14:14 | 2026-03-29 14:43 | 0.020139 | E/O | Oil leakage maintenance | 0 | 0 | No interruption
Maijdee 132/33kV | TR-01 HT | 2026-03-16 12:22 | 2026-03-16 13:03 | 0.028472 | E/O | Emergency maint.work | 0 | 0 | No interruption
Beanibazar 132/33kV | 132 KV Transformer TR-01 HT | 2026-03-24 10:13 | 2026-03-24 11:18 | 0.045139 | E/O | Emergency shutdown | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 03:06 |  | Unserved Energy: |  | 318.4133
Khulna Grid Circle :
Barishal 132/33kV | T-2 (415T) | 2026-03-09 13:52 | 2026-03-09 14:05 | 0.0090278 | T | PBS Charbaria 33kV feeder fault Instt.E/F , Definite E/F , lock out Realy | 50 | 10.8333 | Power interruption
Barishal 132/33kV | T-1 (405T) | 2026-03-20 16:36 | 2026-03-20 17:06 | 0.020833 | T | T-1 & T-2 33kV trip for pbs Charbaria 33kV bus loop fault Inst. O/C, Deff. O/C | 22 | 11 | Power interruption
Barishal 132/33kV | T-2 (415T) | 2026-03-20 16:36 | 2026-03-20 18:26 | 0.076389 | T | Pbs Charbaria 33kV feeder bus loop fault Inst. O/c, Deff. O/C | 12 | 22 | Power interruption
Barishal 132/33kV | T-1 (405T) | 2026-03-22 05:52 | 2026-03-22 06:09 | 0.011806 | T | WZPDCL 33kV feeder fault (Polashpur, Dopdopia 1) Instt. O/V, Definite O/V, 86X | 30 | 8.5 | Power interruption
Bhandaria 132/33kV | Transformer-1 | 2026-03-05 05:21 | 2026-03-05 05:36 | 0.010417 | T | 33kV kathalia feeder fault Over current pro. Trip, K86.1trip, K86.2 trip | 15 | 3.75 | Power interruption
Bhandaria 132/33kV | Transformer-2 | 2026-03-05 05:21 | 2026-03-05 05:36 | 0.010417 | T | 33 kV kathalia feeder fault Over current pro. Trip, K86.1 trip, K86.2 trip | 15 | 3.75 | Power interruption
Faridpur 132/33kV | Transformer-1 | 2026-03-21 03:15 | 2026-03-21 03:33 | 0.0125 | T | 33kV Khalil Mondol feeder fault 33kV over current and Earth Fault. | 36 | 10.8 | Power interruption
Faridpur 132/33kV | Transformer-2 | 2026-03-21 03:15 | 2026-03-21 03:33 | 0.0125 | T | 33kV khalil mondol feeder fault. 33kV o/c & E/F | 36 | 10.8 | Power interruption
Faridpur 132/33kV | Transformer-1 | 2026-03-28 02:44 | 2026-03-28 03:03 | 0.013194 | T | 33kV CB trip 132kV o/c | 45 | 14.25 | Power interruption
Faridpur 132/33kV | Transformer-2 | 2026-03-28 02:44 | 2026-03-28 03:03 | 0.013194 | T | 33kV CB trip 132kV O/C | 45 | 14.25 | Power interruption
Khulna (C) | Tr-3 405T | 2026-03-21 03:50 | 2026-03-21 05:15 | 0.059028 | T | E/F Inst 33kv side Chandanimahal feeder fault. No relay. | 8 | 11.3333 | Power interruption
Mongla 132/33kV | T-2 | 2026-03-16 23:47 | 2026-03-17 01:06 | 0.054861 | T | Auxiliary Tx-2 trip Over current pro. Fault | 27 | 35.55 | Power interruption
Mongla 132/33kV | T-1 | 2026-03-16 23:48 | 2026-03-17 01:05 | 0.053472 | T | Mongla cement trip Overcurrent pro.Trip &Earth fault pro. Trip | 8 | 10.2667 | Power interruption
Mongla 132/33kV | T-1 | 2026-03-17 06:35 | 2026-03-17 09:45 | 0.13194 | T | Auxiliary Tx-1 blast and oil leakage Lockout Reay | 8 | 25.3333 | Power interruption
Mongla 132/33kV | T-2 | 2026-03-20 15:52 | 2026-03-20 17:55 | 0.085417 | T | Due to 33 KV Bus PT Blast Over Current/Earth Fault | 9 | 18.45 | Power interruption
Satkhira 132/33kV | Transformer-1 (T-1) | 2026-03-26 07:30 | 2026-03-26 07:37 | 0.0048611 | T | Due to 33 kv kajirhat feeder fault Over current relay | 80 | 9.3333 | Power interruption
Bhandaria 132/33kV | Transformer-1 HT | 2026-03-05 05:21 | 2026-03-05 05:21 | 0 | T | Kathalia 33 kv feedar fault | 0 | 0 | No interruption
Bhandaria 132/33kV | Transformer-1 HT | 2026-03-15 15:50 | 2026-03-15 16:47 | 0.039583 | E/O | Bus D/S maintenances for Pbs bamna feeder. | 10 | 9.5 | Power interruption
Bhandaria 132/33kV | Transformer-2 HT | 2026-03-17 12:12 | 2026-03-17 12:35 | 0.015972 | E/O | Remove polybag from 33kv bushing of T2 | 0 | 0 | No interruption
Benapole 132/33kV | Transformer-2(416T) HT | 2026-03-12 11:29 | 2026-03-12 11:37 | 0.0055556 | E/O | Bus Separation | 20 | 2.6667 | Power interruption
Borhanuddin 230/33kV | Tr-Load HT | 2026-03-25 07:10 | 2026-03-25 09:23 | 0.092361 | E/O | Incomma 33 kv source kalam & bus bar maintenance . | 60 | 133 | Power interruption
Madaripur 132/33kV | T3-426T HT | 2026-03-20 15:03 | 2026-03-20 18:52 | 0.15903 | E/O | Due to fault | 20 | 76.3333 | Power interruption
Barishal 230/132kV | ATR-1 | 2026-03-07 15:53 | 2026-03-07 16:24 | 0.021528 | E/O | Oil Refiled for Aux-1 | 0 | 0 | No interruption
Benapole 132/33kV | Transformer-2(416T) | 2026-03-12 11:28 | 2026-03-12 11:38 | 0.0069444 | E/O | Bus Separation | 20 | 3.3333 | Power interruption
Bhandaria 132/33kV | Transformer-1 | 2026-03-15 15:49 | 2026-03-15 16:50 | 0.042361 | E/O | Bus D/S maintenances for Pbs bamna feeder. | 10 | 10.1667 | Power interruption
Bhandaria 132/33kV | Transformer-2 | 2026-03-17 12:11 | 2026-03-17 12:36 | 0.017361 | E/O | Remove polybag from 33kv bushing of T2 | 0 | 0 | No interruption
Mongla 132/33kV | T-2 | 2026-03-28 11:05 | 2026-03-28 13:07 | 0.084722 | E/O | Red Hot | 26 | 52.8667 | Power interruption
Rampal 400/230kV | Bus Reactor | 2026-03-27 19:22 | 2026-03-28 02:57 | 0.31597 | E/O | Khulna ALDC Demand | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 09:09 |  | Unserved Energy: |  | 508.0667
HVDC Grid Circle :
BIPTC | 20DF22 | 2026-03-31 05:22 | 2026-03-31 10:26 | 0.21111 | T | Tripped | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-1(403T) | 2026-03-29 16:45 | 2026-03-29 17:31 | 0.031944 | E/O | 33 kv bus red hot remove | 10 | 7.6667 | Power interruption
Bhangura 132/33kV | Tr-1(403T) | 2026-03-31 20:25 | 2026-03-31 21:09 | 0.030556 | E/O | 33 KV TR-1 CT Y phase Red Hot | 0 | 0 | No interruption
BIPTC | 20DF24 | 2026-03-09 10:14 | 2026-03-09 11:24 | 0.048611 | E/O | Shutdown is taken for corrective maintenance work. | 0 | 0 | No interruption
BIPTC | 10CF14 | 2026-03-09 10:58 | 2026-03-09 11:24 | 0.018056 | E/O | Emergency shutdown to remove twisted kite string from the C1 capacitor cell tower. | 0 | 0 | No interruption
BIPTC | 10CF25 | 2026-03-16 10:18 | 2026-03-16 10:57 | 0.027083 | E/O | Emergency maint.work | 0 | 0 | No interruption
BIPTC | 10CF16 | 2026-03-16 10:49 | 2026-03-16 11:59 | 0.048611 | E/O | Emergency maint.work | 0 | 0 | No interruption
BIPTC | 10CF15 | 2026-03-19 08:25 | 2026-03-19 10:57 | 0.10556 | E/O | Shutdown is taken for emergency maintenance | 0 | 0 | No interruption
BIPTC | 20DF32 | 2026-03-27 17:09 | 2026-03-27 17:32 | 0.015972 | E/O | Tripped | 0 | 0 | No interruption
BIPTC | 20DF22 | 2026-03-31 09:05 | 2026-03-31 10:26 | 0.05625 | E/O | 20DF22 tripped at 05:22 today. | 0 | 0 | No interruption
BIPTC | 20DF24 | 2026-03-31 10:07 | 2026-04-01 12:41 | 1899-12-31 02:34 | E/O | Flashing spot at some location has been noticed. | 0 | 0 | No interruption
BIPTC | 20DF11 | 2026-03-31 10:34 | 2026-03-31 12:14 | 0.069444 | E/O | Emergency maint.work | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T3 | 2026-03-24 15:30 | 2026-03-24 16:57 | 0.060417 | E/O | Red Hot Maintenance work at 33kV Feeder | 26 | 37.7 | Power interruption
Bhangura 132/33kV | Tr-2(413T) | 2026-03-05 19:58 | 2026-03-05 21:45 | 0.074306 | E/O | Redhot ct | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-2(413T) | 2026-03-06 20:00 | 2026-03-06 20:58 | 0.040278 | E/O | 33 KV CT Red hot | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-2(413T) | 2026-03-13 22:16 | 2026-03-13 22:59 | 0.029861 | E/O | 33 Kv Tr-2 CT Red hot removing. | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-1(403T) | 2026-03-29 16:45 | 2026-03-29 17:32 | 0.032639 | E/O | 33 Kv bus red hot removeing | 10 | 7.8333 | Power interruption
Bhangura 132/33kV | Tr-1(403T) | 2026-03-31 20:23 | 2026-03-31 21:11 | 0.033333 | E/O | 33 KV TR-1 CT Y phase Red Hot | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T3 | 2026-03-24 15:30 | 2026-03-24 16:58 | 0.061111 | E/O | Red Hot Maintenance work at 33kV Feeder | 26 | 38.1333 | Power interruption
Ishurdi 230/132kV | 230/132 kV T-01 | 2026-03-16 11:02 | 2026-03-16 12:46 | 0.072222 | E/O | 230/132kv transformer T01 red hot maintenance | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-02 | 2026-03-16 12:52 | 2026-03-16 14:55 | 0.085417 | E/O | red hot maintenance work | 0 | 0 | No interruption
Kushtia 132/33kV | T2 | 2026-03-15 14:49 | 2026-03-15 15:02 | 0.0090278 | E/O | The power at the grid substation dropped to zero due to transmission line trip. | 50 | 10.8333 | Power interruption
Kushtia 132/33kV | T-1 | 2026-03-15 14:50 | 2026-03-15 15:03 | 0.0090278 | E/O | Power at the Kushtia Grid Substation dropped to zero following a trip on the Bheramara-Kushtia Circuit-1 (Bheramara end) and the Kushtia-Jhenaidah Circuit-1 (Kushtia end). | 15 | 3.25 | Power interruption
Kushtia 132/33kV | T-3 | 2026-03-15 14:51 | 2026-03-15 15:03 | 0.0083333 | E/O | Power at the Kushtia Grid Substation dropped to zero following a trip on the Bheramara-Kushtia Circuit-1 (Bheramara end) and the Kushtia-Jhenaidah Circuit-1 (Kushtia end). | 61 | 12.2 | Power interruption
Shahjadpur 132/33kV | T-1(405T) | 2026-03-24 14:46 | 2026-03-25 12:32 | 0.90694 | E/O | 33 kV Ds maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 04:38 |  | Unserved Energy: |  | 117.6167
Bogura Grid Circle:
Barapukuria 230/132/33kV | 132/33 KV T-5, 424T | 2026-03-23 06:08 | 2026-03-23 12:29 | 0.26458 | T | Under ground cable fault (Y-phase) ALSTOM MCGG | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-1 (404T) | 2026-03-15 23:49 | 2026-03-16 00:10 | 0.014583 | T | Over current Over current protection (P142) | 10 | 3.5 | Power interruption
Bog-Sherpur 132/33kV | Transformer-2 (414T) | 2026-03-15 23:49 | 2026-03-16 00:10 | 0.014583 | T | Over current Over current protection (P142) | 0 | 0 | No interruption
Jaldhaka 132/33kV | 406T-1 | 2026-03-17 06:07 | 2026-03-17 06:29 | 0.015278 | T | Frequency unbalance. Micom P142 | 11 | 4.0333 | Power interruption
Jaldhaka 132/33kV | 416T-2 | 2026-03-17 06:07 | 2026-03-17 06:30 | 0.015972 | T | Frequency unbalance Micom P142 | 11 | 4.2167 | Power interruption
Mahasthangarh 132/33kV | 406T MTR1 | 2026-03-18 19:45 | 2026-03-18 21:40 | 0.079861 | T | Nesco 33 C.T Burst Micom P139 | 31 | 59.4167 | Power interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2026-03-18 19:45 | 2026-03-18 20:47 | 0.043056 | T | Nesco 33 C.T Burst MiCOM P139 | 31 | 32.0333 | Power interruption
Mahasthangarh 132/33kV | 406T MTR1 | 2026-03-19 12:35 | 2026-03-19 13:37 | 0.043056 | T | Nesco 33 kv feeder Fault. over curent P142 | 20 | 20.6667 | Power interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2026-03-19 12:35 | 2026-03-19 12:52 | 0.011806 | T | Nesco 33 kv feeder Fault. OVER Current P142 | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-2 (417T) | 2026-03-17 07:02 | 2026-03-17 07:37 | 0.024306 | T | Birds are causing flashover on the PBS 33 kV feeder (Niamatpur-2). Siprotec 7SJ1 | 15 | 8.75 | Power interruption
Rajshahi 132/33kV | Transformer T-2(415T) | 2026-03-15 22:30 | 2026-03-16 02:33 | 0.16875 | T | টি-২ ৩৩ কেভি বাস-কাপলারের ইনসুলেটর Cracked O/C | 8 | 32.4 | Power interruption
Rajshahi 132/33kV | Transformer T-3 (425T) | 2026-03-21 00:46 | 2026-03-21 01:30 | 0.030556 | T | 67 67 | 20 | 14.6667 | Power interruption
Rajshahi 132/33kV | Transformer T-2(415T) | 2026-03-21 01:27 | 2026-03-21 01:53 | 0.018056 | T | Mohonpur Feeder Faulty 67 | 0 | 0 | No interruption
Saidpur 132/33kV | TR-4 (414T) | 2026-03-20 06:15 | 2026-03-20 06:28 | 0.0090278 | T | O/C Siemens | 0 | 0 | No interruption
Saidpur 132/33kV | TR-5 (434T) | 2026-03-21 02:25 | 2026-03-21 03:26 | 0.042361 | T | No Relay | 0 | 0 | No interruption
Sirajganj 132/33kV | T1-(415) | 2026-03-16 14:34 | 2026-03-16 14:54 | 0.013889 | T | 33 KV Sialkole Feeder BUS DS (R PH) Insulator Failure Schneider MICOM P142 (Over Current Protection ) | 20 | 6.6667 | Power interruption
Sirajganj 132/33kV | T2-(425) | 2026-03-16 14:34 | 2026-03-16 14:54 | 0.013889 | T | 33 KV Sialkole Feeder BUS DS (R PH) Insulator Failure Schneider MICOM P142 (Over Current Protection ) | 20 | 6.6667 | Power interruption
Niamatpur 132/33kV | Transformer-2 (417T) | 2026-03-17 07:02 | 2026-03-17 07:37 | 0.024306 | T | Birds are causing flashover on the PBS 33 kV feeder(Niamatpur-2). | 15 | 8.75 | Power interruption
Rajshahi 132/33kV | Transformer T-2(415T) | 2026-03-21 00:46 | 2026-03-21 01:24 | 0.026389 | T | Mohonpur Feeder Faulty | 10 | 6.3333 | Power interruption
Rajshahi 132/33kV | Transformer T-2(415T) | 2026-03-21 01:27 | 2026-03-21 01:50 | 0.015972 | T | Mohonpur Feeder Faulty | 0 | 0 | No interruption
Saidpur 132/33kV | TR-5 (434T) | 2026-03-21 02:25 | 2026-03-21 03:25 | 0.041667 | T | For 33kv Trillion gold feeder trail. | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 406T MTR1 | 2026-03-19 12:35 | 2026-03-19 13:34 | 0.040972 | T | Nesco 33 kv feeder Fault. | 20 | 19.6667 | Power interruption
Niamatpur 132/33kV | Transformer-2 (417T) | 2026-03-17 07:02 | 2026-03-17 07:37 | 0.024306 | T | Birds are causing flashover on the PBS 33 kV feeder(Niamatpur-2). | 15 | 8.75 | Power interruption
Rajshahi 132/33kV | Transformer T-2(415T) | 2026-03-21 00:46 | 2026-03-21 01:24 | 0.026389 | T | Mohonpur Feeder Faulty | 10 | 6.3333 | Power interruption
Rajshahi 132/33kV | Transformer T-2(415T) | 2026-03-21 01:27 | 2026-03-21 01:50 | 0.015972 | T | Mohonpur Feeder Faulty | 0 | 0 | No interruption
Saidpur 132/33kV | TR-5 (434T) | 2026-03-21 02:25 | 2026-03-21 03:25 | 0.041667 | T | For 33kv Trillion gold feeder trail. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 230/132 KV T-02, 713T | 2026-03-09 10:06 | 2026-03-09 14:26 | 0.18056 | E/O | Oil leakage Maintenance work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132/33 KV T-5, 424T | 2026-03-10 09:52 | 2026-03-10 10:28 | 0.025 | E/O | Emergency maintenance work. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-1 (404T) | 2026-03-15 15:49 | 2026-03-15 17:23 | 0.065278 | E/O | 33kV Feeder Redhot Maintenance work by PBS. | 40 | 62.6667 | Power interruption
Bog-Sherpur 132/33kV | Transformer-2 (414T) | 2026-03-16 01:48 | 2026-03-16 11:51 | 0.41875 | E/O | 33 kV bus conductor snapped. | 10 | 100.5 | Power interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2026-03-18 09:21 | 2026-03-18 12:13 | 0.11944 | E/O | 33 kv feeder red hot . | 15 | 43 | Power interruption
Mahasthangarh 132/33kV | 406T MTR1 | 2026-03-19 08:55 | 2026-03-19 10:34 | 0.06875 | E/O | 33 KV Bus-1 work | 15 | 24.75 | Power interruption
Naogaon 132/33kV | T-1 | 2026-03-17 07:29 | 2026-03-17 07:42 | 0.0090278 | E/O | T-1 CB SF6 gas Low | 0 | 0 | No interruption
Rangpur 132/33kV | T-2 (404T) | 2026-03-27 14:45 | 2026-03-27 17:25 | 0.11111 | E/O | 33Kv bus- 3 Y -Phase red hot | 45 | 120 | Power interruption
Sirajganj 132/33kV | T3-(435) | 2026-03-19 01:01 | 2026-03-19 02:10 | 0.047917 | E/O | kazipur feeder Bus Ds insulator replace work. | 10 | 11.5 | Power interruption
Thakurgaon 132/33kV | T-3(432T) | 2026-03-26 19:36 | 2026-03-26 20:26 | 0.034722 | E/O | LT side R-Phase bushing red hot | 0 | 0 | No interruption
Thakurgaon 132/33kV | T-2(412T) | 2026-03-30 07:21 | 2026-03-30 09:03 | 0.070833 | E/O | Due to red hot maintenance in 33kV Incoming-2 CT. | 28 | 47.6 | Power interruption
Barapukuria 230/132/33kV | 230/132 KV T-02, 713T | 2026-03-09 10:07 | 2026-03-09 14:25 | 0.17917 | E/O | Oil leakage Maintenance work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132/33 KV T-5, 424T | 2026-03-10 09:54 | 2026-03-10 10:24 | 0.020833 | E/O | Emergency maintenance work. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-1 (404T) | 2026-03-15 15:50 | 2026-03-15 17:21 | 0.063194 | E/O | 33kV Feeder Redhot Maintenance work by PBS. | 40 | 60.6667 | Power interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2026-03-18 09:22 | 2026-03-18 12:12 | 0.11806 | E/O | 33 kv feeder red hot . | 15 | 42.5 | Power interruption
Mahasthangarh 132/33kV | 406T MTR1 | 2026-03-19 08:55 | 2026-03-19 10:34 | 0.06875 | E/O | 33 KV Bus-1 work | 15 | 24.75 | No interruption
Saidpur 132/33kV | TR-01 | 2026-03-12 03:03 | 2026-03-12 15:36 | 0.52292 | E/O | For a fire in a DAM transformer 11/.4 kv of 20 MW GTPS. | 0 | 0 | No interruption
Sirajganj 132/33kV | T3-(435) | 2026-03-19 01:01 | 2026-03-19 02:10 | 0.047917 | E/O | kazipur feeder Bus Ds insulator replace work. | 10 | 11.5 | Power interruption
|  |  | Total : | 1900-01-02 06:05 |  | Unserved Energy: |  | 792.2833
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 1900-01-15 08:48 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: March 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Manikgonj Power Plant-01 | 2026-03-01 04:37 | 2026-03-01 06:33 | 0.080556 | T | Manikgonj ckt-1 trip | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-02 | 2026-03-01 04:47 | 2026-03-01 05:44 | 0.039583 | T | Meghnaghat ckt-2 trip | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Gopalganj-1 | 2026-03-01 05:30 | 2026-03-02 17:23 | 1899-12-31 11:53 | T | General trip, dustance trip | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Keranigonj-01 | 2026-03-25 18:59 | 2026-03-25 20:55 | 0.080556 | T | Trip | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 01 | 2026-03-17 05:44 | 2026-03-17 06:42 | 0.040278 | T | Distance Trip 3-PHASE | 17 | 16.4333 | Power interruption
Bhaluka 132/33kV | Mymensingh Ckt- 02 | 2026-03-17 05:44 | 2026-03-17 06:42 | 0.040278 | T | Distance Trip 3-Phase | 17 | 16.4333 | Power interruption
Bhaluka 132/33kV | BR Powergen Ckt- 01 | 2026-03-17 05:44 | 2026-03-17 06:45 | 0.042361 | T | Trip (OV RED Broken Cond (GR) | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 02 | 2026-03-17 05:44 | 2026-03-17 06:45 | 0.042361 | T | OV RED broken CoND (GR) | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-01 | 2026-03-14 22:26 | 2026-03-14 22:57 | 0.021528 | T | Zone -2,distance trip,C-phase. | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-01 | 2026-03-24 19:08 | 2026-03-24 19:40 | 0.022222 | T | Earth fault | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-2 | 2026-03-05 15:52 | 2026-03-05 16:27 | 0.024306 | T | Operational fault | 170 | 99.1667 | Power interruption
Kabirpur 132/33kV | Kaliakair-1 | 2026-03-05 15:52 | 2026-03-05 16:45 | 0.036806 | T | Operational fault | 52 | 45.9333 | Power interruption
Kabirpur 132/33kV | Manikganj-2 | 2026-03-05 15:52 | 2026-03-05 16:43 | 0.035417 | T | Operational fault | 35 | 29.75 | Power interruption
Kabirpur 132/33kV | Tongi-1 | 2026-03-13 19:12 | 2026-03-13 19:21 | 0.00625 | T | Bad weather | 0 | 0 | No interruption
Kabirpur 132/33kV | Kaliakair-2 | 2026-03-14 07:48 | 2026-03-14 07:57 | 0.00625 | T | Trip | 0 | 0 | No interruption
Mirpur 132/33kV | T3 HT | 2026-03-14 09:50 | 2026-03-16 14:24 | 1900-01-01 04:34 | T | Trip | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Sector-18 | 2026-03-18 20:20 | 2026-03-18 20:24 | 0.0027778 | T | Over Voltage | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Jamalpur Ckt-1 | 2026-03-24 19:08 | 2026-03-24 19:43 | 0.024306 | T | Trip | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Ashuganj Ckt-1 | 2026-03-17 05:42 | 2026-03-17 06:51 | 0.047917 | T | DTT | 48 | 55.2 | Power interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-2 | 2026-03-17 05:42 | 2026-03-17 06:40 | 0.040278 | T | DTT | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2026-03-05 15:55 | 2026-03-05 16:17 | 0.015278 | T | Due fault at kabirpur ss | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2026-03-05 15:55 | 2026-03-05 16:28 | 0.022917 | T | Due to fault at kabirpur ss | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2026-03-13 20:34 | 2026-03-13 20:56 | 0.015278 | T | Trip | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2026-03-17 05:44 | 2026-03-17 06:52 | 0.047222 | T | Trip | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2026-03-18 17:38 | 2026-03-18 18:07 | 0.020139 | T | Trip | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2026-03-18 22:11 | 2026-03-18 22:14 | 0.0020833 | T | Trip | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Summit PS(Kodda) | 2026-03-20 19:10 | 2026-03-20 20:50 | 0.069444 | T | 230 kv bus 2, B phase PT Blast | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kaliakoir Ckt | 2026-03-20 19:10 | 2026-03-20 20:48 | 0.068056 | T | 230 kv bus 2, B phase PT Blast | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Uttara 3rd Phase Ckt | 2026-03-21 12:16 | 2026-03-21 12:50 | 0.023611 | T | Trip | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2026-03-28 12:43 | 2026-03-28 13:31 | 0.033333 | E/O | Broken birds nest | 0 | 0 | No interruption
|  |  | Total : | 1900-01-03 15:17 |  | Unserved Energy: |  | 262.9167
Dhaka (South) Grid Circle :
Bhulta 400/230kV | Ashuganj-01 | 2026-03-13 14:23 | 2026-03-13 18:58 | 0.19097 | T | trip | 0 | 0 | No interruption
Bhulta 400/230kV | Ashuganj-02 | 2026-03-13 14:23 | 2026-03-17 19:23 | 1900-01-03 05:00 | T | trip | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2026-03-01 05:25 | 2026-03-01 05:40 | 0.010417 | T | trip | 170 | 42.5 | Power interruption
Haripur 230/132kV | Ullon (Maniknagar-2) | 2026-03-01 04:38 | 2026-03-01 05:01 | 0.015972 | T | Unknown | 0 | 0 | No interruption
Haripur 230/132kV | Ullon (Maniknagar-2) | 2026-03-02 15:59 | 2026-03-02 16:31 | 0.022222 | T | Rainning | 0 | 0 | No interruption
Haripur 230/132kV | Siddhirganj-1 | 2026-03-04 10:35 | 2026-03-04 11:44 | 0.047917 | T | trip | 0 | 0 | No interruption
Haripur 230/132kV | Ullon (Maniknagar-2) | 2026-03-09 06:47 | 2026-03-09 07:02 | 0.010417 | T | trip | 0 | 0 | No interruption
Haripur 230/132kV | Ullon (Maniknagar-2) | 2026-03-13 20:11 | 2026-03-13 21:34 | 0.057639 | T | trip | 0 | 0 | No interruption
Haripur 230/132kV | Madanganj-1 | 2026-03-18 20:23 | 2026-03-18 20:51 | 0.019444 | T | trip | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Sreenagar Ckt. 2 | 2026-03-18 22:40 | 2026-03-18 23:37 | 0.039583 | T | Thundering | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 1 | 2026-03-19 01:05 | 2026-03-19 14:49 | 0.57222 | T | Bad Weather With Thundering. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 1 | 2026-03-25 18:59 | 2026-03-25 20:03 | 0.044444 | T | 67N Directional Earth Fault trip. | 0 | 0 | No interruption
Madanganj 132/33kV | GT-2 HT | 2026-03-13 20:30 | 2026-03-15 00:20 | 1899-12-31 03:50 | T | NoneB phase CT fail | 0 | 0 | No interruption
Madanganj 132/33kV | GT-1 HT | 2026-03-13 20:30 | 2026-03-13 23:25 | 0.12153 | T | trip | 10 | 29.1667 | Power interruption
Madanganj 132/33kV | Madanganj -Bashundhara 132 kv Ckt | 2026-03-13 20:30 | 2026-03-14 12:55 | 0.68403 | T | trip | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Munshiganj 132 kv Ckt-1 | 2026-03-13 20:30 | 2026-03-14 00:44 | 0.17639 | T | trip | 32 | 135.4667 | Power interruption
Madanganj 132/33kV | Madanganj -Haripur 132 kv Ckt-1 | 2026-03-13 20:30 | 2026-03-13 22:00 | 0.0625 | T | trip | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Summit 55 MW 132 kv Ckt | 2026-03-13 22:30 | 2026-03-14 16:17 | 0.74097 | T | trip | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Haripur 132 kv Ckt-1 | 2026-03-18 20:24 | 2026-03-18 20:56 | 0.022222 | T | trip | 8 | 4.2667 | Power interruption
Madanganj 132/33kV | Madanganj -Summit 55 MW 132 kv Ckt | 2026-03-18 21:00 | 2026-03-18 21:00 | 0 | T | trip | 0 | 0 | No interruption
Maniknagar 230/132kV | 230kV Siddhirganj-Maniknagar ckt-1 | 2026-03-18 18:25 | 2026-03-18 19:57 | 0.063889 | T | Distance Tripping Zone 1 | 0 | 0 | No interruption
Maniknagar 230/132kV | Auto Transformer-01(705T) HT | 2026-03-18 18:25 | 2026-03-18 19:57 | 0.063889 | T | Distance Tripping Zone 1 | 0 | 0 | No interruption
Matuail 132/33kV | 132 kV Maniknagar | 2026-03-15 10:08 | 2026-03-15 13:45 | 0.15069 | T | trip | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2026-03-01 04:47 | 2026-03-01 06:44 | 0.08125 | T | Tripped by 87L, Ground fault & ZCOM | 11 | 21.45 | Power interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-1 | 2026-03-01 06:32 | 2026-03-01 08:56 | 0.1 | T | Tripped 87L, Ground fault & ZCOM | 18 | 43.2 | Power interruption
Meghnaghat 400/230kV | Meghnaghat-Shyampur 230kV Ckt-1 | 2026-03-09 05:32 | 2026-03-10 16:19 | 1899-12-31 10:47 | T | Meghnaghat -Shyampur 230kV ckt 1 SOTF Operated Fault Distance: 9.9 km | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-02 | 2026-03-04 16:37 | 2026-03-04 16:37 | 0 | T | U/G Cable injury | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Meghnaghat-1(D06) | 2026-03-09 05:32 | 2026-03-09 09:39 | 0.17153 | T | trip | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Shyampur old-2(E10) | 2026-03-18 18:32 | 2026-03-18 23:59 | 0.22708 | T | Stormy weather | 34 | 185.3 | Power interruption
Siddhirganj 132/33kV | Ullon 1 | 2026-03-04 10:35 | 2026-03-04 14:32 | 0.16458 | T | N/A | 0 | 0 | No interruption
Siddhirganj 132/33kV | Haripur 1 | 2026-03-04 10:35 | 2026-03-04 11:49 | 0.051389 | T | N/A | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT1 | 2026-03-04 10:35 | 2026-03-04 11:16 | 0.028472 | T | N/A | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT2 | 2026-03-04 10:35 | 2026-03-04 11:14 | 0.027083 | T | N/A | 0 | 0 | No interruption
Siddhirganj 132/33kV | Matuail | 2026-03-10 08:13 | 2026-03-10 16:31 | 0.34583 | T | Unknown | 70 | 581 | Power interruption
Siddhirganj 132/33kV | 120MW EGCB GT1 | 2026-03-13 20:10 | 2026-03-13 22:20 | 0.090278 | T | N/A | 0 | 0 | No interruption
Siddhirganj 132/33kV | Matuail | 2026-03-15 11:42 | 2026-03-15 12:54 | 0.05 | T | trip | 70 | 84 | Power interruption
Siddhirganj 230/132kV | Maniknagar 1 | 2026-03-18 18:27 | 2026-03-18 19:54 | 0.060417 | T | Storm | 0 | 0 | No interruption
Sonargaon 132/33kV | OPSL(IEL-2) | 2026-03-01 03:52 | 2026-03-01 04:15 | 0.015972 | T | line distance protection showing | 0 | 0 | No interruption
Sonargaon 132/33kV | Bashundhara Line | 2026-03-13 20:25 | 2026-03-14 14:10 | 0.73958 | T | Due to flashing and overvoltage | 4 | 71 | Power interruption
Sonargaon 132/33kV | Daudkandi-2 | 2026-03-18 19:35 | 2026-03-18 22:36 | 0.12569 | T | Due to bad weather | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-1 HT | 2026-03-18 20:42 | 2026-03-19 03:30 | 0.28333 | T | DUE TO BAD WEATHER. T-1 auxiliary TRANSFORMER droup out fuse burst. | 4 | 27.2 | Power interruption
Sonargaon 132/33kV | Daudkandi-2 | 2026-03-18 23:02 | 2026-03-18 23:02 | 0 | T | Due to bad weather | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-01 | 2026-03-18 23:02 | 2026-03-19 03:17 | 0.17708 | T | Due to bus coupler CB trip | 0 | 0 | No interruption
Sonargaon 132/33kV | OPSL(IEL-2) | 2026-03-18 23:02 | 2026-03-19 03:56 | 0.20417 | T | Due to bus coupler CB trip | 0 | 0 | No interruption | 6:17
Ghorashal 230kV | Ghorashal-Ishwardi Circuit-2 | 2026-03-18 17:22 | 2026-03-18 17:22 | 0 | E/O | Distance Realy Trip. Line check Require | 0 | 0 | No interruption | 0:20
Haripur 230/132kV | Ullon (Maniknagar-2) | 2026-03-07 23:59 | 2026-03-08 02:12 | 0.092361 | E/O | Sky Wire Damaged | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Bashundhara 132 kv Ckt | 2026-03-02 10:56 | 2026-03-02 17:13 | 0.26181 | E/O | Emergency maintenance of R-ph CT at their end | 7 | 43.9833 | Power interruption
Madanganj 132/33kV | Madanganj -Haripur 132 kv Ckt-2 | 2026-03-16 23:10 | 2026-03-17 00:34 | 0.058333 | E/O | Y-ph CT clamp redhot | 0 | 0 | No interruption
Madanganj 132/33kV | GT-1 HT | 2026-03-18 22:00 | 2026-03-18 22:20 | 0.013889 | E/O | Nutral grounding bushing clam flashing | 12 | 4 | Power interruption
Madanganj 132/33kV | Madanganj -Haripur 132 kv Ckt-1 | 2026-03-22 14:42 | 2026-03-22 17:26 | 0.11389 | E/O | Hedhot maintenance | 0 | 0 | No interruption
Rampura 230/132kV | Madertek-01 | 2026-03-13 14:25 | 2026-03-13 15:09 | 0.030556 | E/O | Force Shutdown by NLDC | 0 | 0 | No interruption
Rampura 230/132kV | Madertek-02 | 2026-03-13 14:25 | 2026-03-13 15:09 | 0.030556 | E/O | Force Shutdown by NLDC | 0 | 0 | No interruption
Rampura 230/132kV | Moghbazar-01 | 2026-03-13 14:26 | 2026-03-13 15:00 | 0.023611 | E/O | Force Shutdown by NLDC | 0 | 0 | No interruption
Rampura 230/132kV | Moghbazar-02 | 2026-03-13 14:26 | 2026-03-13 15:16 | 0.034722 | E/O | Force Shutdown by NLDC | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-01 | 2026-03-13 14:28 | 2026-03-13 15:06 | 0.026389 | E/O | Force Shutdown by NLDC | 0 | 0 | No interruption
Rampura 230/132kV | Madertek-01 | 2026-03-22 12:23 | 2026-03-22 12:53 | 0.020833 | E/O | Bird Nest on line DS 281S | 0 | 0 | No interruption
Siddhirganj 132/33kV | Matuail | 2026-03-10 11:30 | 2026-03-10 16:31 | 0.20903 | E/O | Under ground cable test | 0 | 0 | No interruption
|  |  | Total : | 1900-01-12 19:04 |  | Unserved Energy: |  | 1272.5333
Chattogram Grid Circle :
Bakulia 132/33kV | Bakalia-Sikalbaha Ckt-01 | 2026-03-06 06:45 | 2026-03-06 07:04 | 0.013194 | T | Tripped | 0 | 0 | No interruption
Baroaulia 132/33kV | Hat-1 | 2026-03-19 01:42 | 2026-03-19 02:22 | 0.027778 | T | Unexpected | 0 | 0 | No interruption
Baroaulia 132/33kV | Hat-1 | 2026-03-20 15:21 | 2026-03-20 15:50 | 0.020139 | T | Unexpected | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2026-03-16 02:25 | 2026-03-16 02:37 | 0.0083333 | T | Tripped | 39 | 7.8 | Power interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-1 | 2026-03-20 16:26 | 2026-03-20 16:56 | 0.020833 | T | ***Tripped portion: Dohazari to Patiya. Stormy Weather | 0 | 0 | No interruption
GPH 230/33kV | BSRM CKT-1 | 2026-03-16 02:39 | 2026-03-16 03:07 | 0.019444 | T | line tripped for bad weather | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Ananda Bazar Ckt-2 | 2026-03-17 11:04 | 2026-03-17 11:19 | 0.010417 | T | Zone -1,general trip, B-phase trip | 0 | 0 | No interruption
Hathazari 230/132/33kV | AKSML-02 | 2026-03-05 07:20 | 2026-03-05 09:56 | 0.10833 | T | Tripped | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroaulia-01 | 2026-03-07 03:35 | 2026-03-08 00:27 | 0.86944 | T | R-phase wire broken | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroaulia-01 | 2026-03-19 01:42 | 2026-03-19 02:23 | 0.028472 | T | Alstome Quadrahmo | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroaulia-01 | 2026-03-20 15:20 | 2026-03-20 15:52 | 0.022222 | T | Tripped | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroiarhat-01 | 2026-03-31 16:17 | 2026-03-31 17:03 | 0.031944 | T | Tripped | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2026-03-13 10:52 | 2026-03-13 11:14 | 0.015278 | T | Transient Fault. | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-01(506T) HT | 2026-03-14 19:39 | 2026-03-16 14:50 | 1899-12-31 19:11 | T | 132/33 KV, 44.1/63 MVA Tr-1 LT side cable blust. | 0 | 0 | No interruption
Shikalbaha 230/132kV | Bakulia-1 | 2026-03-06 06:40 | 2026-03-06 07:06 | 0.018056 | T | Tripped | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Kaptai Ckt-01 | 2026-03-25 08:28 | 2026-03-25 12:07 | 0.15208 | E/O | OPGW work | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Kaptai Ckt-02 | 2026-03-25 08:55 | 2026-03-25 12:20 | 0.14236 | E/O | OPGW work | 0 | 0 | No interruption
Halishahar 132/33kV | 405T(TR-1) HT | 2026-03-08 16:05 | 2026-03-08 16:53 | 0.033333 | E/O | Due to 33Kv side CT unbalanced problem to B phase CT Protection core Short. | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroiarhat-01 | 2026-03-04 10:30 | 2026-03-04 11:37 | 0.046528 | E/O | Hathazari–Korerhat Ckt-01 to carry out Emergency Right of Way work. | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Sikalbaha | 2026-03-29 19:11 | 2026-03-29 19:48 | 0.025694 | E/O | There is an abnormal sound of the cvt earth connection being disconnected on the 132kv julda to shikalbaha line | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Sikalbaha | 2026-03-31 10:34 | 2026-03-31 14:37 | 0.16875 | E/O | Conductor Armouring is required between towers 45-46 R Phase.There will be no Load shedding. | 0 | 0 | No interruption
Rampur 230/132/33 | Khulshi-1 | 2026-03-11 23:31 | 2026-03-15 17:15 | 1900-01-02 17:44 | E/O | by the order of NLDC | 0 | 0 | No interruption
|  |  | Total : | 1900-01-06 07:42 |  | Unserved Energy: |  | 7.8
Cumilla Grid Circle :
Bibiana 400/230kV | Bibi-Shahzi Ckt-II | 2026-03-04 06:18 | 2026-03-04 06:28 | 0.0069444 | T | L2 to N trip at 33.84km | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-1 | 2026-03-18 18:49 | 2026-03-18 21:14 | 0.10069 | T | Tripped | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-1 | 2026-03-18 18:56 | 2026-03-18 20:47 | 0.077083 | T | Tripped | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-2 | 2026-03-24 21:33 | 2026-03-24 21:56 | 0.015972 | T | None | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | Ramganj line-02 | 2026-03-31 16:46 | 2026-03-31 16:46 | 0 | T | Stormy wind. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Ashuganj Ckt-1 | 2026-03-01 02:46 | 2026-03-01 03:11 | 0.017361 | T | Tripped | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Ashuganj Ckt-1 | 2026-03-01 03:12 | 2026-03-01 06:08 | 0.12222 | T | Tripped | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2026-03-01 03:31 | 2026-03-01 05:39 | 0.088889 | T | Tripped | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Ashuganj Ckt-1 | 2026-03-03 03:57 | 2026-03-03 05:21 | 0.058333 | T | Tripped | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2026-03-03 04:45 | 2026-03-03 05:32 | 0.032639 | T | Tripped | 0 | 0 | No interruption
Daudkandi 132/33kV | Sonargaon-1 | 2026-03-01 05:02 | 2026-03-01 05:13 | 0.0076389 | T | Sonargaon-1 | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-2 | 2026-03-17 03:37 | 2026-03-17 04:28 | 0.035417 | T | Bad Weather | 0 | 0 | No interruption
Feni 132/33kV | Feni Ckt-1 | 2026-03-26 14:23 | 2026-03-26 15:02 | 0.027083 | T | Tripped | 0 | 0 | No interruption
Feni 132/33kV | Feni Ckt-1 | 2026-03-27 13:05 | 2026-03-27 13:32 | 0.01875 | T | Distance trip, O/C | 0 | 0 | No interruption
Kasba 132/33kV | Muradnagar-Kasba Ckt-2 | 2026-03-16 16:10 | 2026-03-16 17:03 | 0.036806 | T | bad weather | 0 | 0 | No interruption
Kasba 132/33kV | Muradnagar-Kasba Ckt-2 | 2026-03-30 19:31 | 2026-03-30 19:50 | 0.013194 | T | fault | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shajibazar-Sreemongal Ckt-01 | 2026-03-16 00:42 | 2026-03-16 10:06 | 0.39167 | T | Heavy rain | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 HT | 2026-03-17 02:50 | 2026-03-17 03:09 | 0.013194 | T | Shaistaganj Feeder OC/EF Fault. | 55 | 17.4167 | Power interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2026-03-20 10:51 | 2026-03-20 11:27 | 0.025 | T | Heavy rain With Thundering | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-01 | 2026-03-20 10:58 | 2026-03-20 11:27 | 0.020139 | T | Heavy Rain With Thundering | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-Ashuganj Ckt-03 | 2026-03-28 21:41 | 2026-03-28 21:51 | 0.0069444 | T | Tripped | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 HT | 2026-03-30 21:45 | 2026-03-30 21:54 | 0.00625 | T | Chunarughat feeder Trip Under PBS. | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-3 HT | 2026-03-11 07:45 | 2026-03-11 08:22 | 0.025694 | T | 33kv Tr-3 circuit breaker is burst | 45 | 27.75 | Power interruption
Sreemongol 132/33kV | Sreemangal - Shahjibazar circuit-1 | 2026-03-16 00:42 | 2026-03-16 10:07 | 0.39236 | T | BY FAULT | 0 | 0 | No interruption
Beanibazar 132/33kV | 132 KV Transformer TR-01 HT | 2026-03-24 10:13 | 2026-03-24 11:18 | 0.045139 | E/O | Emergency shutdown | 0 | 0 | No interruption
Bibiana 400/230kV | Bibi-Shahzi Ckt-II | 2026-03-04 06:28 | 2026-03-04 06:28 | 0 | E/O | Tripped | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-1 | 2026-03-02 12:03 | 2026-03-02 16:41 | 0.19306 | E/O | Due to overload of Srimangal - Fenchuganj ckt. | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-2 | 2026-03-02 12:03 | 2026-03-02 16:41 | 0.19306 | E/O | Due to overload of Srimangal - Fenchuganj ckt. | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-2 | 2026-03-08 09:42 | 2026-03-08 10:33 | 0.035417 | E/O | Tripped | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 00:10 |  | Unserved Energy: |  | 45.1667
Khulna Grid Circle :
Amtali 400/132kV | Amtali - RNPL 400 kV Ckt - 2 | 2026-03-01 22:12 | 2026-03-02 15:35 | 0.72431 | T | DTT Trip | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2026-03-17 00:43 | 2026-03-17 05:11 | 0.18611 | T | System over voltage 145kv increase by Thunderstorm Rain | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Orion P/S Line | 2026-03-17 02:35 | 2026-03-17 10:08 | 0.31458 | T | Thunder storm | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2026-03-17 05:43 | 2026-03-17 09:42 | 0.16597 | T | System over voltage. | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2026-03-20 15:40 | 2026-03-20 20:05 | 0.18403 | T | Tripped | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2026-03-21 04:20 | 2026-03-21 12:39 | 0.34653 | T | Over voltage | 0 | 0 | No interruption
Faridpur 132/33kV | 132 KV 50MW Power Station ckt-1 | 2026-03-29 12:00 | 2026-03-29 14:27 | 0.10208 | T | Tripped | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Orion | 2026-03-20 16:58 | 2026-03-20 17:27 | 0.020139 | T | distance trip bagerhat-2 zone-1 trip bagerhat-2 phace -c, circuit km-28km | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-NWPGCL | 2026-03-28 02:24 | 2026-03-28 06:42 | 0.17917 | T | earth fault | 0 | 0 | No interruption
Gopalganj 132/33kV | Gopalganj North-1 | 2026-03-18 22:57 | 2026-03-18 23:31 | 0.023611 | T | Zone-1 3.6 km | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-1 | 2026-03-01 05:30 | 2026-03-01 05:43 | 0.0090278 | T | C phase Ground fault | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-1 | 2026-03-17 05:42 | 2026-03-17 07:48 | 0.0875 | T | Tripped | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-2 | 2026-03-17 05:42 | 2026-03-17 06:06 | 0.016667 | T | Tripped | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- Noapara-2 | 2026-03-17 00:29 | 2026-03-17 07:43 | 0.30139 | T | E/F TRIP R Phase | 0 | 0 | No interruption
Khulna (C) | 132kV Central-Noapara-1 | 2026-03-28 02:25 | 2026-03-28 03:07 | 0.029167 | T | unknown | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- Noapara-2 | 2026-03-29 20:16 | 2026-03-29 20:50 | 0.023611 | T | unknown | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 2 | 2026-03-17 00:29 | 2026-03-17 07:44 | 0.30208 | T | Distance Relay Trip | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 1 | 2026-03-28 02:25 | 2026-03-28 03:08 | 0.029861 | T | Distance Relay Trip | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 2 | 2026-03-29 20:16 | 2026-03-29 20:51 | 0.024306 | T | Distance Relay Trip. | 0 | 0 | No interruption
Patuakhali 132/33kV | Bakergonj-Pautakhali 132kV Line | 2026-03-14 10:12 | 2026-03-14 10:26 | 0.0097222 | T | Patuakhali-Bakergonj 132 kV line | 17 | 3.9667 | Power interruption
Benapole 132/33kV | Jashore-2 | 2026-03-16 08:27 | 2026-03-16 10:16 | 0.075694 | E/O | Tree trimming | 0 | 0 | No interruption
Bhandaria 132/33kV | Barishal (L4) | 2026-03-30 09:06 | 2026-03-30 16:18 | 0.3 | E/O | Barishal-Bhandaria line maintenance work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2026-03-01 05:34 | 2026-03-01 07:57 | 0.099306 | E/O | 0 | 0 | 0 | No interruption
Khulna (C) | 132kV Central-Noapara-1 | 2026-03-15 19:12 | 2026-03-15 22:55 | 0.15486 | E/O | Spark in lighting arrester | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- Noapara-2 | 2026-03-15 23:13 | 2026-03-15 23:38 | 0.017361 | E/O | Emergency maintenance | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-1 Reactor | 2026-03-27 18:45 | 2026-03-28 02:11 | 0.30972 | E/O | Khulna ALDC Demand | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-2 Reactor | 2026-03-27 18:45 | 2026-03-28 02:13 | 0.31111 | E/O | Khulna ALDC Demand | 0 | 0 | No interruption
|  |  | Total : | 1900-01-03 08:21 |  | Unserved Energy: |  | 3.9667
HVDC Grid Circle :
Bheramara 230/132kV | Kushtia 1 | 2026-03-15 14:17 | 2026-03-15 14:55 | 0.026389 | T | CB pole discrepancy. | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 2 | 2026-03-18 17:51 | 2026-03-22 17:03 | 1900-01-02 23:12 | T | Tripped | 0 | 0 | No interruption
Jashore 132/33kV | Cap. Bank-1 | 2026-03-27 06:56 | 2026-03-27 12:17 | 0.22292 | T | Tripped | 0 | 0 | No interruption
Jashore 132/33kV | Cap. Bank-2 | 2026-03-27 06:56 | 2026-03-27 12:17 | 0.22292 | T | Tripped | 126 | 674.1 | Power interruption
Kushtia 132/33kV | Kushtia-Jhenaidah-1 | 2026-03-15 14:18 | 2026-03-15 15:13 | 0.038194 | T | L-L-G Trip | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Pabna | 2026-03-18 21:20 | 2026-03-18 22:22 | 0.043056 | E/O | La flashing | 0 | 0 | No interruption
Ullahpara 132/33kV | Shahjadpur Ckt | 2026-03-12 13:32 | 2026-03-12 14:08 | 0.025 | E/O | 132 CT terminal (R-Phase) Red-hot Maintenance. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-03 13:05 |  | Unserved Energy: |  | 674.1
Bogura Grid Circle:
Bogura 230/132kV | Naogaon 132 KV Line-2 | 2026-03-12 08:22 | 2026-03-12 09:10 | 0.033333 | T | Tripped | 0 | 0 | No interruption
Bogura 230/132kV | Confidance UN-2 | 2026-03-12 08:22 | 2026-03-12 09:24 | 0.043056 | T | Tripped | 0 | 0 | No interruption
Bogura 230/132kV | Confidance UN-1 | 2026-03-15 22:29 | 2026-03-16 05:06 | 0.27569 | T | Stromy weather | 0 | 0 | No interruption
Bogura 230/132kV | Confidance UN-2 | 2026-03-17 05:44 | 2026-03-17 09:02 | 0.1375 | T | Tripped | 0 | 0 | No interruption
Bogura 230/132kV | Confidance UN-2 | 2026-03-21 00:06 | 2026-03-21 05:46 | 0.23611 | T | Over Voltage . | 0 | 0 | No interruption
Bogura 230/132kV | Confidance UN-2 | 2026-03-21 00:06 | 2026-03-21 05:46 | 0.23611 | T | Over Voltage . | 0 | 0 | No interruption
Joypurhat 132/33kV | Naogaon Ckt.-1 | 2026-03-20 23:09 | 2026-03-20 23:23 | 0.0097222 | T | over Voltage | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Kurigram-Lalmonirhat Ckt | 2026-03-16 23:25 | 2026-03-17 00:41 | 0.052778 | T | Tripped | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Kurigram-Lalmonirhat Ckt | 2026-03-21 03:59 | 2026-03-24 19:29 | 1900-01-02 15:30 | T | PT Burn(B-phase) | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Kurigram-Lalmonirhat | 2026-03-16 23:22 | 2026-03-17 00:42 | 0.055556 | T | Bad Weather & Stormy wind. | 0 | 0 | No interruption
Mithapukur 132/33kV | Confidence-1 | 2026-03-20 06:30 | 2026-03-20 07:14 | 0.030556 | T | None | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Bogura Ckt-1 | 2026-03-12 08:21 | 2026-03-12 10:21 | 0.083333 | T | Naogaon ckt-1 is in trip from Bogura end. | 22 | 44 | Power interruption
Naogaon 132/33kV | Naogaon-Bogura Ckt-1 | 2026-03-20 23:10 | 2026-03-20 23:45 | 0.024306 | T | Deractional Earth Fault (Whether: Thunderstorm and storm) | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Jaldhaka CKT-01 | 2026-03-20 05:00 | 2026-03-20 05:20 | 0.013889 | T | Distance relay | 0 | 0 | No interruption
Sirajganj 132/33kV | Solar Park 1 | 2026-03-18 20:28 | 2026-03-18 21:46 | 0.054167 | T | Thundering | 0 | 0 | No interruption
Sirajganj 132/33kV | Solar Park 2 | 2026-03-18 20:28 | 2026-03-18 21:46 | 0.054167 | T | Thundering. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Sirajgonj Ckt-1 | 2026-03-17 09:29 | 2026-03-17 11:46 | 0.095139 | E/O | Red hot Maintenance | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2026-03-19 17:48 | 2026-03-20 05:08 | 0.47222 | E/O | As per NLDC"s instruction | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2026-03-27 07:59 | 2026-03-28 03:29 | 0.8125 | E/O | Emergency maint.work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2026-03-28 04:58 | 2026-03-28 14:45 | 0.40764 | E/O | Due to reduce system voltage. NLDC Instruction. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2026-03-28 04:58 | 2026-03-28 14:45 | 0.40764 | E/O | Due to reduce system voltage. NLDC Instruction. | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Kurigram-Lalmonirhat Ckt | 2026-03-24 10:30 | 2026-03-24 19:29 | 0.37431 | E/O | Kurigram to Lalmonirhat 132kv line PT (B Phase) Change | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Bogura Ckt-1 | 2026-03-12 11:47 | 2026-03-12 14:46 | 0.12431 | E/O | Relay test work by SPMD . | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV Raj(new)-2 | 2026-03-07 10:37 | 2026-03-07 11:18 | 0.028472 | E/O | E/S maintenance | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-GTPS | 2026-03-20 23:57 | 2026-03-21 00:40 | 0.029861 | E/O | Emergency Demand of GTPS End | 0 | 0 | No interruption
Sirajganj 132/33kV | Sherpur-1 | 2026-03-17 09:33 | 2026-03-17 11:46 | 0.092361 | E/O | Red Hot at Sherpur End | 0 | 0 | No interruption
Sirajganj 132/33kV | Ullapara -2 | 2026-03-25 12:21 | 2026-03-25 13:21 | 0.041667 | E/O | Read hot maintenance at Ullapara SS end | 0 | 0 | No interruption
|  |  | Total : | 1900-01-06 20:56 |  | Unserved Energy: |  | 44
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1900-02-12 12:35 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
| Ashuganj-2 | 2024-11-13 12:06 | 2024-11-13 12:18

## QF-LDC-25
QF-LDC-25
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:March 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | 230/132kv Tr-03 | 2026-03-07 09:47 | 2026-03-07 11:09 | 1:22 | S/O | Scheduled shutdown | 0 | 0 | No interruption
Bajitpur 132/33kV | 132 kV Bus Coupler | 2026-03-01 10:18 | 2026-03-01 11:05 | 0:47 | S/O | 132 Kv CT Oil leakage maintenance. | 0 | 0 | No interruption
Bajitpur 132/33kV | 132 kV Bus-1 | 2026-03-01 10:18 | 2026-03-01 11:05 | 0:47 | S/O | For 132 kv CT oil leakage maintenance. | 0 | 0 | No interruption
Bajitpur 132/33kV | Tr-2(414T) | 2026-03-31 13:54 | 2026-03-31 16:23 | 2:29 | S/O | Due to Tr-02 PDB 33kV Spare feeder DS Maintenance and BPDB Feeder isolator Maintenance. Load shed 12MW for BPDB | 0 | 0 | No interruption
Dhamrai 132/33kV | Main Bus-1 | 2026-03-08 09:43 | 2026-03-13 15:58 | 126:15 | S/O | Project work | 0 | 0 | No interruption
Dhamrai 132/33kV | Main Bus-2 | 2026-03-14 09:15 | 2026-03-16 11:45 | 50:30 | S/O | Nabinagor project work. | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-2 | 2026-03-19 14:18 | 2026-03-19 15:56 | 1:38 | S/O | PBS work | 0 | 0 | No interruption
Dhamrai 132/33kV | 33 KV Bus Section-02 | 2026-03-19 14:28 | 2026-03-19 15:51 | 1:23 | S/O | PBS WORK | 0 | 0 | No interruption
Kabirpur 132/33kV | Reserve bus | 2026-03-02 12:18 | 2026-03-02 14:38 | 2:20 | S/O | Reserve BUS DS changing work of Manikganj Ckt-1&2. | 0 | 0 | No interruption
Kabirpur 132/33kV | Main bus | 2026-03-07 07:50 | 2026-03-07 15:38 | 7:48 | S/O | DS changing work | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-3 | 2026-03-07 07:55 | 2026-03-07 10:30 | 2:35 | S/O | DS changing work | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-2 | 2026-03-07 10:43 | 2026-03-07 13:31 | 2:48 | S/O | For 132 kV Main Bus DS Changing Work | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-2 | 2026-03-14 07:41 | 2026-03-14 10:14 | 2:33 | S/O | 132 kV Main Bus DS Changing Work. | 100 | 255 | Power interruption
Kabirpur 132/33kV | XFR, T-I | 2026-03-14 07:41 | 2026-03-14 11:45 | 4:04 | S/O | 132 kV Main Bus DS Changing Work. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/132kV TR-3 | 2026-03-13 10:34 | 2026-03-13 20:19 | 9:45 | S/O | CSD Commmisioning | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2026-03-01 09:46 | 2026-03-16 10:44 | 360:58 | S/O | Line disk cleaning | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-4 (50/75 MVA) | 2026-03-16 10:45 | 2026-03-16 11:24 | 0:39 | S/O | Red hot Maintanence work | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-4 (50/75 MVA) | 2026-03-30 11:25 | 2026-03-30 13:53 | 2:28 | S/O | Maint.work | 0 | 0 | No interruption
Mirpur 132/33kV | T1 | 2026-03-14 09:11 | 2026-03-14 11:46 | 2:35 | S/O | Maint.work | 0 | 0 | No interruption
Mirpur 132/33kV | Reserve Bus | 2026-03-14 09:32 | 2026-03-14 11:46 | 2:14 | S/O | Maint.work | 0 | 0 | No interruption
Muktagacha 132/33kV | T-2(414T) | 2026-03-02 14:03 | 2026-03-05 09:39 | 67:36 | S/O | Maint.work | 0 | 0 | No interruption
Muktagacha 132/33kV | T-3(424T) | 2026-03-05 09:32 | 2026-03-08 10:12 | 72:40 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Bus A | 2026-03-03 06:55 | 2026-03-03 15:03 | 8:08 | S/O | Installing Bus loop of solar ckt. | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-3 (424T) | 2026-03-04 06:50 | 2026-03-04 11:15 | 4:25 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Bus B | 2026-03-04 07:26 | 2026-03-04 10:30 | 3:04 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Bus B | 2026-03-12 07:36 | 2026-03-12 08:58 | 1:22 | S/O | Netrakona 2 ar B BUS loop high temperature maintenance work. | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-II | 2026-03-14 08:30 | 2026-03-14 11:53 | 3:23 | S/O | Red hot maintenance | 0 | 0 | No interruption
Savar 132/33kV | T-4 | 2026-03-14 10:33 | 2026-03-14 11:54 | 1:21 | S/O | Red hot maintenance | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-I | 2026-03-15 09:08 | 2026-03-15 13:30 | 4:22 | S/O | Red hot maintenance | 0 | 0 | No interruption
Savar 132/33kV | T-1 | 2026-03-15 09:20 | 2026-03-15 10:46 | 1:26 | S/O | Red hot maintenance | 0 | 0 | No interruption
Savar 132/33kV | T-2 | 2026-03-15 10:50 | 2026-03-15 13:31 | 2:41 | S/O | Red hot maintenance | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 04 | 2026-03-14 09:43 | 2026-03-14 11:35 | 1:52 | S/O | red hot reduce | 10 | 18.6667 | Power interruption
Sherpur 132/33kV | Transformer- 01 | 2026-03-19 10:49 | 2026-03-19 11:31 | 0:42 | S/O | OLTC oil Fill. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 | 2026-03-19 11:32 | 2026-03-19 11:59 | 0:27 | S/O | OLTC oil Fill | 0 | 0 | No interruption
Tongi 230/132/33kV | T-01 | 2026-03-01 05:55 | 2026-03-01 06:49 | 0:54 | S/O | Rectification work | 0 | 0 | No interruption
Tongi 230/132/33kV | 132 kV Bus-1 | 2026-03-02 11:38 | 2026-03-02 13:46 | 2:08 | S/O | Shutdown taken by PSDC | 0 | 0 | No interruption
Tongi 230/132/33kV | 230 kV Bus-2 | 2026-03-05 09:12 | 2026-03-05 17:38 | 8:26 | S/O | Shutdown taken by G2G | 0 | 0 | No interruption
Tongi 230/132/33kV | 230 kV Bus-2 | 2026-03-13 08:25 | 2026-03-13 17:39 | 9:14 | S/O | Maint.work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-31 12:09 |  | Unserved Energy: |  | 273.6667
Dhaka (South) Grid Circle :
Haripur 230/132kV | 230kV Bhult | 2026-03-09 10:10 | 2026-03-09 15:21 | 5:11 | S/O | Work at Bhulta 400kV S/S. | 0 | 0 | No interruption
Haripur 230/132kV | 230kV Bhult | 2026-03-11 09:58 | 2026-03-15 17:28 | 103:30 | S/O | QPGW Changing work. | 0 | 0 | No interruption
Haripur 230/132kV | Auto TR-3 | 2026-03-12 11:53 | 2026-03-12 14:13 | 2:20 | S/O | High Tempareture Junction Point Maintenance. | 0 | 0 | No interruption
Haripur 230/132kV | Bus-1 | 2026-03-29 09:22 | 2026-03-29 17:05 | 7:43 | S/O | Due to maint.work | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 414 T-2 | 2026-03-14 11:47 | 2026-03-14 14:16 | 2:29 | S/O | Red hot maintenance work | 0 | 0 | No interruption
Hasnabad 132/33kV | 33kv Reserve Bus | 2026-03-14 11:47 | 2026-03-14 14:16 | 2:29 | S/O | Red hot maintenance work 33 kv R.Bus T-2 Incomer | 0 | 0 | No interruption
Hasnabad 132/33kV | 33kv Main Bus | 2026-03-20 20:42 | 2026-03-20 23:48 | 3:06 | S/O | Red hot at 33kv main bus isolator of Transformer-5 | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 424 T-5 | 2026-03-20 20:42 | 2026-03-20 23:48 | 3:06 | S/O | Red hot at 33 kv bus isolator | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-3 | 2026-03-28 08:24 | 2026-03-28 12:35 | 4:11 | S/O | High Temperature Maintenance | 0 | 0 | No interruption
Meghnaghat 400/230kV | ATR-1 | 2026-03-06 08:27 | 2026-03-06 10:38 | 2:11 | S/O | for maintenance work. | 0 | 0 | No interruption
Munshiganj 132/33kV | Transformer-2 | 2026-03-17 07:15 | 2026-03-17 08:22 | 1:07 | S/O | PBS maintenance work | 20 | 22.3333 | Power interruption
Munshiganj 132/33kV | Transformer-2 | 2026-03-19 14:22 | 2026-03-19 15:27 | 1:05 | S/O | Maintenance by pbs bus-2 | 0 | 0 | No interruption
Narshingdi 132/33kV | T-2 | 2026-03-10 09:16 | 2026-03-10 12:20 | 3:04 | S/O | Oil leakage maintenance | 0 | 0 | No interruption
Rampura 230/132kV | Bhulta Ckt | 2026-03-28 13:15 | 2026-03-28 14:45 | 1:30 | S/O | To remove external object which dropped by bird's that Spark at Tower 45. | 0 | 0 | No interruption
Siddhirganj 132/33kV | T-1 | 2026-03-27 07:17 | 2026-03-27 07:49 | 0:32 | S/O | Maintenance work | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-2 | 2026-03-01 06:19 | 2026-03-01 07:50 | 1:31 | S/O | Due to red hot corrective maintenance | 38 | 57.6333 | Power interruption
Sonargaon 132/33kV | Tr-1 | 2026-03-04 07:11 | 2026-03-04 08:42 | 1:31 | S/O | PBS 33 MIEZ FEEDER heat shrink maintenance | 52 | 78.8667 | Power interruption
Sonargaon 132/33kV | Tr-1 | 2026-03-04 12:30 | 2026-03-04 13:45 | 1:15 | S/O | PBS 33 MIEZ FEEDER heat shrink maintenance | 52 | 65 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2026-03-22 09:10 | 2026-03-22 11:50 | 2:40 | S/O | Pbs insulator changing | 16 | 42.6667 | Power interruption
Sonargaon 132/33kV | Tr-1 | 2026-03-22 09:15 | 2026-03-22 10:53 | 1:38 | S/O | Pbs insulator changing | 9 | 14.7 | Power interruption
Sonargaon 132/33kV | Tr-1 | 2026-03-28 11:19 | 2026-03-28 15:33 | 4:14 | S/O | Auxiliary Transformer-01 replacing. | 35 | 148.1667 | Power interruption
Srinagar 132/33kV | Tr-02 | 2026-03-13 15:41 | 2026-03-13 16:43 | 1:02 | S/O | Red hot maintenance at F-5 by Pbs | 0 | 0 | No interruption
Ghorashal 230kV | TARFO-2 HT | 2026-03-17 11:15 | 2026-03-17 12:39 | 1:24 | S/O | Transformer Body Grounding, LA grounding Maintenance Work | 80 | 112 | Power interruption
Hasnabad 132/33kV | 132/33kV 414 T-2 HT | 2026-03-14 11:47 | 2026-03-14 14:16 | 2:29 | S/O | Red hot maintenance work | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 424 T-5 HT | 2026-03-20 20:42 | 2026-03-20 23:48 | 3:06 | S/O | Red hot at 33 kv bus isolator | 0 | 0 | No interruption
Meghnaghat 400/230kV | ATR-1 HT | 2026-03-06 08:18 | 2026-03-06 10:37 | 2:19 | S/O | for maintenance work. | 0 | 0 | No interruption
Munshiganj 132/33kV | Transformer-2 HT | 2026-03-18 21:10 | 2026-03-19 15:26 | 18:16 | S/O | Maintenance by pbs | 0 | 0 | No interruption
Munshiganj 132/33kV | Transformer-2 HT | 2026-03-19 14:22 | 2026-03-19 15:26 | 1:04 | S/O | Maintenance by pbs bus-2 | 0 | 0 | No interruption
Shyampur 132/33kV | GT-4 HT | 2026-03-02 09:25 | 2026-03-02 12:04 | 2:39 | S/O | GT-4 Transformer oil leakage for Y- phase PT. | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV APR (D04) | 2026-03-02 10:18 | 2026-03-02 15:12 | 4:54 | S/O | Take shutdown by NLDC for relay work at Hasnabad SS end. | 0 | 0 | No interruption
Siddhirganj 132/33kV | 132kV MTR 1 | 2026-03-02 08:42 | 2026-03-09 15:42 | 175:00 | S/O | Coatings Work of Transformer Body. | 0 | 0 | No interruption
Siddhirganj 132/33kV | 132kV MTR 2 | 2026-03-09 15:56 | 2026-03-16 17:27 | 169:31 | S/O | Due to Transformer painting Work. | 0 | 0 | No interruption
Siddhirganj 230/132kV | MTR 1 HT | 2026-03-02 08:45 | 2026-03-09 15:40 | 174:55 | S/O | Painting of Transformer | 0 | 0 | No interruption
Siddhirganj 230/132kV | MTR 2 HT | 2026-03-09 15:57 | 2026-03-16 17:25 | 169:28 | S/O | Transformer painting work | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-1 HT | 2026-03-04 07:12 | 2026-03-04 08:40 | 1:28 | S/O | PBS 33KV MIEZ FEEDER heat shrink maintenance | 52 | 76.2667 | Power interruption
Sonargaon 132/33kV | Tr-1 HT | 2026-03-04 12:31 | 2026-03-04 13:44 | 1:13 | S/O | PBS 33 MIEZ FEEDER heat shrink maintenance | 52 | 63.2667 | Power interruption
Sonargaon 132/33kV | Tr-1 HT | 2026-03-22 09:16 | 2026-03-22 10:52 | 1:36 | S/O | Pbs insulator changing | 9 | 14.4 | Power interruption
Sonargaon 132/33kV | Tr-1 HT | 2026-03-28 11:19 | 2026-03-28 15:32 | 4:13 | S/O | Auxiliary Transformer-01 replacing. | 35 | 147.5833 | Power interruption
Srinagar 132/33kV | Tr-02 HT | 2026-03-13 15:43 | 2026-03-13 16:42 | 0:59 | S/O | Red hot maintenance at F-5 by Pbs | 0 | 0 | No interruption
|  |  | Total : | 1900-02-05 03:59 |  | Unserved Energy: |  | 842.8833
Chattogram Grid Circle :
Baroirhat 132/33kV | TR-1, 406T | 2026-03-07 09:19 | 2026-03-07 11:10 | 1:51 | S/O | Pbs 33 kv red hot Maintenance work | 0 | 0 | No interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2026-03-27 15:03 | 2026-03-27 16:03 | 1:00 | S/O | chandanaish 33kv Feeder redhot maintenance. | 61 | 61 | Power interruption
Shikalbaha 230/132kV | ATR 02 | 2026-03-01 08:16 | 2026-03-01 15:39 | 7:23 | S/O | Gas purification work | 0 | 0 | No interruption
Shikalbaha 230/132kV | ATR 01 | 2026-03-02 08:24 | 2026-03-02 15:41 | 7:17 | S/O | Sf6 gas refill | 0 | 0 | No interruption
Baroirhat 132/33kV | TR-1, 406T HT | 2026-03-07 09:18 | 2026-03-07 11:09 | 1:51 | S/O | Pbs 33 kv red hot Maintenance work | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-01 HT | 2026-03-30 09:49 | 2026-03-30 17:47 | 7:58 | S/O | Shutdown Grid Transformer 01 (35/50 MVA) for secondary CT (33kv side) maintenance | 0 | 0 | No interruption
Mirsorai 230/33kV | TR-1, 718T HT | 2026-03-30 16:35 | 2026-03-30 18:35 | 2:00 | S/O | testing for SPMD | 0 | 0 | No interruption
Shikalbaha 230/132kV | ATR 02 HT | 2026-03-01 08:16 | 2026-03-01 15:38 | 7:22 | S/O | Gas purification work | 0 | 0 | No interruption
Shikalbaha 230/132kV | ATR 01 HT | 2026-03-02 08:27 | 2026-03-02 15:39 | 7:12 | S/O | Sf6 gas refill | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 19:54 |  |  |  | 61
Cumilla Grid Circle :
Chandpur 132/33kV | 412T (T-2) | 2026-03-02 11:09 | 2026-03-02 13:00 | 1:51 | S/O | DS maintenance | 0 | 0 | No interruption
Chhatak 132/33kV | T-3 | 2026-03-03 11:01 | 2026-03-03 13:11 | 2:10 | S/O | Shutdown for T-3 GCB Hydraulic Oil Leakage Problem. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | ATR-02 | 2026-03-08 08:47 | 2026-03-08 14:56 | 6:09 | S/O | Outside painting Final work. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | ATR-02 | 2026-03-11 08:31 | 2026-03-11 15:11 | 6:40 | S/O | Shield wire and PI resplendent. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | ATR-03 | 2026-03-12 09:29 | 2026-03-12 14:30 | 5:01 | S/O | Shield wire and PI replacement | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-1 | 2026-03-05 08:37 | 2026-03-05 11:30 | 2:53 | S/O | SARF Test by RTS | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-1 | 2026-03-20 16:06 | 2026-03-20 16:07 | 0:01 | S/O | Bus Shifting Tripura to Bd | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-3 | 2026-03-20 16:12 | 2026-03-20 16:13 | 0:01 | S/O | Bus Shifting Tripura to Bd | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-2 | 2026-03-25 07:53 | 2026-03-25 09:53 | 2:00 | S/O | None | 0 | 0 | No interruption
Daudkandi 132/33kV | Transformer-2 | 2026-03-05 07:10 | 2026-03-05 10:20 | 3:10 | S/O | T-2 Shutdown For 33 KV side Bay Breaker Extention Work by PBS-3 Team. | 0 | 0 | No interruption
Daudkandi 132/33kV | Transformer-2 | 2026-03-06 07:14 | 2026-03-06 10:14 | 3:00 | S/O | PBS 33kv bay extension. | 0 | 0 | No interruption
Daudkandi 132/33kV | Transformer-2 | 2026-03-07 10:01 | 2026-03-07 13:04 | 3:03 | S/O | 33 KV side- bay extension work by Comilla PBS-3 | 30 | 91.5 | Power interruption
Daudkandi 132/33kV | Transformer-3 | 2026-03-07 10:07 | 2026-03-07 13:07 | 3:00 | S/O | 33 KV side- bay extension work by Comilla PBS-3 | 20 | 60 | Power interruption
Kachua 230/132/33kV | ATR-2 | 2026-03-10 10:58 | 2026-03-10 15:14 | 4:16 | S/O | DFDR Test | 0 | 0 | No interruption
Kachua 230/132/33kV | ATR-2 | 2026-03-12 10:39 | 2026-03-12 16:35 | 5:56 | S/O | project work for DFDR test | 0 | 0 | No interruption
Kachua 230/132/33kV | Main Bus-2 (230 kV) | 2026-03-12 10:55 | 2026-03-12 16:29 | 5:34 | S/O | project work for DFDR test | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 AB | 2026-03-19 19:50 | 2026-03-19 20:11 | 0:21 | S/O | TR-01(A+B) 33kV Side CT Redhot maintenance | 5 | 1.75 | Power interruption
Kulaura 132/33kV | TR-1 AB | 2026-03-19 22:14 | 2026-03-19 23:21 | 1:07 | S/O | TR-01(A+B) 33kV Side CT Redhot maintenance | 5 | 5.5833 | Power interruption
Kulaura 132/33kV | TR-1 AB | 2026-03-30 16:03 | 2026-03-30 17:01 | 0:58 | S/O | PBS DS Redhot maintenance | 23 | 22.2333 | Power interruption
Ramganj 132/33kV | 132 Kv Bus-B | 2026-03-12 07:20 | 2026-03-12 09:17 | 1:57 | S/O | Hot spot maintenance. | 0 | 0 | No interruption
Ramganj 132/33kV | Transformer-01 | 2026-03-12 07:21 | 2026-03-12 09:16 | 1:55 | S/O | Hot spot maintenance. | 0 | 0 | No interruption
Ramganj 132/33kV | Transformer-01 | 2026-03-19 09:34 | 2026-03-19 10:59 | 1:25 | S/O | 33 KV PBS Feeder Red hot maintenance work at 33 kv Bus Ds | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2026-03-22 07:52 | 2026-03-22 09:23 | 1:31 | S/O | Redhot Maintenance work at 33kv bus by pdb | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2026-03-30 19:48 | 2026-03-30 22:09 | 2:21 | S/O | Shutdown Taken By PBS for Bus Coupler Maintenance | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-1AB | 2026-03-28 11:18 | 2026-03-28 13:05 | 1:47 | S/O | For 33 kV DS red hot removing work. | 0 | 0 | No interruption
Sylhet 132/33kV | T4 | 2026-03-23 07:42 | 2026-03-23 08:36 | 0:54 | S/O | Shutdown taken by S&D-4 for 33kv IC-2 feeder red hot maintanance. Order by NLDC, AE(299725) . | 12 | 10.8 | Power interruption
Chandpur 132/33kV | 412T (T-2) HT | 2026-03-02 11:09 | 2026-03-02 13:00 | 1:51 | S/O | DS maintenance | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | ATR-01 HT | 2026-03-07 08:55 | 2026-03-07 14:30 | 5:35 | S/O | 230 KV Outside painting final work. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | ATR-02 HT | 2026-03-08 08:48 | 2026-03-08 14:55 | 6:07 | S/O | Outside painting Final work. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | ATR-02 HT | 2026-03-11 08:31 | 2026-03-11 15:11 | 6:40 | S/O | Shield wire and PI resplendent. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | ATR-03 HT | 2026-03-12 09:29 | 2026-03-12 14:30 | 5:01 | S/O | Shield wire and PI replacement | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-1 HT | 2026-03-05 08:37 | 2026-03-05 11:30 | 2:53 | S/O | SARF Test by RTS | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-1 HT | 2026-03-20 16:07 | 2026-03-20 16:07 | 0:00 | S/O | Bus Shifting Tripura to Bd | 0 | 0 | No interruption
Daudkandi 132/33kV | Transformer-2 HT | 2026-03-05 07:12 | 2026-03-05 10:19 | 3:07 | S/O | T-2 Shutdown For 33 KV side Bay Breaker Extention Work by PBS-3 Team. | 0 | 0 | No interruption
Daudkandi 132/33kV | Transformer-2 HT | 2026-03-07 10:02 | 2026-03-07 13:02 | 3:00 | S/O | 33 KV side- bay extension work by Comilla PBS-3 | 0 | 0 | No interruption
Daudkandi 132/33kV | Transformer-3 HT | 2026-03-07 10:08 | 2026-03-07 13:05 | 2:57 | S/O | 33 KV side- bay extension work by Comilla PBS-3 | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 AB HT | 2026-03-19 19:52 | 2026-03-19 20:10 | 0:18 | S/O | TR-01(A+B) 33kV Side CT Redhot maintenance | 5 | 1.5 | Power interruption
Kulaura 132/33kV | TR-1 AB HT | 2026-03-19 22:14 | 2026-03-19 23:19 | 1:05 | S/O | TR-01(A+B) 33kV Side CT Redhot maintenance | 5 | 5.4167 | Power interruption
Kulaura 132/33kV | TR-1 AB HT | 2026-03-30 16:04 | 2026-03-30 17:00 | 0:56 | S/O | PBS DS Redhot maintenance | 23 | 21.4667 | Power interruption
Ramganj 132/33kV | Transformer-01 HT | 2026-03-12 07:22 | 2026-03-12 09:16 | 1:54 | S/O | Hot spot maintenance | 0 | 0 | No interruption
Ramganj 132/33kV | Transformer-01 HT | 2026-03-19 09:34 | 2026-03-19 10:59 | 1:25 | S/O | 33 KV PBS Feeder Red hot maintenance work at 33 kv Bus Ds | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 HT | 2026-03-22 07:52 | 2026-03-22 09:22 | 1:30 | S/O | Redhot Maintenance work at 33kv bus by pdb | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 HT | 2026-03-30 19:49 | 2026-03-30 22:08 | 2:19 | S/O | Shutdown Taken By Pbs for Bus Coupler Maintenance | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-1AB HT | 2026-03-28 11:19 | 2026-03-28 13:05 | 1:46 | S/O | For 33 kV DS red hot removing work. | 0 | 0 | No interruption
Sylhet 132/33kV | T4 HT | 2026-03-23 07:42 | 2026-03-23 08:35 | 0:53 | S/O | Shutdown taken by S&D-4 for 33kv IC-2 feeder red hot maintanance. Order by NLDC, AE(299725) . | 12 | 10.6 | Power interruption
|  |  | Total : | 1900-01-03 22:18 |  |  |  | 230.85
Khulna Grid Circle :
Bagerhat 132/33kV | Transformer-3 ( 423 T) | 2026-03-12 10:54 | 2026-03-12 14:50 | 3:56 | S/O | 33 kv fakirhat 2 maintenance work | 0 | 0 | No interruption
Bakerganj 132/33kV | T1 | 2026-03-11 12:24 | 2026-03-11 12:35 | 0:11 | S/O | 33 kV incoming 1 CT connection change. | 0 | 0 | No interruption
Barishal 132/33kV | T-2 (415T) | 2026-03-14 13:28 | 2026-03-14 14:10 | 0:42 | S/O | Oil sample collection | 0 | 0 | No interruption
Barishal 230/132kV | T-5 | 2026-03-06 21:51 | 2026-03-07 00:07 | 2:16 | S/O | 33 kV section DS-C and Mehendigonj source DS repair | 35 | 79.3333 | Power interruption
Barishal 230/132kV | T-5 | 2026-03-18 07:40 | 2026-03-18 10:07 | 2:27 | S/O | Nut Bolt tighting | 30 | 73.5 | Power interruption
Bhandaria 132/33kV | Transformer-1 | 2026-03-05 12:11 | 2026-03-05 16:17 | 4:06 | S/O | 33kv kathalia feeder emergency maintenance | 8 | 32.8 | Power interruption
Bhandaria 132/33kV | Transformer-1 | 2026-03-12 15:47 | 2026-03-12 17:36 | 1:49 | S/O | Due to maint.work | 10 | 18.1667 | Power interruption
Borhanuddin 230/33kV | Tr-Load | 2026-03-25 07:10 | 2026-03-25 07:10 | 0:00 | S/O | Red Hot Maintenance By PBS | 55 | 0 | Power interruption
Gopalganj 132/33kV | T2 | 2026-03-17 08:24 | 2026-03-17 10:37 | 2:13 | S/O | 33kV incoming DS maintenance | 15 | 33.25 | Power interruption
Khulna (C) | Tr-3 405T | 2026-03-12 11:27 | 2026-03-12 12:36 | 1:09 | S/O | Joragate to red hot maintenance. | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2026-03-25 07:11 | 2026-03-25 09:31 | 2:20 | S/O | Maintenance work done by PBS khulna | 5 | 11.6667 | Power interruption
Khulna (C) | Tr-3 405T | 2026-03-27 08:12 | 2026-04-04 12:48 | 196:36 | S/O | oil centrifuzing. | 0 | 0 | No interruption
Noapara 132/33kV | T-1 | 2026-03-16 07:05 | 2026-03-16 07:57 | 0:52 | S/O | Due to maint.work | 0 | 0 | No interruption
Patuakhali 132/33kV | 425T (T-3) | 2026-03-09 17:22 | 2026-03-09 17:58 | 0:36 | S/O | 33 KV Bus section DS Y phase Maintenance | 15 | 9 | Power interruption
Patuakhali 132/33kV | 425T (T-3) | 2026-03-13 07:03 | 2026-03-13 09:16 | 2:13 | S/O | 33 kV Bus Red hot maintenance work | 15 | 33.25 | Power interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-02 | 2026-03-31 06:46 | 2026-03-31 16:47 | 10:01 | S/O | Maintenance | 0 | 0 | No interruption
Bagerhat 132/33kV | Transformer-3 ( 423 T) | 2026-03-12 10:55 | 2026-03-12 14:47 | 3:52 | S/O | 33 kv fakirhat 2 maintenance work | 0 | 0 | No interruption
Bakerganj 132/33kV | T1 | 2026-03-11 12:25 | 2026-03-11 12:35 | 0:10 | S/O | 33 kV incoming 1 CT connection change | 0 | 0 | No interruption
Barishal 230/132kV | T-5 | 2026-03-06 21:51 | 2026-03-07 00:05 | 2:14 | S/O | 33 kV section DS-C and Mehendigonj source DS repair | 35 | 78.1667 | Power interruption
Barishal 230/132kV | ATR-1 | 2026-03-07 15:53 | 2026-03-07 16:27 | 0:34 | S/O | Maint.work | 0 | 0 | No interruption
Barishal 230/132kV | T-5 | 2026-03-18 07:41 | 2026-03-18 10:03 | 2:22 | S/O | Maint.work | 30 | 71 | Power interruption
Bhandaria 132/33kV | Transformer-1 | 2026-03-05 12:12 | 2026-03-05 16:17 | 4:05 | S/O | 33kv kathalia pbs Feeder emergency maintenance | 8 | 32.6667 | Power interruption
Bhandaria 132/33kV | Transformer-1 | 2026-03-12 15:47 | 2026-03-12 17:36 | 1:49 | S/O | Maint.work | 10 | 18.1667 | Power interruption
Borhanuddin 230/33kV | Tr-Load | 2026-03-25 07:15 | 2026-03-25 09:23 | 2:08 | S/O | Red Hot maintenance by PBS | 55 | 117.3333 | Power interruption
Faridpur 132/33kV | Transformer-3 | 2026-03-01 10:54 | 2026-03-01 15:20 | 4:26 | S/O | bus pt oil leakage maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV | T2 | 2026-03-17 08:25 | 2026-03-17 10:36 | 2:11 | S/O | bus pt oil leakage maintenance | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2026-03-25 07:12 | 2026-03-25 09:30 | 2:18 | S/O | 33kV incoming DS maintenance | 15 | 34.5 | Power interruption
Khulna (C) | TR-1 425T | 2026-03-25 07:12 | 2026-03-25 09:30 | 2:18 | S/O | Maint. Work done by PBS Khulna | 5 | 11.5 | Power interruption
Patuakhali 132/33kV | 425T (T-3) | 2026-03-09 17:22 | 2026-03-09 17:57 | 0:35 | S/O | 33 KV Bus section DS Y phase Maintenance | 15 | 8.75 | Power interruption
Patuakhali 132/33kV | 425T (T-3) | 2026-03-13 07:04 | 2026-03-13 09:15 | 2:11 | S/O | 33 kV Bus Red hot maintenance work | 15 | 32.75 | Power interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-02 | 2026-03-31 07:01 | 2026-03-31 16:47 | 9:46 | S/O | Maintenance | 0 | 0 | No interruption
Rampal 400/230kV | ICT-1 | 2026-03-01 15:07 | 2026-03-01 15:07 | 0:00 | S/O | NA | 0 | 0 | No interruption
|  |  | Total : | 1900-01-10 08:26 |  | Unserved Energy : |  | 695.8
HVDC Grid Circle
Baghabari 230/132kV | T-1 | 2026-03-09 14:34 | 2026-03-09 19:18 | 4:44 | S/O | ট্রান্সফরমারের তেল সেন্টিফিউজ করার জন্য | 0 | 0 | No interruption
Baghabari 230/132kV | T-1 | 2026-03-11 12:06 | 2026-03-13 09:36 | 45:30 | S/O | Maintenance work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132/33 kV T-3 | 2026-03-19 08:38 | 2026-03-19 11:10 | 2:32 | S/O | Maintenance work | 15 | 38 | Power interruption
Magura 132/33kV | T-3 (425T) | 2026-03-09 06:35 | 2026-03-09 10:45 | 4:10 | S/O | 33kV Bus, section - 3 bay extention. | 20 | 83.3333 | Power interruption
Pabna 132/33kV | T-3 | 2026-03-14 19:44 | 2026-03-14 20:10 | 0:26 | S/O | Emergency Maintenance | 18 | 7.8 | Power interruption
Baghabari 230/132kV | Auxiliary X-Former-01(Turtiary) | 2026-03-09 14:20 | 2026-03-09 19:21 | 5:01 | S/O | ট্রান্সফরমারের তেল সেন্টিফিউজ করার জন্য | 0 | 0 | No interruption
BIPTC | 20DF31 | 2026-03-11 13:14 | 2026-03-11 13:58 | 0:44 | S/O | Tripped by Capacitor Unbalance R PH Stage 3 Operated. | 0 | 0 | No interruption
Ishurdi 132/33kV | 132/33 kV T-3 HT | 2026-03-19 08:38 | 2026-03-19 11:09 | 2:31 | S/O | Maintenance work | 15 | 37.75 | Power interruption
|  |  | Total : | 1900-01-01 17:38 |  | Unserved Energy : |  | 166.8833
Bogura Grid Circle:
Amnura 132/33kV | T-1 (406T) | 2026-03-17 09:56 | 2026-03-17 11:06 | 1:10 | S/O | 33kV Bus Section-1 Shutdown. | 0 | 0 | No interruption
Amnura 132/33kV | T-1 (406T) | 2026-03-29 08:48 | 2026-04-03 12:41 | 123:53 | S/O | Oil leakage maintenance | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-2 (414T) | 2026-03-25 11:36 | 2026-03-25 13:09 | 1:33 | S/O | Maintenance | 10 | 15.5 | Power interruption
Bogura 400/230kV | ATR-01 | 2026-03-10 12:56 | 2026-03-12 11:49 | 46:53 | S/O | Oil centrifuging | 0 | 0 | No interruption
Chapai 132/33kV | Main Bus | 2026-03-06 06:24 | 2026-03-06 11:26 | 5:02 | S/O | T01 x-former upgrading | 45 | 226.5 | Power interruption
Naogaon 132/33kV | T-3 | 2026-03-27 10:07 | 2026-03-27 10:07 | 0:00 | S/O | Project work | 0 | 0 | No interruption
Purbasadipur 230/132/33kV | TR-1 (H01R22) | 2026-03-13 09:34 | 2026-03-13 10:34 | 1:00 | S/O | 33kv bus coupler maintenance | 35 | 35 | Power interruption
Purbasadipur 230/132/33kV | ATR-3 | 2026-03-30 07:10 | 2026-03-30 08:38 | 1:28 | S/O | 33KV BUS COUPLER Maintenance. | 40 | 58.6667 | Power interruption
Rajshahi 132/33kV | Transformer T-2(415T) | 2026-03-14 07:54 | 2026-03-14 10:33 | 2:39 | S/O | 33 Kv BUS Cleaning & Maintenance Work. | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-3 (425T) | 2026-03-14 07:54 | 2026-03-14 10:41 | 2:47 | S/O | 33 Kv BUS Cleaning Switchgear maintenance work. | 10 | 27.8333 | Power interruption
Rajshahi 132/33kV | Transformer T-1(405T) | 2026-03-14 10:48 | 2026-03-14 12:13 | 1:25 | S/O | Maintenance | 0 | 0 | No interruption
Rangpur 132/33kV | Auxiliary Transformer-2 | 2026-03-03 06:34 | 2026-03-03 06:34 | 0:00 | S/O | 132kV CT Maintenance | 0 | 0 | No interruption
Rangpur 132/33kV | T-2 (404T) | 2026-03-03 06:36 | 2026-03-03 08:02 | 1:26 | S/O | 132kV CT Maintenance | 0 | 0 | No interruption
Saidpur 132/33kV | 33 kV Bus | 2026-03-30 07:48 | 2026-03-30 09:23 | 1:35 | S/O | Red hot removal of 33kv BPBS feeder. | 15 | 23.75 | Power interruption
Rangpur 132/33kV | Auxiliary Transformer-2 HT | 2026-03-03 06:36 | 2026-03-03 06:36 | 0:00 | S/O | 132kV CT Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-06 22:51 |  | Unserved Energy : |  | 387.25
Others :Nil
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 2363:15 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:March 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Meghnaghat-02 | 2026-03-05 08:23 | 2026-03-05 13:22 | 4:59 | S/O | Disc cleaning | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-01 | 2026-03-07 08:43 | 2026-03-08 15:51 | 31:08 | S/O | Scheduled shutdown | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Kaliakoir-02 | 2026-03-10 08:32 | 2026-03-10 14:20 | 5:48 | S/O | Disc cleaning | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Keranigonj-02 | 2026-03-11 08:41 | 2026-03-11 15:02 | 6:21 | S/O | Disc cleaning | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Keranigonj-01 | 2026-03-12 09:01 | 2026-03-12 14:38 | 5:37 | S/O | Disc cleaning and deadline checking | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Gopalganj-2 | 2026-03-13 07:31 | 2026-03-13 15:50 | 8:19 | S/O | Disc cleaning | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-01 | 2026-03-28 14:10 | 2026-03-29 17:01 | 26:51 | S/O | Scheduled shutdown | 0 | 0 | No interruption
Bajitpur 132/33kV | Ashuganj Ckt-1 | 2026-03-19 13:47 | 2026-03-19 15:32 | 1:45 | S/O | Tree trimming. | 0 | 0 | No interruption
Bajitpur 132/33kV | Ashuganj Ckt-2 | 2026-03-28 08:01 | 2026-03-28 12:30 | 4:29 | S/O | Ashuganj ckt-2 shutdown for ashuganj end maintenance work | 0 | 0 | No interruption
Dhamrai 132/33kV | 132 KV Kaliakoir-Dhamrai CKT-02 | 2026-03-12 13:48 | 2026-03-12 19:41 | 5:53 | S/O | Project work | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-1 | 2026-03-27 10:38 | 2026-03-27 14:32 | 3:54 | S/O | S/D From pubail end. | 0 | 0 | No interruption
Kabirpur 132/33kV | Kadda-1 | 2026-03-05 08:30 | 2026-03-05 17:03 | 8:33 | S/O | 230 kV GIS Work | 0 | 0 | No interruption
Kabirpur 132/33kV | Manikganj-2 | 2026-03-29 10:18 | 2026-03-29 12:00 | 1:42 | S/O | Maintenance work between main bus and reserve bus DS (Point No. 07). | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Bibiyana 2 | 2026-03-04 09:10 | 2026-03-04 19:12 | 10:02 | S/O | Line Insulator Disk Cleaning. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Bibiyana 2 | 2026-03-31 10:25 | 2026-03-31 17:09 | 6:44 | S/O | Tree Trimming and Disc Cleaning | 0 | 0 | No interruption
Kodda 132/33kV | Rajendrapur Ckt-1 | 2026-03-09 12:05 | 2026-03-09 13:26 | 1:21 | S/O | Rajendrapur work | 0 | 0 | No interruption
Manikganj 132/33kV | Manikganj- Kabirpur CKT-1 | 2026-03-01 10:01 | 2026-03-01 13:06 | 3:05 | S/O | Line disk cleaning | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Sector-18 | 2026-03-18 20:25 | 2026-03-30 10:22 | 277:57 | S/O | None | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Netrakona Ckt-2 | 2026-03-12 06:36 | 2026-03-12 10:54 | 4:18 | S/O | High temperature maintenance work | 0 | 0 | No interruption
Savar 132/33kV | 132kV Manikganj PS-Savar Ckt-1 | 2026-03-14 08:16 | 2026-03-14 10:30 | 2:14 | S/O | Red hot maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Ghorashal Ckt-1 | 2026-03-04 09:15 | 2026-03-04 17:40 | 8:25 | S/O | Maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Ghorashal Ckt-2 | 2026-03-05 08:39 | 2026-03-05 15:54 | 7:15 | S/O | Shutdown taken by DWZTGEP | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2026-03-12 07:39 | 2026-03-12 11:35 | 3:56 | S/O | Shutdown taken by kabirpur via nldc | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2026-03-19 15:37 | 2026-03-19 16:29 | 0:52 | S/O | for Nest romove | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2026-03-20 22:15 | 2026-03-20 23:08 | 0:53 | S/O | Bird nest remove | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2026-03-20 23:10 | 2026-03-21 00:22 | 1:12 | S/O | Nest remove | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2026-03-28 14:37 | 2026-03-28 14:46 | 0:09 | S/O | Shutdown taken by NLDC | 0 | 0 | No interruption
|  |  | Total : | 1900-01-28 21:27 |  | Unserved Energy:
Dhaka (South) Grid Circle :
Bhulta 400/230kV | Horipur-01 | 2026-03-09 10:09 | 2026-03-09 15:19 | 5:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhulta 400/230kV | Horipur-01 | 2026-03-11 09:56 | 2026-03-15 17:27 | 103:31 | S/O | OPGW Stringing by EEGBPSP | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2026-03-03 08:56 | 2026-03-03 16:17 | 7:21 | S/O | Disc cleaning work in manikgonj grid | 0 | 0 | No interruption
Haripur 230/132kV | Madanganj-1 | 2026-03-22 14:44 | 2026-03-22 17:26 | 2:42 | S/O | Annual Maintenance | 0 | 0 | No interruption
Haripur 230/132kV | HPL-1 | 2026-03-29 10:10 | 2026-03-29 17:10 | 7:00 | S/O | TB changing work at MK box. | 0 | 0 | No interruption
Haripur 230/132kV | Meghnaghat-1 | 2026-03-31 07:22 | 2026-03-31 09:29 | 2:07 | S/O | Ordered by NLDC | 0 | 0 | No interruption
Hasnabad 230/132kV | Shyampur-APR-Hasnabad Ckt-2 | 2026-03-02 10:20 | 2026-03-02 15:20 | 5:00 | S/O | Z2 (21) relay Card changing by SPDM-1 | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 1 | 2026-03-02 09:56 | 2026-03-02 10:38 | 0:42 | S/O | NLDC Instruction | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Hasnabad Ckt. 2 | 2026-03-02 10:00 | 2026-03-02 10:38 | 0:38 | S/O | NLDC Instruction | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 2 | 2026-03-11 08:33 | 2026-03-11 15:01 | 6:28 | S/O | Line disk insulator cleaning from Aminbazar end. Shut-down according to NLDC instraction. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 1 | 2026-03-12 09:00 | 2026-03-12 14:38 | 5:38 | S/O | Disk cleaning and deadline checking at Aminbazar end. | 0 | 0 | No interruption
Matuail 132/33kV | 132 kV Siddhirgonj | 2026-03-29 09:20 | 2026-03-29 14:59 | 5:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Meghnaghat 230/132kV | Meghnaghat-Haripur-01 | 2026-03-31 07:48 | 2026-03-31 09:32 | 1:44 | S/O | red hot mainteance | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-1 | 2026-03-01 13:01 | 2026-03-01 21:09 | 8:08 | S/O | 400 kV Aminbazar ckt- 1 shutdown instructed by NLDC. Munshiganj SS will do their maintenance work. | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2026-03-03 08:52 | 2026-03-03 16:19 | 7:27 | S/O | Requested by NLDC | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2026-03-04 09:19 | 2026-03-04 16:30 | 7:11 | S/O | Transmission Line maintenance. | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2026-03-05 08:22 | 2026-03-05 13:20 | 4:58 | S/O | For maintenace work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-1 | 2026-03-08 08:46 | 2026-03-08 15:49 | 7:03 | S/O | Shutdown instructed by NLDC | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Shyampur 230kV Ckt-1 | 2026-03-09 09:42 | 2026-03-10 16:19 | 30:37 | S/O | 230 kV Shyampur ckt- 1 shutdown for Trip | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-1 | 2026-03-28 13:47 | 2026-03-29 17:15 | 27:28 | S/O | Maintenance work | 0 | 0 | No interruption
Rampura 230/132kV | Basundhara-01 | 2026-03-23 08:55 | 2026-03-23 12:42 | 3:47 | S/O | Annual maintenance | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Meghnaghat-1(D06) | 2026-03-09 09:40 | 2026-03-10 16:18 | 30:38 | S/O | The Broken overhead line reconnecting. | 0 | 0 | No interruption
Siddhirganj 132/33kV | Matuail | 2026-03-29 09:20 | 2026-04-03 00:01 | 110:41 | S/O | For work on Matuail end. | 0 | 0 | No interruption
Siddhirganj 230/132kV | 335MW EGCB 1 | 2026-03-27 09:30 | 2026-03-27 18:24 | 8:54 | S/O | Emergency maintenance work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-15 16:32 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Baroirhat 132/33kV | Hat-1 | 2026-03-07 08:48 | 2026-03-07 16:48 | 8:00 | S/O | Annual deadline checking | 0 | 0 | No interruption
Baroirhat 132/33kV | Hat-2 | 2026-03-12 08:48 | 2026-03-12 15:49 | 7:01 | S/O | Annual deadline checking | 0 | 0 | No interruption
BSRM 230/33kV | Mirsarai Ckt-2 | 2026-03-07 09:56 | 2026-03-07 09:56 | 0:00 | S/O | For Project Work | 0 | 0 | No interruption
BSRM 230/33kV | GPH Ispat Ckt. -02 | 2026-03-10 10:50 | 2026-03-10 17:16 | 6:26 | S/O | GPH works | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Kaptai Ckt-01 | 2026-03-03 08:29 | 2026-03-03 15:22 | 6:53 | S/O | Annual dead line check | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Kaptai Ckt-01 | 2026-03-04 08:29 | 2026-03-04 15:59 | 7:30 | S/O | Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Kaptai Ckt-02 | 2026-03-08 09:11 | 2026-03-08 15:00 | 5:49 | S/O | Maintenance work | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Kaptai Ckt-02 | 2026-03-09 08:31 | 2026-03-09 16:39 | 8:08 | S/O | Annual Maintenance | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-1 | 2026-03-16 10:53 | 2026-03-16 13:48 | 2:55 | S/O | Disc Cleaning | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-2 | 2026-03-17 08:52 | 2026-03-17 12:28 | 3:36 | S/O | Disc Cleaning | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-1 | 2026-03-16 10:54 | 2026-03-16 13:46 | 2:52 | S/O | Disk Ceaning | 39 | 111.8 | Power interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-2 | 2026-03-17 08:53 | 2026-03-17 12:27 | 3:34 | S/O | Disk Cleaning | 0 | 0 | No interruption
GPH 230/33kV | BSRM CKT-2 | 2026-03-10 10:50 | 2026-03-10 17:15 | 6:25 | S/O | OPGW String repair and maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroiarhat-01 | 2026-03-11 09:15 | 2026-03-11 16:05 | 6:50 | S/O | Maintenance work | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroiarhat-02 | 2026-03-12 09:03 | 2026-03-12 16:30 | 7:27 | S/O | Maintenance work | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroiarhat-02 | 2026-03-14 09:12 | 2026-03-14 14:54 | 5:42 | S/O | Maintenance work | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroiarhat-02 | 2026-03-15 09:04 | 2026-03-15 16:52 | 7:48 | S/O | none | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroiarhat-02 | 2026-03-16 09:04 | 2026-03-16 16:06 | 7:02 | S/O | Maintenance work | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Sikalbaha | 2026-03-05 10:14 | 2026-03-05 14:49 | 4:35 | S/O | Replacement of Disc Insulator. | 0 | 0 | No interruption
Kalurghat 132/33kV | MODUNAGHAT-02 | 2026-03-14 06:28 | 2026-03-14 12:02 | 5:34 | S/O | Khulshi - Madunaghat 230 KV underground cable line installation. | 7 | 38.9667 | Power interruption
Shahmirpur 132/33kV | Sikalbaha-2 | 2026-03-04 11:09 | 2026-03-04 12:11 | 1:02 | S/O | For Relay Testing | 0 | 0 | No interruption
Shahmirpur 132/33kV | Sikalbaha-1 | 2026-03-04 12:15 | 2026-03-04 12:39 | 0:24 | S/O | Maintenance work | 0 | 0 | No interruption
Shahmirpur 132/33kV | Julda-1 | 2026-03-04 12:43 | 2026-03-04 13:12 | 0:29 | S/O | For Relay Testing | 0 | 0 | No interruption
Shahmirpur 132/33kV | Julda-2 | 2026-03-04 13:14 | 2026-03-04 13:42 | 0:28 | S/O | For Relay Testing | 0 | 0 | No interruption
|  |  | Total : | 1900-01-03 20:30 |  | Unserved Energy: |  | 150.7667
Cumilla Grid Circle :
Ashuganj 230/132/33kV | Cumilla(N) 230 kV Ckt-2 | 2026-03-04 12:40 | 2026-03-04 14:48 | 2:08 | S/O | Maintenance | 0 | 0 | No interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-1 | 2026-03-02 06:20 | 2026-03-02 11:25 | 5:05 | S/O | Line maintenance | 28 | 142.3333 | Power interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-2 | 2026-03-02 06:21 | 2026-03-02 11:26 | 5:05 | S/O | Line maintenance | 0 | 0 | No interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-1 | 2026-03-12 08:35 | 2026-03-12 10:55 | 2:20 | S/O | Schedule work | 40 | 93.3333 | No interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-2 | 2026-03-12 08:36 | 2026-03-12 10:55 | 2:19 | S/O | Schedule work | 0 | 0 | No interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-2 | 2026-03-12 08:36 | 2026-03-12 10:55 | 2:19 | S/O | Schedule work | 0 | 0 | No interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-1 | 2026-03-14 07:13 | 2026-03-14 09:40 | 2:27 | S/O | Line work | 20 | 49 | Power interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-2 | 2026-03-14 07:14 | 2026-03-14 09:41 | 2:27 | S/O | Line work | 0 | 0 | No interruption
Bibiana 400/230kV | Bibi-Kalia Ckt-I | 2026-03-02 09:11 | 2026-03-02 15:25 | 6:14 | S/O | Emergency Maintenance | 0 | 0 | No interruption
Bibiana 400/230kV | Bibi-Kalia Ckt-I | 2026-03-10 08:42 | 2026-03-10 15:16 | 6:34 | S/O | line maintenance | 0 | 0 | No interruption
Bibiana 400/230kV | Bibi-Kalia Ckt-II | 2026-03-31 09:40 | 2026-04-02 17:01 | 55:21 | S/O | Emergency Maintenance | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Desh Energy Ckt-1 | 2026-03-02 13:13 | 2026-03-02 14:42 | 1:29 | S/O | DS maintenance | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | Kachua-03 | 2026-03-09 11:43 | 2026-03-09 16:26 | 4:43 | S/O | Relay Teat at Kachua End. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | Korerhat-04 | 2026-03-11 08:25 | 2026-03-11 16:46 | 8:21 | S/O | Painting and Silicon work | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | Korerhat-04 | 2026-03-12 09:11 | 2026-03-12 17:08 | 7:57 | S/O | Painting and Silicon work | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | Korerhat-04 | 2026-03-13 09:34 | 2026-03-13 16:30 | 6:56 | S/O | For painting and Silicon work. | 0 | 0 | No interruption
Daudkandi 132/33kV | Titas 50 MW Power Plant Line | 2026-03-31 09:12 | 2026-03-31 12:56 | 3:44 | S/O | Titas power plant end ground CT work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2026-03-02 06:34 | 2026-03-02 11:24 | 4:50 | S/O | Beanibazar Grid SS end reconductoring work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2026-03-12 08:39 | 2026-03-12 10:47 | 2:08 | S/O | Sylhet(South) SS end project work. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2026-03-14 07:14 | 2026-03-14 09:32 | 2:18 | S/O | For project work at the Sylhet South SS end. | 0 | 0 | No interruption
Kachua 230/132/33kV | Laksam CKT-1 | 2026-03-31 09:53 | 2026-03-31 17:51 | 7:58 | S/O | DFDR Test. | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-Ashuganj Ckt-03 | 2026-03-14 09:06 | 2026-03-14 17:35 | 8:29 | S/O | None | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-Ashuganj Ckt-03 | 2026-03-15 09:10 | 2026-03-15 15:54 | 6:44 | S/O | Annaul Maintenance. | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2026-03-02 06:35 | 2026-03-02 11:26 | 4:51 | S/O | Line bypass Through ERS Tower. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Sylhet (S) Ckt | 2026-03-11 09:06 | 2026-03-11 16:26 | 7:20 | S/O | Work of Sylhet (South) end | 0 | 0 | No interruption
|  |  | Total : | 1900-01-06 02:07 |  | Unserved Energy: |  | 284.6667
Khulna Grid Circle :
Barishal 132/33kV | 132kv Bhandaria ckt | 2026-03-30 09:05 | 2026-03-30 09:05 | 0:00 | S/O | Shutdown by ALDC | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Orion | 2026-03-08 10:34 | 2026-03-08 16:32 | 5:58 | S/O | Boring work for Earthing | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-NWPGCL | 2026-03-09 10:34 | 2026-03-09 15:50 | 5:16 | S/O | None | 0 | 0 | No interruption
Gollamari 132/33kV | E01 Gollamari-Gopalgonj Line - 1 | 2026-03-09 10:13 | 2026-03-09 17:12 | 6:59 | S/O | Khulna South-Rupsha line development work | 0 | 0 | No interruption
Gollamari 132/33kV | E07 Gollamari-Gopalgonj Line - 2 | 2026-03-09 10:13 | 2026-03-09 17:13 | 7:00 | S/O | Khulna South-Rupsha line development work | 0 | 0 | No interruption
Gollamari 132/33kV | E01 Gollamari-Gopalgonj Line - 1 | 2026-03-10 09:50 | 2026-03-10 16:44 | 6:54 | S/O | Rupsha - khulna south 230kv line Lilo work. | 0 | 0 | No interruption
Gollamari 132/33kV | E07 Gollamari-Gopalgonj Line - 2 | 2026-03-10 09:50 | 2026-03-10 16:45 | 6:55 | S/O | Rupsha - khulna south 230kv line Lilo work. | 0 | 0 | No interruption
Gollamari 132/33kV | E03 Gollamari-Khulna(S) Line-1 | 2026-03-11 08:20 | 2026-03-11 14:37 | 6:17 | S/O | OPGW inspection work. | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-1 | 2026-03-09 10:09 | 2026-03-09 17:13 | 7:04 | S/O | project work | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-2 | 2026-03-09 10:09 | 2026-03-09 17:23 | 7:14 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-1 | 2026-03-10 09:47 | 2026-03-10 16:43 | 6:56 | S/O | ALDC | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-2 | 2026-03-10 09:47 | 2026-03-10 16:43 | 6:56 | S/O | ALDC | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2026-03-02 07:47 | 2026-03-02 17:24 | 9:37 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-1 | 2026-03-02 07:49 | 2026-03-02 17:24 | 9:35 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2026-03-13 07:27 | 2026-03-13 16:25 | 8:58 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-2 | 2026-03-13 07:32 | 2026-03-13 15:48 | 8:16 | S/O | Maint.work | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -1 | 2026-03-13 09:55 | 2026-03-13 10:21 | 0:26 | S/O | Yarn Removal | 0 | 0 | No interruption
Khulna (C) | 132kV Central-Noapara-1 | 2026-03-31 14:42 | 2026-03-31 19:24 | 4:42 | S/O | near phultala lilo line OTG wire maintenance. | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- Noapara-2 | 2026-03-31 14:44 | 2026-03-31 20:32 | 5:48 | S/O | near phultala lilo line OPG wire maintenance. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Rupsha Ckt-1 | 2026-03-09 09:55 | 2026-03-10 17:54 | 31:59 | S/O | Project Work for DWZTGE Project. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Gallamari Ckt-1 | 2026-03-11 08:20 | 2026-03-11 14:36 | 6:16 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Rupsha Ckt-2 | 2026-03-11 09:33 | 2026-03-11 09:33 | 0:00 | S/O | Project work at Transmission line. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-2 | 2026-03-13 08:47 | 2026-03-13 10:30 | 1:43 | S/O | Red Hot Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-1 | 2026-03-13 09:55 | 2026-03-13 10:21 | 0:26 | S/O | Maintenance work at central s/s end. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-1 | 2026-03-13 10:31 | 2026-03-13 10:41 | 0:10 | S/O | Maintenance work at KSS end. | 0 | 0 | No interruption
Noapara 132/33kV | Jashore-1 | 2026-03-11 14:18 | 2026-03-11 14:56 | 0:38 | S/O | By the instruction of ALDC. | 0 | 0 | No interruption
Noapara 132/33kV | Jashore-2 | 2026-03-11 14:18 | 2026-03-11 14:56 | 0:38 | S/O | By the instruction of ALDC. | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 1 | 2026-03-15 19:15 | 2026-03-15 22:58 | 3:43 | S/O | Maint.work | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 2 | 2026-03-15 23:11 | 2026-03-15 23:39 | 0:28 | S/O | By ALDC. | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 1 | 2026-03-31 14:40 | 2026-03-31 19:26 | 4:46 | S/O | Instructed By ALDC | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 2 | 2026-03-31 14:43 | 2026-03-31 20:32 | 5:49 | S/O | Instructed By ALDC | 0 | 0 | No interruption
|  |  | Total : | 1900-01-06 09:27 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2026-03-03 08:57 | 2026-03-03 16:18 | 7:21 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 2 | 2026-03-27 09:39 | 2026-03-27 09:39 | 0:00 | S/O | reconductoring work by kEC | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-2 | 2026-03-16 12:50 | 2026-03-16 17:26 | 4:36 | S/O | Project Work | 0 | 0 | No interruption
Ullahpara 132/33kV | Shahjadpur Ckt | 2026-03-25 11:11 | 2026-03-25 12:20 | 1:09 | S/O | Red hot maintenance work. | 0 | 0 | No interruption
Ullahpara 132/33kV | 132 KV Sirajgonj Ckt-2 | 2026-03-25 12:23 | 2026-03-25 13:21 | 0:58 | S/O | Red hot maintenance work. | 0 | 0 | No interruption
|  |  | Total : | 0.58611 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Amnura 132/33kV | Amnura - Chapai Nawabganj | 2026-03-06 06:15 | 2026-03-06 11:44 | 5:29 | S/O | Work done by Chapai Grid SS | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt1 | 2026-03-02 10:56 | 2026-03-02 14:30 | 3:34 | S/O | 230 kv upper Bus maintenance. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt2 | 2026-03-03 09:25 | 2026-03-07 19:48 | 106:23 | S/O | LILO Work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt2 | 2026-03-10 07:49 | 2026-03-10 13:31 | 5:42 | S/O | Project work(LILO). | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt1 | 2026-03-13 09:40 | 2026-03-15 13:04 | 51:24 | S/O | Lilo work. | 0 | 0 | No interruption
Bogura 132/33kV | Natore-1 | 2026-03-31 08:30 | 2026-03-31 15:08 | 6:38 | S/O | maitenance work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-1 | 2026-03-02 10:51 | 2026-03-02 14:32 | 3:41 | S/O | Emergency BUS maintenance at Barapukuria Coal Base Thermal Power Plant | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-2 | 2026-03-03 09:27 | 2026-03-07 19:50 | 106:23 | S/O | Project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-2 | 2026-03-10 07:54 | 2026-03-10 13:28 | 5:34 | S/O | Project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-1 | 2026-03-13 08:40 | 2026-03-15 13:05 | 52:25 | S/O | Project work (LILO) at Barapukuria site | 0 | 0 | No interruption
Chapai 132/33kV | Chapai-Amnura | 2026-03-06 06:13 | 2026-03-06 11:40 | 5:27 | S/O | T01 x-former upgrading | 0 | 0 | No interruption
Chapai 132/33kV | Chapai-Rajshahi | 2026-03-06 06:15 | 2026-03-06 11:46 | 5:31 | S/O | T01 x-former upgrading. | 0 | 0 | No interruption
Chapai 132/33kV | Chapai Rahanpur ckt 1 | 2026-03-06 06:18 | 2026-03-06 11:26 | 5:08 | S/O | T01 x-former upgrading | 0 | 0 | No interruption
Chapai 132/33kV | Chapai Rahanpur ckt 2 | 2026-03-06 06:24 | 2026-03-06 11:26 | 5:02 | S/O | T01 x-former upgrading. | 0 | 0 | No interruption
Natore 132/33kV | Rajshahi-1 | 2026-03-04 11:23 | 2026-03-04 18:03 | 6:40 | S/O | Maintenance work | 0 | 0 | No interruption
Natore 132/33kV | Rajshahi-1 | 2026-03-05 10:47 | 2026-03-05 15:09 | 4:22 | S/O | Raj S/S work. | 0 | 0 | No interruption
Natore 132/33kV | Bogura-1 | 2026-03-31 08:31 | 2026-03-31 15:06 | 6:35 | S/O | Maintenance work | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Naogaon ckt-1 | 2026-03-01 08:58 | 2026-03-16 13:30 | 364:32 | S/O | Multi-ckt terminal tower create. | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Naogaon ckt-2 | 2026-03-01 08:58 | 2026-03-16 13:31 | 364:33 | S/O | Multi-ckt terminal tower create. | 0 | 0 | No interruption
Purbasadipur 230/132/33kV | EPVTL-2 | 2026-03-02 11:01 | 2026-03-02 14:58 | 3:57 | S/O | GIS to AIS loop and DS removal work by EEGBPS Project | 0 | 0 | No interruption
Purbasadipur 230/132/33kV | EPVTL-1 | 2026-03-02 15:02 | 2026-03-02 17:34 | 2:32 | S/O | Project work | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Monakasha 400KV Line ckt-01 | 2026-03-02 09:06 | 2026-03-02 17:06 | 8:00 | S/O | For red hot rectification work at adani side | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Chapainawabganj 132 KV Line Ckt-01 | 2026-03-06 06:23 | 2026-03-06 11:24 | 5:01 | S/O | Maintenance work | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Chapainawabganj 132 KV Line Ckt-02 | 2026-03-06 06:26 | 2026-03-06 11:25 | 4:59 | S/O | Maintenance work | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Monakasha 400KV Line ckt-01 | 2026-03-13 06:39 | 2026-03-13 17:36 | 10:57 | S/O | Maintenance work | 0 | 0 | No interruption
Rajshahi 230/132/33kV | 132 kV Rajshahi ckt-02 | 2026-03-07 10:38 | 2026-03-07 11:18 | 0:40 | S/O | 132kV Rajshahi SS end project work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Taraganj-2 | 2026-03-03 07:37 | 2026-03-03 17:44 | 10:07 | S/O | Maintenance work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Taraganj-1 | 2026-03-04 08:04 | 2026-03-04 11:42 | 3:38 | S/O | Maintenance work | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Taraganj CKT-01 | 2026-03-04 08:05 | 2026-03-04 11:44 | 3:39 | S/O | OPGW work | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Rangpur CKT-02 | 2026-03-03 07:35 | 2026-03-03 17:45 | 10:10 | S/O | Maintenance work | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Saidpur CKT-02 | 2026-03-03 07:35 | 2026-03-03 17:42 | 10:07 | S/O | OPGW Joint box connection work purpose | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Rangpur CKT-01 | 2026-03-04 08:04 | 2026-03-04 11:44 | 3:40 | S/O | Maintenance work | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Saidpur CKT-01 | 2026-03-04 08:05 | 2026-03-04 11:45 | 3:40 | S/O | Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 1900-02-17 20:10 |  | Unserved Energy: |  | 0
Others :Nil
No interruption
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1900-04-25 08:17 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:March 2026
| Area | Previous Month (February' 2026) |  |  |  | Current Month (March'2026)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 4 | 1 | 56 | 61 | 38 | 6 | 65 | 109
2 | Dhaka (South) Grid Circle. | 7 | 3 | 21 | 31 | 62 | 22 | 63 | 147
3 | Chattogram Grid Circle. | 5 | 13 | 35 | 53 | 19 | 10 | 33 | 62
4 | Cumilla Grid Circle. | 14 | 8 | 44 | 66 | 40 | 14 | 70 | 124
5 | Khulna Grid Circle. | 4 | 9 | 33 | 46 | 37 | 19 | 68 | 124
6 | HVDC Grid Circle | 3 | 9 | 16 | 28 | 6 | 26 | 13 | 45
7 | Bogura Grid Circle. | 2 | 17 | 31 | 50 | 41 | 29 | 48 | 118
8 | Others
9 | Total | 39 | 60 | 236 | 335 | 243 | 126 | 360 | 729
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month: March 2026
| Area | Previous Month (February' 2026) |  |  |  | Current Month (March '2026)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 59.73 | - | 595.75 | 655.48 | 572.4 | 363.87 | 273.67 | 1209.94
2 | Dhaka (South) Grid Circle. | 76 | 29.63 | - | 105.63 | 1887.22 | 156.96 | 842.88 | 2887.06
3 | Chattogram Grid Circle. | 11.87 | 9.17 | 102.62 | 123.66 | 39.93 | 1.33 | 211.76 | 253.02
4 | Cumilla Grid Circle. | 98.77 | 139.42 | 239.07 | 477.26 | 228.3 | 135.28 | 515.52 | 879.1
5 | Khulna Grid Circle. | 10 | 22.67 | 61.37 | 94.04 | 224.17 | 364.2 | 695.8 | 1284.17
6 | HVDC Grid Circle | - | 89.3 | - | 89.3 | 674.1 | 117.62 | 166.88 | 958.6
7 | Bogura Grid Circle. | 7.6 | 128.87 | 1133.83 | 1270.3 | 286.85 | 549.43 | 387.25 | 1223.53
8 | Others | bar: Energy unserved ( MWH ) due to T to Energy unserved ( MWH ) due to Total; Energy unserved ( MWH ) due to Total
9 | Total | 263.97 | 419.06 | 2132.64 | 2815.67 | 3912.97 | 1688.69 | 3093.76 | 8695.42
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-29
QF-LDC-29
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:March 2026
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 10 | 2 | 12 | 4 | - | 8 | 947.01
2 | Dhaka (South) | 5031.6 | 18 | 12 | 30 | 7 | 3 | 20 | 1614.53
3 | Chattogram | 2042 | 4 | 1 | 5 | 3 | 1 | 1 | 94.47
4 | Khulna | 2434 | 24 | 17 | 41 | 12 | 4 | 25 | 1280.2
5 | HVDC | 5954.3 | 7 | 4 | 11 | 4 | 2 | 5 | 284.5
6 | Bogura | 3145.6 | 27 | 6 | 33 | 5 | 7 | 21 | 1179.53
7 | Cumilla | 2981 | 14 | 10 | 24 | 7 | 8 | 9 | 549.26
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 5949.5
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.97%
3 | Chattogram | 99.98%
4 | Khulna | 99.98%
5 | HVDC | 99.99%
6 | Bogura | 99.97%
7 | Cumilla | 99.99% | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:March 2026
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 6 | - | 6 | 5 | - | 1 | 262.92
2 | Dhaka (South) | 990.29 | - | 13 | - | 13 | 2 | 1 | 10 | 1272.5333
3 | Chattogram | 917 | - | - | 3 | 3 | - | 1 | 2 | 158.57
4 | Khulna | 1238.4 | - | 1 |  | 1 | 1 | - | - | 3.9667
5 | HVDC | 1325 | - | 1 | - | 1 | - | - | 1 | 674.1
6 | Bogura | 1803.3 |  | 1 | - | 1 |  |  | 1 | 44
7 | Cumilla | 1648.16 | - | 2 | 3 | 5 | 1 | 1 | 3 | 329.83
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 2745.92
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 100%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 100%
7 | Cumilla | 99.99% | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:March 2026
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2026-03-01 | 10 | - | 9 | 8 hr 18 min | 2 | 6 hr 37 min
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-32
QF-LDC-32
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:March 2026
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Jamalpur 132/33kV | 2 | 0.24583 | 184.5
Kabirpur 132/33kV | 1 | 0:23 | 25.6833
Sreepur 230/132/33kV | 1 | 2:51 | 99.3
Kabirpur 132/33kV | 4 | 11:57 | 363.87
Bhaluka 132/33kV | 2 | 1:56 | 32.87
Kabirpur 132/33kV | 3 | 4:03 | 174.85
Sreepur 230/132/33kV | 1 | 1:09 | 55.2
Kabirpur 132/33kV | 1 | 2:33 | 255
Sherpur 132/33kV | 1 | 1:52 | 18.67
Hasnabad 132/33kV | 5 | 1:18 | 29.5
Narshingdi 132/33kV | 1 | 0:30 | 15
Sonargaon 132/33kV | 7 | 19:24 | 618.17
Madanganj 132/33kV | 1 | 0.095833 | 4.4
Munshiganj 132/33kV | 2 | 0.080556 | 77.33
Nawabganj 132/33kV | 2 | 0.098611 | 27.25
Ghorashal 230kV | 1 | 0.010417 | 42.5
Madanganj 132/33kV | 3 | 0.32014 | 168.9
Meghnaghat 400/230kV | 2 | 0.18125 | 64.65
Shyampur 230/132kV | 1 | 0.22708 | 185.3
Siddhirganj 132/33kV | 2 | 0.39583 | 665
Sonargaon 132/33kV | 2 | 1899-12-31 00:33 | 98.2
Madanganj 132/33kV | 2 | 0.27569 | 47.98
Munshiganj 132/33kV | 1 | 0.046528 | 22.3333
Sonargaon 132/33kV | 6 | 0.53403 | 407.03
Ghorashal 230kV | 1 | 1:24 | 112
Sonargaon 132/33kV | 4 | 8:30 | 301.52
Bakulia 132/33kV | 1 | 1:28 | 17.6
Dohazari 132/33kV | 2 | 0:33 | 14.53
Sholosohor 132/33kV | 1 | 0:08 | 1.3333
Dohazari 132/33kV | 3 | 4:04 | 180.6
Kalurghat 132/33kV | 1 | 5:34 | 38.9667
Brahmanbaria 132/33kV | 2 | 1:26 | 28.88
Cumilla(S) 132/33kV | 2 | 0:52 | 37
Daudkandi 132/33kV | 1 | 0:27 | 9
Shahjibazar 132/33kV | 1 | 0:40 | 36.6667
Sreemongol 132/33kV | 1 | 0:05 | 0.16667
Sylhet (South) | 2 | 3:30 | 26.25
Shahjibazar 132/33kV | 1 | 0:19 | 17.4167
Sreemongol 132/33kV | 1 | 0:37 | 27.75
Chowmuhani 230/132/33kV | 1 | 2:30 | 50
Daganbhuiyan 132/33kV | 1 | 6:02 | 66.3667
Sreemongol 132/33kV | 1 | 3:47 | 18.9167
Shahjibazar 132/33kV | 1 | 0:19 | 17.4167
Sreemongol 132/33kV | 1 | 0:37 | 27.75
Daudkandi 132/33kV | 2 | 3:03 | 91.5
Daudkandi 132/33kV | 2 | 3:00 | 60
Kulaura 132/33kV | 3 | 2:26 | 29.57
Sylhet 132/33kV | 1 | 0:54 | 10.8
Kulaura 132/33kV | 3 | 2:19 | 28.38
Sylhet 132/33kV | 1 | 0:53 | 10.6
Beanibazar 132/33kV | 3 | 9:52 | 284.67
Barishal 132/33kV | 4 | 2:50 | 52.33
Bhandaria 132/33kV | 2 | 0:30 | 7.5
Faridpur 132/33kV | 4 | 1:14 | 50.1
Khulna (C) | 1 | 1:25 | 11.3333
Mongla 132/33kV | 4 | 7:49 | 89.6
Satkhira 132/33kV | 1 | 0:07 | 9.3333
Bhandaria 132/33kV | 1 | 0:57 | 9.5
Benapole 132/33kV | 1 | 0:08 | 2.6667
Borhanuddin 230/33kV | 1 | 2:13 | 133
Madaripur 132/33kV | 1 | 3:49 | 76.3333
Benapole 132/33kV | 1 | 0:10 | 3.3333
Bhandaria 132/33kV | 1 | 1:01 | 10.1667
Madaripur 132/33kV | 1 | 3:49 | 76.3333
Mongla 132/33kV | 1 | 2:02 | 52.8667
Patuakhali 132/33kV | 1 | 0:14 | 3.9667
Barishal 230/132kV | 2 | 4:43 | 152.83
Bhandaria 132/33kV | 2 | 5:55 | 50.97
Gopalganj 132/33kV | 1 | 2:13 | 33.25
Khulna (C) | 1 | 2:20 | 11.6667
Patuakhali 132/33kV | 2 | 2:49 | 42.25
Barishal 230/132kV | 2 | 4:36 | 149.17
Bhandaria 132/33kV | 2 | 5:54 | 50.83
Borhanuddin 230/33kV | 1 | 2:08 | 117.3333
Khulna (C) | 2 | 4:36 | 46
Patuakhali 132/33kV | 2 | 2:46 | 41.5
Bhangura 132/33kV | 1 | 0:46 | 7.6667
Chuadanga 132/33kV | 1 | 1:27 | 37.7
Bhangura 132/33kV | 1 | 0:47 | 7.8333
Chuadanga 132/33kV | 1 | 1:28 | 38.1333
Kushtia 132/33kV | 3 | 0:38 | 26.28
Jashore 132/33kV | 1 | 5:21 | 674.1
Ishurdi 132/33kV | 1 | 2:32 | 38
Magura 132/33kV | 1 | 4:10 | 83.3333
Pabna 132/33kV | 1 | 0:26 | 7.8
Ishurdi 132/33kV | 1 | 2:31 | 37.75
Bog-Sherpur 132/33kV | 1 | 0:21 | 3.5
Jaldhaka 132/33kV | 2 | 0:45 | 8.25
Mahasthangarh 132/33kV | 3 | 3:59 | 112.12
Niamatpur 132/33kV | 1 | 0:35 | 8.75
Rajshahi 132/33kV | 2 | 4:47 | 47.07
Sirajganj 132/33kV | 2 | 0:40 | 13.33
Mahasthangarh 132/33kV | 1 | 0:59 | 19.6667
Niamatpur 132/33kV | 1 | 0:35 | 8.75
Rajshahi 132/33kV | 1 | 0:38 | 6.3333
Niamatpur 132/33kV | 1 | 0:35 | 8.75
Rajshahi 132/33kV | 1 | 0:38 | 6.3333
Bog-Sherpur 132/33kV | 2 | 11:37 | 163.17
Mahasthangarh 132/33kV | 2 | 6:31 | 67.75
Rangpur 132/33kV | 1 | 2:40 | 120
Sirajganj 132/33kV | 1 | 1:09 | 11.5
Thakurgaon 132/33kV | 1 | 1:42 | 47.6
Bog-Sherpur 132/33kV | 1 | 1:31 | 60.6667
Mahasthangarh 132/33kV | 2 | 4:29 | 67.25
Sirajganj 132/33kV | 1 | 1:09 | 11.5
Naogaon 132/33kV | 1 | 2:00 | 44
Bog-Sherpur 132/33kV | 1 | 1:33 | 15.5
Chapai 132/33kV | 1 | 5:02 | 226.5
Purbasadipur 230/132/33kV | 2 | 2:28 | 93.67
Rajshahi 132/33kV | 1 | 2:47 | 27.8333
Saidpur 132/33kV | 1 | 1:35 | 23.75
| 186 | 347:04 | 8695.44
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: March-2026
Sl No. | Sub-station | Load (MW) | Date & Time
1 | AKS | 18 | 2026-03-17 06:00
2 | AKSML | 20 | 2026-03-24 02:00
3 | Aftabnagar | 38 | 2026-03-09 19:00
4 | Agargaon | 121 | 2026-03-31 13:00
5 | Agrabad | 68 | 2026-03-30 12:00
6 | Amnura | 41 | 2026-03-27 19:30
7 | Ashuganj | 114 | 2026-03-11 00:00
8 | BSRM | 208 | 2026-03-10 23:00
9 | Bagerhat | 86 | 2026-03-29 18:30
10 | Bajitpur | 87 | 2026-03-16 21:00
11 | Bakerganj | 13.1 | 2026-03-14 21:00
12 | Bakulia | 91 | 2026-03-14 12:00
13 | Banani | 55.6 | 2026-03-11 15:00
14 | Bangabhaban | 19 | 2026-03-31 11:00
15 | Barapukuria | 69 | 2026-03-10 21:00
16 | Barguna | 20 | 2026-03-18 21:00
17 | Barishal | 103 | 2026-03-12 13:00
18 | Barishal-230 | 100 | 2026-03-30 18:30
19 | Baroaulia | 73 | 2026-03-17 15:00
20 | Baroirhat | 61 | 2026-03-30 20:00
21 | Bashundhara | 198 | 2026-03-11 14:00
22 | BashundharaCement | 14 | 2026-03-18 20:00
23 | Beanibazar | 68 | 2026-03-12 18:30
24 | Benapole | 84 | 2026-03-13 18:30
25 | Bhaluka | 157 | 2026-03-16 17:00
26 | Bhandaria | 55 | 2026-03-11 21:00
27 | Bhangura | 45 | 2026-03-18 14:00
28 | Bheramara(GK) | 63 | 2026-03-14 19:00
29 | Bhulta | 234 | 2026-03-04 11:00
30 | Bog-Sherpur | 76 | 2026-03-27 19:30
31 | Bogura | 159 | 2026-03-11 18:00
32 | Borhanuddin | 92 | 2026-03-27 22:00
33 | Brahmanbaria | 126 | 2026-03-27 19:00
34 | Cantonment | 158 | 2026-03-30 12:00
35 | Chandina | 25 | 2026-03-19 15:00
36 | Chandpur | 84 | 2026-03-30 20:00
37 | Chandraghona | 37 | 2026-03-27 19:00
38 | Chapai | 77 | 2026-03-15 03:00
39 | Charsaidpur | 55 | 2026-03-06 16:00
40 | Chauddagram | 81 | 2026-03-30 18:30
41 | Chhatak | 36 | 2026-03-11 21:00
42 | Chowmuhani | 149 | 2026-03-30 19:30
43 | Chuadanga | 126 | 2026-03-14 03:00
44 | Coxsbazar | 151 | 2026-03-29 18:30
45 | Cumilla(N) | 125 | 2026-03-11 23:00
46 | Cumilla(S) | 188 | 2026-03-16 14:00
47 | Daganbhuiyan | 38 | 2026-03-21 07:00
48 | Daudkandi | 154 | 2026-03-30 18:30
49 | DhakaUniversity | 74 | 2026-03-11 13:00
50 | Dhamrai | 138 | 2026-03-30 09:00
51 | Dhanmondi | 114 | 2026-03-30 13:00
52 | Dohazari | 110 | 2026-03-10 18:00
53 | Faridpur | 160 | 2026-03-14 19:30
54 | Fatullah | 104 | 2026-03-10 15:00
55 | Fenchuganj | 35 | 2026-03-11 18:30
56 | Feni | 102 | 2026-03-30 18:30
57 | GPH | 96 | 2026-03-02 17:00
58 | Ghatail | 100 | 2026-03-14 19:00
59 | Ghorashal | 57 | 2026-03-23 09:00
60 | Ghorashal-230 | 117 | 2026-03-10 22:00
61 | Goalpara | 42 | 2026-03-11 19:00
62 | Gollamari | 102 | 2026-03-14 19:00
63 | Gopalganj | 110 | 2026-03-29 19:00
64 | Gulshan | 122 | 2026-03-30 13:00
65 | Halishahar | 100 | 2026-03-30 16:00
66 | HaripurSBU | 139 | 2026-03-15 09:00
67 | Hasnabad | 90 | 2026-03-16 20:00
68 | Hathazari | 81 | 2026-03-18 19:00
69 | Hatirjheel | 44 | 2026-03-11 15:00
70 | Ishurdi | 77 | 2026-03-14 19:00
71 | Jaldhaka | 78 | 2026-03-08 18:00
72 | Jamalpur | 122 | 2026-03-27 14:00
73 | Jashore | 150 | 2026-03-30 19:30
74 | Jhenaidah | 107 | 2026-03-18 18:30
75 | Joydebpur | 146 | 2026-03-09 14:00
76 | Joypurhat | 66 | 2026-03-11 21:00
77 | Juldah | 20 | 2026-03-19 17:00
78 | KSRM | 28 | 2026-03-01 09:00
79 | Kabirpur | 264 | 2026-03-15 16:00
80 | Kachua | 99 | 2026-03-30 19:30
81 | Kaliganj | 31 | 2026-03-14 19:00
82 | Kallyanpur | 114 | 2026-03-29 09:00
83 | Kalurghat | 55 | 2026-03-10 14:00
84 | Kamrangirchar | 85 | 2026-03-09 17:00
85 | Kaptai | N/A | N/A
86 | Kasba | 38 | 2026-03-11 21:00
87 | Kazla | 113 | 2026-03-11 15:00
88 | Keranigonj | 90 | 2026-03-01 17:00
89 | Khagrachori | 38 | 2026-03-19 18:30
90 | Khulna | 65 | 2026-03-28 18:30
91 | Khulshi | 192 | 2026-03-14 16:00
92 | Kishoreganj | 130 | 2026-03-12 18:00
93 | Kodda | 350 | 2026-03-14 00:00
94 | Kulaura | 43 | 2026-03-11 18:30
95 | Kurigram | 74 | 2026-03-10 17:00
96 | Kushtia | 145 | 2026-03-15 02:00
97 | Laksam | 111 | 2026-03-15 10:00
98 | Lakshmipur | 49 | 2026-03-19 20:00
99 | Lalbag | 75 | 2026-03-10 17:00
100 | Lalmonirhat | 58 | 2026-03-11 18:00
101 | MI_Cement | 19.3 | 2026-03-15 00:00
102 | Madanganj | 52 | 2026-03-08 17:00
103 | Madaripur | 111 | 2026-03-29 21:00
104 | Madartek | 78 | 2026-03-13 23:00
105 | Madunaghat | 55 | 2026-03-14 22:00
106 | Magura | 70 | 2026-03-27 19:00
107 | Mahasthangarh | 82 | 2026-03-12 03:00
108 | Maijdee | 50 | 2026-03-30 20:00
109 | Manikganj | 129 | 2026-03-31 19:00
110 | Maniknagar | 74 | 2026-03-31 13:00
111 | Matarbari | 56 | 2026-03-30 20:00
112 | Matuail | 72 | 2026-03-05 09:00
113 | Metrorail_Motijheel | 46 | 2026-03-09 17:00
114 | Metrorail_Uttara | 5 | 2026-03-18 17:00
115 | Millgate | 97 | 2026-03-31 12:00
116 | Mirpur | 149 | 2026-03-12 20:00
117 | Mirsorai | 51 | 2026-03-08 06:00
118 | Mirzapur | 56 | 2026-03-31 18:30
119 | Mithapukur | 67 | 2026-03-13 03:00
120 | Modern | N/A | N/A
121 | Mogbazar | 94.6 | 2026-03-02 14:00
122 | Mongla | 54 | 2026-03-29 20:00
123 | Motijheel | 47 | 2026-03-31 13:00
124 | Muktagacha | 42 | 2026-03-14 18:00
125 | Munshiganj | 125 | 2026-03-31 21:00
126 | Muradnagar | 50 | 2026-03-30 19:00
127 | Mymensingh | 223 | 2026-03-11 18:00
128 | Nabinagar | 16 | 2026-03-30 20:00
129 | Naogaon | 136 | 2026-03-11 22:00
130 | Narail | 63.5 | 2026-03-18 21:00
131 | Narinda | 68 | 2026-03-10 14:00
132 | Narshingdi | 177 | 2026-03-15 19:30
133 | Natore | 155 | 2026-03-15 04:00
134 | Nawabganj | 58 | 2026-03-30 22:00
135 | Netrakona | 156 | 2026-03-03 18:00
136 | New | 77 | 2026-03-11 14:00
137 | Niamatpur | 101 | 2026-03-03 13:00
138 | Noapara | 51 | 2026-03-15 14:00
139 | PHP | 12 | 2026-03-12 11:00
140 | Pabna | 94 | 2026-03-14 21:00
141 | Palashbari | 110 | 2026-03-14 18:30
142 | Panchagarh | 59 | 2026-03-07 17:00
143 | Patiya | 10 | 2026-03-17 00:00
144 | Patuakhali | 65.5 | 2026-03-27 22:00
145 | Payra | 34 | 2026-03-10 20:00
146 | Postogola | 51 | 2026-03-10 13:00
147 | Pubail | 29 | 2026-03-16 15:00
148 | Purbachal | 30 | 2026-03-30 13:00
149 | Purbasadipur | 77 | 2026-03-26 19:30
150 | Rahanpur | 42 | 2026-03-11 04:00
151 | Rahim | 80 | 2026-03-06 16:00
152 | Rajbari | 82 | 2026-03-30 19:00
153 | Rajendrapur | 133 | 2026-03-12 13:00
154 | Rajshahi | 112 | 2026-03-27 21:00
155 | Rajshahi-230 | 92 | 2026-03-31 22:00
156 | Ramganj | 116 | 2026-03-21 07:00
157 | Rampur | 39 | 2026-03-30 21:00
158 | Rangamati | 20 | 2026-03-30 18:30
159 | Rangpur | 148 | 2026-03-10 18:00
160 | Ruppur | 5.2 | 2026-03-23 06:00
161 | SSM | 14 | 2026-03-12 06:00
162 | Saidpur | 108 | 2026-03-01 17:00
163 | Satkhira | 138 | 2026-03-14 18:30
164 | Satmasjid | 100 | 2026-03-11 19:30
165 | Savar | 234 | 2026-03-11 14:00
166 | SevenRings | 20.49 | 2026-03-03 13:00
167 | ShahCement | 40 | 2026-03-24 01:00
168 | Shahjadpur | 88 | 2026-03-15 07:00
169 | Shahjibazar | 118 | 2026-03-10 23:00
170 | Shahmirpur | 61 | 2026-03-12 00:00
171 | Shariatpur | 87 | 2026-03-30 19:00
172 | Sherpur | 170 | 2026-03-10 18:00
173 | Shikalbaha | 33 | 2026-03-15 19:30
174 | Shitalakhya | 83.6 | 2026-03-11 16:00
175 | Sholosohor | 48 | 2026-03-31 15:00
176 | Shyampur | 192 | 2026-03-15 12:00
177 | Siddhirganj | 129 | 2026-03-10 12:00
178 | Sirajganj | 116 | 2026-03-14 20:00
179 | Sonargaon | 164 | 2026-03-14 17:00
180 | Sreemongol | 78 | 2026-03-14 18:30
181 | Sreepur | 119 | 2026-03-10 17:00
182 | Srinagar | 48.8 | 2026-03-30 21:00
183 | Sunamganj | 55 | 2026-03-11 21:00
184 | Sylhet | 56 | 2026-03-15 17:00
185 | Sylhet-132 | 105 | 2026-03-12 21:00
186 | TK | 27 | 2026-03-13 12:00
187 | Tangail | 196 | 2026-03-15 03:00
188 | Taraganj | 24 | 2026-03-10 17:00
189 | Tasnim | 37 | 2026-03-14 15:00
190 | Thakurgaon | 100 | 2026-03-11 19:00
191 | Tongi | 173 | 2026-03-10 13:00
192 | Ullahpara | 45 | 2026-03-15 03:00
193 | Ullon | 59 | 2026-03-05 19:30
194 | Uttara | 83 | 2026-03-30 13:00
195 | UttaraNew | 34 | 2026-03-01 22:00
196 | Zigatola | 90 | 2026-03-14 19:30
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID BANGLADESH PLC. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: March 2026
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5534.07 | 2026-03-11 | 14:00
Chattogram | 1432 | 2026-03-10 | 19:30
Cumilla | 1390 | 2026-03-12 | 22:00
Mymensingh | 1219 | 2026-03-14 | 18:00
Sylhet | 562 | 2026-03-11 | 22:00
Khulna | 1770.8 | 2026-03-18 | 19:30
Barishal | 457 | 2026-03-27 | 22:00
Rajshahi | 1497.9 | 2026-03-14 | 21:00
Rangpur | 990 | 2026-03-10 | 17:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: March-2026
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 422 | 2026-03-22 05:00 | 349 | 2026-03-08 18:30
2 | Amtali | 400 | 426 | 2026-03-19 04:00 | 403 | 2026-03-10 12:00
3 | Ashuganj | 400 | N/A | N/A | N/A | N/A
4 | Bhulta | 400 | 414 | 2026-03-21 11:00 | 357 | 2026-03-11 12:00
5 | Bibiana | 400 | 419 | 2026-03-23 17:00 | 392 | 2026-03-06 16:00
6 | BIPTC | 400 | 409 | 2026-03-22 02:00 | 387 | 2026-03-10 13:00
7 | Bogura | 400 | 422 | 2026-03-21 02:00 | 370 | 2026-03-11 17:00
8 | Gopalganj | 400 | 423 | 2026-03-22 05:00 | 359 | 2026-03-15 10:00
9 | Kaliakoir | 400 | 416 | 2026-03-22 06:00 | 355 | 2026-03-11 11:00
10 | Korerhat | 400 | 422 | 2026-03-22 05:00 | 383 | 2026-03-10 11:00
11 | Madunaghat | 400 | 415 | 2026-03-21 18:00 | 386 | 2026-03-10 11:00
12 | Meghnaghat | 400 | 423 | 2026-03-22 05:00 | 369 | 2026-03-11 12:00
13 | Payra | 400 | 424 | 2026-03-23 05:00 | 406 | 2026-03-11 13:00
14 | Rahanpur | 400 | 423 | 2026-03-21 01:00 | 382 | 2026-03-13 13:00
15 | Rampal | 400 | 418 | 2026-03-19 06:00 | 389 | 2026-03-14 13:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 243 | 2026-03-19 01:00 | 213 | 2026-03-02 10:00
2 | AKSML | 230 | 240 | 2026-03-22 03:00 | 218 | 2026-03-10 11:00
3 | Aminbazar | 230 | 242 | 2026-03-18 19:30 | 210 | 2026-03-02 10:00
4 | Ashuganj | 230 | 244 | 2026-03-23 04:00 | 209 | 2026-03-11 13:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 243 | 2026-03-21 02:00 | 220 | 2026-03-11 11:00
7 | Barapukuria | 230 | 245 | 2026-03-21 01:00 | 192 | 2026-03-05 12:00
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 238 | 2026-03-19 01:00 | 222 | 2026-03-10 15:00
10 | Bheramara | 230 | 243 | 2026-03-22 03:00 | 220 | 2026-03-05 10:00
11 | Bhulta | 230 | 242 | 2026-03-23 04:00 | 205 | 2026-03-11 12:00
12 | Bibiana | 230 | 244 | 2026-03-22 06:00 | 209 | 2026-03-18 06:00
13 | BIPTC | 230 | 244 | 2026-03-22 04:00 | 221 | 2026-03-06 16:00
14 | Bogura | 230 | 246 | 2026-03-21 02:00 | 216 | 2026-03-11 17:00
15 | Bogura-400 | 230 | 245 | 2026-03-21 02:00 | 214 | 2026-03-11 17:00
16 | Borhanuddin | 230 | 240 | 2026-03-19 02:00 | 227 | 2026-03-17 15:00
17 | BSRM | 230 | 241 | 2026-03-21 15:00 | 216 | 2026-03-10 11:00
18 | Chowmuhani | 230 | 239 | 2026-03-20 15:00 | 215 | 2026-03-10 11:00
19 | Cumilla(N) | 230 | 239 | 2026-03-19 05:00 | 215 | 2026-03-11 12:00
20 | Faridpur | 230 | 237 | 2026-03-23 04:00 | 215 | 2026-03-10 13:00
21 | Fenchuganj | 230 | 245 | 2026-03-23 06:00 | 229 | 2026-03-11 14:00
22 | Feni | 230 | 242 | 2026-03-19 01:00 | 217 | 2026-03-10 11:00
23 | Ghorashal | 230 | 245 | 2026-03-19 01:00 | 215 | 2026-03-05 15:00
24 | Ghorashal-230 | 230 | 241 | 2026-03-19 06:00 | 205 | 2026-03-11 13:00
25 | Gopalganj | 230 | 236 | 2026-03-22 04:00 | 215 | 2026-03-11 12:00
26 | GPH | 230 | 241 | 2026-03-21 15:00 | 217 | 2026-03-10 11:00
27 | Haripur | 230 | 241 | 2026-03-21 12:00 | 211 | 2026-03-31 11:00
28 | Hasnabad | 230 | 241 | 2026-03-22 06:00 | 211 | 2026-03-10 11:00
29 | Hathazari | 230 | 238 | 2026-03-17 06:00 | 216 | 2026-03-04 15:00
30 | Ishurdi | 230 | 244 | 2026-03-21 02:00 | 223 | 2026-03-06 16:00
31 | Jhenaidah | 230 | 244 | 2026-03-03 04:00 | 216 | 2026-03-24 19:00
32 | Kachua | 230 | 241 | 2026-03-19 06:00 | 217 | 2026-03-04 15:00
33 | Kaliakoir | 230 | 248 | 2026-03-19 06:00 | 213 | 2026-03-02 10:00
34 | Keranigonj | 230 | 241 | 2026-03-19 06:00 | 210 | 2026-03-11 12:00
35 | Khulna(S) | 230 | 244 | 2026-03-22 03:00 | 218 | 2026-03-11 19:00
36 | Korerhat | 230 | 241 | 2026-03-19 01:00 | 218 | 2026-03-04 14:00
37 | Madunaghat | 230 | 241 | 2026-03-22 04:00 | 220 | 2026-03-10 11:00
38 | Madunaghat-400 | 230 | 241 | 2026-03-22 04:00 | 220 | 2026-03-10 11:00
39 | Maniknagar | 230 | 241 | 2026-03-22 05:00 | 210 | 2026-03-11 12:00
40 | Meghnaghat | 230 | 246 | 2026-03-22 02:00 | 217 | 2026-03-31 11:00
41 | Meghnaghat-400 | 230 | 241 | 2026-03-18 18:30 | 213 | 2026-03-31 11:00
42 | Mirsorai | 230 | 246 | 2026-03-19 02:00 | 218 | 2026-03-04 15:00
43 | Naogaon | 230 | N/A | N/A | N/A | N/A
44 | Purbasadipur | 230 | 248 | 2026-03-21 02:00 | 196 | 2026-03-11 17:00
45 | Rajshahi | 230 | 242 | 2026-03-22 05:00 | 218 | 2026-03-25 19:00
46 | Rampal | 230 | 241 | 2026-03-22 04:00 | 221 | 2026-03-11 13:00
47 | Rampur | 230 | N/A | N/A | N/A | N/A
48 | Rampura | 230 | 241 | 2026-03-21 11:00 | 200 | 2026-03-11 13:00
49 | Shikalbaha | 230 | 238 | 2026-03-19 02:00 | 218 | 2026-03-10 11:00
50 | Shyampur | 230 | 240 | 2026-03-21 15:00 | 211 | 2026-03-31 12:00
51 | Siddhirganj | 230 | 242 | 2026-03-22 05:00 | 211 | 2026-03-31 11:00
52 | Sirajgonj | 230 | 247 | 2026-03-21 02:00 | 224 | 2026-03-11 12:00
53 | Sreepur | 230 | 237 | 2026-03-21 05:00 | 206 | 2026-03-11 12:00
54 | Tongi | 230 | 244 | 2026-03-22 01:00 | 207 | 2026-03-11 11:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 138 | 2026-03-05 05:00 | 121 | 2026-03-11 12:00
2 | Agargaon | 132 | 142 | 2026-03-18 18:30 | 120 | 2026-03-02 10:00
3 | Agrabad | 132 | 139 | 2026-03-21 15:00 | 120 | 2026-03-10 22:00
4 | AKS | 132 | 137 | 2026-03-17 06:00 | 123 | 2026-03-10 11:00
5 | Aminbazar | 132 | 142 | 2026-03-18 19:30 | 120 | 2026-03-02 10:00
6 | Amnura | 132 | 141 | 2026-03-21 01:00 | 125 | 2026-03-02 09:00
7 | Ashuganj | 132 | N/A | N/A | N/A | N/A
8 | Ashuganj-230 | 132 | 145 | 2026-03-13 21:00 | 128 | 2026-03-11 12:00
9 | Bagerhat | 132 | 144 | 2026-03-17 01:00 | 114 | 2026-03-29 18:30
10 | Bajitpur | 132 | 138 | 2026-03-21 14:00 | 121 | 2026-03-10 16:00
11 | Bakerganj | 132 | 139 | 2026-03-17 06:00 | 129 | 2026-03-10 12:00
12 | Bakulia | 132 | 139 | 2026-03-03 12:00 | 123 | 2026-03-10 11:00
13 | Banani | 132 | 143 | 2026-03-18 18:30 | 118 | 2026-03-11 12:00
14 | Bangabhaban | 132 | 141 | 2026-03-13 21:00 | 118 | 2026-03-05 12:00
0 | Barapukuria | 132 | 143 | 2026-03-21 00:00 | 118 | 2026-03-03 16:00
16 | Barguna | 132 | 140 | 2026-03-19 01:00 | 128 | 2026-03-13 13:00
17 | Barishal | 132 | 140 | 2026-03-19 01:00 | 127 | 2026-03-10 12:00
18 | Barishal-230 | 132 | 139 | 2026-03-19 01:00 | 128 | 2026-03-10 13:00
19 | Baroaulia | 132 | 140 | 2026-03-22 00:00 | 124 | 2026-03-10 11:00
20 | Baroirhat | 132 | 138 | 2026-03-19 02:00 | 123 | 2026-03-10 11:00
21 | Bashundhara | 132 | 143 | 2026-03-18 18:30 | 118 | 2026-03-11 12:00
22 | BashundharaCement | 132 | 143 | 2026-03-20 12:00 | 119 | 2026-03-11 12:00
23 | Beanibazar | 132 | 140 | 2026-03-28 07:00 | 121 | 2026-03-10 16:00
24 | Benapole | 132 | 140 | 2026-03-17 01:00 | 112 | 2026-03-16 21:00
25 | Bhaluka | 132 | 141 | 2026-03-16 00:00 | 120 | 2026-03-11 13:00
26 | Bhandaria | 132 | 141 | 2026-03-19 01:00 | 113 | 2026-03-30 15:00
27 | Bhangura | 132 | 140 | 2026-03-21 02:00 | 122 | 2026-03-11 12:00
28 | Bheramara | 132 | 140 | 2026-03-21 02:00 | 126 | 2026-03-17 08:00
29 | Bheramara(GK) | 132 | 140 | 2026-03-22 03:00 | 127 | 2026-03-17 07:00
30 | Bhulta | 132 | 137 | 2026-03-18 19:00 | 115 | 2026-03-11 12:00
31 | Bog-Sherpur | 132 | 143 | 2026-03-21 01:00 | 123 | 2026-03-11 17:00
32 | Bogura | 132 | 144 | 2026-03-21 01:00 | 126 | 2026-03-05 10:00
33 | Bogura-230 | 132 | 144 | 2026-03-21 01:00 | 126 | 2026-03-02 10:00
34 | Brahmanbaria | 132 | 142 | 2026-03-13 21:00 | 120 | 2026-03-11 12:00
35 | Cantonment | 132 | 142 | 2026-03-18 18:30 | 117 | 2026-03-02 10:00
36 | Chandina | 132 | 141 | 2026-03-19 01:00 | 123 | 2026-03-11 12:00
37 | Chandpur | 132 | 139 | 2026-03-19 01:00 | 122 | 2026-03-04 15:00
39 | Chandraghona | 132 | 140 | 2026-03-17 06:00 | 127 | 2026-03-10 10:00
40 | Chapai | 132 | 141 | 2026-03-21 03:00 | 125 | 2026-03-02 09:00
41 | Charsaidpur | 132 | 142 | 2026-03-18 18:30 | 118 | 2026-03-11 12:00
42 | Chauddagram | 132 | 138 | 2026-03-19 01:00 | 120 | 2026-03-26 17:00
43 | Chhatak | 132 | 138 | 2026-03-28 07:00 | 120 | 2026-03-12 17:00
44 | Chowmuhani | 132 | 137 | 2026-03-19 01:00 | 120 | 2026-03-10 10:00
45 | Chuadanga | 132 | 139 | 2026-03-22 03:00 | 115 | 2026-03-28 13:00
46 | Coxsbazar | 132 | 130 | 2026-03-17 05:00 | 103 | 2026-03-26 19:00
47 | Cumilla(N) | 132 | 140 | 2026-03-19 04:00 | 123 | 2026-03-11 13:00
48 | Cumilla(S) | 132 | 138 | 2026-03-18 20:00 | 115 | 2026-03-10 14:00
49 | Daganbhuiyan | 132 | 137 | 2026-03-19 01:00 | 122 | 2026-03-04 15:00
50 | Daudkandi | 132 | 139 | 2026-03-18 21:00 | 115 | 2026-03-31 11:00
51 | DhakaUniversity | 132 | 140 | 2026-03-13 20:00 | 120 | 2026-03-11 12:00
52 | Dhamrai | 132 | 144 | 2026-03-03 06:00 | 119 | 2026-03-02 10:00
53 | Dhanmondi | 132 | 143 | 2026-03-18 18:30 | 120 | 2026-03-11 12:00
54 | Dohazari | 132 | 137 | 2026-03-17 06:00 | 143 | 2026-03-18 18:30
55 | Faridpur | 132 | 137 | 2026-03-22 05:00 | 124 | 2026-03-16 23:00
56 | Fatullah | 132 | 143 | 2026-03-19 00:00 | 118 | 2026-03-10 11:00
57 | Fenchuganj | 132 | 141 | 2026-03-28 08:00 | 129 | 2026-03-07 14:00
58 | Feni | 132 | 136 | 2026-03-19 01:00 | 121 | 2026-03-10 11:00
59 | Feni-230 | 132 | 136 | 2026-03-19 01:00 | 122 | 2026-03-04 15:00
60 | Ghatail | 132 | 143 | 2026-03-15 23:00 | 113 | 2026-03-11 13:00
61 | Ghorashal | 132 | 145 | 2026-03-18 19:30 | 125 | 2026-03-11 12:00
62 | Goalpara | 132 | 144 | 2026-03-21 04:00 | 123 | 2026-03-05 17:00
63 | Gollamari | 132 | 142 | 2026-03-19 06:00 | 125 | 2026-03-06 13:00
64 | Gopalganj | 132 | 141 | 2026-03-20 16:00 | 125 | 2026-03-05 14:00
65 | Gopalganj-400 | 132 | 141 | 2026-03-22 05:00 | 125 | 2026-03-16 06:00
66 | Gulshan | 132 | 140 | 2026-03-11 18:00 | 120 | 2026-03-11 12:00
67 | Halishahar | 132 | 140 | 2026-03-22 05:00 | 123 | 2026-03-10 11:00
68 | Haripur | 132 | 142 | 2026-03-20 12:00 | 122 | 2026-03-30 10:00
69 | HaripurSBU | 132 | 142 | 2026-03-20 12:00 | 119 | 2026-03-11 12:00
70 | Hasnabad | 132 | 144 | 2026-03-18 20:00 | 120 | 2026-03-10 11:00
71 | Hathazari | 132 | 140 | 2026-03-17 06:00 | 127 | 2026-03-05 13:00
72 | Hatirjheel | 132 | 139 | 2026-03-10 04:00 | 119 | 2026-03-11 12:00
73 | Ishurdi | 132 | 142 | 2026-03-21 01:00 | 130 | 2026-03-10 16:00
74 | Jaldhaka | 132 | 143 | 2026-03-21 01:00 | 113 | 2026-03-05 12:00
75 | Jamalpur | 132 | 144 | 2026-03-15 23:00 | 111 | 2026-03-03 17:00
76 | Jashore | 132 | 140 | 2026-03-22 02:00 | 114 | 2026-03-28 18:30
77 | Jhenaidah | 132 | 141 | 2026-03-22 06:00 | 115 | 2026-03-06 13:00
78 | Jhenaidah-230 | 132 | 141 | 2026-03-22 04:00 | 121 | 2026-03-31 19:30
79 | Joydebpur | 132 | 144 | 2026-03-18 18:30 | 117 | 2026-03-11 12:00
80 | Joypurhat | 132 | 141 | 2026-03-21 00:00 | 116 | 2026-03-05 10:00
81 | Juldah | 132 | 139 | 2026-03-22 00:00 | 124 | 2026-03-10 11:00
82 | Kabirpur | 132 | 146 | 2026-03-18 18:00 | 114 | 2026-03-02 10:00
83 | Kachua | 132 | 138 | 2026-03-19 06:00 | 123 | 2026-03-04 15:00
84 | Kaliakoir | 132 | 144 | 2026-03-18 18:00 | 124 | 2026-03-31 11:00
85 | Kaliganj | 132 | 140 | 2026-03-01 06:00 | 120 | 2026-03-22 10:00
86 | Kallyanpur | 132 | 142 | 2026-03-18 19:30 | 120 | 2026-03-02 10:00
87 | Kalurghat | 132 | 140 | 2026-03-22 02:00 | 127 | 2026-03-05 15:00
88 | Kamrangirchar | 132 | 143 | 2026-03-03 18:00 | 117 | 2026-03-31 11:00
89 | Kaptai | 132 | N/A | N/A | N/A | N/A
90 | Kasba | 132 | 139 | 2026-03-19 00:00 | 119 | 2026-03-11 11:00
91 | Kazla | 132 | 141 | 2026-03-13 21:00 | 117 | 2026-03-05 13:00
92 | Keranigonj | 132 | 143 | 2026-03-18 20:00 | 122 | 2026-03-02 10:00
93 | Khagrachori | 132 | 139 | 2026-03-19 03:00 | 125 | 2026-03-10 11:00
94 | Khulna | 132 | 142 | 2026-03-21 04:00 | 120 | 2026-03-13 19:00
95 | Khulna(S) | 132 | 142 | 2026-03-19 06:00 | 124 | 2026-03-27 19:00
96 | Khulshi | 132 | 138 | 2026-03-17 06:00 | 122 | 2026-03-10 11:00
97 | Kishoreganj | 132 | 139 | 2026-03-18 19:00 | 118 | 2026-03-11 13:00
98 | Kodda | 132 | 143 | 2026-03-20 11:00 | 118 | 2026-03-09 14:00
99 | Korerhat | 132 | 139 | 2026-03-19 01:00 | 125 | 2026-03-11 10:00
100 | KSRM | 132 | 140 | 2026-03-22 09:00 | 124 | 2026-03-10 11:00
101 | Kulaura | 132 | 140 | 2026-03-28 08:00 | 128 | 2026-03-07 14:00
102 | Kurigram | 132 | 143 | 2026-03-21 02:00 | 110 | 2026-03-25 19:00
103 | Kushtia | 132 | 139 | 2026-03-18 22:00 | 121 | 2026-03-10 13:00
104 | Laksam | 132 | 139 | 2026-03-16 06:00 | 122 | 2026-03-04 14:00
105 | Lakshmipur | 132 | 137 | 2026-03-19 01:00 | 120 | 2026-03-10 11:00
106 | Lalbag | 132 | 142 | 2026-03-03 18:00 | 121 | 2026-03-11 12:00
107 | Lalmonirhat | 132 | 138 | 2026-03-12 07:00 | 115 | 2026-03-05 12:00
108 | Madanganj | 132 | 143 | 2026-03-20 12:00 | 119 | 2026-03-11 12:00
109 | Madaripur | 132 | 140 | 2026-03-19 00:00 | 127 | 2026-03-10 15:00
110 | Madartek | 132 | 138 | 2026-03-05 06:00 | 118 | 2026-03-11 12:00
111 | Madunaghat | 132 | 140 | 2026-03-17 06:00 | 128 | 2026-03-04 14:00
112 | Magura | 132 | 139 | 2026-03-01 06:00 | 118 | 2026-03-24 19:00
113 | Mahasthangarh | 132 | 142 | 2026-03-21 01:00 | 122 | 2026-03-02 09:00
114 | Maijdee | 132 | 137 | 2026-03-19 01:00 | 120 | 2026-03-10 11:00
115 | Manikganj | 132 | 140 | 2026-03-18 19:00 | 113 | 2026-03-11 12:00
116 | Maniknagar | 132 | 142 | 2026-03-13 21:00 | 118 | 2026-03-05 13:00
117 | Matarbari | 132 | 134 | 2026-03-17 06:00 | 104 | 2026-03-26 19:30
118 | Matuail | 132 | 143 | 2026-03-13 21:00 | 116.4 | 2026-03-12 16:00
119 | Metrorail_Motijheel | 132 | 142 | 2026-03-13 21:00 | 118 | 2026-03-05 13:00
120 | Metrorail_Uttara | 132 | 141 | 2026-03-18 20:00 | 118 | 2026-03-02 10:00
121 | Millgate | 132 | 142 | 2026-03-18 18:30 | 118 | 2026-03-11 12:00
122 | Mirpur | 132 | 142 | 2026-03-19 01:00 | 119 | 2026-03-31 11:00
123 | Mirzapur | 132 | 140 | 2026-03-18 18:30 | 117 | 2026-03-31 11:00
124 | Mithapukur | 132 | 143 | 2026-03-21 01:00 | 117 | 2026-03-05 12:00
125 | MI_Cement | 132 | 143.4 | 2026-03-19 01:00 | 117 | 2026-03-10 11:00
126 | Modern | 132 | N/A | N/A | N/A | N/A
127 | Mogbazar | 132 | 139 | 2026-03-10 04:00 | 120 | 2026-03-11 12:00
128 | Mongla | 132 | 142 | 2026-03-20 17:00 | 115 | 2026-03-25 19:00
129 | Motijheel | 132 | 141 | 2026-03-13 21:00 | 118 | 2026-03-05 12:00
130 | Muktagacha | 132 | 143 | 2026-03-15 23:00 | 112 | 2026-03-03 17:00
131 | Munshiganj | 132 | 141 | 2026-03-18 18:30 | 117 | 2026-03-11 11:00
132 | Muradnagar | 132 | 140 | 2026-03-19 01:00 | 119 | 2026-03-11 11:00
133 | Mymensingh | 132 | 142 | 2026-03-15 23:00 | 114 | 2026-03-03 17:00
134 | Nabinagar | 132 | 145 | 2026-03-30 18:00 | 120 | 2026-03-31 11:00
135 | Naogaon | 132 | 145 | 2026-03-21 | 120 | 2026-03-05 12:00
136 | Narail | 132 | 140 | 2026-03-28 03:00 | 114 | 2026-03-28 18:30
137 | Narinda | 132 | 0 | 2026-03-01 00:00 | N/A | N/A
139 | Narshingdi | 132 | 140 | 2026-03-18 18:30 | 113 | 2026-03-11 12:00
140 | Natore | 132 | 139 | 2026-03-21 00:00 | 125 | 2026-03-10 13:00
141 | Nawabganj | 132 | 142 | 2026-03-18 20:00 | 121 | 2026-03-11 12:00
142 | Netrakona | 132 | 141 | 2026-03-16 00:00 | 108 | 2026-03-04 17:00
143 | New | 132 | 143 | 2026-03-17 06:00 | 119 | 2026-03-11 11:00
144 | Niamatpur | 132 | 142 | 2026-03-21 01:00 | 126 | 2026-03-13 12:00
145 | Noapara | 132 | 141 | 2026-03-21 05:00 | 115 | 2026-03-31 19:00
146 | Pabna | 132 | 140 | 2026-03-21 01:00 | 127 | 2026-03-10 12:00
147 | Palashbari | 132 | 143 | 2026-03-21 02:00 | 116 | 2026-03-11 17:00
148 | Panchagarh | 132 | 144 | 2026-03-21 01:00 | 117 | 2026-03-05 11:00
149 | Patiya | 132 | 139 | 2026-03-17 06:00 | 124 | 2026-03-04 21:00
150 | Patuakhali | 132 | 138 | 2026-03-19 01:00 | 128 | 2026-03-10 12:00
151 | Payra | 132 | 140 | 2026-03-19 01:00 | 131 | 2026-03-31 11:00
152 | PHP | 132 | 137 | 2026-03-19 01:00 | 123 | 2026-03-10 11:00
153 | Postogola | 132 | 144 | 2026-03-18 20:00 | 120 | 2026-03-10 11:00
154 | Pubail | 132 | 146 | 2026-03-18 18:00 | 124 | 2026-03-12 16:00
155 | Purbachal | 132 | 142 | 2026-03-18 18:30 | 118 | 2026-03-11 12:00
156 | Purbasadipur | 132 | 143 | 2026-03-21 01:00 | 116 | 2026-03-25 19:00
157 | Rahanpur | 132 | 142 | 2026-03-21 01:00 | 128 | 2026-03-13 12:00
158 | Rahanpur-400 | 132 | 142 | 2026-03-21 01:00 | 128 | 2026-03-13 12:00
159 | Rahim | 132 | 142 | 2026-03-20 12:00 | 119 | 2026-03-11 12:00
160 | Rajbari | 132 | 138 | 2026-03-06 12:00 | 122 | 2026-03-10 15:00
161 | Rajendrapur | 132 | 143 | 2026-03-20 11:00 | 121 | 2026-03-11 12:00
162 | Rajshahi | 132 | 138 | 2026-03-21 | 124 | 2026-03-10 12:00
163 | Rajshahi-230 | 132 | 140 | 2026-03-22 03:00 | 125 | 2026-03-25 13:00
164 | Ramganj | 132 | 137 | 2026-03-19 01:00 | 119 | 2026-03-04 15:00
165 | Rampur | 132 | 139 | 2026-03-22 00:00 | 122 | 2026-03-10 11:00
166 | Rampura | 132 | 139 | 2026-03-05 06:00 | 120 | 2026-03-11 12:00
167 | Rangamati | 132 | 139 | 2026-03-17 06:00 | 126 | 2026-03-10 11:00
168 | Rangpur | 132 | 142 | 2026-03-21 01:00 | 118 | 2026-03-05 12:00
169 | Ruppur | 132 | 141 | 2026-03-21 03:00 | 129 | 2026-03-10 16:00
170 | Saidpur | 132 | 142 | 2026-03-21 02:00 | 116 | 2026-03-05 10:00
171 | Satkhira | 132 | 141 | 2026-03-17 01:00 | 116 | 2026-03-27 19:00
172 | Satmasjid | 132 | 140 | 2026-03-03 06:00 | 120 | 2026-03-02 10:00
173 | Savar | 132 | 141 | 2026-03-18 20:00 | 117 | 2026-03-02 10:00
174 | SevenRings | 132 | 146 | 2026-03-18 19:00 | 124 | 2026-03-11 12:00
175 | ShahCement | 132 | 142 | 2026-03-18 18:30 | 118 | 2026-03-11 12:00
176 | Shahjadpur | 132 | 142 | 2026-03-19 04:00 | 129 | 2026-03-11 13:00
177 | Shahjibazar | 132 | 142 | 2026-03-13 14:00 | 119 | 2026-03-11 12:00
178 | Shahmirpur | 132 | 139 | 2026-03-17 06:00 | 126 | 2026-03-04 20:00
179 | Shariatpur | 132 | 140 | 2026-03-19 00:00 | 125 | 2026-03-10 13:00
180 | Sherpur | 132 | 142 | 2026-03-21 02:00 | 106 | 2026-03-26 15:00
181 | Shikalbaha | 132 | 129 | 2026-03-22 04:00 | 116 | 2026-03-10 11:00
182 | Shikalbaha-230 | 132 | 140 | 2026-03-21 14:00 | 126 | 2026-03-10 11:00
183 | Shitalakhya | 132 | 143.4 | 2026-03-19 01:00 | 117 | 2026-03-10 11:00
184 | Sholosohor | 132 | 139 | 2026-03-17 06:00 | 126 | 2026-03-10 11:00
185 | Shyampur | 132 | 139 | 2026-03-22 17:00 | 119 | 2026-03-11 11:00
186 | Shyampur-230 | 132 | 140 | 2026-03-21 15:00 | 121 | 2026-03-10 11:00
187 | Siddhirganj | 132 | 143 | 2026-03-13 21:00 | 120 | 2026-03-11 11:00
188 | Sirajganj | 132 | 142 | 2026-03-21 02:00 | 116 | 2026-03-11 17:00
189 | Sonargaon | 132 | 142 | 2026-03-18 19:00 | 112 | 2026-03-12 14:00
190 | Sreemongol | 132 | 138 | 2026-03-20 11:00 | 121 | 2026-03-11 20:00
191 | Sreepur | 132 | 143 | 2026-03-16 00:00 | 125 | 2026-03-11 12:00
192 | Srinagar | 132 | 143 | 2026-03-04 05:00 | 122 | 2026-03-11 12:00
193 | SSM | 132 | 142 | 2026-03-17 06:00 | 125 | 2026-03-04 10:00
194 | Sunamganj | 132 | 139 | 2026-03-28 07:00 | 118 | 2026-03-12 21:00
195 | Sylhet | 132 | 139 | 2026-03-28 07:00 | 122 | 2026-03-12 21:00
196 | Sylhet-132 | 132 | 138 | 2026-03-28 07:00 | 125 | 2026-03-10 13:00
197 | Tangail | 132 | 141 | 2026-03-15 23:00 | 115 | 2026-03-11 13:00
198 | Taraganj | 132 | 142 | 2026-03-21 01:00 | 115 | 2026-03-05 12:00
199 | Tasnim | 132 | 142 | 2026-03-13 21:00 | 117 | 2026-03-11 12:00
200 | Thakurgaon | 132 | 144 | 2026-03-21 01:00 | 114 | 2026-03-05 11:00
201 | TK | 132 | 140 | 2026-03-21 16:00 | 126 | 2026-03-10 11:00
202 | Tongi | 132 | 145 | 2026-03-17 06:00 | 122 | 2026-03-11 11:00
203 | Ullahpara | 132 | 141 | 2026-03-21 01:00 | 124 | 2026-03-10 13:00
204 | Ullon | 132 | 138 | 2026-03-05 06:00 | 120 | 2026-03-11 12:00
205 | Uttara | 132 | 142 | 2026-03-19 01:00 | 118 | 2026-03-31 11:00
206 | UttaraNew | 132 | 141 | 2026-03-18 20:00 | 118 | 2026-03-02 10:00
207 | Zigatola | 132 | 143 | 2026-03-03 07:00 | 122 | 2026-03-11 12:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-36
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: March 2026
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Aminbazar 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 03-03-2026 | 16:00 | 431 | 144 | 87.3883
Aminbazar 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 03-03-2026 | 16:00 | 431 | 144 | 87.3883
Aminbazar 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 520 | 03-03-2026 | 16:00 | 431 | 144 | 87.3883
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 325 | 01-03-2026 | 00:00 | 0 | 0 | 0
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 01-03-2026 | 11:00 | 274 | 128 | 58.1584
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 01-03-2026 | 11:00 | 274 | 128 | 58.1584
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 520 | 27-03-2026 | 12:00 | 173 | 29 | 33.7334
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 520 | 27-03-2026 | 12:00 | 164 | 22 | 31.821
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 750 | 08-03-2026 | 04:00 | 380 | 98 | 52.3245
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 750 | 11-03-2026 | 17:00 | 563 | 168 | 78.3375
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 750 | 11-03-2026 | 17:00 | 563 | 168 | 78.3375
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 325 | 31-03-2026 | 21:00 | 187 | 58 | 60.2425
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 325 | 31-03-2026 | 21:00 | 187 | 58 | 60.2425
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 325 | 31-03-2026 | 21:00 | 187 | 58 | 60.2425
Gopalganj 400/230kV Grid Sub-Station | ATR-04 | 400/230 | 750 | 17-03-2026 | 21:00 | 126 | 86 | 20.3402
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 520 | 12-03-2026 | 13:00 | 296 | 178 | 66.4228
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 520 | 12-03-2026 | 13:00 | 296 | 178 | 66.4228
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 325 | 07-03-2026 | 22:00 | 285 | 69 | 90.2258
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 325 | 07-03-2026 | 22:00 | 285 | 69 | 90.2258
Madunaghat 400/230kV Grid Sub-Station | ATR-1 7006T | 400/230 | 750 | 30-03-2026 | 11:00 | 311 | 143 | 45.6401
Madunaghat 400/230kV Grid Sub-Station | ATR-2 7106T | 400/230 | 750 | 30-03-2026 | 11:00 | 311 | 143 | 45.6401
Madunaghat 400/230kV Grid Sub-Station | ATR-3 7206T | 400/230 | 750 | 30-03-2026 | 11:00 | 311 | 143 | 45.6401
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 750 | 03-03-2026 | 16:00 | 448 | 184 | 64.5752
Meghnaghat 400/230kV Grid Sub-Station | ATR-2 | 400/230 | 750 | 06-03-2026 | 10:00 | 499 | 225 | 72.9841
Meghnaghat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 750 | 06-03-2026 | 10:00 | 508 | 223 | 73.9721
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 520 | 11-03-2026 | 19:30 | 348 | 59 | 67.8781
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 520 | 10-03-2026 | 13:00 | 363 | 56 | 70.6335
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 325 | 31-03-2026 | 13:00 | 210 | 53 | 66.6415
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 325 | 27-03-2026 | 22:00 | 138 | 34 | 43.7313
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 520 | 15-03-2026 | 04:00 | 127 | 30 | 25.0952
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 520 | 15-03-2026 | 04:00 | 127 | 30 | 25.0952
Koerhat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 1000 | 29-03-2026 | 20:00 | 314 | 14 | 31.4312
Koerhat 400/132kV Grid Sub-Station | ATR-4 | 400/230 | 1000 | 29-03-2026 | 20:00 | 314 | 14 | 31.4312
Koerhat 400/132kV Grid Sub-Station | ATR-2 | 400/132 | 325 | 16-02-2026 | 17:00 | 0 | 0 | 0
Koerhat 400/132kV Grid Sub-Station | ATR-3 | 400/132 | 325 | 29-03-2026 | 22:00 | 138 | 72 | 47.8934
Mirsharai 400/230 kV Grid Sub-Station | ATR-1 | 400/230 | 1000 | 14-03-2026 | 19:00 | 135 | 87 | 16.0605
Mirsharai 400/230 kV Grid Sub-Station | ATR-2 | 400/230 | 1000 | ------- |  |  |  | 0
Ashuganj 400/230 kV GIS Grid Sub-Station | Interbus-1 | 400/230 | 325 | ------- |  |  |  | 0
Ashuganj 400/230 kV GIS Grid Sub-Station | Interbus-2 | 400/230 | 325 | ------- |  |  |  | 0
Amtali 400/132kV Grid Sub-Station
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 300 | 30-03-2026 | 15:00 | 182 | 69 | 64.8802
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 300 | 30-03-2026 | 15:00 | 182 | 69 | 64.8802
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 225 | 03-03-2026 | 21:00 | 186 | 82 | 83.2263
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 225 | 03-03-2026 | 21:00 | 186 | 82 | 83.2263
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 225 | 03-03-2026 | 21:00 | 186 | 82 | 83.2263
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 300 | 12-03-2026 | 20:00 | 226 | 96 | 81.8481
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 300 | 27-03-2026 | 13:00 | 175 | 62 | 61.8861
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 300 | 13-03-2026 | 21:00 | 148 | 20 | 49.7817
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 225 | 11-03-2026 | 19:00 | 165 | 30 | 74.5356
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 225 | 19-03-2026 | 18:00 | 119 | 54 | 58.0796
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 225 | 28-03-2026 | 18:00 | 127 | 63 | 63.0077
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 300 | 09-03-2026 | 13:00 | 160 | 69 | 58.0814
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 18-03-2026 | 22:00 | 86 | 22 | 29.5898
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 18-03-2026 | 22:00 | 86 | 22 | 29.5898
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 225 | 17-03-2026 | 06:00 | 100 | 29 | 46.2756
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 225 | 17-03-2026 | 06:00 | 100 | 29 | 46.2756
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 225 | 12-03-2026 | 04:00 | 166 | 56 | 77.8628
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 225 | 12-03-2026 | 04:00 | 166 | 56 | 77.8628
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 300 | 12-03-2026 | 04:00 | 224 | 77 | 78.955
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 300 | 12-03-2026 | 04:00 | 224 | 77 | 78.955
Naogaon 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | ------- |  |  |  | 0
Naogaon 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | ------- |  |  |  | 0
Naogaon 230/132kV Grid Sub-Station | ATR-3 | 230/132 | 300 | ------- |  |  |  | 0
Purbasadipur 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | ------- |  |  |  | 0
Purbasadipur 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | ------- |  |  |  | 0
Purbasadipur 230/132kV Grid Sub-Station | ATR-3 | 230/132 | 300 | ------- |  |  |  | 0
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 225 | 23-03-2026 | 19:30 | 97 | 50 | 48.5015
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 225 | 24-03-2026 | 18:30 | 97 | 42 | 46.9788
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 225 | 23-03-2026 | 19:30 | 105 | 50 | 51.6876
Chowmohani 230/132 kV Grid Sub-Station | ATR-1 | 230/132 | 350 | 12-03-2026 | 12:00 | 82 | 19 | 24.0493
Chowmohani 230/132 kV Grid Sub-Station | ATR-2 | 230/132 | 350 | 06-03-2026 | 13:00 | 94 | 25 | 27.7908
Chowmohani 230/132 kV Grid Sub-Station | ATR-3 | 230/132 | 350 | 06-03-2026 | 13:00 | 94 | 25 | 27.7908
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 300 | 27-03-2026 | 19:00 | 166 | 56 | 58.3971
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 300 | 27-03-2026 | 19:00 | 184 | 68 | 65.3877
Feni 230/132 kV GIS Grid Sub-Station | ATR-1 | 230/132 | 300 | 19-03-2026 | 18:30 | 53 | 3 | 17.6949
Feni 230/132 kV GIS Grid Sub-Station | ATR-2 | 230/132 | 300 | 13-02-2026 | 13:00 | 46 | 13 | 15.9339
Feni 230/132 kV GIS Grid Sub-Station | ATR-3 | 230/132 | 300 | 13-02-2026 | 13:00 | 46 | 13 | 15.9339
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 125 | 12-03-2026 | 07:00 | 95 | 0 | 76
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 125 | 12-03-2026 | 07:00 | 95 | 0 | 76
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 225 | 16-03-2026 | 00:00 | 112 | 106 | 68.5367
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 225 | 16-03-2026 | 00:00 | 120 | 107 | 71.4561
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 225 | 16-03-2026 | 00:00 | 115 | 110 | 70.7281
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 225 | 28-03-2026 | 12:00 | 127 | 60 | 62.4266
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 225 | 28-03-2026 | 12:00 | 127 | 60 | 62.4266
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 225 | 05-03-2026 | 15:00 | 109 | 55 | 54.2623
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 150 | 25-03-2026 | 18:00 | 96 | 38 | 68.8315
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 150 | 01-03-2026 | 00:00 | 0 | 0 | 0
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 150 | 15-03-2026 | 19:00 | 86 | 43 | 64.1006
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 150 | 15-03-2026 | 19:00 | 86 | 43 | 64.1006
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 225 | 02-03-2026 | 17:00 | 106 | 51 | 52.2803
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 225 | 02-03-2026 | 17:00 | 106 | 50 | 52.0892
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 225 | 01-03-2026 | 00:00 | 0 | 0 | 0
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 300 | 31-03-2026 | 19:00 | 225 | 54 | 77.1298
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 300 | 14-03-2026 | 11:00 | 236 | 20 | 78.9486
Kaliakoir 230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 300 | 06-03-2026 | 22:00 | 207 | 156 | 86.4002
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 02-03-2026 | 14:00 | 198 | 73 | 70.3428
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 02-03-2026 | 14:00 | 198 | 73 | 70.3428
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 01-03-2026 | 00:00 | 0 | 0 | 0
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 225 | 01-03-2026 | 19:00 | 164 | 39 | 74.9215
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 225 | 01-03-2026 | 19:00 | 164 | 39 | 74.9215
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 300 | 01-03-2026 | 19:00 | 212 | 45 | 72.2411
Madunaghat 230/132/33kV Grid Sub-Station | ATR-1(705T) | 230/132 | 300 | 15-03-2026 | 19:30 | 126 | 15 | 42.2966
Madunaghat 230/132/33kV Grid Sub-Station | ATR-2(715T) | 230/132 | 300 | 15-03-2026 | 19:30 | 126 | 15 | 42.2966
Madunaghat 230/132/33kV Grid Sub-Station | ATR-3(725T) | 230/132 | 300 | 15-03-2026 | 19:30 | 126 | 15 | 42.2966
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 300 | 10-03-2026 | 14:00 | 178 | 75 | 64.3851
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 300 | 10-03-2026 | 14:00 | 178 | 75 | 64.3851
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 300 | 09-03-2026 | 08:00 | 99 | 9 | 33.1361
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 300 | 20-03-2026 | 04:00 | 98 | 10 | 32.8363
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 300 | 01-03-2026 | 00:00 | 1 | 1 | 0.4714
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 300 | 01-03-2026 | 00:00 | 0 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 230/132 | 450 | 11-03-2026 | 14:00 | 262 | 34 | 58.7104
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 230/132 | 450 | 11-03-2026 | 14:00 | 262 | 34 | 58.7104
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 230/132 | 450 | 11-03-2026 | 14:00 | 262 | 34 | 58.7104
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 15-03-2026 | 18:30 | 228 | 150 | 90.9725
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 30-03-2026 | 14:00 | 224 | 154 | 90.6103
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 300 | 15-03-2026 | 12:00 | 90 | 45 | 33.541
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 300 | 15-03-2026 | 12:00 | 90 | 45 | 33.541
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 300 | 11-03-2026 | 10:00 | 131 | 68 | 49.1991
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 300 | 03-03-2026 | 22:00 | 129 | 61 | 47.5652
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 300 | 10-03-2026 | 17:00 | 259 | 115 | 94.461
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 300 | 10-03-2026 | 17:00 | 259 | 115 | 94.461
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 14-03-2026 | 18:30 | 205 | 24 | 91.7334
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 15-03-2026 | 17:00 | 188 | 32 | 84.7573
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 15-03-2026 | 17:00 | 188 | 32 | 84.7573
Tongi 230/132/33kV Grid Sub-Station | T-04 | 230/132 | 450 |  |  |  |  | 0
Bhulta 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 15-03-2026 | 0:00 | 145 | 27 | 49.1641
Bhulta 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 15-03-2026 | 0:00 | 145 | 27 | 49.1641
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF_LDC_37
|  |  |  | POWER GRID BANGLADESH PLC. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID BANGLADESH PLC. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [12 empty] | Report on load shedding
Month: March-2026 |  |  |  | (For Evening Peak) | [10 empty] | Month: March-2026 |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur
2026-03-01 | 12760.03 | 12760.03 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-01 | 12060.25 | 12060.25 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-02 | 12921 | 12921 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-02 | 12529.17 | 12529.17 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-03 | 12957.59 | 12967.59 | 10 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | - | 2026-03-03 | 12436.75 | 12436.75 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-04 | 12757.4 | 12775.4 | 17 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | - | 2026-03-04 | 12364.74 | 12364.74 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-05 | 13104.3 | 13104.3 | 0 | 20:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-05 | 12226.63 | 12453.63 | 217 | 12:00 Hr. | 120 | 0 | 0 | 20 | 0 | 52 | 0 | 0 | 25 | -
2026-03-06 | 12749.4 | 12749.4 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-06 | 11475.99 | 11475.99 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-07 | 13746.98 | 13746.98 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-07 | 11734.42 | 11902.42 | 161 | 12:00 Hr. | 71 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 30 | -
2026-03-08 | 13910.45 | 13910.45 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-08 | 12624.34 | 12903.34 | 267 | 12:00 Hr. | 74 | 0 | 88 | 25 | 34 | 0 | 0 | 0 | 46 | -
2026-03-09 | 13917.31 | 13917.31 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-09 | 12641.8 | 12735.8 | 90 | 12:00 Hr. | 10 | 0 | 20 | 60 | 0 | 0 | 0 | 0 | 0 | -
2026-03-10 | 14565.3 | 14565.3 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-10 | 12846.29 | 13153.29 | 294 | 12:00 Hr. | 224 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 60 | - | 0
2026-03-11 | 14856.09 | 14960.09 | 100 | 21:00 Hr. | 0 | 40 | 15 | 25 | 10 | 10 | 0 | 0 | 0 | - | 2026-03-11 | 13333.42 | 13624.42 | 278 | 12:00 Hr. | 0 | 90 | 40 | 25 | 0 | 43 | 0 | 45 | 35 | -
2026-03-12 | 14100.59 | 14136.59 | 34 | 21:00 Hr. | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-12 | 12258.15 | 12483.15 | 215 | 12:00 Hr. | 105 | 90 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-13 | 12353 | 12353 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-13 | 11000.61 | 11000.61 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-14 | 14539 | 14560 | 20 | 19:30 Hr | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-14 | 11805.15 | 11805.15 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-15 | 14128.14 | 14150.14 | 21 | 19:30 Hr | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-15 | 12036.3 | 12355.3 | 305 | 12:00 Hr. | 240 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-16 | 13804.4 | 13880.4 | 73 | 19:30 Hr | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-16 | 11578 | 11964 | 369 | 12:00 Hr. | 205 | 85 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-17 | 13456.7 | 13456.7 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-17 | 11284.47 | 11284.47 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-18 | 11495.64 | 11495.64 | 0 | 18:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-18 | 11702.81 | 11702.81 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-19 | 11630.91 | 11630.91 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-19 | 9012.51 | 9012.51 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-20 | 8758 | 8758 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-20 | 7934.87 | 7934.87 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-21 | 8067.71 | 8067.71 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-21 | 8045.26 | 8045.26 | 0 | 09:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-22 | 8788.74 | 8788.74 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-22 | 7128.84 | 7128.84 | 0 | 09:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-23 | 9782.5 | 9782.5 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-23 | 8047.35 | 8047.35 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-24 | 10590 | 10590 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-24 | 9271.17 | 9271.17 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-25 | 10950.74 | 10950.74 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-25 | 10112.17 | 10112.17 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-26 | 12142.31 | 12142.31 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-26 | 10282.32 | 10282.32 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-27 | 12729.5 | 12729.5 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-27 | 11055.38 | 11055.38 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-28 | 12401.75 | 12401.75 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-28 | 10404.39 | 10404.39 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-29 | 13418.66 | 13418.66 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-29 | 12175.48 | 12175.48 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-03-30 | 13035 | 13370.2 | 100 | 19:30 Hr. | 20 | 0 | 0 | 20 | 0 | 30 | 15 | 0 | 15 | - | 2026-03-30 | 12435.5 | 12701.5 | 255 | 12:00 Hr. | 200 | 25 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | -
2026-03-31 | 13839.85 | 13999.38 | 39 | 19:30 Hr. | 0 | 0 | 8 | 31 | 0 | 0 | 0 | 0 | 0 | - | 2026-03-31 | 12570.15 | 12905.15 | 321 | 12:00 Hr. | 214 | 28 | 47 | 32 | 0 | 0 | 0 | 0 | 0 | -
[16 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: March 2026
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 14856.09 | 2026-03-11 | 21:00 Hr.
2 | Maximum Day Peak Genaration | MW | 13333.42 | 2026-03-11 | 12:00 Hr.
3 | Maximum Evening Peak Demand | MW | 14960.09 | 2026-03-11 | 21:00 Hr.
4 | Minimum Generation | MW | 5964.82 | 2026-03-22 | 06:00 Hr.
5 | Average of the daily evening peak Genaration | MW | 12524.5352 | - | -
6 | Average of the daily day peak Genaration | MW | 11174.6671 | - | -
7 | Maximum load shed (Evening Peak) | MW | 100 | 2026-03-11 | 21:00 Hr.
8 | Minimum load shed | MW | 10 | 2026-03-03 | 19:30 Hr.
9 | Total nos. of load shed days | Day | 9 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 13.3548 | - | -
11 | Total Generation | MkWh | 8317.0187 | - | -
12 | Total Generation by BPDB | MkWh | 885.5136 | % of total Gen. | 10.65%
13 | Total Generation by IPP | MkWh | 2322.2578 | '' | 27.92%
14 | A) Total Generation by Generation Companies | MkWh | 3481.2826 | '' | 41.86%
| B) Total Generation by REB | MkWh | 49.7992 | " | 0.5988%
| C) Total Generation by RENTAL | MkWh | 54.0965 | " | 0.6504%
| D) Total Imported from India (BIPTC) | MkWh | 607.5338 | " | 7.305%
| E) Total Imported from Tripura, India (A.C) | MkWh | 94.6877 | " | 1.138%
| F) Total Imported from Nepal | MkWh | 0 | " | 0%
| E) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 821.8475 | " | 9.882%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3548.1844 | % of total Gen. | 42.66%
| B) Oil | MkWh | 438.8774 | '' | 5.277%
| C) Hydro | MkWh | 56.2631 | '' | 0.6765%
| D) Solar | MkWh | 120.8884 | '' | 1.454%
| E) Coal | MkWh | 2624.9585 | '' | 31.56%
| F) BIPTC (Import from India) | MkWh | 607.5338 | '' | 7.305%
| G) A.C (Import from Tripura, India) | MkWh | 94.6877 | '' | 1.138%
| H) Total Imported from Nepal | MkWh | 0 | '' | 0%
| I) Adani (Import from India) | MkWh | 821.8475 | '' | 9.882%
| J) Wind | MkWh | 3.7781 | '' | 0.04543%
16 | Maximun of the daily total Generation . | MkWh | 320.2188 | 2026-03-11
17 | Monthly Load factor | % | 75.2472 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 47875.4925 | - | -
| A) Gas | M.Taka | 12284.418 | - | -
| B) Coal | M.Taka | 17377.8847 | - | -
| C) HFO | M.Taka | 7544.8101 | - | -
| D) HSD | M.Taka | 0 | - | -
| E) Hydro | M.Taka | 5.6263 | - | -
| F) Solar | M.Taka | 1929.4128 | - | -
| G) Total Import | M.Taka | 8677.7652 | - | -
| H) Wind | M.Taka | 55.5756 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2133.5824 | 2026-03-11
| A) Gas | M.Taka | 540.6046 | 2026-03-24
| B) Coal | M.Taka | 775.6691 | 2026-03-31
| C) HFO | M.Taka | 657.03 | 2026-03-11
| D) HSD | M.Taka | 0 | 2026-03-01 | -
| E) Hydro | M.Taka | 0.19455 | 2026-03-03 | -
| F) Solar | M.Taka | 85.7463 | 2026-03-26 | -
| G) Total Import | M.Taka | 341.3628 | 2026-03-10
| H) Wind | M.Taka | 5.924 | 2026-03-13
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 5.7563
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 5.8843
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 93.15 | 31/3/2026 | 06:00
b) | Actual | FT (MSL) | 91.74 | 31/3/2026 | 06:00
22 | Peak Genaration of March 2025 | MW | 15336.92 | 2025-03-15 | 21:00 Hr.
23 | Peak Demand of March 2025 | MW | 15376.92 | 2025-03-15 | 21:00 Hr.
24 | Maximum peak Generation recorded upto 31/03/2026 | MW | 16794 | 2025-07-23 | 21:00
25 | Maximum peak Demand recorded upto 31/03/2026 | MW | 16794 | 2025-07-23 | 21:00
26 | Maximum load shed recorded upto 31/03/2026 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## FGMO Weekly
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status | [57 empty] | SR at 50 Hz (MW)
SL | Plant Name | Owner | Fuel | Installed capacity (MW) | Capability Status of Last Week | 26.03.2026 | 19.03.2026 | 12.03.2026 | 05.03.2026 | 26.02.2026 | 19.02.2026 | 12.02.2026 | 05.02.2026 | 29.01.2026 | 22.01.2026 | 15.01.2026 | 08.01.2026 | 01.01.2026 | 25.12.2025 | 18.12.2025 | 11.12.2025 | 04.12.2025 | 27.11.2025 | 20.11.2025 | 13.11.2025 | 06.11.2025 | 30.10.2025 | 23.10.2025 | 16.10.2025 | 09.10.2025 | 02.10.2025 | 25.09.2025 | 18.09.2025 | 11.09.2025 | 04.09.2025 | 28.08.2025 | 21.08.2025 | 14.08.2025 | 07.08.2025 | 31.07.2025 | 24.07.2025 | 17.07.2025 | 10.07.2025 | 03.07.2025 | 26.06.2025 | 19.06.2025 | 12.06.2025 | 05.06.2025 | 29.05.2025 | 22.05.2025 | 15.05.2025 | 08.05.2025 | 01.05.2025 | 24.04.2025 | 17.04.2025 | 10.04.2025 | 03.04.2025 | 27.03.2025 | 20.03.2025 | 13.03.2025 | 06.03.2025 | 27.02.2025 | 20.02.2025 | 13.02.2025 | 06.02.2025 | 30.01.2025 | 23.01.2025 | 16.01.2025 | 09.01.2025 | 02.01.2025 | 28.11.2024 | 21.11.2024 | 14.11.2024 | 07.11.2024 | 31.10.2024 | 24.10.2024 | 17.10.2024 | 10.10.2024 | 03.10.2024 | 26.09.2024 | 19.09.2024 | 05.09.2024 | 12.09.2024 | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 | Capable | 15 | 15 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 | Capable | 30 | 30 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220 | Capable | [32 empty] | 20 | 20 | [7 empty] | 20 | [41 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220 | Capable | [13 empty] | 20 | 20 | [18 empty] | 20 | [5 empty] | 20 | 20 | 20 | 20 | [40 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305 | Capable | [23 empty] | 7 | 7 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 10 | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 15 | 30 | [7 empty] | 35 | [6 empty] | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360 | Capable |  |  |  | 30 | 30 | 30 | 30 | 30 | [56 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 | Capable | 16 | 16 | 20 | 20 | 20 | 20 | 20 |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | [11 empty] | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410 | Capable | [33 empty] | 45 | [47 empty] | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
9 | Haripur 412 MW CCPP | EGCB | Gas | 412 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97 | Capable | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [24 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163 | Capable
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210 | Capable
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225 | Capable
14 | Shikalbaha Peaking GT | BPDB | Gas | 150 | Capable
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330 | Capable | [57 empty] | 40 | [20 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360 | Capable | 20 | 20 | [52 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104 | Capable | [31 empty] | 2 |  |  | 2 | 2 | [18 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
18 | Bhola 225 MW CCPP | BPDB | Gas | 194 | Capable | [36 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365 | Capable
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210 | Capable | [5 empty] | 16 | 16 |  |  | 20 | 20 | 20 | 20 |  |  | 20 | 20 | 20 |  |  |  | 20 | [10 empty] | 20 | 16 | [7 empty] | 20 | 20 | [38 empty] | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335 | Capable | [42 empty] | 30 | 30 | 30 | 30 |  | 30 | 30
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400 | Capable | 30 | 30 | 35 | 35 | 35 | 35 | [11 empty] | 30 | 30 | 30 | 30 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | [14 empty] | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231 | Capable
24 | RPCL 210 MW CCPP | IPP | Gas | 210 | Capable but not tested recently
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100 | Not Capable but feasible
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50 | Not Capable but feasible
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410 | Not Capable but feasible
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400 | Capable | [62 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274 | Not Capable but feasible
16 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 | Capable | 20 | 20 | 30 | 30 | 30 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 60 | 60 | 60 | 60 | 60 |  |  |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | [7 empty] | 20 | 20
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 | Capable | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 16 | 16 | 30 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 16 | 16 | 16 | 16 | 10 | 10 | 10 | 10 | 10
32 | Bhola Nutan Bidyut | IPP | Gas | 220 | Capable
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360 | Not Capable but feasible
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450 | Not Capable but feasible
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150 | Capable | [31 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30
36 | Anwara 300 MW PP (United) | IPP | HFO | 300 | Capable
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 | Capable
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104 | Capable
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105 | Capable
40 | Gazipur 100 MW PP | IPP | HFO | 105 | Capable
41 | United Payra Power Ltd. | IPP | HFO | 150 | Capable
42 | Madhumati 100 MW PP | IPP | HFO | 100 | Capable
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105 | Capable
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 | Capable
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300 | Capable
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55 | Capable
47 | Kodda 149 MW PP Unit-1 (Summit) | IPP | HFO | 149 | Capable
48 | Feni Lanka Power | IPP | HFO | 114 | Capable
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110 | Capable
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162 | Capable
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55 | Capable
52 | Zodiac 54 MW | IPP | HFO | 54 | Capable
53 | Anlima Energy Ltd | IPP | HFO | 116 | Capable
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115 | Capable
55 | Confidence Unit-2 Bogura | IPP | HFO | 113 | Capable
56 | Confidence Unit-1 Bogura | IPP | HFO | 113 | Capable
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54 | Capable
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55 | Capable
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149 | Capable
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115 | Capable
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55 | Capable
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 | Capable | 20 | 40 | 66 | 66 | 66 | 66 |  | 66 | 33 | 66 | 66 | 66 | 66 | 66 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 66 | 66
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 | Capable | 40 | 40 | 40 | 40 | 40 | 40 | 66 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  | 50 | 50 | 50 | 50 | 20 | 20 | 40 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 | Capable | 25 | 50 | 50 | 50 | 50 | 25 | 40 | 25 | 25 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 50 | 50 | 50 | 50
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307 | Capable | 20 | 20 | 30 | 30 | 30 | 30 | 25 | 30 | 30 | 30 | 30 | [11 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
66 | Unique Meghnaghat Power Ltd(UMPL) | IPP | Gas | 584 | Capable | 40 | 40 | 50 | 50 | 50 |  | 30 | [12 empty] | 24 | 24 | 24 |  |  |  |  | 50 | 24 | 24 | 50
67 | Meghnaghat CCPP Unit 2 (Summit) | IPP | Gas | 583 | Capable | 25 | 25 | 50 | 50 | 50 | 50 |  |  |  | 50 | 50 | 50 | 50 | 50 | 50
68 | Jera Meghnaghat Power Ltd. | IPP | Gas | 718 | Capable | [6 empty] | 50 | 70
| Payra 1320 MW Unit-2 | BCPCL |  | 622 | Capable | [46 empty] | 20 | 20
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70 | Capable
| Shajibazar 100 MW PP | BPDB |  | 100 | Not Capable but feasible
| Khulna 225 MW CCPP | NWPGCL |  | 230 | Capable but not tested recently
Total Installed capacity | [5 empty] | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 20506 | 20506 | 20506 | 20506 | 20506 | 20506 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19739 | 19739 | 19739 | 19739 | 14388 | 14388 | 14388 | 14388 | 14388 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity | [5 empty] | 6978 | 8164 | 7834 | 8174 | 8174 | 7698 | 7298 | 6286 | 4146 | 5722 | 6660 | 6754 | 7086 | 6756 | 5564 | 5851 | 5937 | 5232 | 5185 | 3503 | 3503 | 6403 | 6525 | 5821 | 6221 | 6871 | 7523 | 8031 | 7313 | 7523 | 6939 | 8121 | 8527 | 9061 | 8099 | 8099 | 7580 | 8537 | 6163 | 6795 | 6632 | 2862 | 3135 | 2325 | 2165 | 2165 | 2525 | 2855 | 2325 | 1595 | 1635 | 1072 | 1812 | 1432 | 1464 | 1064 | 592 | 1332 | 1282 | 1682 | 1302 | 1302 | 1685 | 1685 | 1315 | 1813 | 2027 | 1475 | 1475 | 1092 | 1124 | 744 | 712 | 712 | 1802 | 1492 | 1152 | 1492 | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve | [5 empty] | 349 | 394 | 489 | 519 | 519 | 490 | 455 | 419 | 256 | 359 | 399 | 429 | 443 | 398 | 365 | 358 | 358 | 328 | 324 | 228 | 228 | 351 | 372 | 349 | 379 | 427 | 477 | 471 | 451 | 477 | 427 | 459 | 452 | 503 | 386 | 404 | 382 | 452 | 356 | 424 | 408 | 262 | 288 | 218 | 193 | 193 | 202 | 232 | 212 | 152 | 137 | 92 | 172 | 142 | 144 | 109 | 67 | 137 | 132 | 167 | 137 | 137 | 162 | 162 | 122 | 160 | 179 | 132 | 132 | 107 | 109 | 79 | 77 | 77 | 172 | 137 | 107 | 137 | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO | [5 empty] | 15 | 15 | 14 |  |  | 15 | 14 | 12 | 10 | 11 | 12 | 12 | 11 | 10 | 10 | 9 | 9 | 9 | 9 | 7 | 7 | 9 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 12 | 14 | 13 | 15 | 12 | 12 | 12 | 13 | 11 | 14 | 13 | 11 | 12 | 9 | 9 | 9 | 10 | 11 | 9 | 7 | 7 | 5 | 7 | 6 | 7 | 6 | 3 | 5 | 5 | 6 | 5 | 5 | 6 | 6 | 5 | 6 | 8 | 5 | 5 | 4 | 5 | 4 | 3 | 3 | 6 | 5 | 4 | 5 | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list | [5 empty] | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 68 | 68 | 68 | 68 | 64 | 64 | 64 | 64 | 64 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list | [5 empty] | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 74 | 74 | 74 | 74 | 70 | 70 | 70 | 70 | 70 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable | [5 empty] | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 63 | 63 | 61 | 61 | 61 | 61 | 62 | 62 | 62 | 62 | 58 | 58 | 58 | 58 | 58 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible | [5 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant

## FGMO
Power Grid Bangladesh PLC.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: March 2026
SL | Plant Name | Owner | Fuel | Installed capacity | FGMO Status
|  |  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220 | [24 empty] | √ | √ | √ | √ | √ | √ | √
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360 | √ | √ | √ | √ | √ |  |  | √ | √ |  |  | √ | √ |  | √
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410 | [22 empty] | √ |  | √
9 | Haripur 412 MW CCPP | EGCB | Gas | 412 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [12 empty] | √ | √ |  |  |  | √
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225
14 | Shikalbaha Peaking GT | BPDB | Gas | 150
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360 |  |  |  |  | √ | [6 empty] | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104
18 | Bhola 225 MW CCPP | BPDB | Gas | 194
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400 | √ |  |  | √ | [5 empty] | √ |  | √ |  |  | √ | √ | √ | √ | √ | √ |  | √ |  |  | √ | √ | √ | √ | √ | √ | √
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231
24 | RPCL 210 MW CCPP | IPP | Gas | 210
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274
30 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
32 | Bhola Nutan Bidyut | IPP | Gas | 220
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150
36 | Anwara 300 MW PP (United) | IPP | HFO | 300
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ |  | √ |  |  | √
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105
40 | Gazipur 100 MW PP | IPP | HFO | 105
41 | United Payra Power Ltd. | IPP | HFO | 150
42 | Madhumati 100 MW PP | IPP | HFO | 100
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ |  | √ |  |  | √
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55
47 | Kodda 150 MW PP BRPL | IPP | HFO | 149
48 | Feni Lanka Power | IPP | HFO | 114 | [11 empty] | √ | √ |  | √ |  | √ | √ | √ | √ |  | √ |  |  | √
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ |  |  | √ |  |  |  |  | √ | √
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55
52 | Jodiac Power | IPP | HFO | 54
53 | Anlima Energy Ltd | IPP | HFO | 116 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ |  | √ |  |  | √
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115
55 | Confidence Unit-2 Bogura | IPP | HFO | 113
56 | Confidence Unit-1 Bogura | IPP | HFO | 113
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ |  |  | √ |  |  |  |  | √ | √
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ |  | √ |  |  | √
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 |  | √ | √ | √ |  | √ | √ |  | √ | √ | √ | √ | √ | √ | [9 empty] | √
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 | [22 empty] | √
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ |  |  | √
66 | Unique Meghnaghat Power Limited (UMPL) | IPP | Gas | 584 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
67 | Meghnaghat CCPP(Summit)-2 | IPP | Gas/HSD | 583 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ | √ | √ |  | √
| JERA Meghnaghat Power Limited | IPP | Gas | 718 | [22 empty] | √ | √ | √ |  |  |  | √
| United Payra Power Ltd. | IPP |  | 150
| Mirsharai 150 MW | IPP | HFO/Gas | 150 | √ | √ | √ | [8 empty] | √ | √ | √ | √ |  | √ | √ | √ | √ |  | √ |  |  | √
Jangalia 52 MW PP (Lakdanavi)
| Ashuganj 420 MW CCPP(East) | APSCL |  | 400 | [6 empty] | √ | [15 empty] | √ |  |  | √ | √
| Ashuganj 55 MW PP (Precision) | QRPP |  | 55
| Bagura 113 MW PP (Confidence)-2 | IPP |  | 113
| Energypac Power Venture Thakurgaon Ltd. | IPP |  | 115
| Chandpur 150 MW CCPP | BPDB |  | 163
| Khulna 225 MW CCPP | NWPGCL |  | 230
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70
| Shajibazar 100 MW PP | BPDB |  | 100
| Payra 1320 MW Unit-1 | BCPCL |  | 622