## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 28-04-2026 | [28 empty] | Date: | 28-04-2026 | [28 empty] | Date: | 28-04-2026 | [28 empty] | Date: | 28-04-2026 | [28 empty] | Date: | 28-04-2026 | [17 empty] | Date: | 28-04-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 297 | 16.2 | 0 | 47 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 20 | 14 | 0 | 350 | 0 | 0 | 0 | 0 | 8 | 34 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 27 | 935 | 0 | 0 | 26 | 0 | 0 | 219 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 225 | 357 | 300 | 51 | 0 | 191 | 0 | 0 | 97 | 0 | 0 | 5 | 0 | 128 | 0 | 0 | 0 | 300 | 0 | 380 | 0 | 30 | 147 | 0 | 17 | 0 | 84 | 30 | 111 | 0 | 100 | 0 | 9 | 58 | 0 | 0 | 0 | 0 | 6517.2 | 875 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 1295.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 150 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 128 | 220 | 0 | 262 | 1100 | 0 | 6038.65 | 12555.85 | 76.71
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 314 | 0 | 0 | 34 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 20 | 14 | 0 | 350 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 800 | 0 | 0 | 26 | 0 | 0 | 220 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 225 | 357 | 250 | 51 | 0 | 192 | 0 | 0 | 98 | 0 | 0 | 5 | 0 | 124 | 0 | 0 | 0 | 295 | 0 | 367 | 0 | 30 | 148 | 0 | 17 | 0 | 11 | 30 | 111 | 0 | 100 | 0 | 9 | 58 | 0 | 0 | 0 | 0 | 6076 | 927 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 985 | 0 | 0 | 0 | 1326.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 150 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 128 | 220 | 0 | 251 | 1060 | 0 | 5967.98 | 12043.98 | 76.72
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 314 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 20.5 | 14 | 0 | 350 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 27 | 800 | 0 | 0 | 20 | 0 | 0 | 220 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 225 | 357 | 250 | 51 | 0 | 194 | 0 | 0 | 98 | 0 | 0 | 5 | 0 | 126 | 0 | 0 | 0 | 295 | 0 | 367 | 0 | 30 | 141 | 0 | 17 | 0 | 84 | 30 | 111 | 0 | 100 | 0 | 9 | 35 | 0 | 0 | 0 | 0 | 6096.5 | 926 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 969 | 0 | 0 | 0 | 1124.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 130 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 128 | 220 | 0 | 251 | 920 | 0 | 5567.84 | 11664.34 | 76.72
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 20.5 | 14 | 0 | 350 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 13 | 800 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 225 | 356 | 250 | 51 | 0 | 194 | 0 | 0 | 98 | 0 | 0 | 5 | 0 | 126 | 0 | 0 | 0 | 300 | 0 | 354 | 0 | 30 | 142 | 0 | 17 | 0 | 84 | 30 | 110 | 0 | 100 | 0 | 9 | 8 | 22 | 0 | 0 | 0 | 6051.5 | 927 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 775 | 0 | 0 | 0 | 1018.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 128 | 220 | 0 | 252 | 900 | 0 | 5203.04 | 11254.54 | 76.72
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 20.5 | 14 | 0 | 350 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 13 | 720 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 225 | 357 | 250 | 51 | 0 | 187 | 0 | 0 | 97 | 0 | 0 | 5 | 0 | 114 | 0 | 0 | 0 | 300 | 0 | 355 | 0 | 30 | 141 | 0 | 17 | 0 | 84 | 30 | 111 | 0 | 100 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 5762.5 | 927 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 0 | 0 | 0 | 934.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 128 | 220 | 0 | 252 | 740 | 0 | 4920.18 | 10682.68 | 76.73
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 20.5 | 14 | 0 | 360 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 15 | 720 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 845 | 0 | 0 | 0 | 225 | 357 | 250 | 51 | 0 | 196 | 0 | 0 | 98 | 0 | 0 | 5 | 0 | 116 | 0 | 0 | 0 | 300 | 0 | 355 | 0 | 30 | 139 | 0 | 17 | 0 | 84 | 30 | 111 | 0 | 100 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 5812.5 | 927 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 778 | 0 | 0 | 0 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 0 | 0 | 130 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 128 | 220 | 0 | 252 | 700 | 0 | 4926.22 | 10738.72 | 76.73
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 304 | 0 | 0 | 6 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 1 | 0 | 20.5 | 14 | 0 | 310 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0.01 | 35 | 0 | 15 | 720 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 840 | 1 | 0 | 0 | 225 | 357 | 250 | 51 | 0 | 193 | 0 | 0 | 98 | 0 | 0 | 5 | 0 | 112 | 0 | 1 | 0 | 295 | 0 | 319 | 0 | 30 | 136 | 0 | 17 | 0 | 84 | 30 | 111 | 0 | 100 | 0 | 9 | 56 | 22 | 0 | 0.01 | 0 | 5768.52 | 927 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 763 | 0 | 0 | 0 | 933.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 140 | 128 | 180 | 0 | 252 | 700 | 0 | 4838.43 | 10606.95 | 76.73
07:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 313 | 0 | 0 | 90 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 3 | 0 | 20.5 | 15 | 0 | 380 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0.54 | 35 | 0 | 12 | 720 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 902 | 4 | 0 | 0 | 225 | 357 | 290 | 51 | 0 | 198 | 0 | 0 | 97 | 0 | 0 | 5 | 0 | 120 | 0 | 17 | 0 | 295 | 0 | 300 | 0 | 30 | 139 | 0 | 17 | 0 | 84 | 30 | 0 | 0 | 100 | 0 | 9 | 56 | 18 | 0.2 | 0 | 0 | 5956.24 | 926 | 218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 776 | 0 | 0 | 0 | 935.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.68 | 1 | 0 | 0 | 0.68 | 130 | 0 | 0 | 0 | 130 | 0 | 410 | 0 | 0.08 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.8 | 11 | 0.15 | 0 | 181 | 128 | 180 | 0 | 252 | 740 | 0 | 5037.7 | 10993.94 | 76.74
08:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 320 | 0 | 0 | 102 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 20.5 | 15 | 0 | 340 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 2.03 | 35 | 0 | 2 | 720 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 908 | 4 | 0 | 0 | 225 | 357 | 290 | 51 | 0 | 202 | 0 | 0 | 97 | 0 | 0 | 5 | 0 | 126 | 0 | 22 | 0 | 295 | 0 | 301 | 0 | 30 | 137 | 0 | 17 | 0 | 32 | 30 | 0 | 0 | 100 | 0 | 9 | 56 | 10 | 0 | 0.03 | 0 | 5918.56 | 927 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 774 | 0 | 0 | 0 | 832.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98 | 37 | 0 | 0 | 1.99 | 130 | 0 | 0 | 0 | 130 | 0 | 367 | 0 | 0.13 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 21 | 0.22 | 0 | 181 | 128 | 180 | 0 | 252 | 800 | 0 | 5024.75 | 10943.31 | 76.74
09:00 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 305 | 0 | 0 | 115 | 148 | 0 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 7 | 0 | 20.5 | 15 | 0 | 310 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 2.84 | 35 | 0 | 2 | 720 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 907 | 5 | 0 | 0 | 225 | 357 | 290 | 51 | 0 | 188 | 0 | 0 | 39 | 0 | 0 | 3 | 0 | 128 | 0 | 24 | 0 | 300 | 0 | 301 | 0 | 30 | 140 | 0 | 17 | 0 | 32 | 30 | 0 | 0 | 100 | 0 | 9 | 56 | 10 | 0 | 0.77 | 0 | 5897.11 | 925 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 789 | 0 | 0 | 0 | 834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 45 | 0 | 0 | 8.37 | 122 | 0 | 0 | 0 | 130 | 0 | 335 | 0 | 0.37 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 4.6 | 16 | 0.04 | 0 | 178 | 128 | 180 | 0 | 254 | 800 | 0 | 5022.38 | 10919.49 | 76.74
10:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 316 | 17 | 0 | 110 | 78 | 0 | 30 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 5 | 0 | 20.5 | 0 | 0 | 425 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 1.17 | 35 | 0 | 2 | 720 | 0 | 0 | 19 | 0 | 0 | 217 | 0 | 0 | 0 | 908 | 5 | 0 | 0 | 225 | 357 | 290 | 51 | 0 | 186 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 84 | 0 | 7 | 0 | 300 | 0 | 329 | 0 | 30 | 140 | 0 | 0 | 0 | 32 | 30 | 0 | 0 | 101 | 0 | 9 | 74 | 10 | 0.2 | 1.85 | 0 | 5929.72 | 925 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.93 | 802 | 0 | 0 | 0 | 828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.45 | 23 | 0 | 0 | 3.75 | 0 | 0 | 0 | 0 | 140 | 0 | 368 | 0 | 0.46 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 5.7 | 15 | 0.11 | 0 | 181 | 128 | 180 | 0 | 259 | 800 | 0 | 4952.4 | 10882.12 | 76.74
11:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 302 | 17 | 0 | 85 | 45 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 19 | 0 | 20.5 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0.52 | 35 | 0 | 2 | 720 | 0 | 0 | 19 | 0 | 0 | 218 | 0 | 0 | 0 | 844 | 2 | 0 | 0 | 300 | 357 | 290 | 51 | 0 | 156 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 12 | 0 | 2 | 0 | 305 | 0 | 360 | 0 | 30 | 137 | 0 | 8 | 0 | 33 | 30 | 0 | 0 | 100 | 0 | 0 | 86 | 10 | 0.85 | 15.71 | 0 | 5789.58 | 925 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.01 | 794 | 0 | 0 | 0 | 829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.65 | 46 | 0 | 0 | 9.44 | 0 | 0 | 0 | 0 | 140 | 0 | 334 | 0 | 0.32 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 7.9 | 20 | 0.18 | 0 | 177 | 100 | 180 | 0 | 303 | 796 | 0 | 4929.5 | 10719.08 | 76.74
12:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 320 | 17 | 0 | 70 | 30 | 0 | 15 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 20.5 | 14 | 0 | 420 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0.05 | 35 | 0 | 10 | 720 | 0 | 0 | 19 | 0 | 0 | 217 | 0 | 0 | 0 | 850 | 5 | 0 | 0 | 325 | 357 | 345 | 51 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 300 | 0 | 380 | 0 | 30 | 138 | 0 | 12 | 0 | 34 | 30 | 0 | 0 | 100 | 0 | 0 | 65 | 8 | 0.68 | 2.67 | 0 | 5937.9 | 924 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.83 | 785 | 0 | 0 | 0 | 831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.27 | 56 | 0 | 0 | 7.17 | 0 | 0 | 0 | 0 | 140 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 4.4 | 73 | 0.69 | 0 | 181 | 100 | 180 | 0 | 304 | 750 | 0 | 5041.36 | 10979.26 | 76.74
13:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 290 | 17 | 0 | 68 | 15 | 0 | 15 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 22 | 0 | 20.5 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 700 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 840 | 2 | 0 | 0 | 309 | 340 | 280 | 10 | 0 | 173 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 295 | 0 | 318 | 0 | 30 | 138 | 0 | 16 | 0 | 22 | 30 | 8 | 0 | 102 | 0 | 0 | 55 | 8 | 0.8 | 10.45 | 0 | 5601.75 | 923 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.13 | 768 | 0 | 0 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.04 | 13 | 0 | 0 | 20.8 | 0 | 0 | 0 | 0 | 190 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 5.6 | 108 | 0.3 | 0 | 158 | 100 | 180 | 0 | 304 | 745 | 0 | 4925.87 | 10527.62 | 76.74
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 245 | 0 | 0 | 34 | 15 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 8 | 0 | 21 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 2 | 685 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 830 | 1 | 0 | 0 | 320 | 340 | 280 | 10 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 68 | 0 | 2 | 0 | 240 | 0 | 321 | 30 | 30 | 138 | 0 | 16 | 0 | 11 | 30 | 8 | 0 | 101 | 0 | 0 | 45 | 6 | 0.7 | 32.45 | 0 | 5412.15 | 925 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.91 | 776 | 0 | 0 | 0 | 828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.92 | 10 | 0 | 0 | 24.56 | 0 | 0 | 0 | 0 | 160 | 0 | 270 | 0 | 1.74 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 2.1 | 53 | 0.06 | 0 | 154 | 100 | 180 | 0 | 302 | 660 | 0 | 4761.29 | 10173.44 | 76.74
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 180 | 0 | 0 | 34 | 15 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 20 | 0 | 21 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 2 | 680 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 815 | 0 | 0 | 0 | 315 | 340 | 280 | 10 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 240 | 0 | 318 | 30 | 30 | 138 | 0 | 16 | 0 | 11 | 30 | 110 | 0 | 101 | 0 | 0 | 45 | 6 | 0.6 | 13 | 0 | 5451.6 | 924 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.68 | 770 | 0 | 0 | 0 | 831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.43 | 12 | 0 | 0 | 16.75 | 0 | 0 | 0 | 0 | 196 | 0 | 352 | 0 | 1.5 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 3.1 | 94 | 0 | 0 | 154 | 100 | 180 | 0 | 311 | 650 | 0 | 4915.46 | 10367.06 | 76.74
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 238 | 0 | 0 | 34 | 15 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 2 | 0 | 21 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 2 | 685 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 806 | 0 | 0 | 0 | 316 | 340 | 280 | 10 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 240 | 0 | 318 | 30 | 30 | 139 | 1 | 16 | 0 | 11 | 30 | 110 | 0 | 101 | 0 | 9 | 45 | 6 | 0.35 | 11.28 | 0 | 5443.63 | 924 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.43 | 765 | 0 | 0 | 0 | 833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.04 | 26 | 0 | 0 | 6.94 | 0 | 0 | 0 | 0 | 163 | 0 | 360 | 0 | 0.5 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 3.4 | 15 | 0 | 0 | 153 | 100 | 180 | 0 | 304 | 600 | 0 | 4731.31 | 10174.94 | 76.74
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 215 | 0 | 0 | 34 | 15 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 0 | 0 | 5 | 0 | 21 | 14 | 0 | 440 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 2 | 710 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 825 | 0 | 0 | 0 | 310 | 340 | 280 | 10 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 240 | 0 | 320 | 30 | 30 | 140 | 1 | 16 | 0 | 11 | 30 | 112 | 0 | 101 | 0 | 9 | 45 | 10 | 0.3 | 6.52 | 1 | 5510.82 | 925 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 770 | 0 | 0 | 0 | 849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.09 | 15 | 0 | 0 | 7.55 | 0 | 0 | 0 | 0 | 199 | 0 | 348 | 0 | 0.73 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1.5 | 4 | 0 | 0 | 176 | 100 | 180 | 0 | 317 | 590 | 0 | 4736.87 | 10247.69 | 76.74
18:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 235 | 17 | 15 | 34 | 15 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 2 | 0 | 21 | 14 | 0 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 4 | 730 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 838 | 0 | 0 | 0 | 315 | 340 | 250 | 10 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 240 | 0 | 321 | 30 | 30 | 140 | 0 | 16 | 0 | 11 | 30 | 110 | 0 | 101 | 0 | 9 | 45 | 10 | 0 | 2.25 | 12 | 5669.25 | 924 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.42 | 772 | 0 | 0 | 0 | 1007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 | 0 | 196 | 0 | 320 | 0 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 2 | 0.01 | 0 | 167 | 100 | 180 | 0 | 329 | 600 | 0 | 4860.93 | 10530.18 | 76.74
19:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 245 | 16.5 | 17 | 34 | 15 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 20 | 21 | 14 | 0 | 480 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 2 | 770 | 35 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 891 | 0 | 0 | 0 | 345 | 357 | 260 | 23 | 0 | 196 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 260 | 0 | 364 | 30 | 30 | 146 | 0 | 16 | 0 | 50 | 30 | 109 | 0 | 101 | 0 | 9 | 66 | 11 | 0 | 0 | 12 | 6154.5 | 925 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 852 | 0 | 0 | 0 | 1132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 374 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 120 | 220 | 0 | 333 | 800 | 0 | 5459 | 11613.5 | 76.75
19:30 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 196 | 16.3 | 17 | 34 | 15 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 35 | 21 | 14 | 0 | 478 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 2 | 725 | 19 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 932 | 0 | 0 | 0 | 393 | 356 | 300 | 51 | 0 | 192 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 310 | 0 | 385 | 30 | 30 | 152 | 0 | 16 | 0 | 75 | 30 | 111 | 0 | 101 | 0 | 9 | 66 | 11 | 0 | 0 | 12 | 6318.3 | 925 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 842 | 0 | 0 | 0 | 1086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 353 | 0 | 0 | 0 | 0 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 130 | 220 | 0 | 372 | 920 | 0 | 5520 | 11838.3
20:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 226 | 15.4 | 0 | 34 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 21 | 14 | 0 | 465 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 5 | 702 | 19 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 898 | 0 | 0 | 0 | 350 | 358 | 300 | 51 | 0 | 187 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 305 | 0 | 386 | 30 | 30 | 154 | 0 | 16 | 0 | 83 | 30 | 112 | 0 | 101 | 0 | 9 | 67 | 11 | 0 | 0 | 12 | 6225.4 | 925 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 0 | 0 | 0 | 1037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 355 | 0 | 0 | 0 | 0 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 130 | 220 | 0 | 446 | 900 | 0 | 5484 | 11709.4 | 76.75
21:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 306 | 16.2 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 21 | 14 | 0 | 465 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 18 | 730 | 19 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 849 | 0 | 0 | 0 | 215 | 358 | 342 | 51 | 0 | 194 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 305 | 0 | 386 | 30 | 30 | 156 | 0 | 16 | 0 | 83 | 30 | 112 | 0 | 101 | 0 | 9 | 68 | 11 | 0 | 0 | 12 | 6224.2 | 925 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802 | 0 | 0 | 0 | 1058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 130 | 220 | 0 | 512 | 880 | 0 | 5550 | 11774.2 | 76.75
22:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 293 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 20 | 14 | 0 | 460 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 20 | 740 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 215 | 357 | 345 | 51 | 0 | 180 | 0 | 0 | 50 | 0 | 0 | 5 | 0 | 108 | 0 | 0 | 0 | 305 | 0 | 386 | 30 | 30 | 152 | 0 | 16 | 0 | 83 | 30 | 0 | 0 | 101 | 0 | 9 | 58 | 11 | 0 | 0 | 12 | 6017 | 925 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 0 | 0 | 0 | 1010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 130 | 220 | 0 | 548 | 850 | 0 | 5446 | 11463 | 76.75
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 288 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 20 | 14 | 0 | 460 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 28 | 740 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 847 | 0 | 0 | 0 | 215 | 357 | 345 | 51 | 0 | 173 | 0 | 0 | 77 | 0 | 0 | 5 | 0 | 106 | 0 | 0 | 0 | 305 | 0 | 386 | 30 | 30 | 153 | 0 | 16 | 0 | 83 | 30 | 0 | 0 | 101 | 0 | 9 | 58 | 11 | 0 | 0 | 12 | 6042 | 925 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 130 | 220 | 0 | 598 | 850 | 0 | 5379 | 11421 | 76.75
Total KWH | 0 | 205440 | 78720 | 0 | 0 | 0 | 0 | 0 | 9313200 | 0 | 6831790 | 137520 | 50760 | 1077264 | 673440 | 0 | 248584 | 227799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7361676 | 0 | 0 | 102581 | 72000 | 495600 | 326520 | 0 | 9693181.82 | 0 | 0 | 0 | 0 | 792960 | 22304 | 0 | 0 | 0 | 0 | 5055 | 843720 | 0 | 249120 | 17563636.36 | 66909 | 0 | 137280 | 0 | 0 | 5153228 | 0 | 0 | 0 | 21114543 | 37260 | 0 | 0 | 6383000 | 8820300 | 7046000 | 1054860 | 0 | 4494000 | 0 | 0 | 1433324 | 0 | 0 | 69150 | 0 | 2369280 | 0 | 78200 | 0 | 6952000 | 0 | 8441000 | 306000 | 717960 | 3436200 | 3912 | 370848 | 0 | 1234560 | 719520 | 1415400 | 0 | 2418690 | 0 | 158400 | 1212000 | 254400 | 4000 | 84190 | 75120 | 142434405.18 | 22348364 | 5660928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324720 | 19309091 | 0 | 0 | 0 | 22725990 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198192 | 340730 | 0 | 0 | 133504 | 0 | 0 | 0 | 0 | 4196400 | 0 | 8470691 | 0 | 5700 | 0 | 0 | 89618 | 118577 | 130944 | 0 | 0 | 0 | 43633.92 | 444240 | 1353 | 0 | 4211000 | 2852000 | 5131020 | 0 | 7905454 | 19425454.55 | 0 | 124067604.47 | 266502009.65

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 29-04-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-04-2026 | during | 29-04-2026 | during | 29-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 353 | 350 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 0 | 55 | 55 | 45 | 45 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 317 | 335 | 335 | 290 | 290 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 16.3 | 53.97 | 53.97 | 55 | 55 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 15 | 149.36 | 149.36 | 15 | 149
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20.5 | 21 | 33 | 33 | 21 | 21 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 14 | 14 | 14 | 14 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 8 | 52.19 | 52.19 | 8 | 17 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 48 | 294 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 34 | 149 | 149 | 52 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 17 | 105 | 105 | 17 | 34 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 35 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 0 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0.01 | 0.01 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 420 | 478 | 584 | 584 | 450 | 450 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 320 | 196 | 718 | 718 | 380 | 380 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 35 | 160 | 160 | 17 | 108 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1619.5 | 1535.3 | 5939.22 | 5907.22 | 1981.01 | 2616.01
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 0 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 5 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 0 | 50 | 50 | 19 | 50 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 35 | 35 | 35 | 35 | 35 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 224 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 34 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 68 | 68 | 68 | 68 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 10 | 2 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 12 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0.05 | 0 | 3.48 | 0 | 3.48 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 0 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 54 | 54 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 19 | 163 | 163 | 17 | 90 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 850 | 932 | 1224 | 1224 | 1204 | 1204 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 46 | 60 | 2 | 7 | 2 | 7 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 720 | 725 | 935 | 1000 | 935 | 1000 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1902.05 | 1997 | 3737.34 | 3810.86 | 2798.48 | 3052
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 150 | 192 | 221.25 | 221.25 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 357 | 356 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 345 | 300 | 342.01 | 342.01 | 310 | 310 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 325 | 393 | 393 | 393 | 226 | 226 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 30 | 140 | 18 | 140 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 100 | 100 | machine problem.
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 17 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 106 | 84 | 78 | 132 | 132 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 0 | 24.5 | 24.5 | 5 | 5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 17 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 17 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 0 | 0 | 30 | 0 | 30 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1316 | 1448 | 2604.44 | 2678.44 | 1519.01 | 1931.01
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-04-2026 | during | 29-04-2026 | during | 29-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 8 | 11 | 157.5 | 157.5 | 25 | 25 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.68 | 0 | 1.6 | 0 | 1.6 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 65 | 66 | 50 | 10 | 50 | 10 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 0 | 9 | 70 | 70 | 70 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 2.67 | 0 | 32 | 0 | 32 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 76.35 | 98 | 387.6 | 314 | 195.6 | 134
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 30 | 0 | 0 | 0 | 0 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 138 | 152 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 111 | 100 | 100 | 100 | 100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 0 | 0 | 30 | 30 | plant availability zero
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 34 | 75 | 85 | 85 | 84 | 84 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 101 | 100 | 100 | 98 | 98 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 12 | 16 | 25 | 25 | 17 | 17 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 380 | 385 | 370 | 370 | 380 | 380 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1024 | 1240 | 1234 | 1234 | 1193 | 1193
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 925 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 32 | 32 | 30 | 30 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 228 | 255 | 410 | 410 | 222 | 222 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 45.83 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 785 | 842 | 1234.2 | 1234.2 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1982.83 | 2022 | 3571.2 | 3496.2 | 2568.1 | 2493.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 304 | 372 | 250 | 450 | 250 | 450 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 100 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 750 | 920 | 1244 | 1244 | 1184 | 1184 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 181 | 165 | 307 | 307 | 280 | 280 | Bad quality coal
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.69 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1515.69 | 1807 | 2412 | 2611 | 2098 | 2297
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 39.27 | 0 | 51 | 0 | 51 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | 1 unit is under maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Under Maintenance
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 168 | 220 | 220 | 160 | 160 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 371 | 353 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 21 | 21 | 21 | 21 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0.03 | 0.03 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 92 | 92 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 0.02 | 0.02 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 3.2 | 0 | 3.2 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 831 | 1086 | 1435.88 | 1435.88 | 1356 | 1356 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 7.17 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 56 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1444.44 | 1607 | 3210.07 | 2994.87 | 2305.66 | 2175.46
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Tripped
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 35 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.4 | 0 | 6.8 | 0 | 6.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 0 | 70 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 21 | 0 | 24 | 0 | 24 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 73 | 0 | 114.3 | 0 | 114.3 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 98.4 | 84 | 387.1 | 242 | 180.1 | 183
System Total |  |  |  |  | 28823.2 | 29270.237 | 10979.26 | 11838.3 | 23482.97 | 23288.59 | 14838.96 | 16074.58
Forecast Scenario (29-04-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12200 |  | 0 |  | 12200
|  |  |  | 1:00 | 11690 |  | 0 |  | 11690
|  |  |  | 2:00 | 11470 |  | 0 |  | 11470
|  |  |  | 3:00 | 11350 |  | 0 |  | 11350
|  |  |  | 4:00 | 11240 |  | 0 |  | 11240
|  |  |  | 5:00 | 11220 |  | 0 |  | 11220
|  |  |  | 6:00 | 11050 |  | 0 |  | 11050
|  |  |  | 7:00 | 10890 |  | 0 |  | 10890
|  |  |  | 8:00 | 11170 |  | 0 |  | 11170
|  |  |  | 9:00 | 11400 |  | 0 |  | 11400
|  |  |  | 10:00 | 11780 |  | 0 |  | 11780
|  |  |  | 11:00 | 12370 |  | 0 |  | 12370
|  |  |  | 12:00 | 12600 |  | 0 |  | 12600
|  |  |  | 13:00 | 12590 |  | 0 |  | 12590
|  |  |  | 14:00 | 12530 |  | 0 |  | 12530
|  |  |  | 15:00 | 12590 |  | 0 |  | 12590
|  |  |  | 16:00 | 12530 |  | 0 |  | 12530
|  |  |  | 17:00 | 12340 |  | 0 |  | 12340
|  |  |  | 18:00 | 12370 |  | 0 |  | 12370
|  |  |  | 18:30 | 12800 |  | 0 |  | 12800
|  |  |  | 19:00 | 13380 |  | 0 |  | 13380
|  |  |  | 19:30 | 13420 |  | 0 |  | 13420
|  |  |  | 20:00 | 13450 |  | 0 |  | 13450
|  |  |  | 21:00 | 13500 |  | 0 |  | 13500
|  |  |  | 22:00 | 13460 |  | 0 |  | 13460
|  |  |  | 23:00 | 13360 |  | 0 |  | 13360
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 12600.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13500.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13500.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 292.53 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:48 hrs on 29-04-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 28-04-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10979.26 | MW | 12:00 Hr. | Energy Generated |  |  | 266.502 |  | MKWHr.
| Day Peak Demand |  |  | 10979.26 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.116 |  | MKWHr.
| Evening Peak Generation |  |  | 11838.3 | MW | 19:30 Hr. | Energy Demand |  |  | 266.618 |  | MKWHr.
| Evening Peak Demand |  |  | 11838.3 | MW | 19:30 Hr. | Maximum Temperature |  |  | 27.2 |  | °C
| Minimum Generation of the Day |  |  | 10173.44 | MW | 14:00 Hr. | Total Gas Supplied |  |  | 834.79 |  | MMCFD
| Maximum Generation of the Day |  |  | 12555.85 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.3135 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.022 | 0 | 2.7715 | 0 | 0 | 0.10258 | 0 | 0 | 36.8961 | Gas | 121.3026 | Gas | 421218966.2394
| Chattogram Zone |  |  | 5.4023 | 38.6782 | 0.22649 | 0 | 0.84372 | 0.042315 | 0 | 0.79296 | 45.986 | Coal | 89.5292 | Coal | 610524596.8923
| Cumilla Zone |  |  | 29.3006 | 0 | 0 | 0 | 0 | 0.0782 | 2.3693 | 0 | 31.7481 | HFO | 4.6641 | HFO | 81342256.84
| Mymensingh Zone |  |  | 0.2544 | 0 | 1.4455 | 0 | 0 | 0.08819 | 0 | 0 | 1.7881 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.0122 | 0 | 0 | 0 | 0 | 0.003912 | 0 | 0 | 26.0161 | Hydro | 0.84372 | Hydro | 84372
| Khulna Zone |  |  | 5.6609 | 19.3091 | 0 | 0 | 0 | 0.32472 | 22.3484 | 0 | 47.6431 | Solar | 1.9258 | Solar | 31252923.734
| Barishal Zone |  |  | 7.983 | 31.5419 | 0 | 0 | 0 | 0.001353 | 0 | 0 | 39.5263 | Import | 47.4436 | Import | 259970221.7
| Rajshahi Zone |  |  | 12.6671 | 0 | 0 | 0 | 0 | 0.67813 | 22.726 | 0 | 36.0712 | Wind | 0.79296 | Wind | 11664441.6
| Rangpur Zone |  |  | 0 | 0 | 0.22056 | 0 | 0 | 0.60645 | 0 | 0 | 0.82701
| Total |  |  | 121.3026 | 89.5292 | 4.6641 | 0 | 0.84372 | 1.9258 | 47.4436 | 0.79296 | 266.502
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 421218966.2394 |  | Hydro | 84372
|  |  |  | Coal | 610524596.8923 |  | Solar | 31252923.734
|  |  |  | HFO | 81342256.84 |  | Import | 259970221.7
|  |  |  | HSD | 0 |  | Wind | 11664441.6
[5 empty] | Total: | 141,60,57,779 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.3484 | Peak Hr Flow | 925.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 35239872.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.726 | Peak Hr Flow | 1086.00 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1694 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.3693 | Peak Hr Flow | 106.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2070 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.4436 | Peak Hr Flow | 2117.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4746
|  |  |  | Chattogram |  | 0 |  | 944
|  |  |  | Cumilla |  | 0 |  | 859
|  |  |  | Mymensingh |  | 0 |  | 901
|  |  |  | Sylhet |  | 0 |  | 365
|  |  |  | Khulna |  | 0 |  | 1459
|  |  |  | Barishal |  | 0 |  | 171
|  |  |  | Rajshahi |  | 0 |  | 1231
|  |  |  | Rangpur |  | 0 |  | 747
|  |  |  | Total |  | 0 |  | 11423
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 320
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:10 | 17:47 | Khulna (C) S/S TR-1 425T LT Project Work S/D Due to Project work
| 08:10 | 17:46 | Khulna (C) S/S TR-1 425T HT Project Work S/D Due to Project work
|  | 08:19 | Kaliakoir 400/230/132kV S/S 400/132kV TR2 HT is restored.
|  | 08:26 | Kaliakoir 400/230/132kV S/S 400/132kV TR2 LT is restored.
|  | 08:36 | Hasnabad-Sitalakhya 132kV Ckt-1 is restored.
|  | 08:37 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 HT is restored.
|  | 08:39 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 HT is restored.
|  | 08:41 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 HT is restored.
|  | 08:45 | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) is restored.
|  | 09:04 | Ashuganj-Kishoreganj 132kV Ckt-1 is restored.
| 09:22 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- ST
| 09:29 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- GT
| 09:36 | 10:10 | Narshingdi 132/33kV S/S T-2 LT Tripped showing REF 630 relays Due to 33kV feeder tripped | [7 empty] | 5.0MW load
|  |  | by Over current | [7 empty] | interrup.
| 09:36 | 10:05 | Narshingdi 132/33kV S/S T-2 HT Tripped showing RET 607,RET 605 relays Due to 33 kV feeder | [7 empty] | 5.0MW load
|  |  | fault by Over current. | [7 empty] | interrup.
|  | 10:36 | Brahmanbaria-Shahjibazar 132 kV Ckt-1 is restored.
|  | 10:36 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 is restored.
| 10:42 | 11:45 | Chauddagram-Cumilla(S) 132 kV Ckt-2 Tripped from Cumilla(S) 132/33kV end showing REL670
relays Due to Zone-1, AR Operated
| 10:50 | 13:50 | Khulna(C )-Noapara 132kV Ckt-2 Scheduled S/D from Noapara 132/33kV end Due to According
to ALDC's Instruction. and from Khulna (C) end Due to ঘুড়ির সুতা নামানোর জন্য
| 10:59 | 11:44 | Cumilla(S) 132/33kV S/S TR-4 LT Tripped showing REF615 relays Due to Kotbari PDB Feeder | [7 empty] | 2.0MW load
|  |  | fault | [7 empty] | interrup.
| 10:59 | 11:44 | Cumilla(S) 132/33kV S/S TR-3 LT Tripped showing REF615 relays Due to 33KV PDB feeder | [7 empty] | 2.0MW load
|  |  | fault | [7 empty] | interrup.
| 11:09 | 12:09 | Feni 132/33kV S/S T-2(415T) LT Tripped showing Inst,O/C. relays Due to fault | [7 empty] | 26.0MW load
interrup.
| 11:25 | 12:44 | Chauddagram-Feni 132 kV Ckt-1 Tripped from Feni 132/33kV end showing Distance
relay, O/C,A/R lockout relays Due to Fault
| 11:38 | 13:15 | Khulna (S)-Satkhira 132kV Ckt-1 Forced S/D from Satkhira 132/33kV end Due to R ফেজে
ঘুড়ির সুতা অপসারণ and from Khulna(S) 230/132kVend.
|  | 11:50 | Kaliakoir 400/230/132kV S/S 132 kV Bus-1 is restored.
| 12:07 |  | Hathazari 230/132/33kV S/S Raojan-02 Forced S/D Due to DC problem.
| 12:33 |  | Joypurhat 132/33kV S/S Naogaon Ckt.-2 Scheduled S/D Due to Project Work Naogaon end
| 12:35 |  | Bogura(New)-Naogaon 132 kV Ckt-1 Project Work S/D from Bogura 230/132kV end Due to
Project Work at Naogaon Sub-Station and from Naogaon 132/33kV end Due to Naogaon-Bogura
Ckt-1 will be shifted from AIS to GIS Bus. That's why EEGBPS Project took this line
shutdown for Line and XLPE Cable Pot-Head loop Connection.
| 12:49 |  | Hathazari 230/132/33kV S/S MT-01 LT Forced S/D Due to DC problem.
| 12:49 |  | Hathazari 230/132/33kV S/S MT-01 HT Forced S/D Due to DC problem.
| 12:58 | 14:26 | Hathazari-Raozan 230kV Ckt-1 Forced S/D from Hathazari 230/132/33kV end Due to DC
problem.
| 13:05 | 13:21 | Gopalganj (O) - Gopalgan (N) Ckt-1 Tripped from Gopalganj 132/33kV end showing Z1,
Definite earth fault,A phase relays Due to Thundering
| 13:21 | 13:25 | Khagrachari-Rangamati 132kV Ckt-2 Tripped from Khagrachori 132/33kV end showing REL670
relays Due to Thundering
| 13:46 | 18:46 | Khulna(S) 230/132kV S/S Rupsha Ckt-1 Forced S/D
| 14:08 | 21:59 | Barishal(N)-Madaripur 132 kV Ckt-1 Forced S/D from Barishal 230/132kV end Due to
Conductor torn out
| 14:08 | 21:59 | Barishal(N)-Madaripur 132 kV Ckt-1 Tripped from Barishal 230/132kV end showing REL650
relays Due to Distance Relay
| 15:51 | 15:57 | Kaliakoir 400/230/132kV S/S 132kV Bus 2 Scheduled S/D Due to 230/132kv Transformer on
| 16:28 | 18:14 | Lakshmipur 132/33kV S/S Transformer-2 LT Forced S/D Due to Red Hot work
| 16:33 | 18:12 | Lakshmipur 132/33kV S/S Transformer-2 HT Forced S/D Due to Red hot Maintenance
| 16:44 | 17:14 | Shahjibazar-Sreemangal 132kV Ckt-1 Scheduled S/D from Shahjibazar 132/33kV end Due to
N/A
| 17:21 | 18:38 | Mongla 132/33kV S/S T-2 LT Tripped showing Protection rely relays. | [7 empty] | 1.0MW load
interrup.
|  | 18:26 | Sylhet (South) S/S Sylhet (S)-Biyanibazar 132KV Ckt-1 is restored.
| 03:30 |  | Orion Rupsha PP-Bagerhat Ckt tripped from Orion Rupsha end but showing no relay.
| 03:33 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 Forced S/D Due to Dear sir
Kaliakoir ckt- 01 & 02 has been shutdown instructed by NLDC XEN sir due to reduce
system voltage . Date: 29-04-2026 Time: 03:33 am Previous voltage : 414/242
kV After S/D voltage : 410/240 kV Thank you Bogura 400/230kV GIS Grid Sub-Station
| 03:33 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Forced S/D Due to Dear sir
Kaliakoir ckt- 01 & 02 has been shutdown instructed by NLDC XEN sir due to reduce
system voltage . Date: 29-04-2026 Time: 03:33 am Previous voltage : 414/242
kV After S/D voltage : 410/240 kV Thank you Bogura 400/230kV GIS Grid Sub-Station
| 03:44 | 05:03 | Jhenaidah-Kushtia 132kV Ckt-2 Tripped from Kushtia 132/33kV end showing Distance Relay
(F21) and Overcurrent Relay (F67). relays.
| 03:45 | 04:59 | Jhenaidah-Kushtia 132kV Ckt-1 Tripped from Kushtia 132/33kV end showing Distance Relay
(F21) and Overcurrent Relay (F67). relays.
| 04:11 |  | Orion Rupsha PP-Bagerhat Ckt is restored.
| 04:50 | 06:22 | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat Tripped showing 59 Overvoltage relays Due
to STORM
| 04:52 | 06:17 | Lalmonirhat-Rangpur 132 kV Ckt-2 Tripped from Kurigram 132/33kV end showing Distance
Triped, Zone-2, B-phase relays Due to Heavy thurstorm happening
| 06:13 |  | Sirajganj 132/33kV S/S T3-(435) LT Tripped showing 132/33 kV T4-(445) HT Tripped showing
87-Differential Relay relays and Relay Signal: 87 Dif> Trip, 87 Dif>> Trip, at CP Signal:
Transformer Main-1 87T1 Trip, Transformer Main-1 general trip. signals relays Due to
heavy storm.
| 06:13 |  | Sirajganj 132/33kV S/S T3-(435) HT Tripped showing 87-Differential Relay relays Due to
heavy storm
| 06:49 | 07:14 | Barapukuria-Rangpur 132 kV Ckt-2 Tripped from Barapukuria 230/132/33kV end showing Simens
siprotec relays Due to Earth fault
| 06:49 | 07:12 | Barapukuria-Rangpur 132 kV Ckt-1 Tripped from Barapukuria 230/132/33kV end showing REL
511 relays Due to Earth fault
| 06:55 |  | Mirpur-Uttara 3PH 132kV Ckt-1 Forced S/D from Mirpur 132/33kV end Due to Over voltage
| 07:00 |  | Minimum Generation: 7319 MW.
| 07:10 | 07:53 | Muktagacha 132/33kV S/S T-3(424T) LT Tripped showing 24 over voltage relays.
| 07:10 | 07:50 | Muktagacha 132/33kV S/S T-3(424T) HT Tripped showing 24 over voltage relays.
| 07:10 | 07:53 | Muktagacha 132/33kV S/S T-2(414T) LT Tripped showing 24 over voltage relays.
| 07:10 | 07:53 | Muktagacha 132/33kV S/S T-2(414T) HT Tripped showing 24 over voltage relays Due to over
excitation
| 07:10 | 07:49 | Muktagacha 132/33kV S/S T-1(404T) HT Tripped showing over excitation relays.
| 07:10 | 07:54 | Muktagacha 132/33kV S/S T-1(404T) LT Tripped showing over excitation relays.
| 07:24 | 07:48 | Jamalpur 132/33kV S/S T-4 LT Tripped showing Locout operate relays Due to Over voltage
| 07:24 | 07:48 | Jamalpur 132/33kV S/S T-4 HT Tripped showing Siemens 7ut86 relays Due to Over voltage
| 07:33 | 07:45 | Kabirpur -Tongi 132kV Ckt-2 Tripped from Tongi 230/132/33kV end showing Distance relay
relays Due to Bad weather and over voltage
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 28-04-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 350 | 9313200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 248584 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 317 | 7361676 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 16.3 | 137520 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 15 | 673440 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 227799 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 495600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 326520 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 78720 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 34 | 1077264 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 205440 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 102581 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 50760 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 478 | 9693181.82 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 196 | 6831790 | FGMO
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 35 | 72000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1535.3 | 36896075.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 37260 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 137280 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 35 | 843720 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 224 | 5153228 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 22304 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 2 | 249120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 5055 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 19 | 66909 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 932 | 21114543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 60 | 792960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 725 | 17563636.36 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 1997 | 45986015.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 192 | 4494000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 356 | 8820300 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 300 | 7046000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 6383000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1054860 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1433324 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 106 | 2369280 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 0 | 69150 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 78200 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1448 | 31748114
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 11 | 254400 | Grid fault
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 4000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 66 | 1212000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 158400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 84190 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 75120 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 98 | 1788110
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 3912 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 306000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 717960 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3436200 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 111 | 1415400 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719520 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1234560 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2418690 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 370848 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 6952000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 385 | 8441000 | plant availability zero
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1240 | 26016090
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 925 | 22348364 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 255 | 5660928 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 324720 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 842 | 19309091 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2022 | 47643103
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 372 | 7905454 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 2852000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 920 | 19425454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5131020 | -
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 165 | 4211000 | Bad quality coal
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1353 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1807 | 39526281.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 198192 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | 1 unit is under maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 168 | 4196400 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 353 | 8470691 | Gas shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 5700 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1086 | 22725990 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 133504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 340730 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1607 | 36071207
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Tripped
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 130944 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 43633.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 89618 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 118577 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 444240 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 84 | 827012.92
Eastern Grid Total |  |  |  |  | 17418.042 | 6318.3 | 142434405.18
Western Grid Total |  |  |  |  | 11852.195 | 5520 | 124067604.47
National Grid Total |  |  |  |  | 29270.237 | 11838.3 | 266502009.65
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 28-04-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7814.61 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3607.9 | MW
i) Dhaka area |  |  | 4745.61 |  | MW | i) Khulna area |  |  |  | 1458.8 | MW
ii) Chattogram area |  |  | 944 |  | MW | ii) Barishal area |  |  |  | 170.9 | MW
iii) Cumilla area |  |  | 859 |  | MW | iii) Rajshahi area |  |  |  | 1231.2 | MW
iv) Mymensingh area |  |  | 901 |  | MW | iv) Rangpur area |  |  |  | 747 | MW
v) Sylhet area |  |  | 365 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11422.51 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 11 | 14:00 | 67 | Hasnabad | 83 | 10:00 | 133 | Natore | 127 | 19:30
2 | AKSML | 17 | 13:00 | 68 | Hathazari | 76 | 00:00 | 134 | Nawabganj | 52 | 00:00
3 | Aftabnagar | 34 | 10:00 | 69 | Hatirjheel | 30 | 10:00 | 135 | Netrakona | 100 | 19:30
4 | Agargaon | 101 | 10:00 | 70 | Ishurdi | 78 | 12:00 | 136 | New | 78 | 11:00
5 | Agrabad | 68 | 12:00 | 71 | Jaldhaka | 62 | 19:00 | 137 | Niamatpur | 54 | 22:00
6 | Amnura | 27 | 19:30 | 72 | Jamalpur | 83 | 21:00 | 138 | Noapara | 45 | 00:00
7 | Ashuganj | 63 | 00:00 | 73 | Jashore | 140 | 14:00 | 139 | PHP | 12 | 17:00
8 | BSRM | 201 | 14:00 | 74 | Jhenaidah | 101 | 00:00 | 140 | Pabna | 93 | 12:00
9 | Bagerhat | 87 | 00:00 | 75 | Joydebpur | 128 | 11:00 | 141 | Palashbari | 83 | 19:00
10 | Bajitpur | 57 | 00:00 | 76 | Joypurhat | 44 | 21:00 | 142 | Panchagarh | 51 | 19:00
11 | Bakerganj | 9.5 | 00:00 | 77 | Juldah | 15 | 00:00 | 143 | Patiya | 10 | 00:00
12 | Bakulia | 82 | 00:00 | 78 | KSRM | 12 | 03:00 | 144 | Patuakhali | 69 | 00:00
13 | Banani | 42 | 10:00 | 79 | Kabirpur | 277 | 10:00 | 145 | Payra | 32 | 02:00
14 | Bangabhaban | 17 | 10:00 | 80 | Kachua | 70 | 01:00 | 146 | Postogola | 48 | 10:00
15 | Barapukuria | 52 | 19:30 | 81 | Kaliganj | 25 | 00:00 | 147 | Pubail | 32 | 06:00
16 | Barguna | 22 | 00:00 | 82 | Kallyanpur | 93 | 01:00 | 148 | Purbachal | 26 | 12:00
17 | Barishal | 110 | 13:00 | 83 | Kalurghat | 134 | 18:30 | 149 | Purbasadipur | 95 | 19:30
18 | Barishal-230 | 96 | 00:00 | 84 | Kamrangirchar | 74 | 13:00 | 150 | Rahanpur | 26 | 19:30
19 | Baroaulia | 72 | 15:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 31 | 08:00
20 | Baroirhat | 53 | 00:00 | 86 | Kasba | 25 | 00:00 | 152 | Rajbari | 80 | 00:00
21 | Bashundhara | 169 | 10:00 | 87 | Kazla | 107 | 11:00 | 153 | Rajendrapur | 110 | 15:00
22 | BashundharaCement | 6 | 00:00 | 88 | Keranigonj | 79 | 09:00 | 154 | Rajshahi | 111 | 19:30
23 | Beanibazar | 50 | 18:30 | 89 | Khagrachori | 20 | 00:00 | 155 | Rajshahi-230 | 70 | 13:00
24 | Benapole | 64 | 00:00 | 90 | Khulna | 68 | 13:00 | 156 | Ramganj | 100 | 00:00
25 | Bhaluka | 125 | 19:00 | 91 | Khulshi | 170 | 09:00 | 157 | Rampur | 40 | 00:00
26 | Bhandaria | 57 | 01:00 | 92 | Kishoreganj | 93 | 21:00 | 158 | Rangamati | 11 | 10:00
27 | Bhangura | 33 | 14:00 | 93 | Kodda | 279 | 08:00 | 159 | Rangpur | 118 | 19:00
28 | Bheramara(GK) | 60 | 12:00 | 94 | Kulaura | 28 | 21:00 | 160 | Ruppur | 4.4 | 10:00
29 | Bhulta | 202 | 12:00 | 95 | Kurigram | 46 | 18:00 | 161 | SSM | 9 | 23:00
30 | Bog-Sherpur | 60 | 19:00 | 96 | Kushtia | 149 | 13:00 | 162 | Saidpur | 86 | 19:00
31 | Bogura | 124 | 21:00 | 97 | Laksam | 28 | 00:00 | 163 | Santhia | 25 | 19:30
32 | Borhanuddin | 94 | 01:00 | 98 | Lakshmipur | 32 | 00:00 | 164 | Satkhira | 126 | 00:00
33 | Brahmanbaria | 98 | 00:00 | 99 | Lalbag | 68 | 13:00 | 165 | Satmasjid | 90 | 13:00
34 | Cantonment | 94 | 13:00 | 100 | Lalmonirhat | 48 | 18:00 | 166 | Savar | 220 | 10:00
35 | Chandina | 18 | 00:00 | 101 | MI_Cement | 17.9 | 00:00 | 167 | SevenRings | 15.59 | 00:00
36 | Chandpur | 73 | 01:00 | 102 | Madanganj | 40 | 09:00 | 168 | ShahCement | 42 | 01:00
37 | Chandraghona | 31 | 00:00 | 103 | Madaripur | 113 | 00:00 | 169 | Shahjadpur | 69 | 10:00
38 | Chapai | 59 | 19:30 | 104 | Madartek | 67 | 13:00 | 170 | Shahjibazar | 63 | 21:00
39 | Charsaidpur | 29 | 00:00 | 105 | Madunaghat | 45 | 00:00 | 171 | Shahmirpur | 53 | 03:00
40 | Chauddagram | 59 | 00:00 | 106 | Magura | 62 | 00:00 | 172 | Shariatpur | 80 | 01:00
41 | Chhatak | 25 | 18:30 | 107 | Mahasthangarh | 55 | 19:00 | 173 | Sherpur | 104 | 19:30
42 | Chowmuhani | 135 | 00:00 | 108 | Maijdee | 47 | 00:00 | 174 | Shikalbaha | 19 | 12:00
43 | Chuadanga | 115 | 00:00 | 109 | Manikganj | 122 | 11:00 | 175 | Shitalakhya | 76.3 | 12:00
44 | Coxsbazar | 135 | 00:00 | 110 | Maniknagar | 63 | 13:00 | 176 | Sholosohor | 45 | 12:00
45 | Cumilla(N) | 83 | 00:00 | 111 | Matarbari | 51 | 01:00 | 177 | Shyampur | 164 | 11:00
46 | Cumilla(S) | 129 | 00:00 | 112 | Matuail | 78 | 12:00 | 178 | Siddhirganj | 121 | 12:00
47 | Daganbhuiyan | 32 | 00:00 | 113 | Metrorail_Motijheel | 21 | 11:00 | 179 | Sirajganj | 98 | 20:00
48 | Daudkandi | 123 | 01:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sonargaon | 123 | 04:00
49 | DhakaUniversity | 76 | 13:00 | 115 | Millgate | 93 | 12:00 | 181 | Sreemongol | 35 | 18:30
50 | Dhamrai | 106 | 08:00 | 116 | Mirpur | 130.5 | 13:00 | 182 | Sreepur | 104 | 19:00
51 | Dhanmondi | 97 | 10:00 | 117 | Mirsorai | 40 | 02:00 | 183 | Srinagar | 46.6 | 00:00
52 | Dohazari | 103 | 00:00 | 118 | Mirzapur | 39 | 18:30 | 184 | Sunamganj | 40 | 20:00
53 | Faridpur | 168 | 00:00 | 119 | Mithapukur | 42 | 19:30 | 185 | Sylhet | 32 | 16:00
54 | Fatullah | 89 | 10:00 | 120 | Modern | N/A | N/A | 186 | Sylhet-132 | 87 | 18:00
55 | Fenchuganj | 35 | 19:30 | 121 | Mogbazar | 77.8 | 10:00 | 187 | TK | 22 | 00:00
56 | Feni | 86 | 01:00 | 122 | Mongla | 48 | 00:00 | 188 | Tangail | 136 | 07:00
57 | GPH | 79 | 09:00 | 123 | Motijheel | 40 | 14:00 | 189 | Taraganj | 17 | 18:30
58 | Ghatail | 72 | 18:30 | 124 | Muktagacha | 26 | 19:00 | 190 | Tasnim | 26 | 11:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 102 | 00:00 | 191 | Thakurgaon | 80 | 19:00
60 | Ghorashal-230 | 96 | 22:00 | 126 | Muradnagar | 35 | 01:00 | 192 | Tongi | 128 | 09:00
61 | Goalpara | 42 | 00:00 | 127 | Mymensingh | 155 | 19:30 | 193 | Ullahpara | 27 | 22:00
62 | Gollamari | 102 | 00:00 | 128 | Nabinagar | 26 | 10:00 | 194 | Ullon | 46 | 12:00
63 | Gopalganj | 101.4 | 00:00 | 129 | Naogaon | 96 | 19:30 | 195 | Uttara | 75 | 13:00
64 | Gulshan | 106 | 10:00 | 130 | Narail | 57 | 00:00 | 196 | UttaraNew | 43 | 12:00
65 | Halishahar | 102 | 16:00 | 131 | Narinda | 62 | 13:00 | 197 | Zigatola | 74 | 10:00
66 | HaripurSBU | 140 | 00:00 | 132 | Narshingdi | 151 | 01:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 28-04-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 12555.85 | 0 |  | 12555.85
1:00 | 12043.98 | 0 |  | 12043.98
2:00 | 11664.34 | 0 |  | 11664.34
3:00 | 11254.54 | 0 |  | 11254.54
4:00 | 10682.68 | 0 |  | 10682.68
5:00 | 10738.72 | 0 |  | 10738.72
6:00 | 10606.95 | 0 |  | 10606.95
7:00 | 10993.94 | 0 |  | 10993.94
8:00 | 10943.31 | 48 |  | 10993.31
9:00 | 10919.49 | 32 |  | 10952.49
10:00 | 10882.12 | 36 |  | 10920.12
11:00 | 10719.08 | 0 |  | 10719.08
12:00 | 10979.26 | 0 |  | 10979.26
13:00 | 10527.62 | 0 |  | 10527.62
14:00 | 10173.44 | 0 |  | 10173.44
15:00 | 10367.06 | 0 |  | 10367.06
16:00 | 10174.94 | 0 |  | 10174.94
17:00 | 10247.69 | 0 |  | 10247.69
18:00 | 10530.18 | 0 |  | 10530.18
19:00 | 11613.5 | 0 |  | 11613.5
19:30 | 11838.3 | 0 |  | 11838.3
20:00 | 11709.4 | 0 |  | 11709.4
21:00 | 11774.2 | 0 |  | 11774.2
22:00 | 11463 | 0 |  | 11463
23:00 | 11421 | 0 |  | 11421
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 28-04-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6517.2 | 6038.65 | 12555.85 | DAILY GENERATION CURVE
00:30 | 6296.6 | 6003.315 | 12299.915
01:00 | 6076 | 5967.98 | 12043.98 | 28-04-2026
01:30 | 6086.25 | 5767.91 | 11854.16
02:00 | 6096.5 | 5567.84 | 11664.34
02:30 | 6074 | 5385.44 | 11459.44
03:00 | 6051.5 | 5203.04 | 11254.54
03:30 | 5907 | 5061.61 | 10968.61
04:00 | 5762.5 | 4920.18 | 10682.68
04:30 | 5787.5 | 4923.2 | 10710.7
05:00 | 5812.5 | 4926.22 | 10738.72
05:30 | 5790.51 | 4882.325 | 10672.835
06:00 | 5768.52 | 4838.43 | 10606.95
06:30 | 5862.38 | 4938.065 | 10800.445
07:00 | 5956.24 | 5037.7 | 10993.94
07:30 | 5937.4 | 5031.225 | 10968.625
08:00 | 5918.56 | 5024.75 | 10943.31
08:30 | 5907.835 | 5023.565 | 10931.4
09:00 | 5897.11 | 5022.38 | 10919.49
09:30 | 5913.415 | 4987.39 | 10900.805
10:00 | 5929.72 | 4952.4 | 10882.12
10:30 | 5859.65 | 4940.95 | 10800.6
11:00 | 5789.58 | 4929.5 | 10719.08
11:30 | 5863.74 | 4985.43 | 10849.17
12:00 | 5937.9 | 5041.36 | 10979.26
12:30 | 5769.825 | 4983.615 | 10753.44
13:00 | 5601.75 | 4925.87 | 10527.62
13:30 | 5506.95 | 4843.58 | 10350.53
14:00 | 5412.15 | 4761.29 | 10173.44
14:30 | 5431.875 | 4838.375 | 10270.25
15:00 | 5451.6 | 4915.46 | 10367.06
15:30 | 5447.615 | 4823.385 | 10271
16:00 | 5443.63 | 4731.31 | 10174.94
16:30 | 5477.225 | 4734.09 | 10211.315
17:00 | 5510.82 | 4736.87 | 10247.69
17:30 | 5590.035 | 4798.9 | 10388.935
18:00 | 5669.25 | 4860.93 | 10530.18
18:30 | 5911.875 | 5159.965 | 11071.84
19:00 | 6154.5 | 5459 | 11613.5
19:30 | 6318.3 | 5520 | 11838.3
20:00 | 6225.4 | 5484 | 11709.4
20:30 | 6224.8 | 5517 | 11741.8 |  | Executive Engineer
21:00 | 6224.2 | 5550 | 11774.2 |  | Network Operation Division
21:30 | 6120.6 | 5498 | 11618.6
22:00 | 6017 | 5446 | 11463
22:30 | 6029.5 | 5412.5 | 11442
23:00 | 6042 | 5379 | 11421

## En-Curve
QF-LDC-12
Date | 28-04-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3738 | 1532 | 875 | 0 | 128 | 1295.65 | 35 | 4722 | 0 | 51 | 171.2 | 0 | 0 | 8 | 0 | DAILY ENERGY CURVE
00:30 | 3719 | 1501 | 901 | 0 | 126 | 1311.315 | 35 | 4519 | 0 | 25.5 | 156.6 | 0 | 0 | 5.5 | 0 | 28-04-2026
01:00 | 3700 | 1470 | 927 | 0 | 124 | 1326.98 | 35 | 4316 | 0 | 0 | 142 | 0 | 0 | 3 | 0
01:30 | 3680.5 | 1504.25 | 926.5 | 0 | 125 | 1225.91 | 35 | 4238 | 0 | 0 | 112.5 | 0 | 0 | 6.5 | 0 | Energy Generated | 266.502 |  | MKWHr
02:00 | 3661 | 1538.5 | 926 | 0 | 126 | 1124.84 | 35 | 4160 | 0 | 0 | 83 | 0 | 0 | 10 | 0 | Energy not Served | 0.116 |  | MKWHr
02:30 | 3663.5 | 1535 | 926.5 | 0 | 126 | 1071.44 | 35 | 4029.5 | 0 | 0 | 50 | 0 | 0 | 22.5 | 0 | Total Energy Requirement | 266.618 |  | MKWHr
03:00 | 3666 | 1531.5 | 927 | 0 | 126 | 1018.04 | 35 | 3899 | 0 | 0 | 17 | 0 | 0 | 35 | 0
03:30 | 3665 | 1527 | 927 | 0 | 120 | 976.11 | 35 | 3679.5 | 0 | 0 | 8.5 | 0 | 0 | 30.5 | 0
04:00 | 3664 | 1522.5 | 927 | 0 | 114 | 934.18 | 35 | 3460 | 0 | 0 | 0 | 0 | 0 | 26 | 0
04:30 | 3684.5 | 1537.5 | 927 | 0 | 115 | 934.7 | 35 | 3447.5 | 0 | 0 | 0 | 0 | 0 | 29.5 | 0
05:00 | 3705 | 1552.5 | 927 | 0 | 116 | 935.22 | 35 | 3435 | 0 | 0 | 0 | 0 | 0 | 33 | 0
05:30 | 3656 | 1492 | 927 | 0 | 114 | 934.315 | 35 | 3425 | 3.52 | 21.5 | 35.5 | 0 | 0 | 29 | 0
06:00 | 3607 | 1431.5 | 927 | 0 | 112 | 933.41 | 35 | 3415 | 7.04 | 43 | 71 | 0 | 0 | 25 | 0
06:30 | 3585.5 | 1471.5 | 926.5 | 0 | 116 | 934.36 | 35 | 3493 | 31.585 | 73 | 113 | 0 | 0 | 21 | 0
07:00 | 3564 | 1511.5 | 926 | 0 | 120 | 935.31 | 35 | 3571 | 56.13 | 103 | 155 | 0 | 0 | 17 | 0
07:30 | 3540 | 1463 | 926.5 | 0 | 123 | 883.87 | 35 | 3603 | 95.255 | 127.5 | 161 | 0 | 0 | 10.5 | 24
08:00 | 3516 | 1414.5 | 927 | 0 | 126 | 832.43 | 35 | 3635 | 134.38 | 152 | 167 | 0 | 0 | 4 | 48
08:30 | 3460.5 | 1395 | 926 | 0 | 127 | 833.215 | 35 | 3641.5 | 152.185 | 150.5 | 185.5 | 0 | 0 | 25 | 40
09:00 | 3405 | 1375.5 | 925 | 0 | 128 | 834 | 35 | 3648 | 169.99 | 149 | 204 | 0 | 0 | 46 | 32
09:30 | 3358.5 | 1421 | 925 | 0 | 106 | 831 | 35 | 3659 | 156.305 | 122 | 240 | 0 | 0 | 47 | 34
10:00 | 3312 | 1466.5 | 925 | 0 | 84 | 828 | 35 | 3670 | 142.62 | 95 | 276 | 0 | 0 | 48 | 36
10:30 | 3317 | 1452.5 | 925 | 0 | 48 | 828.5 | 35 | 3652 | 155.1 | 82.5 | 257.5 | 0 | 0 | 47.5 | 18
11:00 | 3322 | 1438.5 | 925 | 0 | 12 | 829 | 35 | 3634 | 167.58 | 70 | 239 | 0 | 0 | 47 | 0
11:30 | 3403 | 1469 | 924.5 | 0 | 25 | 830 | 35 | 3612 | 211.67 | 62.5 | 230 | 0 | 0 | 46.5 | 0
12:00 | 3484 | 1499.5 | 924 | 0 | 38 | 831 | 35 | 3590 | 255.76 | 55 | 221 | 0 | 0 | 46 | 0
12:30 | 3363 | 1442.5 | 923.5 | 0 | 44 | 828 | 35 | 3552.5 | 259.94 | 47.5 | 205.5 | 0 | 0 | 52 | 0
13:00 | 3242 | 1385.5 | 923 | 0 | 50 | 825 | 35 | 3515 | 264.12 | 40 | 190 | 0 | 0 | 58 | 0
13:30 | 3249.5 | 1331.25 | 924 | 0 | 59 | 826.5 | 35 | 3461 | 237.78 | 27.5 | 150.5 | 0 | 0 | 48.5 | 0
14:00 | 3257 | 1277 | 925 | 0 | 68 | 828 | 35 | 3407 | 211.44 | 15 | 111 | 0 | 0 | 39 | 0
14:30 | 3365 | 1244.5 | 924.5 | 0 | 76 | 829.5 | 35 | 3393.5 | 224.25 | 15 | 111 | 0 | 0 | 52 | 0
15:00 | 3473 | 1212 | 924 | 0 | 84 | 831 | 35 | 3380 | 237.06 | 15 | 111 | 0 | 0 | 65 | 0
15:30 | 3438 | 1241.5 | 924 | 0 | 90 | 832 | 35 | 3346.5 | 178.5 | 15 | 115.5 | 0 | 0 | 55 | 0
16:00 | 3403 | 1271 | 924 | 0 | 96 | 833 | 35 | 3313 | 119.94 | 15 | 120 | 0 | 0 | 45 | 0
16:30 | 3435.5 | 1280 | 924.5 | 0 | 90 | 841 | 35 | 3350.5 | 83.815 | 15 | 120.5 | 0 | 0 | 35.5 | 0
17:00 | 3468 | 1289 | 925 | 0 | 84 | 849 | 35 | 3388 | 47.69 | 15 | 121 | 0 | 0 | 26 | 0
17:30 | 3467.5 | 1315 | 924.5 | 0 | 90 | 928 | 35 | 3412 | 33.935 | 27.5 | 142.5 | 0 | 0 | 13 | 0
18:00 | 3467 | 1341 | 924 | 0 | 96 | 1007 | 35 | 3436 | 20.18 | 40 | 164 | 0 | 0 | 0 | 0
18:30 | 3582.5 | 1409 | 924.5 | 0 | 103 | 1069.5 | 35 | 3635.5 | 10.09 | 50 | 227.25 | 0 | 0 | 25.5 | 0
19:00 | 3698 | 1477 | 925 | 0 | 110 | 1132 | 35 | 3835 | 0 | 60 | 290.5 | 0 | 0 | 51 | 0
19:30 | 3786 | 1535 | 925 | 0 | 106 | 1086 | 35 | 3956 | 0 | 75 | 274.3 | 0 | 0 | 60 | 0
20:00 | 3756 | 1560 | 925 | 0 | 106 | 1037 | 35 | 3909 | 0 | 59 | 257.4 | 0 | 0 | 65 | 0
20:30 | 3743.5 | 1607.5 | 925 | 0 | 109 | 1047.5 | 35 | 3925.5 | 0 | 59 | 224.8 | 0 | 0 | 65 | 0
21:00 | 3731 | 1655 | 925 | 0 | 112 | 1058 | 35 | 3942 | 0 | 59 | 192.2 | 0 | 0 | 65 | 0
21:30 | 3680 | 1647 | 925 | 0 | 110 | 1034 | 35 | 3939.5 | 0 | 42 | 150.6 | 0 | 0 | 55.5 | 0
22:00 | 3629 | 1639 | 925 | 0 | 108 | 1010 | 35 | 3937 | 0 | 25 | 109 | 0 | 0 | 46 | 0
22:30 | 3656.5 | 1641 | 925 | 0 | 107 | 944.5 | 35 | 3961.5 | 0 | 21 | 102.5 | 0 | 0 | 48 | 0
23:00 | 3684 | 1643 | 925 | 0 | 106 | 879 | 35 | 3986 | 0 | 17 | 96 | 0 | 0 | 50 | 0
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 28-04-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 114 | -10 | 502 | 70 | 1426 | 380 | Ishurdi-Ghorashal Ckt-1 | Export | 2540872.73
1:00 | 132 | -13 | 544 | 108 | 1394 | 382
2:00 | 128 | -10 | 492 | 94 | 1258 | 394 |  | Import | 0
3:00 | 118 | -9 | 454 | 78 | 1108 | 424
4:00 | 124 | -6 | 434 | 72 | 1116 | 470 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 129 | -5 | 444 | 74 | 1094 | 464
6:00 | 110 | -9 | 382 | 60 | 1020 | 404 |  | Import | 0
7:00 | 98 | -14 | 346 | 46 | 1042 | 398
8:00 | 106 | -11 | 296 | 36 | 1062 | 412 | Sirajganj-Sreepur Ckt-1 | Export | 2200000
9:00 | 115 | -11 | 302 | 26 | 1184 | 424
10:00 | 106 | -11 | 308 | 40 | 1144 | 450 |  | Import | 0
11:00 | 89 | -18 | 270 | 26 | 1008 | 386
12:00 | 86 | -19 | 292 | 50 | 962 | 392 | Sirajganj-Sreepur Ckt-2 | Export | 2219000
13:00 | 75 | -20 | 254 | 56 | 940 | 398
14:00 | 96 | -18 | 360 | 72 | 1162 | 482 |  | Import | 0
15:00 | 107 | -14 | 360 | 80 | 1202 | 492
16:00 | 114 | -11 | 390 | 82 | 1214 | 490 | Gopalganj-Aminbazar Ckt-1 | Export | 14130000
17:00 | 123 | -8 | 364 | 74 | 1270 | 486
18:00 | 120 | -12 | 390 | 74 | 1322 | 448 |  | Import | 0
18:30 | 127 | -10 | 424 | 82 | 1442 | 452
19:00 | 102 | -14 | 394 | 54 | 1362 | 434 | Gopalganj-Aminbazar Ckt-2 | Export | 14150000
19:30 | 92 | -13 | 336 | 88 | 1266 | 440
20:00 | 90 | -16 | 360 | 94 | 1244 | 414 |  | Import | 0
21:00 | 89 | -17 | 370 | 94 | 1284 | 406
22:00 | 84 | -20 | 370 | 74 | 1242 | 380 |  | Total Export | 35239872.73
23:00 | 89 | -19 | 320 | 62 | 1248 | 360 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 28-04-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 390 | 11:00 | 377 | 00:00 | Madunaghat | 404 | 14:00 | 388 | 00:00
Amtali | 414 | 14:00 | 405 | 01:00 | Meghnaghat | 394 | 13:00 | 380 | 00:00
Ashuganj | 412 | 11:00 | 398 | 1:00 | Payra | 415 | 14:00 | 406 | 00:00
Bhulta | 404 | 11:00 | 390 | 00:00 | Rahanpur | 415 | 04:00 | 405 | 01:00
Bibiana | 408 | 06:00 | 400 | 00:00 | Rampal | 406 | 06:00 | 389 | 00:00
BIPTC | 400 | 04:00 | 393 | 13:00
Bogura | 408 | 04:00 | 394 | 00:00
Gopalganj | 403 | 16:00 | 389 | 00:00
Kaliakoir | 386 | 06:00 | 373 | 00:00
Korerhat | 408 | 13:00 | 387 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 235 | 06:00 | 226 | 00:00 | Jhenaidah | 229 | 05:00 | 215 | 00:00
AKSML | 236 | 13:00 | 223 | 00:00 | Kachua | 236 | 13:00 | 216 | 01:00
Aminbazar | 234 | 06:00 | 227 | 00:00 | Kaliakoir | 237 | 07:00 | 229 | 00:00
Ashuganj | 234 | 09:00 | 225 | 00:00 | Keranigonj | 233 | 06:00 | 223 | 00:00
Ashuganj-400 | 234 | 09:00 | 225 | 00:00 | Khulna(S) | 233 | 05:00 | 217 | 00:00
Baghabari | 236 | 05:00 | 229 | 00:00 | Korerhat | 235 | 13:00 | 218 | 00:00
Barapukuria | 230 | 04:00 | 218 | 07:00 | Madunaghat | 240 | 13:00 | 224 | 01:00
Barapukuria-230 | 230 | 04:00 | 218 | 07:00 | Madunaghat-400 | 239 | 14:00 | 226 | 01:00
Barishal | 231 | 15:00 | 218 | 00:00 | Maniknagar | 228 | 06:00 | 221 | 00:00
Bheramara | 232 | 04:00 | 223 | 00:00 | Meghnaghat | 237 | 13:00 | 228 | 00:00
Bhulta | 229 | 06:00 | 222 | 00:00 | Meghnaghat-400 | 232 | 11:00 | 223 | 00:00
Bibiana | 239 | 06:00 | 232 | 00:00 | Mirsorai | 236 | 13:00 | 224 | 00:00
BIPTC | 234 | 04:00 | 223 | 00:00 | Naogaon | 226 | 04:00 | 214 | 19:00
Bogura | 238 | 04:00 | 230 | 00:00 | Purbasadipur | 234 | 04:00 | 216 | 22:00
Bogura-400 | 238 | 04:00 | 229 | 19:00 | Rajshahi | 232 | 06:00 | 222 | 00:00
Borhanuddin | 234 | 15:00 | 224 | 00:00 | Rampal | 231 | 05:00 | 219 | 00:00
BSRM | 233 | 13:00 | 219 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 235 | 14:00 | 217 | 00:00 | Rampura | 229 | 06:00 | 221 | 01:00
Cumilla(N) | 232 | 11:00 | 222 | 00:00 | Shikalbaha | 238 | 13:00 | 221 | 00:00
Faridpur | 226 | 14:00 | 213 | 00:00 | Shyampur | 231 | 06:00 | 222 | 00:00
Fenchuganj | 242 | 08:00 | 236 | 01:00 | Siddhirganj | 230 | 21:00 | 222 | 00:00
Feni | 234 | 13:00 | 219 | 00:00 | Sirajgonj | 242 | 04:00 | 236 | 19:00
Ghorashal | 232 | 11:00 | 220 | 00:00 | Sreepur | 233 | 09:00 | 224 | 00:00
Ghorashal-230 | 228 | 11:00 | 221 | 00:00 | Tongi | 230 | 17:00 | 221 | 01:00
Gopalganj | 226 | 14:00 | 215 | 00:00
GPH | 236 | 13:00 | 222 | 00:00
Haripur | 230 | 11:00 | 222 | 00:00
Hasnabad | 232 | 18:00 | 224 | 00:00
Hathazari | 236 | 13:00 | 221 | 00:00
Ishurdi | 234 | 04:00 | 226 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 06:00 | 130 | 00:00 | Madunaghat | 141 | 13:00 | 130 | 00:00
Agargaon | 134 | 06:00 | 128 | 00:00 | Magura | 136 | 06:00 | 123 | 00:00
Agrabad | 141 | 13:00 | 128 | 00:00 | Mahasthangarh | 136 | 04:00 | 130 | 19:00
AKS | 136 | 13:00 | 126 | 00:00 | Maijdee | 132 | 13:00 | 120 | 00:00
Aminbazar | 134 | 02:00 | 129 | 00:00 | Manikganj | 131 | 03:00 | 121 | 00:00
Amnura | 136 | 04:00 | 128 | 00:00 | Maniknagar | 135 | 23:00 | 130 | 00:00
Ashuganj | 145 | 09:00 | 136 | 03:00 | Matarbari | 136 | 15:00 | 108 | 00:00
Ashuganj-230 | 145 | 09:00 | 136 | 03:00 | Matuail | 134 | 11:00 | 129 | 01:00
Bagerhat | 134 | 17:00 | 116 | 00:00 | Metrorail_Motijheel | 135 | 23:00 | 130 | 00:00
Bajitpur | 136 | 09:00 | 130 | 00:00 | Metrorail_Uttara | 133 | 03:00 | 128 | 00:00
Bakerganj | 136 | 16:00 | 126 | 00:00 | Millgate | 134 | 03:00 | 128 | 00:00
Bakulia | 140 | 13:00 | 127 | 00:00 | Mirpur | 134 | 06:00 | 128 | 00:00
Banani | 134 | 8:00 | 131 | 00:00 | Mirzapur | 135 | 06:00 | 126 | 00:00
Bangabhaban | 134 | 06:00 | 130 | 00:00 | Mithapukur | 133 | 04:00 | 128 | 00:00
Barapukuria | 133 | 04:00 | 126 | 07:00 | MI_Cement | 131.8 | 06:00 | 126 | 00:00
Barguna | 137 | 16:00 | 126 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 137 | 16:00 | 126 | 00:00 | Mogbazar | 136 | 05:00 | 132 | 00:00
Barishal-230 | 136 | 16:00 | 126 | 00:00 | Mongla | 134 | 18:00 | 116 | 00:00
Baroaulia | 138 | 13:00 | 128 | 00:00 | Motijheel | 134 | 06:00 | 130 | 00:00
Baroirhat | 135 | 13:00 | 126 | 00:00 | Muktagacha | 136 | 11:00 | 120 | 18:30
Bashundhara | 135 | 05:00 | 128 | 00:00 | Munshiganj | 134 | 10:00 | 127 | 00:00
BashundharaCement | 134 | 10:00 | 128 | 00:00 | Muradnagar | 136 | 11:00 | 123 | 00:00
Beanibazar | 136 | 04:00 | 130 | 18:00 | Mymensingh | 133 | 09:00 | 119 | 19:00
Benapole | 132 | 04:00 | 118 | 00:00 | Nabinagar | 138 | 16:00 | 128 | 00:00
Bhaluka | 131 | 07:00 | 124 | 19:00 | Naogaon | 136 | 04:00 | 126 | 06:00
Bhandaria | 140 | 17:00 | 126 | 20:00 | Narail | 135 | 04:00 | 123 | 00:00
Bhangura | 136 | 03:00 | 131 | 9:00 | Narinda | 135 | 23:00 | 130 | 00:00
Bheramara | 136 | 04:00 | 132 | 00:00 | Narshingdi | 142 | 09:00 | 120 | 21:00
Bheramara(GK) | 135 | 05:00 | 132 | 00:00 | Natore | 134 | 05:00 | 130 | 00:00
Bhulta | 130 | 10:00 | 124 | 00:00 | Nawabganj | 137 | 06:00 | 130 | 00:00
Bog-Sherpur | 137 | 04:00 | 132 | 19:00 | Netrakona | 135 | 06:00 | 121 | 20:00
Bogura | 138 | 05:00 | 132 | 19:00 | New | 135 | 06:00 | 130 | 00:00
Bogura-230 | 138 | 04:00 | 133 | 00:00 | Niamatpur | 136 | 03:00 | 131 | 18:30
Brahmanbaria | 141 | 09:00 | 127 | 22:00 | Noapara | 135 | 05:00 | 122 | 00:00
Cantonment | 133 | 05:00 | 128 | 00:00 | Pabna | 135 | 04:00 | 130 | 00:00
Chandina | 137 | 11:00 | 127 | 00:00 | Palashbari | 131 | 02:00 | 126 | 19:00
Chandpur | 135 | 13:00 | 121 | 00:00 | Panchagarh | 138 | 04:00 | 130 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 142 | 13:00 | 129 | 00:00 | Patiya | 139 | 13:00 | 126 | 00:00
Chapai | 137 | 04:00 | 131 | 00:00 | Patuakhali | 135 | 16:00 | 125 | 00:00
Charsaidpur | 134 | 10:00 | 127 | 00:00 | Payra | 137 | 14:00 | 132 | 00:00
Chauddagram | 136 | 13:00 | 124 | 00:00 | PHP | 135 | 13:00 | 125 | 00:00
Chhatak | 135 | 03:00 | 128 | 18:30 | Postogola | 134 | 06:00 | 128 | 00:00
Chowmuhani | 132 | 15:00 | 121 | 00:00 | Pubail | 134 | 11:00 | 128 | 00:00
Chuadanga | 134 | 06:00 | 121 | 00:00 | Purbachal | 135 | 04:00 | 128 | 00:00
Coxsbazar | 134 | 16:00 | 111 | 00:00 | Purbasadipur | 135 | 04:00 | 125 | 18:00
Cumilla(N) | 135 | 11:00 | 127 | 00:00 | Rahanpur | 137 | 04:00 | 134 | 00:00
Cumilla(S) | 137 | 11:00 | 126 | 00:00 | Rahanpur-400 | 138 | 04:00 | 134 | 00:00
Daganbhuiyan | 134 | 12:00 | 124 | 00:00 | Rahim | 134 | 10:00 | 128 | 01:00
Daudkandi | 135 | 11:00 | 121 | 00:00 | Rajbari | 130 | 16:00 | 120 | 00:00
DhakaUniversity | 135 | 03:00 | 131 | 00:00 | Rajendrapur | 133 | 09:00 | 124 | 18:30
Dhamrai | 139 | 16:00 | 129 | 00:00 | Rajshahi | 132 | 03:00 | 127 | 13:00
Dhanmondi | 135.5 | 18:30 | 131 | 00:00 | Rajshahi-230 | 133 | 05:00 | 128 | 01:00
Dohazari | 137 | 14:00 | 121 | 00:00 | Ramganj | 132 | 13:00 | 118 | 00:00
Faridpur | 131 | 16:00 | 123 | 00:00 | Rampur | 140 | 13:00 | 127 | 00:00
Fatullah | 133 | 06:00 | 126 | 00:00 | Rampura | 136 | 06:00 | 131 | 01:00
Fenchuganj | 138 | 07:00 | 135 | 01:00 | Rangamati | 140 | 13:00 | 129 | 00:00
Feni | 132 | 15:00 | 125 | 00:00 | Rangpur | 134 | 06:00 | 126 | 18:00
Feni-230 | 134 | 12:00 | 125 | 00:00 | Ruppur | 136 | 05:00 | 132 | 00:00
Ghatail | 132 | 06:00 | 118 | 18:30 | Saidpur | 131 | 05:00 | 124 | 07:00
Ghorashal | 136 | 04:00 | 132 | 00:00 | Santhia | 135 | 06:00 | 132 | 00:00
Goalpara | 137 | 05:00 | 124 | 00:00 | Satkhira | 132 | 09:00 | 118 | 00:00
Gollamari | 136 | 05:00 | 125 | 00:00 | Satmasjid | 133 | 06:00 | 128 | 00:00
Gopalganj | 136 | 4:00 | 124 | 00:00 | Savar | 132 | 04:00 | 126 | 00:00
Gopalganj-400 | 135 | 14:00 | 128 | 00:00 | SevenRings | 137 | 11:00 | 132 | 00:00
Gulshan | 135 | 06:00 | 131 | 00:00 | ShahCement | 134 | 10:00 | 127 | 00:00
Halishahar | 139 | 13:00 | 128 | 00:00 | Shahjadpur | 137 | 03:00 | 135 | 12:00
Haripur | 134 | 11:00 | 129 | 00:00 | Shahjibazar | 141 | 07:00 | 129 | 21:00
HaripurSBU | 134 | 11:00 | 129 | 00:00 | Shahmirpur | 140 | 13:00 | 128 | 00:00
Hasnabad | 134 | 06:00 | 130 | 00:00 | Shariatpur | 136 | 14:00 | 125 | 01:00
Hathazari | 140 | 13:00 | 129 | 00:00 | Sherpur | 136 | 10:00 | 115 | 18:30
Hatirjheel | 136 | 06:00 | 131 | 00:00 | Shikalbaha | 129 | 13:00 | 119 | 00:00
Ishurdi | 137 | 04:00 | 133 | 00:00 | Shikalbaha-230 | 141 | 13:00 | 128 | 00:00
Jaldhaka | 129 | 05:00 | 122 | 18:00 | Shitalakhya | 131.8 | 06:00 | 126 | 01:00
Jamalpur | 137 | 11:00 | 118 | 22:00 | Sholosohor | 139 | 13:00 | 129 | 00:00
Jashore | 134 | 06:00 | 120 | 00:00 | Shyampur | 138 | 10:00 | 127 | 00:00
Jhenaidah | 136 | 05:00 | 124 | 00:00 | Shyampur-230 | 133 | 06:00 | 128 | 00:00
Jhenaidah-230 | 137 | 05:00 | 126 | 00:00 | Siddhirganj | 134 | 11:00 | 129 | 00:00
Joydebpur | 131 | 10:00 | 126 | 00:00 | Sirajganj | 134 | 03:00 | 130 | 19:00
Joypurhat | 136 | 05:00 | 128 | 19:00 | Sonargaon | 134 | 11:00 | 127 | 00:00
Juldah | 140 | 13:00 | 128 | 00:00 | Sreemongol | 139 | 08:00 | 131 | 21:00
Kabirpur | 137 | 06:00 | 125 | 20:00 | Sreepur | 133 | 09:00 | 126 | 19:00
Kachua | 135 | 13:00 | 124 | 01:00 | Srinagar | 137 | 03:00 | 131 | 00:00
Kaliakoir | 139 | 15:00 | 132 | 00:00 | SSM | 142 | 13:00 | 132 | 00:00
Kaliganj | 136 | 06:00 | 124 | 00:00 | Sunamganj | 135 | 03:00 | 128 | 18:30
Kallyanpur | 133 | 05:00 | 128 | 00:00 | Sylhet | 137 | 06:00 | 131 | 21:00
Kalurghat | 140 | 13:00 | 129 | 00:00 | Sylhet-132 | 135 | 04:00 | 131 | 20:00
Kamrangirchar | 137 | 00:00 | 128 | 01:00 | Tangail | 131 | 06:00 | 122 | 18:30
Kaptai | 141 | 13:00 | 131 | 1:00 | Taraganj | 130 | 06:00 | 124 | 18:00
Kasba | 137 | 11:00 | 123 | 00:00 | Tasnim | 132 | 13:00 | 127 | 00:00
Kazla | 134 | 08:00 | 130 | 00:00 | Thakurgaon | 136 | 04:00 | 127 | 18:00
Keranigonj | 138 | 06:00 | 131 | 00:00 | TK | 140 | 13:00 | 129 | 00:00
Khagrachori | 141 | 13:00 | 128 | 00:00 | Tongi | 136 | 13:00 | 132 | 01:00
Khulna | 135 | 05:00 | 128 | 22:00 | Ullahpara | 136 | 03:00 | 131 | 19:30
Khulna(S) | 137 | 05:00 | 125 | 00:00 | Ullon | 134 | 07:00 | 131 | 00:00
Khulshi | 138 | 13:00 | 127 | 00:00 | Uttara | 134 | 05:00 | 129 | 00:00
Kishoreganj | 134 | 04:00 | 127 | 14:00 | UttaraNew | 133 | 03:00 | 127 | 00:00
Kodda | 136 | 06:00 | 124 | 00:00 | Zigatola | 138 | 08:00 | 131 | 00:00
Korerhat | 137 | 13:00 | 127 | 09:00
KSRM | 140 | 13:00 | 128 | 00:00
Kulaura | 139 | 06:00 | 134 | 20:00
Kurigram | 129 | 05:00 | 122 | 18:00
Kushtia | 133 | 18:00 | 128 | 00:00
Laksam | 135 | 13:00 | 122 | 00:00
Lakshmipur | 132 | 13:00 | 120 | 00:00
Lalbag | 138 | 06:00 | 131 | 00:00
Lalmonirhat | 130 | 04:00 | 121 | 18:00
Madanganj | 134 | 10:00 | 128 | 00:00
Madaripur | 136 | 16:00 | 127 | 00:00
Madartek | 135 | 04:00 | 131 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division