## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 30-04-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-04-2026 | during | 30-04-2026 | during | 30-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 349 | 329 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 15 | 55 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 294 | 335 | 335 | 300 | 300 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 32 | 7 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 17 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 15 | 149 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 22.5 | 23 | 33 | 33 | 21 | 21 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 14 | 14 | 14 | 14 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 8 | 52.19 | 52.19 | 8 | 17 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 48 | 294 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 18 | 48 | 149 | 149 | 52 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 34 | 105 | 105 | 17 | 34 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 35 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 4 | 0 | 20 | 0 | 20 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0.01 | 0.01 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 475 | 460 | 584 | 584 | 480 | 480 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 310 | 314 | 718 | 718 | 380 | 380 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 30 | 160 | 160 | 17 | 108 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1500.5 | 1554 | 5959.22 | 5914.22 | 1903.01 | 2626.01
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 0 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 6 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 19 | 50 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 35 | 35 | 35 | 35 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 224 | 224 | 220 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 34 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 68 | 68 | 0 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 5 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 12 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0 | 0 | 3.15 | 0 | 3.15 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 0 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 54 | 54 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 17 | 90 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 765 | 895 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 56 | 30 | 15 | 30 | 15 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 360 | 465 | 1150 | 1150 | 935 | 1000
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1398 | 1685 | 4033.01 | 4032.86 | 2750.15 | 3060
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 187 | 195 | 221.25 | 221.25 | 0 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 365 | 358 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 345 | 345 | 342.01 | 342.01 | 342.01 | 342.01 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 353 | 330 | 393 | 393 | 350 | 350 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 10 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 8 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 36 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 60 | 140 | 18 | 140 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 103 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 17 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 114 | 102 | 84 | 78 | 128 | 128 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 3 | 24.5 | 24.5 | 5 | 5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 17 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 17 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 5 | 0 | 30 | 0 | 30 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1500 | 1490 | 2634.44 | 2678.44 | 1366.02 | 1983.02
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-04-2026 | during | 30-04-2026 | during | 30-04-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 17 | 18 | 157.5 | 157.5 | 22 | 22 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.18 | 0 | 1.81 | 0 | 1.81 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 0 | 9 | 90 | 80 | 10 | 10 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 0 | 38 | 10 | 10 | 80 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 11 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 9 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 28.18 | 74 | 377.81 | 324 | 172.81 | 131
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 30 | 30 | 30 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 147 | 155 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 10 | 110 | 100 | 100 | 0 | 100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 25 | 76 | 85 | 85 | 84 | 84 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 101 | 98 | 98 | 98 | 98 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 16 | 25 | 25 | 17 | 17 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 377 | 385 | 380 | 380 | 380 | 380
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 989 | 1213 | 1272 | 1272 | 1063 | 1163
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 550 | 925 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 36 | 36 | 30 | 30 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 300 | 300 | 410 | 410 | 250 | 250 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 1 | 0 | 40 | 0 | 40 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 763 | 1005 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1614 | 2230 | 3540.2 | 3500.2 | 2601.3 | 2561.3
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 253 | 313 | 250 | 450 | 250 | 450 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 0 | 65 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 510 | 640 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 172 | 279 | 307 | 307 | 280 | 280 | Bad quality coal
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.01 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1155.01 | 1517 | 2412 | 2611 | 2158 | 2357
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 14.06 | 0 | 51 | 0 | 51 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 70 | 199 | 220 | 220 | 198 | 198 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 20 | 20 | 20 | 20 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0.03 | 0.03 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 90 | 90 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 50 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.16 | 0 | 3 | 0 | 3 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 825 | 974 | 748 | 748 | 748 | 1356 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 34.54 | 0 | 51.97 | 0 | 51.97 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 80 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1440.76 | 1587 | 2509.96 | 2303.99 | 1612 | 2184.03
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 35 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.9 | 0 | 6.8 | 0 | 6.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 0 | 70 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 6 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 15 | 0 | 70.54 | 0 | 70.54 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 28.9 | 34 | 349.34 | 242 | 142.34 | 183
System Total |  |  |  |  | 28823.2 | 29270.237 | 9654.35 | 11384 | 23087.98 | 22878.71 | 13768.63 | 16248.36
Forecast Scenario (30-04-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 10800 |  | 0 |  | 10800
|  |  |  | 1:00 | 10400 |  | 0 |  | 10400
|  |  |  | 2:00 | 10130 |  | 0 |  | 10130
|  |  |  | 3:00 | 9820 |  | 0 |  | 9820
|  |  |  | 4:00 | 9360 |  | 0 |  | 9360
|  |  |  | 5:00 | 9520 |  | 0 |  | 9520
|  |  |  | 6:00 | 9490 |  | 0 |  | 9490
|  |  |  | 7:00 | 9990 |  | 0 |  | 9990
|  |  |  | 8:00 | 10090 |  | 0 |  | 10090
|  |  |  | 9:00 | 10160 |  | 0 |  | 10160
|  |  |  | 10:00 | 10230 |  | 0 |  | 10230
|  |  |  | 11:00 | 10140 |  | 0 |  | 10140
|  |  |  | 12:00 | 10500 |  | 0 |  | 10500
|  |  |  | 13:00 | 10110 |  | 0 |  | 10110
|  |  |  | 14:00 | 9820 |  | 0 |  | 9820
|  |  |  | 15:00 | 10070 |  | 0 |  | 10070
|  |  |  | 16:00 | 9940 |  | 0 |  | 9940
|  |  |  | 17:00 | 10080 |  | 0 |  | 10080
|  |  |  | 18:00 | 10420 |  | 0 |  | 10420
|  |  |  | 18:30 | 10900 |  | 0 |  | 10900
|  |  |  | 19:00 | 11560 |  | 0 |  | 11560
|  |  |  | 19:30 | 11650 |  | 0 |  | 11650
|  |  |  | 20:00 | 11580 |  | 0 |  | 11580
|  |  |  | 21:00 | 11700 |  | 0 |  | 11700
|  |  |  | 22:00 | 11590 |  | 0 |  | 11590
|  |  |  | 23:00 | 11450 |  | 0 |  | 11450
Probable Maximum Temperature: |  |  | 27.20°C
Probable Maximum Demand at Day Peak: |  |  | 10500.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11700.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11700.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 248.95 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:45 hrs on 30-04-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 29-04-2026 | [28 empty] | Date: | 29-04-2026 | [28 empty] | Date: | 29-04-2026 | [28 empty] | Date: | 29-04-2026 | [28 empty] | Date: | 29-04-2026 | [17 empty] | Date: | 29-04-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 20 | 14 | 0 | 420 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 28 | 640 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 215 | 357 | 345 | 51 | 0 | 174 | 0 | 0 | 78 | 0 | 0 | 3 | 0 | 108 | 0 | 0 | 0 | 300 | 0 | 386 | 30 | 30 | 152 | 0 | 16 | 0 | 83 | 30 | 0 | 0 | 101 | 0 | 9 | 58 | 11 | 0 | 0 | 0 | 5853 | 925 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 130 | 220 | 0 | 575 | 700 | 0 | 5124 | 10977 | 76.75
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 20.5 | 14 | 0 | 350 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 31 | 640 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 844 | 0 | 0 | 0 | 215 | 357 | 342 | 51 | 0 | 140 | 0 | 0 | 79 | 0 | 0 | 3 | 0 | 102 | 0 | 0 | 0 | 290 | 0 | 386 | 30 | 30 | 133 | 0 | 16 | 0 | 83 | 30 | 0 | 0 | 101 | 0 | 57 | 8 | 17 | 0 | 0 | 0 | 5680.5 | 830 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772 | 0 | 0 | 0 | 831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 130 | 220 | 0 | 501 | 650 | 0 | 4907 | 10587.5 | 76.76
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 20.5 | 14 | 0 | 350 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 32 | 640 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 215 | 300 | 260 | 51 | 0 | 140 | 0 | 0 | 79 | 0 | 0 | 3 | 0 | 100 | 0 | 0 | 0 | 295 | 0 | 376 | 30 | 30 | 135 | 0 | 16 | 0 | 22 | 30 | 0 | 0 | 101 | 0 | 57 | 9 | 18 | 0 | 0 | 0 | 5297.5 | 829 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 100 | 180 | 0 | 376 | 600 | 0 | 4565 | 9862.5 | 76.76
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 21 | 14 | 0 | 300 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 32 | 640 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 215 | 300 | 250 | 10 | 0 | 140 | 0 | 0 | 77 | 0 | 0 | 3 | 0 | 104 | 0 | 0 | 0 | 270 | 0 | 302 | 30 | 20 | 135 | 0 | 16 | 0 | 22 | 20 | 0 | 0 | 101 | 0 | 8 | 9 | 19 | 0 | 0 | 0 | 4937 | 924 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0 | 0 | 826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 100 | 180 | 0 | 251 | 600 | 0 | 4438 | 9375 | 76.76
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 21 | 14 | 0 | 310 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 32 | 630 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 628 | 0 | 0 | 0 | 215 | 300 | 220 | 0 | 0 | 140 | 0 | 0 | 80 | 0 | 0 | 3 | 0 | 94 | 0 | 0 | 0 | 180 | 0 | 303 | 30 | 20 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 4427 | 860 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 252 | 520 | 0 | 4200 | 8627 | 76.76
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 300 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 485 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 215 | 300 | 220 | 0 | 0 | 140 | 0 | 0 | 77 | 0 | 0 | 3 | 0 | 102 | 0 | 0 | 0 | 180 | 0 | 309 | 30 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 4150 | 924 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 70 | 180 | 0 | 252 | 500 | 0 | 4190 | 8340 | 76.77
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 400 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0.21 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 250 | 300 | 250 | 0 | 0 | 199 | 0 | 0 | 77 | 0 | 0 | 3 | 0 | 92 | 0 | 4 | 0 | 180 | 0 | 314 | 30 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 4304.21 | 360 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.71 | 771 | 0 | 0 | 0 | 833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0 | 140 | 60 | 180 | 0 | 252 | 500 | 0 | 3729.75 | 8033.96 | 76.77
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 320 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 615 | 1 | 0 | 0 | 220 | 280 | 220 | 0 | 0 | 140 | 0 | 0 | 79 | 0 | 0 | 3 | 0 | 90 | 0 | 8 | 0 | 180 | 0 | 314 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 3894 | 164 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 779 | 0 | 0 | 0 | 865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0.06 | 0 | 140 | 40 | 180 | 0 | 253 | 500 | 0 | 3425.46 | 7319.46 | 76.77
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.88 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 617 | 3 | 0 | 0 | 220 | 280 | 220 | 0 | 0 | 140 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 92 | 0 | 13 | 0 | 165 | 0 | 314 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 3845.88 | 128 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 773 | 0 | 0 | 0 | 869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0 | 0 | 0 | 0 | 30 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.5 | 4 | 0.13 | 0 | 140 | 0 | 180 | 0 | 254 | 500 | 0 | 3247.82 | 7093.7 | 76.77
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 13 | 5 | 0 | 410 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 1.56 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 619 | 7 | 0 | 0 | 250 | 300 | 220 | 0 | 0 | 192 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 165 | 0 | 321 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 101 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 4156.56 | 216 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 763 | 0 | 0 | 0 | 858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 1.3 | 2 | 0.03 | 0 | 140 | 0 | 220 | 0 | 253 | 500 | 0 | 3559.04 | 7715.6 | 76.78
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 1 | 0 | 23 | 14 | 0 | 470 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0.59 | 0 | 0 | 2 | 310 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 620 | 10 | 0 | 0 | 318 | 352 | 250 | 1 | 0 | 185 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 96 | 0 | 1 | 0 | 180 | 0 | 327 | 0 | 0 | 145 | 2 | 0 | 0 | 11 | 0 | 10 | 0 | 101 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 4591.59 | 218 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 762 | 0 | 0 | 0 | 823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.01 | 2 | 0 | 0 | 0.65 | 0 | 0 | 0 | 0 | 30 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 5.8 | 2 | 0.1 | 0 | 140 | 0 | 220 | 0 | 253 | 500 | 0 | 3591.56 | 8183.15 | 76.78
11:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 5 | 0 | 22.5 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43 | 40 | 0 | 2 | 310 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 620 | 14 | 0 | 0 | 328 | 353 | 280 | 51 | 0 | 180 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 240 | 0 | 327 | 0 | 0 | 143 | 2 | 8 | 0 | 11 | 30 | 12 | 0 | 101 | 0 | 0 | 0 | 18 | 0.32 | 0 | 0 | 4911.25 | 588 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 762 | 0 | 0 | 0 | 822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.01 | 20 | 0 | 0 | 0.47 | 0 | 0 | 0 | 0 | 50 | 0 | 354 | 0 | 0.04 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 3.8 | 3 | 0.01 | 0 | 140 | 0 | 220 | 0 | 253 | 500 | 0 | 3948.33 | 8859.58 | 76.79
12:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 310 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 4 | 0 | 22.5 | 14 | 0 | 475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 3 | 360 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 765 | 6 | 0 | 0 | 353 | 365 | 345 | 51 | 0 | 187 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 114 | 0 | 5 | 0 | 290 | 0 | 377 | 0 | 0 | 147 | 1 | 8 | 0 | 25 | 30 | 10 | 0 | 101 | 0 | 0 | 0 | 17 | 0.18 | 11 | 0 | 5415.68 | 550 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 763 | 0 | 0 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.06 | 80 | 0 | 0 | 34.54 | 0 | 0 | 0 | 0 | 70 | 0 | 414 | 0 | 3.16 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 7.9 | 15 | 0.01 | 0 | 172 | 0 | 220 | 0 | 253 | 510 | 0 | 4238.67 | 9654.35 | 76.79
13:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 300 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 8 | 0 | 23 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 4 | 380 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 840 | 12 | 0 | 0 | 325 | 300 | 300 | 51 | 0 | 176 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 102 | 0 | 1 | 0 | 300 | 0 | 387 | 0 | 0 | 142 | 1 | 16 | 0 | 42 | 30 | 9 | 0 | 101 | 0 | 0 | 0 | 10 | 0.7 | 10.6 | 0 | 5289.3 | 550 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 765 | 0 | 0 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.15 | 37 | 0 | 0 | 65.24 | 0 | 0 | 0 | 0 | 130 | 0 | 348 | 0 | 5.94 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3.7 | 3 | 0.01 | 0 | 140 | 0 | 180 | 0 | 253 | 610 | 0 | 4239.04 | 9528.34 | 76.8
14:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 244 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 23 | 14 | 0 | 380 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 783 | 5 | 0 | 0 | 337 | 320 | 300 | 51 | 0 | 181 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 86 | 0 | 1 | 0 | 310 | 0 | 344 | 0 | 0 | 138 | 2 | 16 | 0 | 42 | 30 | 111 | 0 | 101 | 0 | 0 | 0 | 10 | 0 | 25.32 | 0 | 5332.32 | 550 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 765 | 0 | 0 | 0 | 828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.19 | 87 | 0 | 0 | 44.87 | 0 | 0 | 0 | 0 | 130 | 0 | 363 | 0 | 4.21 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 3.9 | 10 | 0.01 | 0 | 140 | 0 | 180 | 0 | 253 | 590 | 0 | 4232.18 | 9564.5 | 76.8
15:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 218 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 23 | 14 | 0 | 360 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 2 | 374 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 337 | 320 | 295 | 51 | 0 | 190 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 92 | 0 | 1 | 0 | 300 | 0 | 312 | 0 | 0 | 138 | 1 | 16 | 0 | 42 | 30 | 110 | 0 | 101 | 0 | 0 | 0 | 10 | 1.02 | 0.28 | 0 | 5130.3 | 783 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 756 | 0 | 0 | 0 | 826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.36 | 72 | 0 | 0 | 36.87 | 0 | 0 | 0 | 0 | 130 | 0 | 354 | 0 | 3.46 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 1.8 | 11 | 0 | 0 | 140 | 30 | 180 | 0 | 253 | 550 | 0 | 4425.49 | 9555.79 | 76.81
16:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 207 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 9 | 0 | 23 | 14 | 0 | 320 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0.01 | 38 | 0 | 2 | 420 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 710 | 0 | 0 | 0 | 312 | 320 | 250 | 10 | 0 | 184 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 305 | 0 | 316 | 0 | 20 | 137 | 2 | 16 | 0 | 11 | 30 | 110 | 0 | 101 | 0 | 0 | 0 | 11 | 1 | 8.85 | 0 | 4922.86 | 784 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 750 | 0 | 0 | 0 | 822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.26 | 37 | 0 | 0 | 22.87 | 0 | 0 | 0 | 0 | 137 | 0 | 270 | 0 | 1.61 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 1.9 | 108 | 0.03 | 0 | 140 | 30 | 180 | 0 | 253 | 550 | 0 | 4397.67 | 9320.53 | 76.81
17:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 296 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 9 | 0 | 23 | 14 | 0 | 455 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 2 | 445 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 750 | 0 | 0 | 0 | 335 | 320 | 240 | 10 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 3 | 0 | 98 | 0 | 1 | 0 | 310 | 0 | 316 | 0 | 30 | 139 | 0 | 16 | 0 | 11 | 30 | 70 | 0 | 101 | 0 | 0 | 0 | 11 | 0.7 | 7.72 | 0 | 5167.42 | 783 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 765 | 0 | 0 | 0 | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.69 | 24 | 0 | 0 | 15.57 | 0 | 0 | 0 | 0 | 162 | 0 | 250 | 0 | 1.26 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1.2 | 36 | 0.16 | 0 | 140 | 30 | 180 | 0 | 253 | 550 | 0 | 4254.88 | 9422.3 | 76.82
18:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 305 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 2 | 15 | 23 | 14 | 0 | 460 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 465 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 345 | 320 | 265 | 10 | 0 | 198 | 0 | 0 | 50 | 0 | 0 | 3 | 0 | 98 | 0 | 0 | 0 | 310 | 0 | 316 | 0 | 30 | 152 | 0 | 16 | 0 | 11 | 30 | 70 | 0 | 102 | 0 | 13 | 9 | 11 | 0.1 | 1.77 | 0 | 5390.87 | 783 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 770 | 0 | 0 | 0 | 860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 0 | 0 | 3.99 | 0 | 0 | 0 | 0 | 200 | 0 | 370 | 0 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 6 | 0.04 | 0 | 173 | 30 | 180 | 0 | 303 | 560 | 0 | 4512.51 | 9903.38 | 76.83
19:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 314 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 30 | 23 | 14 | 0 | 460 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 465 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 895 | 0 | 0 | 8 | 330 | 358 | 345 | 36 | 0 | 195 | 10 | 0 | 103 | 0 | 0 | 3 | 0 | 102 | 0 | 0 | 0 | 310 | 0 | 385 | 0 | 30 | 155 | 0 | 16 | 0 | 76 | 30 | 110 | 0 | 101 | 0 | 38 | 9 | 18 | 0 | 0 | 9 | 6016 | 925 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 0 | 0 | 0 | 974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 65 | 220 | 0 | 313 | 640 | 0 | 5368 | 11384 | 76.8
19:30 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 250 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 35 | 23 | 14 | 0 | 370 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 3 | 565 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 880 | 0 | 0 | 8 | 385 | 357 | 345 | 51 | 0 | 190 | 10 | 0 | 104 | 0 | 0 | 3 | 0 | 102 | 0 | 0 | 0 | 305 | 0 | 386 | 0 | 30 | 126 | 0 | 16 | 0 | 76 | 30 | 110 | 0 | 101 | 0 | 58 | 9 | 20 | 0 | 0 | 12 | 6013 | 925 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 906 | 0 | 0 | 0 | 981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 65 | 180 | 0 | 304 | 780 | 0 | 5130 | 11143 | 76.8
20:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 233 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 35 | 23 | 14 | 0 | 395 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 4 | 580 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 875 | 0 | 0 | 0 | 300 | 358 | 345 | 51 | 0 | 192 | 0 | 0 | 104 | 0 | 0 | 4 | 0 | 98 | 0 | 0 | 0 | 300 | 0 | 392 | 0 | 30 | 127 | 0 | 16 | 0 | 81 | 30 | 110 | 0 | 101 | 0 | 66 | 9 | 20 | 0 | 0 | 12 | 5953 | 925 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 862 | 0 | 0 | 0 | 942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 65 | 220 | 0 | 306 | 810 | 0 | 5102 | 11055 | 76.85
21:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 237 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 17 | 23 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 12 | 620 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 875 | 0 | 0 | 0 | 220 | 357 | 345 | 51 | 0 | 190 | 0 | 0 | 104 | 0 | 0 | 5 | 0 | 94 | 0 | 0 | 0 | 300 | 0 | 392 | 0 | 30 | 130 | 0 | 16 | 0 | 81 | 30 | 110 | 0 | 101 | 0 | 66 | 9 | 20 | 0 | 0 | 12 | 5892 | 925 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 0 | 0 | 0 | 889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 65 | 220 | 0 | 305 | 795 | 0 | 5030 | 10922 | 76.86
22:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 193 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 17 | 21 | 14 | 0 | 320 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 15 | 540 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 757 | 0 | 0 | 0 | 220 | 357 | 300 | 10 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 5 | 0 | 88 | 0 | 0 | 0 | 285 | 0 | 320 | 0 | 30 | 132 | 0 | 16 | 0 | 11 | 30 | 109 | 0 | 101 | 0 | 57 | 9 | 18 | 0 | 0 | 12 | 5125 | 924 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 747 | 0 | 0 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 65 | 180 | 0 | 303 | 650 | 0 | 4493 | 9618 | 76.87
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 208 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 17 | 21 | 14 | 0 | 320 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 616 | 0 | 0 | 0 | 230 | 340 | 250 | 10 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 7 | 0 | 90 | 0 | 0 | 0 | 295 | 0 | 318 | 0 | 18 | 138 | 0 | 0 | 0 | 0 | 30 | 25 | 0 | 101 | 0 | 58 | 9 | 18 | 0 | 0 | 0 | 4581 | 924 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 746 | 0 | 0 | 0 | 826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 65 | 180 | 0 | 303 | 550 | 0 | 4354 | 8935 | 76.88
Total KWH | 0 | 214084 | 88320 | 0 | 0 | 0 | 0 | 0 | 8157600 | 0 | 5841184 | 0 | 0 | 436320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6081412 | 0 | 0 | 48460 | 168000 | 48300 | 344160 | 0 | 9147727.27 | 0 | 0 | 0 | 0 | 719520 | 0 | 0 | 0 | 0 | 0 | 4723 | 679140 | 0 | 224160 | 11098181.82 | 0 | 0 | 0 | 0 | 0 | 4909613 | 0 | 0 | 0 | 17541816 | 57340 | 0 | 16727 | 6631500 | 8268700 | 6708000 | 672432 | 0 | 4151000 | 11232 | 0 | 1814382 | 0 | 0 | 55990 | 0 | 2203200 | 0 | 39518 | 0 | 6262000 | 0 | 8236000 | 200000 | 349800 | 3223554.54 | 10769 | 257136 | 0 | 577920 | 489696 | 1017900 | 0 | 2425380 | 0 | 434400 | 110400 | 291840 | 4600 | 62910 | 46800 | 120383847.63 | 16629818 | 5600448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168480 | 18705455 | 0 | 0 | 0 | 19937090 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151904 | 485500 | 0 | 0 | 182256 | 0 | 0 | 0 | 0 | 3460764 | 0 | 7821673 | 0 | 15840 | 0 | 0 | 0 | 60267 | 49488 | 0 | 0 | 0 | 29118.36 | 221760 | 501 | 0 | 3862000 | 952000 | 4994380 | 0 | 6916363 | 14682181.82 | 0 | 104927287.18 | 225311134.81

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 29-04-2026
Power Supply Scenario
| Day Peak Generation |  |  | 9654.35 | MW | 12:00 Hr. | Energy Generated |  |  | 225.3111 |  | MKWHr.
| Day Peak Demand |  |  | 9654.35 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11384 | MW | 19:00 Hr. | Energy Demand |  |  | 225.3111 |  | MKWHr.
| Evening Peak Demand |  |  | 11384 | MW | 19:00 Hr. | Maximum Temperature |  |  | 23.4 |  | °C
| Minimum Generation of the Day |  |  | 7093.7 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 792.48 |  | MMCFD
| Maximum Generation of the Day |  |  | 11384 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.1368 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 29.6204 | 0 | 0.90672 | 0 | 0 | 0.04846 | 0 | 0 | 30.5756 | Gas | 109.2446 | Gas | 377882294.3027
| Chattogram Zone |  |  | 5.1338 | 28.64 | 0 | 0 | 0.67914 | 0.062063 | 0 | 0.71952 | 35.2345 | Coal | 72.806 | Coal | 499489501.6052
| Cumilla Zone |  |  | 28.33 | 0 | 0 | 0 | 0 | 0.039518 | 2.2032 | 0 | 30.5727 | HFO | 1.5478 | HFO | 27501856
| Mymensingh Zone |  |  | 0.29184 | 0 | 0.5916 | 0 | 0 | 0.06751 | 0 | 0 | 0.95095 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.0394 | 0 | 0 | 0 | 0 | 0.010769 | 0 | 0 | 23.0502 | Hydro | 0.67914 | Hydro | 67914
| Khulna Zone |  |  | 5.6004 | 18.7055 | 0 | 0 | 0 | 0.16848 | 16.6298 | 0 | 41.1042 | Solar | 1.5439 | Solar | 24088002.732
| Barishal Zone |  |  | 5.9464 | 25.4605 | 0 | 0 | 0 | 0.000501 | 0 | 0 | 31.4074 | Import | 38.7701 | Import | 217761499.4
| Rajshahi Zone |  |  | 11.2824 | 0 | 0 | 0 | 0 | 0.8355 | 19.9371 | 0 | 32.055 | Wind | 0.71952 | Wind | 10584139.2
| Rangpur Zone |  |  | 0 | 0 | 0.049488 | 0 | 0 | 0.31115 | 0 | 0 | 0.36063
| Total |  |  | 109.2446 | 72.806 | 1.5478 | 0 | 0.67914 | 1.5439 | 38.7701 | 0.71952 | 225.3111
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 377882294.3027 |  | Hydro | 67914
|  |  |  | Coal | 499489501.6052 |  | Solar | 24088002.732
|  |  |  | HFO | 27501856 |  | Import | 217761499.4
|  |  |  | HSD | 0 |  | Wind | 10584139.2
[5 empty] | Total: | 115,73,75,207 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 26763.64 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 16.6298 | Peak Hr Flow | 925.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 36337345.45 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 19.9371 | Peak Hr Flow | 974.00 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1779 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.2032 | Peak Hr Flow | 102.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2381 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 38.7701 | Peak Hr Flow | 2001.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4411
|  |  |  | Chattogram |  | 0 |  | 1045
|  |  |  | Cumilla |  | 0 |  | 915
|  |  |  | Mymensingh |  | 0 |  | 824
|  |  |  | Sylhet |  | 0 |  | 351
|  |  |  | Khulna |  | 0 |  | 1415
|  |  |  | Barishal |  | 0 |  | 254
|  |  |  | Rajshahi |  | 0 |  | 1118
|  |  |  | Rangpur |  | 0 |  | 753
|  |  |  | Total |  | 0 |  | 11086
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Rangpur 20 MW GTPP |  |  | 20
|  | 2 | Baghabari 100 MW GTPP |  |  | 100
|  | 3 | Barapukuria TPP Unit-2 |  |  | 85
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 320 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 320
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:07 |  | Sirajgonj 225MW CCPP Unit-1 GT Ready with remarks:- Maintenance has been completed.
| 08:07 |  | Sirajgonj 225MW CCPP Unit-1 ST Ready with remarks:- Maintenance has been completed.
| 08:08 | 10:30 | Kabirpur -Tongi 132kV Ckt-2 Tripped from Tongi 230/132/33kV end showing Distance relay
relays Due to bad Weather and over voltage
| 08:25 | 00:09 | Gopalganj 400/132kV S/S 400kV Bus-01 Scheduled S/D
|  | 08:42 | Hasnabad 230/132kV S/S AUTO TR-2 LT is restored.
|  | 09:32 | Sirajganj 132/33kV S/S T3-(435) LT is restored.
|  | 09:32 | Sirajganj 132/33kV S/S T3-(435) HT is restored.
| 09:37 | 12:54 | Jhenaidah-Kushtia 132kV Ckt-2 Tripped from Kushtia 132/33kV end showing Siemens 7SA87 | [7 empty] | 27.0MW load
|  |  | relays. | [7 empty] | interrup. Kushtia
132/33kV end
| 09:37 | 12:52 | Jhenaidah-Kushtia 132kV Ckt-1 Tripped from Kushtia 132/33kV end showing Siemens 7SA87 | [7 empty] | 27.0MW load
|  |  | relays. | [7 empty] | interrup. Kushtia
132/33kV end
| 09:53 |  | Bashundhara-Tongi 132 kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to for Navy
construction works
| 10:01 | 16:32 | Hasnabad 230/132kV S/S Bus-1 Tripped showing 1) BUS-1 pro (DISC) 2) BUS-2 pro
(check) 3) 86B1 4) 86B4 5) Trip relay BUS-1 relays Due to BUS-1 CVT blust
| 10:47 | 12:56 | Khulna(S) 230/132kV S/S 230 KV Main Bus 2 Scheduled S/D Due to control card change
| 10:58 | 11:45 | Khulna (C) S/S TR-1 425T LT Tripped showing O/C relays Due to Khulna PBS and Paikgasa | [7 empty] | 22.0MW load
|  |  | Feeder fault. | [7 empty] | interrup.
| 10:58 | 11:44 | Khulna (C) S/S TR-1 425T HT Tripped showing No Relay. relays Due to Khulna PBS and | [7 empty] | 22.0MW load
|  |  | paikgasa PBS Fault. | [7 empty] | interrup.
| 11:06 | 11:29 | Gallamari- Khulna (S) 132kV Ckt-2 Tripped from Gollamari 132/33kV end showing Line
Differential and Directional OC/EF Relay relays Due to Thundering and from Khulna(S)
230/132kV end showing Differential relay relays Due to Thundering
| 11:32 | 11:34 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing Definite O/C, instt O/C, instt E/F | [7 empty] | 17.0MW load
|  |  | relays Due to WZPDCL 33kV feeder fault - Dopdapia 2 | [7 empty] | interrup.
| 11:35 | 23:58 | Dohazari 132/33kV S/S 100 MW PPP Tripped showing Differential Relay. relays Due to Due
to R phase LA blast .
| 11:51 | 12:00 | Srinagar 132/33kV S/S Tr-01 LT Tripped showing Lockout Relay-01, 02 Overcurrent | [7 empty] | 3.5MW load
|  |  | Protection Relay relays Due to Fault occur in 33 KV Feeder-02 | [7 empty] | interrup.
| 11:51 | 12:00 | Srinagar 132/33kV S/S Tr-02 LT Tripped showing Lockout Relay-01, 02 Overcorrect | [7 empty] | 3.5MW load
|  |  | Protection Relay relays Due to Fault in 33 KV Feeder-02 | [7 empty] | interrup.
| 11:57 | 00:14 | Hasnabad-Sitalakhya 132kV Ckt-1 Tripped from Shitalakhya 132/33kV end showing SEL relays | [7 empty] | 53.0MW load
|  |  | Due to E/F R phase | [7 empty] | interrup.
Shitalakhya
132/33kV end
| 12:00 |  | Day peak generation is 9652 MW.
| 12:06 |  | Barapukuria-Rangpur 132 kV Ckt-1 Tripped from Barapukuria 230/132/33kV end showing REL
511 relays Due to None
| 12:06 | 12:38 | Barapukuria-Rangpur 132 kV Ckt-2 Tripped from Barapukuria 230/132/33kV end showing Simens
siprotec relays.
| 12:07 | 12:17 | Benapole 132/33kV S/S Transformer-1(406T) LT Tripped showing REF630 relays Due to | [7 empty] | 26.0MW load
|  |  | Benapole Sharsha 33 KV feeder Trip due to heavy wind | [7 empty] | interrup.
| 12:20 | 13:02 | Ishurdi 132/33kV S/S 132/33 kV T-3 LT Tripped showing micom relays Due to 33kv feeder | [7 empty] | 27.0MW load
|  |  | fault | [7 empty] | interrup.
| 12:37 | 14:18 | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT Forced S/D Due to Bagha feeder fault | [7 empty] | 28.0MW load
interrup.
| 12:38 | 14:18 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT Forced S/D Due to Bagha feeder faulty | [7 empty] | 28.0MW load
interrup.
| 13:17 | 13:34 | Cumilla(S) 132/33kV S/S TR-4 LT Tripped showing REF 615 relays Due to 33 KV Kotbari | [7 empty] | 29.0MW load
|  |  | feeder fault. C.B. Not trip. | [7 empty] | interrup.
| 13:17 | 13:32 | Cumilla(S) 132/33kV S/S TR-3 LT Tripped showing REF- 615 relays Due to 33 KV Kotbari | [7 empty] | 30.0MW load
|  |  | feeder fault. C.B. Not trip. | [7 empty] | interrup.
| 13:28 | 14:14 | Chandina 132/33kV S/S TR-3 LT Forced S/D Due to For Red Hot problem at 33 kv R phase bus | [7 empty] | 4.0MW load
|  |  | DS | [7 empty] | interrup.
| 13:28 | 14:13 | Chandina 132/33kV S/S TR-3 HT Forced S/D Due to For Red Hot problem at 33 kv R phase bus | [7 empty] | 4.0MW load
|  |  | DS | [7 empty] | interrup.
| 14:15 |  | Unique Meghnaghat Power Limited (UMPL) record a general event:- @ 14:15hrs AGC test
started and @16:00 hrs AGC with FGMO started.
| 14:32 | 18:27 | Fenchuganj-Sylhet (South) 132KV Ckt-1 Project Work S/D from Sylhet (South) end Due to
Biyanibazar Line disconnect.
| 14:33 | 18:29 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Fenchuganj
230/132/33kV end Due to Beanibazar Grid SS end work
| 14:50 | 18:21 | Cumilla(S)-Kachua 132 kV Ckt-1 Scheduled S/D from Cumilla(S) 132/33kV end Due to Spring
charge maintenance. and from Kachua 230/132/33kV end Due to CB spring charge work
| 16:15 | 18:07 | Barishal 230/132kV S/S ATR-2 HT Tripped showing RET670 relays Due to LV WTI Trip
| 16:15 | 18:06 | Barishal 230/132kV S/S ATR-2 LT Tripped showing RET670 relays Due to WTI Trip LV
| 17:12 | 19:12 | Cumilla(S) 132/33kV S/S TR-2 LT Scheduled S/D Due to Energypac work.
| 17:12 | 19:12 | Cumilla(S) 132/33kV S/S TR-2 HT Scheduled S/D
| 17:55 | 21:56 | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D
| 19:00 |  | Evening Peak Generation is 11384 MW.
| 19:03 | 21:07 | Keraniganj-Nawabganj 132kV Ckt-1 Tripped from Nawabganj 132/33kV end showing Distance | [7 empty] | 17.8MW load
|  |  | protection relay, Lockout relay relays Due to Nawabganj - Keraniganj 132kV Line -1 | [7 empty] | interrup. Nawabganj
|  |  | tripped due to Keraniganj - Aminbazar 230kV Line Sky wire fall down to Nawabganj 132kV | [7 empty] | 132/33kV end and
|  |  | Line. and from Keranigonj 230/132/33kV end showing Distance Relay: Zone-01 (R-phase), | [7 empty] | 17.0MW load
|  |  | 50/67N EF. 86.1 trip relay. relays Due to Due to OPGW wire Broken with flashing at 230 | [7 empty] | interrup.
|  |  | kV Aminbazar Ckt-01, Aminbazar ckt-02. | [7 empty] | Keranigonj
230/132/33kV end
| 19:03 | 20:35 | Keraniganj-Nawabganj 132kV Ckt-2 Tripped from Nawabganj 132/33kV end showing No relays | [7 empty] | 17.9MW load
|  |  | Due to Nawabganj - Keraniganj 132kV Line -2 tripped from Keraniganj Grid due to | [7 empty] | interrup. Nawabganj
|  |  | Keraniganj - Aminbazar 230kV Line Sky wire fall down to Nawabganj 132kV Line. and from | [7 empty] | 132/33kV end and
|  |  | Keranigonj 230/132/33kV end showing Distance Relay: Zone-01 (R-phase), 50/67N EF. 86.1 | [7 empty] | 17.0MW load
|  |  | trip relay. relays Due to Due to OPGW wire Broken with flashing at 230 kV Aminbazar | [7 empty] | interrup.
|  |  | Ckt-01, Aminbazar ckt-02. | [7 empty] | Keranigonj
230/132/33kV end
| 19:04 |  | Aminbazar-Keraniganj 230kV Ckt-2 Tripped from Keranigonj 230/132/33kV end showing
Distance Relay: Zone-01 (R-phase), 50/67N EF. 86.1 trip relay. relays Due to Due to OPGW
wire Broken with flashing at 230 kV Aminbazar Ckt-01, Aminbazar ckt-02.
| 19:04 | 19:16 | Munshiganj 132/33kV S/S Transformer-1 LT Tripped showing None relays Due to PBS faulty | [7 empty] | 39.0MW load
interrup.
| 19:04 | 19:16 | Munshiganj 132/33kV S/S Transformer-2 LT Tripped showing None relays Due to PBS faulty | [7 empty] | 39.0MW load
interrup.
| 19:04 |  | Aminbazar-Keraniganj 230kV Ckt-1 Tripped from Keranigonj 230/132/33kV end showing
Distance Relay: Zone-01 (R-phase), 50/67N EF. 86.1, 86.2 trip relay operated. relays Due
to Due to OPGW wire Broken with flashing at 230 kV Aminbazar Ckt-01, Aminbazar ckt-02.
|  | 21:03 | Bogura(New)-Naogaon 132 kV Ckt-1 is restored.
|  | 21:03 | Bogura(New)-Naogaon 132 kV Ckt-1 is restored.
|  | 21:04 | Joypurhat 132/33kV S/S Naogaon Ckt.-2 is restored.
| 21:51 |  | Aminbazar-Keraniganj 230kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Broken OPGW Inspection
| 21:51 |  | Aminbazar-Keraniganj 230kV Ckt-2 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Broken OPGW Inspection
| 21:52 | 23:14 | Khulna(C )-Noapara 132kV Ckt-2 Tripped from Noapara 132/33kV end showing Distance Relay
(21): Siemens SIPROTEC 7SA87 Relay Info: Zone: Z1, Distance: 11.2km, Phase: A Phase
relays Due to Distance Relay Trip and from Khulna (C) end showing distance relay Zone -1
relays Due to Heavy rain and Storm.
| 23:49 | 23:54 | Mirpur-Uttara 3PH 132kV Ckt-1 Tripped from Mirpur 132/33kV end showing Over Voltage
tripping relays Due to Over Voltage
| 23:55 | 04:13 | Mirpur-Uttara 3PH 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to System Over
Voltage
| 00:10 | 01:34 | Bagerhat-Bhandaria 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing General
Trip OV Alarm OV Trip relays Due to Over Voltage
| 00:11 | 00:26 | Benapole-Jashore 132 kV Ckt-2 Tripped from Jashore 132/33kV end showing Dist.
Trip Zone-1 relays Due to Trip
| 00:13 | 00:33 | Kushtia 132/33kV S/S T-3 LT Tripped showing Inter Lock relays Due to Inter Lock | [7 empty] | 26.0MW load
interrup.
| 00:13 | 00:32 | Kushtia 132/33kV S/S T-3 HT Tripped showing F87T1 Differential Protection Relay relays | [7 empty] | 27.0MW load
|  |  | Due to Over Voltage | [7 empty] | interrup.
| 00:13 | 00:36 | Kushtia 132/33kV S/S T2 LT Tripped showing relays Due to Inter Lock | [7 empty] | 36.0MW load
interrup.
| 00:13 | 00:35 | Kushtia 132/33kV S/S T2 HT Tripped showing F87T1 Differential Protection Relay relays | [7 empty] | 36.0MW load
|  |  | Due to Over Voltage | [7 empty] | interrup.
| 00:29 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- ST
| 00:54 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- GT
| 06:29 |  | Feni 132/33kV S/S T-2(415T) HT Scheduled S/D Due to For Red Hot maintenance at B-Phase | [7 empty] | 24.0MW load
|  |  | 33KV Dead End Clamp | [7 empty] | interrup.
| 06:29 |  | Feni 132/33kV S/S T-2(415T) LT Scheduled S/D Due to Red Hot maintenance at B-Phase 33KV | [7 empty] | 24.0MW load
|  |  | loop Dead end clamp | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 29-04-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 329 | 8157600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 294 | 6081412 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 48300 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 344160 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 88320 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 48 | 436320 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 214084 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 48460 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 460 | 9147727.27 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 314 | 5841184 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 30 | 168000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1554 | 30575567.27
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 57340 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 679140 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 224 | 4909613 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 5 | 224160 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 4723 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 895 | 17541816 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 56 | 719520 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 465 | 11098181.82 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 1685 | 35234493.82
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 195 | 4151000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 358 | 8268700 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 345 | 6708000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 330 | 6631500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 10 | 11232 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 16727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 36 | 672432 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 103 | 1814382 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 102 | 2203200 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 3 | 55990 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 39518 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1490 | 30572681
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 18 | 291840 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 4600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 110400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 38 | 434400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 62910 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 9 | 46800 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 74 | 950950
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 10769 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 200000 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 349800 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3223554.54 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 110 | 1017900 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 489696 | plant availability zero
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 76 | 577920 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2425380 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 257136 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 6262000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 385 | 8236000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1213 | 23050155.54
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 925 | 16629818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 300 | 5600448 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 168480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1005 | 18705455 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2230 | 41104201
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 313 | 6916363 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 65 | 952000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 640 | 14682181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 4994380 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 279 | 3862000 | Bad quality coal
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 501 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1517 | 31407425.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 151904 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | 1 unit is under maintenance
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Under Maintenance
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 199 | 3460764 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 7821673 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 15840 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 974 | 19937090 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 182256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 485500 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1587 | 32055027
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Tripped
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 49488 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 29118.36 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 0 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 60267 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 221760 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 34 | 360633.36
Eastern Grid Total |  |  |  |  | 17418.042 | 6016 | 120383847.63
Western Grid Total |  |  |  |  | 11852.195 | 5368 | 104927287.18
National Grid Total |  |  |  |  | 29270.237 | 11384 | 225311134.81
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 29-04-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7545.68 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3540.3 | MW
i) Dhaka area |  |  | 4410.68 |  | MW | i) Khulna area |  |  |  | 1415 | MW
ii) Chattogram area |  |  | 1045 |  | MW | ii) Barishal area |  |  |  | 254.5 | MW
iii) Cumilla area |  |  | 915 |  | MW | iii) Rajshahi area |  |  |  | 1117.8 | MW
iv) Mymensingh area |  |  | 824 |  | MW | iv) Rangpur area |  |  |  | 753 | MW
v) Sylhet area |  |  | 351 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11085.98 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 16:00 | 67 | Hasnabad | 78 | 13:00 | 133 | Natore | 119 | 20:00
2 | AKSML | 23 | 17:00 | 68 | Hathazari | 56 | 21:00 | 134 | Nawabganj | 48.2 | 21:00
3 | Aftabnagar | 32 | 13:00 | 69 | Hatirjheel | 31 | 13:00 | 135 | Netrakona | 101 | 19:30
4 | Agargaon | 88 | 13:00 | 70 | Ishurdi | 64 | 00:00 | 136 | New | 70.1 | 12:00
5 | Agrabad | 58 | 11:00 | 71 | Jaldhaka | 56 | 19:00 | 137 | Niamatpur | 53 | 00:00
6 | Amnura | 26 | 00:00 | 72 | Jamalpur | 80 | 00:00 | 138 | Noapara | 37 | 19:00
7 | Ashuganj | 58 | 00:00 | 73 | Jashore | 114 | 00:00 | 139 | PHP | 11 | 12:00
8 | BSRM | 191 | 18:00 | 74 | Jhenaidah | 88 | 00:00 | 140 | Pabna | 81 | 19:00
9 | Bagerhat | 78 | 19:00 | 75 | Joydebpur | 126 | 19:00 | 141 | Palashbari | 86 | 19:00
10 | Bajitpur | 52 | 22:00 | 76 | Joypurhat | 46 | 10:00 | 142 | Panchagarh | 51 | 19:30
11 | Bakerganj | 8 | 20:00 | 77 | Juldah | 13 | 22:00 | 143 | Patiya | 8 | 23:00
12 | Bakulia | 66 | 19:00 | 78 | KSRM | 11 | 18:30 | 144 | Patuakhali | 47 | 21:00
13 | Banani | 36 | 13:00 | 79 | Kabirpur | 231 | 18:30 | 145 | Payra | 24 | 23:00
14 | Bangabhaban | 13 | 12:00 | 80 | Kachua | 52 | 22:00 | 146 | Postogola | 42 | 13:00
15 | Barapukuria | 56 | 20:00 | 81 | Kaliganj | 23 | 00:00 | 147 | Pubail | 33 | 14:00
16 | Barguna | 10 | 00:00 | 82 | Kallyanpur | 93 | 13:00 | 148 | Purbachal | 24 | 11:00
17 | Barishal | 84 | 10:00 | 83 | Kalurghat | 50 | 12:00 | 149 | Purbasadipur | 92 | 19:00
18 | Barishal-230 | 66 | 20:00 | 84 | Kamrangirchar | 72 | 13:00 | 150 | Rahanpur | 25 | 19:30
19 | Baroaulia | 58 | 10:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 27 | 12:00
20 | Baroirhat | 45 | 18:30 | 86 | Kasba | 10 | 22:00 | 152 | Rajbari | 62 | 19:00
21 | Bashundhara | 148 | 13:00 | 87 | Kazla | 96 | 12:00 | 153 | Rajendrapur | 109 | 19:00
22 | BashundharaCement | 5 | 01:00 | 88 | Keranigonj | 76 | 13:00 | 154 | Rajshahi | 101 | 00:00
23 | Beanibazar | 50 | 18:30 | 89 | Khagrachori | 20 | 19:00 | 155 | Rajshahi-230 | 64 | 00:00
24 | Benapole | 60 | 00:00 | 90 | Khulna | 58 | 19:00 | 156 | Ramganj | 76 | 19:00
25 | Bhaluka | 104 | 19:30 | 91 | Khulshi | 156 | 11:00 | 157 | Rampur | 32 | 00:00
26 | Bhandaria | 36 | 00:00 | 92 | Kishoreganj | 84 | 20:00 | 158 | Rangamati | 9 | 08:00
27 | Bhangura | 27 | 06:00 | 93 | Kodda | 296 | 12:00 | 159 | Rangpur | 116 | 19:00
28 | Bheramara(GK) | 54 | 00:00 | 94 | Kulaura | 32 | 19:30 | 160 | Ruppur | 3.2 | 11:00
29 | Bhulta | 196 | 16:00 | 95 | Kurigram | 54 | 19:00 | 161 | SSM | 10 | 06:00
30 | Bog-Sherpur | 58 | 00:00 | 96 | Kushtia | 130 | 00:00 | 162 | Saidpur | 83 | 19:00
31 | Bogura | 119 | 19:00 | 97 | Laksam | 25 | 13:00 | 163 | Santhia | 32 | 19:00
32 | Borhanuddin | 65 | 22:00 | 98 | Lakshmipur | 27 | 19:00 | 164 | Satkhira | 113 | 19:00
33 | Brahmanbaria | 79 | 00:00 | 99 | Lalbag | 64 | 13:00 | 165 | Satmasjid | 81 | 13:00
34 | Cantonment | 84 | 13:00 | 100 | Lalmonirhat | 44 | 18:30 | 166 | Savar | 194 | 16:00
35 | Chandina | 14 | 20:00 | 101 | MI_Cement | 17.8 | 01:00 | 167 | SevenRings | 13.81 | 12:00
36 | Chandpur | 57 | 02:00 | 102 | Madanganj | 40 | 13:00 | 168 | ShahCement | 32 | 00:00
37 | Chandraghona | 13 | 16:00 | 103 | Madaripur | 82 | 00:00 | 169 | Shahjadpur | 50 | 00:00
38 | Chapai | 56 | 12:00 | 104 | Madartek | 60 | 13:00 | 170 | Shahjibazar | 77 | 21:00
39 | Charsaidpur | 40 | 00:00 | 105 | Madunaghat | 38 | 11:00 | 171 | Shahmirpur | 37 | 20:00
40 | Chauddagram | 47 | 00:00 | 106 | Magura | 51 | 19:00 | 172 | Shariatpur | 56 | 19:00
41 | Chhatak | 24 | 19:00 | 107 | Mahasthangarh | 51 | 19:00 | 173 | Sherpur | 106 | 19:30
42 | Chowmuhani | 95 | 01:00 | 108 | Maijdee | 32 | 00:00 | 174 | Shikalbaha | 21 | 01:00
43 | Chuadanga | 110 | 00:00 | 109 | Manikganj | 106 | 00:00 | 175 | Shitalakhya | 59.2 | 15:00
44 | Coxsbazar | 105 | 12:00 | 110 | Maniknagar | 57 | 13:00 | 176 | Sholosohor | 41 | 11:00
45 | Cumilla(N) | 88 | 19:00 | 111 | Matarbari | 28 | 11:00 | 177 | Shyampur | 144 | 12:00
46 | Cumilla(S) | 113 | 12:00 | 112 | Matuail | 64 | 00:00 | 178 | Siddhirganj | 108 | 12:00
47 | Daganbhuiyan | 20 | 00:00 | 113 | Metrorail_Motijheel | 16 | 12:00 | 179 | Sirajganj | 88 | 20:00
48 | Daudkandi | 103 | 12:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sonargaon | 106 | 00:00
49 | DhakaUniversity | 68 | 13:00 | 115 | Millgate | 85 | 10:00 | 181 | Sreemongol | 28 | 22:00
50 | Dhamrai | 90 | 00:00 | 116 | Mirpur | 121 | 12:00 | 182 | Sreepur | 99 | 19:00
51 | Dhanmondi | 92 | 13:00 | 117 | Mirsorai | 46 | 08:00 | 183 | Srinagar | 36.6 | 13:00
52 | Dohazari | 58 | 23:00 | 118 | Mirzapur | 36 | 19:30 | 184 | Sunamganj | 38 | 22:00
53 | Faridpur | 124 | 00:00 | 119 | Mithapukur | 46 | 19:00 | 185 | Sylhet | 30 | 14:00
54 | Fatullah | 72 | 12:00 | 120 | Modern | N/A | N/A | 186 | Sylhet-132 | 87 | 13:00
55 | Fenchuganj | 32 | 21:00 | 121 | Mogbazar | 72.3 | 09:00 | 187 | TK | 17 | 19:30
56 | Feni | 59 | 00:00 | 122 | Mongla | 37 | 21:00 | 188 | Tangail | 122 | 20:00
57 | GPH | 76 | 08:00 | 123 | Motijheel | 35 | 13:00 | 189 | Taraganj | 16 | 18:30
58 | Ghatail | 70 | 19:00 | 124 | Muktagacha | 25 | 19:00 | 190 | Tasnim | 22 | 09:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 92 | 13:00 | 191 | Thakurgaon | 80 | 19:30
60 | Ghorashal-230 | 94 | 00:00 | 126 | Muradnagar | 30 | 19:30 | 192 | Tongi | 119 | 11:00
61 | Goalpara | 30 | 00:00 | 127 | Mymensingh | 153 | 18:30 | 193 | Ullahpara | 27 | 18:30
62 | Gollamari | 84 | 00:00 | 128 | Nabinagar | 33 | 12:00 | 194 | Ullon | 41 | 14:00
63 | Gopalganj | 80 | 19:00 | 129 | Naogaon | 98 | 19:30 | 195 | Uttara | 63 | 13:00
64 | Gulshan | 86 | 13:00 | 130 | Narail | 47 | 19:00 | 196 | UttaraNew | 40 | 13:00
65 | Halishahar | 87 | 09:00 | 131 | Narinda | 54 | 13:00 | 197 | Zigatola | 68 | 13:00
66 | HaripurSBU | 135 | 18:00 | 132 | Narshingdi | 152 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 29-04-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 10977 | 0 |  | 10977
1:00 | 10587.5 | 0 |  | 10587.5
2:00 | 9862.5 | 0 |  | 9862.5
3:00 | 9375 | 0 |  | 9375
4:00 | 8627 | 0 |  | 8627
5:00 | 8340 | 0 |  | 8340
6:00 | 8033.96 | 0 |  | 8033.96
7:00 | 7319.46 | 0 |  | 7319.46
8:00 | 7093.7 | 0 |  | 7093.7
9:00 | 7715.6 | 0 |  | 7715.6
10:00 | 8183.15 | 0 |  | 8183.15
11:00 | 8859.58 | 0 |  | 8859.58
12:00 | 9654.35 | 0 |  | 9654.35
13:00 | 9528.34 | 0 |  | 9528.34
14:00 | 9564.5 | 0 |  | 9564.5
15:00 | 9555.79 | 0 |  | 9555.79
16:00 | 9320.53 | 0 |  | 9320.53
17:00 | 9422.3 | 0 |  | 9422.3
18:00 | 9903.38 | 0 |  | 9903.38
19:00 | 11384 | 0 |  | 11384
19:30 | 11143 | 0 |  | 11143
20:00 | 11055 | 0 |  | 11055
21:00 | 10922 | 0 |  | 10922
22:00 | 9618 | 0 |  | 9618
23:00 | 8935 | 0 |  | 8935
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 29-04-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5853 | 5124 | 10977 | DAILY GENERATION CURVE
00:30 | 5766.75 | 5015.5 | 10782.25
01:00 | 5680.5 | 4907 | 10587.5 | 29-04-2026
01:30 | 5489 | 4736 | 10225
02:00 | 5297.5 | 4565 | 9862.5
02:30 | 5117.25 | 4501.5 | 9618.75
03:00 | 4937 | 4438 | 9375
03:30 | 4682 | 4319 | 9001
04:00 | 4427 | 4200 | 8627
04:30 | 4288.5 | 4195 | 8483.5
05:00 | 4150 | 4190 | 8340
05:30 | 4227.105 | 3959.875 | 8186.98
06:00 | 4304.21 | 3729.75 | 8033.96
06:30 | 4099.105 | 3577.605 | 7676.71
07:00 | 3894 | 3425.46 | 7319.46
07:30 | 3869.94 | 3336.64 | 7206.58
08:00 | 3845.88 | 3247.82 | 7093.7
08:30 | 4001.22 | 3403.43 | 7404.65
09:00 | 4156.56 | 3559.04 | 7715.6
09:30 | 4374.075 | 3575.3 | 7949.375
10:00 | 4591.59 | 3591.56 | 8183.15
10:30 | 4751.42 | 3769.945 | 8521.365
11:00 | 4911.25 | 3948.33 | 8859.58
11:30 | 5163.465 | 4093.5 | 9256.965
12:00 | 5415.68 | 4238.67 | 9654.35
12:30 | 5352.49 | 4238.855 | 9591.345
13:00 | 5289.3 | 4239.04 | 9528.34
13:30 | 5310.81 | 4235.61 | 9546.42
14:00 | 5332.32 | 4232.18 | 9564.5
14:30 | 5231.31 | 4328.835 | 9560.145
15:00 | 5130.3 | 4425.49 | 9555.79
15:30 | 5026.58 | 4411.58 | 9438.16
16:00 | 4922.86 | 4397.67 | 9320.53
16:30 | 5045.14 | 4326.275 | 9371.415
17:00 | 5167.42 | 4254.88 | 9422.3
17:30 | 5279.145 | 4383.695 | 9662.84
18:00 | 5390.87 | 4512.51 | 9903.38
18:30 | 5703.435 | 4940.255 | 10643.69
19:00 | 6016 | 5368 | 11384
19:30 | 6013 | 5130 | 11143
20:00 | 5953 | 5102 | 11055
20:30 | 5922.5 | 5066 | 10988.5 |  | Executive Engineer
21:00 | 5892 | 5030 | 10922 |  | Network Operation Division
21:30 | 5508.5 | 4761.5 | 10270
22:00 | 5125 | 4493 | 9618
22:30 | 4853 | 4423.5 | 9276.5
23:00 | 4581 | 4354 | 8935

## En-Curve
QF-LDC-12
Date | 29-04-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3671 | 1584 | 925 | 0 | 108 | 827 | 35 | 3691 | 0 | 17 | 67 | 0 | 0 | 52 | 0 | DAILY ENERGY CURVE
00:30 | 3646.5 | 1541.75 | 877.5 | 0 | 105 | 829 | 35 | 3639.5 | 0 | 8.5 | 66 | 0 | 0 | 33.5 | 0 | 29-04-2026
01:00 | 3622 | 1499.5 | 830 | 0 | 102 | 831 | 35 | 3588 | 0 | 0 | 65 | 0 | 0 | 15 | 0
01:30 | 3441 | 1414 | 829.5 | 0 | 101 | 829.5 | 35 | 3490.5 | 0 | 0 | 65.5 | 0 | 0 | 19 | 0 | Energy Generated | 225.3111 |  | MKWHr
02:00 | 3260 | 1328.5 | 829 | 0 | 100 | 828 | 35 | 3393 | 0 | 0 | 66 | 0 | 0 | 23 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3112 | 1270.75 | 876.5 | 0 | 102 | 827 | 35 | 3325.5 | 0 | 0 | 41.5 | 0 | 0 | 28.5 | 0 | Total Energy Requirement | 225.3111 |  | MKWHr
03:00 | 2964 | 1213 | 924 | 0 | 104 | 826 | 35 | 3258 | 0 | 0 | 17 | 0 | 0 | 34 | 0
03:30 | 2859.5 | 1145 | 892 | 0 | 99 | 827 | 35 | 3099 | 0 | 0 | 8.5 | 0 | 0 | 36 | 0
04:00 | 2755 | 1077 | 860 | 0 | 94 | 828 | 35 | 2940 | 0 | 0 | 0 | 0 | 0 | 38 | 0
04:30 | 2716 | 1049 | 892 | 0 | 98 | 831 | 17.5 | 2844.5 | 0 | 0 | 0 | 0 | 0 | 35.5 | 0
05:00 | 2677 | 1021 | 924 | 0 | 102 | 834 | 0 | 2749 | 0 | 0 | 0 | 0 | 0 | 33 | 0
05:30 | 2788 | 1101 | 642 | 0 | 97 | 833.5 | 0 | 2692 | 2.98 | 0 | 0 | 0 | 0 | 30.5 | 0
06:00 | 2899 | 1181 | 360 | 0 | 92 | 833 | 0 | 2635 | 5.96 | 0 | 0 | 0 | 0 | 28 | 0
06:30 | 2715.5 | 1102 | 262 | 0 | 91 | 849 | 0 | 2616 | 19.71 | 0 | 0 | 0 | 0 | 21.5 | 0
07:00 | 2532 | 1023 | 164 | 0 | 90 | 865 | 0 | 2597 | 33.46 | 0 | 0 | 0 | 0 | 15 | 0
07:30 | 2445.5 | 1006.5 | 146 | 0 | 91 | 867 | 0 | 2595.5 | 47.58 | 0 | 0 | 0 | 0 | 7.5 | 0
08:00 | 2359 | 990 | 128 | 0 | 92 | 869 | 0 | 2594 | 61.7 | 0 | 0 | 0 | 0 | 0 | 0
08:30 | 2543.5 | 1095 | 172 | 0 | 75 | 863.5 | 0 | 2589.5 | 54.65 | 0 | 0 | 0 | 0 | 11.5 | 0
09:00 | 2728 | 1200 | 216 | 0 | 58 | 858 | 0 | 2585 | 47.6 | 0 | 0 | 0 | 0 | 23 | 0
09:30 | 2911.5 | 1253 | 217 | 0 | 77 | 840.5 | 0 | 2585 | 46.875 | 0 | 0 | 0 | 0 | 18.5 | 0
10:00 | 3095 | 1306 | 218 | 0 | 96 | 823 | 0 | 2585 | 46.15 | 0 | 0 | 0 | 0 | 14 | 0
10:30 | 3139.5 | 1383.75 | 403 | 0 | 93 | 822.5 | 20 | 2585 | 63.615 | 4 | 0 | 0 | 0 | 7 | 0
11:00 | 3184 | 1461.5 | 588 | 0 | 90 | 822 | 40 | 2585 | 81.08 | 8 | 0 | 0 | 0 | 0 | 0
11:30 | 3353 | 1513.5 | 569 | 0 | 102 | 823.5 | 40 | 2704 | 134.965 | 8 | 9 | 0 | 0 | 0 | 0
12:00 | 3522 | 1565.5 | 550 | 0 | 114 | 825 | 40 | 2823 | 188.85 | 8 | 18 | 0 | 0 | 0 | 0
12:30 | 3423 | 1518.75 | 550 | 0 | 108 | 825 | 38.5 | 2905.5 | 180.095 | 21 | 21.5 | 0 | 0 | 0 | 0
13:00 | 3324 | 1472 | 550 | 0 | 102 | 825 | 37 | 2988 | 171.34 | 34 | 25 | 0 | 0 | 0 | 0
13:30 | 3370.5 | 1435 | 550 | 0 | 94 | 826.5 | 36.5 | 2949.5 | 193.92 | 34 | 25 | 0 | 0 | 31.5 | 0
14:00 | 3417 | 1398 | 550 | 0 | 86 | 828 | 36 | 2911 | 216.5 | 34 | 25 | 0 | 0 | 63 | 0
14:30 | 3390 | 1371 | 666.5 | 0 | 89 | 827 | 36 | 2869.5 | 196.645 | 25.5 | 25 | 0 | 0 | 64 | 0
15:00 | 3363 | 1344 | 783 | 0 | 92 | 826 | 36 | 2828 | 176.79 | 17 | 25 | 0 | 0 | 65 | 0
15:30 | 3259 | 1284.5 | 783.5 | 0 | 91 | 824 | 37 | 2825.5 | 229.66 | 17 | 22 | 0 | 0 | 65 | 0
16:00 | 3155 | 1225 | 784 | 0 | 90 | 822 | 38 | 2823 | 282.53 | 17 | 19 | 0 | 0 | 65 | 0
16:30 | 3120.5 | 1342 | 783.5 | 0 | 94 | 830 | 38 | 2863 | 202.415 | 17 | 18 | 0 | 0 | 63 | 0
17:00 | 3086 | 1459 | 783 | 0 | 98 | 838 | 38 | 2903 | 122.3 | 17 | 17 | 0 | 0 | 61 | 0
17:30 | 3259 | 1472.5 | 783 | 0 | 98 | 849 | 39 | 2972 | 69.84 | 28.5 | 29 | 0 | 0 | 63 | 0
18:00 | 3432 | 1486 | 783 | 0 | 98 | 860 | 40 | 3041 | 17.38 | 40 | 41 | 0 | 0 | 65 | 0
18:30 | 3636 | 1563 | 854 | 0 | 100 | 917 | 40 | 3319 | 8.69 | 56 | 89.5 | 0 | 0 | 60.5 | 0
19:00 | 3840 | 1640 | 925 | 0 | 102 | 974 | 40 | 3597 | 0 | 72 | 138 | 0 | 0 | 56 | 0
19:30 | 3671 | 1425 | 925 | 0 | 102 | 981 | 40 | 3662 | 0 | 77 | 195 | 0 | 0 | 65 | 0
20:00 | 3683 | 1468 | 925 | 0 | 98 | 942 | 40 | 3612 | 0 | 77 | 159 | 0 | 0 | 51 | 0
20:30 | 3638 | 1503.5 | 925 | 0 | 96 | 915.5 | 40 | 3615 | 0 | 59.5 | 149 | 0 | 0 | 47 | 0
21:00 | 3593 | 1539 | 925 | 0 | 94 | 889 | 40 | 3618 | 0 | 42 | 139 | 0 | 0 | 43 | 0
21:30 | 3404 | 1370.5 | 924.5 | 0 | 91 | 854.5 | 40 | 3395 | 0 | 42 | 125.5 | 0 | 0 | 23 | 0
22:00 | 3215 | 1202 | 924 | 0 | 88 | 820 | 40 | 3172 | 0 | 42 | 112 | 0 | 0 | 3 | 0
22:30 | 3079 | 1197.5 | 924 | 0 | 89 | 823 | 40 | 2978.5 | 0 | 29.5 | 106.5 | 0 | 0 | 9.5 | 0
23:00 | 2943 | 1193 | 924 | 0 | 90 | 826 | 40 | 2785 | 0 | 17 | 101 | 0 | 0 | 16 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 29-04-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 404 | 07:00 | 387 | 12:00 | Madunaghat | 408 | 08:00 | 399 | 01:00
Amtali | 416 | 03:00 | 409 | 00:00 | Meghnaghat | 405 | 08:00 | 392 | 00:00
Ashuganj | 412 | 03:00 | 397 | 19:00 | Payra | 417 | 06:00 | 412 | 19:00
Bhulta | 419 | 08:00 | 394 | 12:00 | Rahanpur | 420 | 03:00 | 407 | 19:00
Bibiana | 414 | 07:00 | 402 | 12:00 | Rampal | 410 | 04:00 | 400 | 00:00
BIPTC | 408 | 07:00 | 394 | 00:00
Bogura | 413 | 03:00 | 395 | 19:00
Gopalganj | 410 | 08:00 | 397 | 19:00
Kaliakoir | 401 | 08:00 | 379 | 12:00
Korerhat | 413 | 08:00 | 401 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 245 | 08:00 | 231 | 12:00 | Jhenaidah | 236 | 23:00 | 220 | 19:00
AKSML | 237 | 08:00 | 232 | 00:00 | Kachua | 237 | 08:00 | 228 | 00:00
Aminbazar | 246 | 07:00 | 232 | 12:00 | Kaliakoir | 248 | 08:00 | 233 | 12:00
Ashuganj | 242 | 07:00 | 229 | 12:00 | Keranigonj | 243 | 08:00 | 225 | 19:30
Ashuganj-400 | 242 | 07:00 | 229 | 12:00 | Khulna(S) | 238 | 23:00 | 224 | 19:00
Baghabari | 240 | 07:00 | 229 | 18:30 | Korerhat | 238 | 08:00 | 229 | 00:00
Barapukuria | 240 | 05:00 | 214 | 19:00 | Madunaghat | 238 | 07:00 | 230 | 08:00
Barapukuria-230 | 240 | 05:00 | 214 | 19:00 | Madunaghat-400 | 238 | 07:00 | 232 | 00:00
Barishal | 232 | 08:00 | 226 | 00:00 | Maniknagar | 241 | 08:00 | 227 | 12:00
Bheramara | 235 | 06:00 | 223 | 00:00 | Meghnaghat | 247 | 08:00 | 234 | 12:00
Bhulta | 242 | 08:00 | 227 | 12:00 | Meghnaghat-400 | 240 | 08:00 | 230 | 12:00
Bibiana | 240 | 07:00 | 233 | 12:00 | Mirsorai | 238 | 08:00 | 231 | 01:00
BIPTC | 237 | 03:00 | 224 | 18:30 | Naogaon | 229 | 06:00 | 215 | 19:00
Bogura | 243 | 06:00 | 230 | 19:00 | Purbasadipur | 241 | 06:00 | 211 | 19:00
Bogura-400 | 243 | 06:00 | 229 | 19:00 | Rajshahi | 232 | 03:00 | 222 | 19:00
Borhanuddin | 234 | 11:00 | 230 | 00:00 | Rampal | 235 | 23:00 | 225 | 00:00
BSRM | 236 | 08:00 | 228 | 01:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 237 | 08:00 | 228 | 00:00 | Rampura | 240 | 08:00 | 227 | 12:00
Cumilla(N) | 240 | 07:00 | 228 | 19:30 | Shikalbaha | 236 | 08:00 | 233 | 00:00
Faridpur | 231 | 09:00 | 222 | 00:00 | Shyampur | 242 | 08:00 | 227 | 21:00
Fenchuganj | 243 | 03:00 | 238 | 12:00 | Siddhirganj | 242 | 06:00 | 229 | 12:00
Feni | 237 | 08:00 | 229 | 00:00 | Sirajgonj | 250 | 13:00 | 236 | 18:30
Ghorashal | 243 | 05:00 | 230 | 00:00 | Sreepur | 239 | 08:00 | 226 | 12:00
Ghorashal-230 | 241 | 08:00 | 226 | 12:00 | Tongi | 242 | 07:00 | 226 | 00:00
Gopalganj | 230 | 08:00 | 222 | 19:00
GPH | 237 | 08:00 | 233 | 00:00
Haripur | 241 | 08:00 | 229 | 12:00
Hasnabad | 245 | 07:00 | 226 | 19:00
Hathazari | 234 | 07:00 | 229 | 00:00
Ishurdi | 238 | 02:00 | 226 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 141 | 06:00 | 127 | 12:00 | Madunaghat | 138 | 07:00 | 135 | 15:00
Agargaon | 140 | 08:00 | 132 | 12:00 | Magura | 140 | 22:00 | 128 | 00:00
Agrabad | 136 | 03:00 | 134 | 00:00 | Mahasthangarh | 142 | 06:00 | 129 | 19:00
AKS | 135 | 13:00 | 132 | 00:00 | Maijdee | 133 | 08:00 | 128 | 00:00
Aminbazar | 142 | 07:00 | 132 | 12:00 | Manikganj | 137 | 09:00 | 128 | 00:00
Amnura | 137 | 06:00 | 130 | 00:00 | Maniknagar | 142 | 08:00 | 134 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 136 | 16:00 | 124 | 12:00
Ashuganj-230 | 146 | 07:00 | 138 | 00:00 | Matuail | 141 | 08:00 | 133 | 00:00
Bagerhat | 139 | 23:00 | 124 | 19:30 | Metrorail_Motijheel | 142 | 08:00 | 130 | 21:00
Bajitpur | 141 | 08:00 | 130 | 17:00 | Metrorail_Uttara | 141 | 08:00 | 131 | 13:00
Bakerganj | 136 | 10:00 | 132 | 19:30 | Millgate | 142 | 08:00 | 132 | 12:00
Bakulia | 138 | 05:00 | 135 | 10:00 | Mirpur | 140 | 07:00 | 131 | 12:00
Banani | 141 | 07:00 | 128 | 12:00 | Mirzapur | 143 | 08:00 | 128 | 19:00
Bangabhaban | 142 | 08:00 | 133 | 12:00 | Mithapukur | 141 | 06:00 | 126 | 19:00
Barapukuria | 140 | 05:00 | 123 | 19:00 | MI_Cement | 140 | 08:00 | 127.4 | 10:00
Barguna | 136 | 05:00 | 133 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 136 | 11:00 | 132 | 00:00 | Mogbazar | 136 | 05:00 | 128 | 13:00
Barishal-230 | 135 | 03:00 | 131 | 19:00 | Mongla | 138 | 23:00 | 125 | 19:00
Baroaulia | 137 | 07:00 | 135 | 00:00 | Motijheel | 142 | 08:00 | 133 | 12:00
Baroirhat | 135 | 07:00 | 130 | 01:00 | Muktagacha | 145 | 07:00 | 123 | 19:00
Bashundhara | 143 | 08:00 | 126 | 14:00 | Munshiganj | 140 | 07:00 | 131 | 00:00
BashundharaCement | 141 | 08:00 | 132 | 00:00 | Muradnagar | 141 | 08:00 | 131 | 00:00
Beanibazar | 134 | 03:00 | 129 | 15:00 | Mymensingh | 143 | 07:00 | 121 | 18:30
Benapole | 139 | 22:00 | 123 | 00:00 | Nabinagar | 146 | 08:00 | 133 | 12:00
Bhaluka | 138 | 07:00 | 126 | 12:00 | Naogaon | 142 | 06:00 | 129 | 19:00
Bhandaria | 140 | 11:00 | 127 | 00:00 | Narail | 140 | 22:00 | 128 | 00:00
Bhangura | 138 | 07:00 | 131 | 00:00 | Narinda | 142 | 08:00 | 134 | 12:00
Bheramara | 138 | 06:00 | 132 | 00:00 | Narshingdi | 140 | 08:00 | 126 | 21:00
Bheramara(GK) | 138 | 22:00 | 133 | 18:30 | Natore | 136 | 06:00 | 129 | 19:00
Bhulta | 136.5 | 08:00 | 128 | 00:00 | Nawabganj | 140 | 04:00 | 126 | 21:00
Bog-Sherpur | 141 | 06:00 | 132 | 19:00 | Netrakona | 139 | 08:00 | 122 | 12:00
Bogura | 142 | 06:00 | 132 | 19:00 | New | 141 | 07:00 | 133 | 12:00
Bogura-230 | 142 | 06:00 | 132 | 19:00 | Niamatpur | 138 | 05:00 | 132 | 00:00
Brahmanbaria | 142 | 07:00 | 132 | 12:00 | Noapara | 138 | 04:00 | 127 | 00:00
Cantonment | 140 | 07:00 | 132 | 12:00 | Pabna | 138 | 23:00 | 131 | 19:00
Chandina | 141 | 08:00 | 133 | 00:00 | Palashbari | 140 | 06:00 | 125 | 18:30
Chandpur | 134 | 08:00 | 128 | 00:00 | Panchagarh | 142 | 03:00 | 127 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 139 | 08:00 | 136 | 01:00 | Patiya | 137 | 03:00 | 134 | 13:00
Chapai | 136 | 05:00 | 133 | 01:00 | Patuakhali | 135 | 08:00 | 129 | 18:30
Charsaidpur | 141 | 08:00 | 132 | 00:00 | Payra | 137 | 08:00 | 134 | 00:00
Chauddagram | 137 | 08:00 | 131 | 00:00 | PHP | 136 | 08:00 | 131 | 00:00
Chhatak | 135 | 07:00 | 128 | 15:00 | Postogola | 143 | 08:00 | 132 | 12:00
Chowmuhani | 131 | 06:00 | 127 | 00:00 | Pubail | 145 | 08:00 | 131 | 03:00
Chuadanga | 139 | 22:00 | 125 | 19:00 | Purbachal | 142 | 07:00 | 127 | 12:00
Coxsbazar | 133 | 16:00 | 123 | 12:00 | Purbasadipur | 139 | 06:00 | 122 | 19:00
Cumilla(N) | 140 | 07:00 | 132 | 12:00 | Rahanpur | 139 | 03:00 | 135 | 18:30
Cumilla(S) | 139 | 08:00 | 129 | 12:00 | Rahanpur-400 | 139 | 03:00 | 134 | 19:00
Daganbhuiyan | 135 | 08:00 | 130 | 00:00 | Rahim | 140 | 08:00 | 133 | 00:00
Daudkandi | 141 | 08:00 | 129 | 00:00 | Rajbari | 134 | 09:00 | 126 | 19:00
DhakaUniversity | 141 | 06:00 | 127 | 12:00 | Rajendrapur | 140 | 08:00 | 125 | 19:00
Dhamrai | 147 | 08:00 | 134 | 00:00 | Rajshahi | 134 | 06:00 | 128 | 00:00
Dhanmondi | 141 | 08:00 | 133.6 | 12:00 | Rajshahi-230 | 134 | 03:00 | 128 | 19:00
Dohazari | 137 | 17:00 | 132 | 11:00 | Ramganj | 133 | 10:00 | 126 | 00:00
Faridpur | 134 | 09:00 | 129 | 00:00 | Rampur | 136 | 07:00 | 134 | 00:00
Fatullah | 141 | 08:00 | 130 | 04:00 | Rampura | 139 | 04:00 | 127 | 12:00
Fenchuganj | 139 | 07:00 | 135 | 12:00 | Rangamati | 138 | 12:00 | 135 | 19:00
Feni | 135 | 08:00 | 130 | 00:00 | Rangpur | 139 | 07:00 | 124 | 19:00
Feni-230 | 136 | 08:00 | 131 | 00:00 | Ruppur | 139 | 23:00 | 133 | 18:30
Ghatail | 147 | 07:00 | 122 | 18:30 | Saidpur | 140 | 06:00 | 125 | 19:00
Ghorashal | 143 | 07:00 | 135 | 12:00 | Santhia | 138 | 07:00 | 132 | 18:00
Goalpara | 142 | 22:00 | 130 | 00:00 | Satkhira | 140 | 23:00 | 124 | 19:00
Gollamari | 140 | 22:00 | 130 | 18:30 | Satmasjid | 140 | 08:00 | 132 | 12:00
Gopalganj | 137 | 23:00 | 129 | 19:00 | Savar | 139 | 07:00 | 128 | 12:00
Gopalganj-400 | 137 | 09:00 | 132 | 19:00 | SevenRings | 146 | 08:00 | 135 | 00:00
Gulshan | 139 | 06:00 | 127 | 12:00 | ShahCement | 141 | 08:00 | 132 | 00:00
Halishahar | 137 | 03:00 | 134 | 11:00 | Shahjadpur | 141 | 07:00 | 136 | 00:00
Haripur | 141 | 08:00 | 132 | 00:00 | Shahjibazar | 139 | 08:00 | 131 | 22:00
HaripurSBU | 141 | 08:00 | 133 | 00:00 | Shahmirpur | 138 | 18:00 | 135 | 00:00
Hasnabad | 142 | 07:00 | 131 | 20:00 | Shariatpur | 136 | 09:00 | 130 | 19:00
Hathazari | 138 | 03:00 | 136 | 00:00 | Sherpur | 144 | 07:00 | 118 | 19:00
Hatirjheel | 139 | 03:00 | 128 | 12:00 | Shikalbaha | 127 | 03:00 | 124 | 00:00
Ishurdi | 140 | 23:00 | 134 | 18:30 | Shikalbaha-230 | 139 | 17:00 | 136 | 11:00
Jaldhaka | 140 | 06:00 | 119 | 19:00 | Shitalakhya | 140 | 08:00 | 129 | 19:30
Jamalpur | 143 | 07:00 | 120 | 17:00 | Sholosohor | 137 | 04:00 | 135 | 00:00
Jashore | 140 | 22:00 | 126 | 00:00 | Shyampur | 139 | 08:00 | 131 | 20:00
Jhenaidah | 143 | 22:00 | 127 | 18:30 | Shyampur-230 | 140 | 08:00 | 131 | 20:00
Jhenaidah-230 | 141 | 22:00 | 130 | 00:00 | Siddhirganj | 141 | 08:00 | 133 | 00:00
Joydebpur | 145 | 08:00 | 130 | 00:00 | Sirajganj | 140 | 07:00 | 130 | 19:00
Joypurhat | 136 | 05:00 | 128 | 19:00 | Sonargaon | 140 | 07:00 | 131 | 00:00
Juldah | 137 | 17:00 | 134 | 12:00 | Sreemongol | 139 | 07:00 | 131 | 22:00
Kabirpur | 142 | 08:00 | 127 | 12:00 | Sreepur | 139 | 08:00 | 128 | 12:00
Kachua | 135 | 09:00 | 129 | 00:00 | Srinagar | 141 | 04:00 | 128 | 19:30
Kaliakoir | 147 | 08:00 | 134 | 12:00 | SSM | 140 | 00:00 | 140 | 00:00
Kaliganj | 142 | 22:00 | 128 | 19:30 | Sunamganj | 134 | 07:00 | 127 | 19:30
Kallyanpur | 140 | 07:00 | 131 | 12:00 | Sylhet | 136 | 07:00 | 130 | 20:00
Kalurghat | 138 | 02:00 | 136 | 00:00 | Sylhet-132 | 134 | 05:00 | 131 | 12:00
Kamrangirchar | 140 | 07:00 | 128 | 19:30 | Tangail | 143 | 07:00 | 124 | 18:30
Kaptai | N/A | N/A | N/A | N/A | Taraganj | 139 | 05:00 | 122 | 19:00
Kasba | 141 | 08:00 | 130 | 00:00 | Tasnim | 139 | 07:00 | 131 | 00:00
Kazla | 142 | 08:00 | 133 | 13:00 | Thakurgaon | 140 | 03:00 | 123 | 19:00
Keranigonj | 140 | 02:00 | 128 | 19:30 | TK | 138 | 05:00 | 135 | 00:00
Khagrachori | 138 | 13:00 | 135 | 01:00 | Tongi | 145 | 07:00 | 134 | 00:00
Khulna | 139 | 22:00 | 130 | 00:00 | Ullahpara | 140 | 07:00 | 131 | 19:00
Khulna(S) | 141 | 22:00 | 130 | 19:00 | Ullon | 138 | 04:00 | 127 | 12:00
Khulshi | 136 | 18:00 | 133 | 00:00 | Uttara | 143 | 08:00 | 132 | 18:30
Kishoreganj | 139 | 08:00 | 125 | 18:30 | UttaraNew | 141 | 08:00 | 131 | 12:00
Kodda | 142 | 08:00 | 122 | 10:00 | Zigatola | 140 | 02:00 | 128 | 21:00
Korerhat | 138 | 08:00 | 134 | 00:00
KSRM | 137 | 07:00 | 134 | 02:00
Kulaura | 138 | 07:00 | 134 | 12:00
Kurigram | 140 | 06:00 | 119 | 19:00
Kushtia | 138 | 23:00 | 130 | 19:00
Laksam | 135 | 09:00 | 129 | 00:00
Lakshmipur | 132 | 09:00 | 127 | 00:00
Lalbag | 140 | 06:00 | 129 | 21:00
Lalmonirhat | 155 | 14:00 | 120 | 19:00
Madanganj | 141 | 08:00 | 132 | 00:00
Madaripur | 136 | 08:00 | 131 | 00:00
Madartek | 138 | 04:00 | 126 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 29-04-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 93 | -19 | 324 | 64 | 1258 | 380 | Ishurdi-Ghorashal Ckt-1 | Export | 2671345.45
1:00 | 83 | -9 | 316 | 64 | 1132 | 398
2:00 | 94 | -13 | 364 | 50 | 1066 | 388 |  | Import | 26763.64
3:00 | 137 | -17 | 394 | 38 | 1208 | 408
4:00 | 153 | -22 | 456 | 30 | 1310 | 404 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 163 | -29 | 454 | 30 | 1334 | 380
6:00 | 80 | -17 | 296 | 2 | 1136 | 374 |  | Import | 0
7:00 | 7 | -28 | 130 | 30 | 792 | 172
8:00 | -18 | -31 | 54 | 48 | 740 | 182 | Sirajganj-Sreepur Ckt-1 | Export | 2214000
9:00 | 15 | -33 | 182 | 26 | 896 | 210
10:00 | 33 | -26 | 228 | 16 | 994 | 278 |  | Import | 0
11:00 | 110 | -27 | 380 | 70 | 1300 | 392
12:00 | 118 | -19 | 404 | 82 | 1308 | 444 | Sirajganj-Sreepur Ckt-2 | Export | 2232000
13:00 | 124 | -16 | 372 | 60 | 1290 | 414
14:00 | 120 | -18 | 410 | 76 | 1250 | 408 |  | Import | 0
15:00 | 146 | -24 | 450 | 70 | 1344 | 418
16:00 | 147 | -25 | 440 | 70 | 1326 | 394 | Gopalganj-Aminbazar Ckt-1 | Export | 14590000
17:00 | 127 | -18 | 436 | 90 | 1216 | 398
18:00 | 117 | -18 | 416 | 80 | 1204 | 370 |  | Import | 0
18:30 | 122 | -31 | 400 | 92 | 1268 | 358
19:00 | 101 | -30 | 376 | 72 | 1302 | 324 | Gopalganj-Aminbazar Ckt-2 | Export | 14630000
19:30 | 89 | -27 | 308 | 84 | 1178 | 290
20:00 | 98 | -26 | 330 | 70 | 1144 | 288 |  | Import | 0
21:00 | 117 | -19 | 380 | 84 | 1186 | 324
22:00 | 196 | -8 | 576 | 106 | 1462 | 372 |  | Total Export | 36337345.45
23:00 | 221 | -6 | 530 | 100 | 1630 | 364 |  | Total Import | 26763.64
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division