## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 03-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-05-2026 | during | 03-05-2026 | during | 03-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 390 | 351 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 15 | 55 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 335 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 32 | 7 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 17 | 17 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 15 | 149 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 0 | 55 | 55 | 17 | 17 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 24 | 33 | 33 | 26 | 26 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 14 | 14 | 14 | 14 | 14 | One unit Schedule maintenance is going on.
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 48 | 294 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 14 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 17 | 34 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 35 | 88 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 16 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 450 | 450 | 584 | 584 | 450 | 450 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 298 | 283 | 718 | 718 | 280 | 280 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 17 | 160 | 160 | 17 | 70 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1474 | 1488 | 5964.22 | 5914.22 | 1941.01 | 2477.01
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 0 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 8 | 0 | 8 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 0 | 50 | 50 | 19 | 50 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 146 | 75 | 150 | 150 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 34 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 68 | 68 | 0 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 12 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 20 | 0 | 108 | 108 | 12 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.76 | 0 | 2.59 | 0 | 2.59 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 54 | 54 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 17 | 54 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 805 | 970 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 44 | 24 | 13 | 38 | 13 | 38 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 315 | 450 | 1150 | 1150 | 935 | 935 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1426.76 | 1571 | 3940.45 | 3985.86 | 2775.59 | 3008
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 206 | 190 | 221.25 | 221.25 | 0 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 320 | 361 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 280 | 320 | 342.01 | 342.01 | 342.01 | 342.01 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 328 | 309 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 42 | 42 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 53 | 53 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 25 | 150 | 25 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 40 | 40 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 102 | 163 | 163 | 110 | 110 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 17 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 120 | 104 | 84 | 80 | 84 | 80 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 7 | 24.5 | 24.5 | 5 | 5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 17 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 17 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 51 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1369 | 1444 | 2627.44 | 2698.44 | 1792.02 | 2388.02
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-05-2026 | during | 03-05-2026 | during | 03-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 160 | 146 | 157.5 | 157.5 | 160 | 160 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.1 | 0 | 2.15 | 0 | 2.15 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 0 | 9 | 10 | 10 | 70 | 70 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 0 | 19 | 80 | 70 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 3.5 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 164.6 | 174 | 371.15 | 314 | 354.15 | 319
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 41 | 41 | 0 | 0 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 145 | 154 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 98 | 109 | 150 | 150 | 110 | 110 | ST is not available
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 84 | 85 | 85 | 84 | 84 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 101 | 100 | 100 | 98 | 98 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 17 | 25 | 25 | 17 | 17 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 344 | 392 | 380 | 380 | 380 | 380 | FGMO not available because of Cooling Tower Fan
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1208 | 1268 | 1365 | 1365 | 1093 | 1093
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 927 | 927 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 36 | 36 | 30 | 30 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 393 | 377 | 410 | 410 | 300 | 300 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 104 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 765 | 956 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2189 | 2260 | 3590.2 | 3500.2 | 2701.3 | 2611.3
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 272 | 300 | 300 | 500 | 300 | 500 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 515 | 895 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 110 | 110 | 110 | 110 | 110 | 110 | Plant availability less
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 140 | 214 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.27 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1167.27 | 1649 | 2352 | 2551 | 2125 | 2324
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 40.35 | 0 | 51 | 0 | 51 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 202 | 183 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 395 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 52 | 0 | 92 | 92 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 35 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 35 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0.02 | 0 | 3.2 | 0 | 3.2 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 835.36 | 1003.13 | 1435.88 | 1435.88 | 1356 | 1356 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 0.23 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 45 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1588.96 | 1581.13 | 3217.07 | 3001.87 | 2738.23 | 2608.03
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 0 | 49 | 49 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 34 | 34 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 0 | 70 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 17 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 97 | 0 | 200 | 0 | 200 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 167 | 0 | 547 | 311 | 320 | 154
System Total |  |  |  |  | 28823.2 | 29270.237 | 10754.59 | 11435.13 | 23974.53 | 23641.59 | 15840.3 | 16982.36
Forecast Scenario (03-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11200 |  | 0 |  | 11200
|  |  |  | 1:00 | 10840 |  | 0 |  | 10840
|  |  |  | 2:00 | 10600 |  | 0 |  | 10600
|  |  |  | 3:00 | 10340 |  | 0 |  | 10340
|  |  |  | 4:00 | 9910 |  | 0 |  | 9910
|  |  |  | 5:00 | 10110 |  | 0 |  | 10110
|  |  |  | 6:00 | 10120 |  | 0 |  | 10120
|  |  |  | 7:00 | 10120 |  | 0 |  | 10120
|  |  |  | 8:00 | 10800 |  | 0 |  | 10800
|  |  |  | 9:00 | 10900 |  | 0 |  | 10900
|  |  |  | 10:00 | 11010 |  | 0 |  | 11010
|  |  |  | 11:00 | 10960 |  | 0 |  | 10960
|  |  |  | 12:00 | 11500 |  | 0 |  | 11500
|  |  |  | 13:00 | 11020 |  | 0 |  | 11020
|  |  |  | 14:00 | 10640 |  | 0 |  | 10640
|  |  |  | 15:00 | 10800 |  | 0 |  | 10800
|  |  |  | 16:00 | 10580 |  | 0 |  | 10580
|  |  |  | 17:00 | 10630 |  | 0 |  | 10630
|  |  |  | 18:00 | 10880 |  | 0 |  | 10880
|  |  |  | 18:30 | 11300 |  | 0 |  | 11300
|  |  |  | 19:00 | 11930 |  | 0 |  | 11930
|  |  |  | 19:30 | 12000 |  | 0 |  | 12000
|  |  |  | 20:00 | 11970 |  | 0 |  | 11970
|  |  |  | 21:00 | 12000 |  | 0 |  | 12000
|  |  |  | 22:00 | 11690 |  | 0 |  | 11690
|  |  |  | 23:00 | 11650 |  | 0 |  | 11650
Probable Maximum Temperature: |  |  | 35.27°C
Probable Maximum Demand at Day Peak: |  |  | 11500.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 12000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12000.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 262.20 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:11 hrs on 03-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 02-05-2026 | [28 empty] | Date: | 02-05-2026 | [28 empty] | Date: | 02-05-2026 | [28 empty] | Date: | 02-05-2026 | [28 empty] | Date: | 02-05-2026 | [17 empty] | Date: | 02-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 450 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 730 | 0 | 0 | 0 | 330 | 358 | 345 | 51 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 92 | 0 | 0 | 0 | 310 | 0 | 394 | 41 | 30 | 143 | 0 | 16 | 0 | 84 | 30 | 38 | 0 | 100 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 5569 | 925 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 738 | 0 | 0 | 0 | 823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 340 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 130 | 110 | 0 | 300 | 610 | 0 | 4665 | 10234 | 77.92
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 350 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 616 | 0 | 0 | 0 | 320 | 358 | 300 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 92 | 0 | 0 | 0 | 305 | 0 | 392 | 41 | 30 | 136 | 0 | 0 | 0 | 0 | 20 | 37 | 0 | 100 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 5024 | 925 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 732 | 0 | 0 | 0 | 823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 332 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 120 | 110 | 0 | 250 | 540 | 0 | 4516 | 9540 | 77.92
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 310 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 624 | 0 | 0 | 0 | 255 | 358 | 275 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 90 | 0 | 0 | 0 | 305 | 0 | 343 | 32 | 12 | 138 | 0 | 0 | 0 | 0 | 20 | 38 | 0 | 100 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 4731 | 925 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762 | 0 | 0 | 0 | 823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 346 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 110 | 0 | 250 | 500 | 0 | 4508 | 9239 | 77.92
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 310 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 618 | 0 | 0 | 0 | 225 | 339 | 250 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 86 | 0 | 0 | 0 | 310 | 0 | 343 | 32 | 12 | 135 | 0 | 0 | 0 | 0 | 20 | 37 | 0 | 100 | 0 | 0 | 0 | 111 | 0 | 0 | 0 | 4464 | 830 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762 | 0 | 0 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 358 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 110 | 0 | 250 | 500 | 0 | 4409 | 8873 | 77.92
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 340 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 608 | 0 | 0 | 0 | 225 | 320 | 250 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 78 | 0 | 0 | 0 | 310 | 0 | 343 | 32 | 12 | 140 | 0 | 0 | 0 | 0 | 20 | 39 | 0 | 100 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 4458 | 397 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 0 | 0 | 0 | 826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 379 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 110 | 0 | 250 | 500 | 0 | 4047 | 8505 | 77.92
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 14 | 14 | 0 | 310 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 605 | 0 | 0 | 0 | 225 | 320 | 250 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 84 | 0 | 0 | 0 | 305 | 0 | 343 | 32 | 12 | 138 | 0 | 0 | 0 | 0 | 20 | 38 | 0 | 100 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 4261 | 361 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 349 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 110 | 0 | 250 | 500 | 0 | 3947 | 8208 | 77.92
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 1 | 0 | 14 | 14 | 0 | 320 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0.01 | 40 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 607 | 1 | 0 | 0 | 225 | 295 | 235 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 80 | 0 | 8 | 0 | 305 | 0 | 343 | 32 | 12 | 136 | 0 | 0 | 0 | 0 | 20 | 38 | 0 | 100 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 4246.01 | 361 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.32 | 748 | 0 | 0 | 0 | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6 | 0 | 0 | 3.19 | 0 | 0 | 0 | 0.62 | 0 | 0 | 0 | 0 | 157 | 0 | 359 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 140 | 100 | 110 | 0 | 250 | 500 | 0 | 4008.75 | 8254.76 | 77.92
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 7 | 0 | 15 | 14 | 0 | 420 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 1.12 | 40 | 0 | 7 | 310 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 608 | 6 | 0 | 0 | 255 | 290 | 250 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 86 | 0 | 18 | 0 | 315 | 0 | 343 | 32 | 12 | 137 | 1 | 8 | 0 | 42 | 30 | 39 | 0 | 100 | 0 | 0 | 0 | 114 | 0.1 | 0.49 | 0 | 4662.71 | 361 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.91 | 774 | 0 | 0 | 0 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6 | 0 | 0 | 5.33 | 18 | 0 | 0 | 6.43 | 0 | 0 | 0 | 0 | 168 | 0 | 382 | 0 | 0.33 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0.12 | 0 | 140 | 130 | 110 | 0 | 250 | 500 | 0 | 4174.02 | 8836.73 | 77.92
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 11 | 0 | 22 | 14 | 0 | 420 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 1.42 | 40 | 0 | 2 | 310 | 0 | 0 | 21 | 0 | 0 | 149 | 0 | 0 | 0 | 605 | 10 | 0 | 0 | 250 | 320 | 250 | 36 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 100 | 0 | 27 | 0 | 310 | 0 | 343 | 32 | 12 | 132 | 2 | 15 | 0 | 84 | 30 | 39 | 0 | 100 | 0 | 0 | 0 | 119 | 0.6 | 0.49 | 0 | 4931.51 | 361 | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 765 | 0 | 0 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 53.6 | 0 | 0 | 5.45 | 48 | 0 | 0 | 14.18 | 0 | 0 | 0 | 0 | 185 | 0 | 414 | 0 | 0.97 | 0 | 47 | 0 | 1 | 0 | 0 | 0 | 0 | 0.9 | 19 | 0.21 | 0 | 140 | 130 | 110 | 0 | 250 | 500 | 0 | 4290.31 | 9221.82 | 77.92
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 2 | 0 | 22 | 5 | 0 | 400 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 3.14 | 40 | 0 | 2 | 315 | 0 | 0 | 50 | 0 | 0 | 148 | 0 | 0 | 0 | 610 | 0 | 0 | 0 | 250 | 320 | 300 | 44 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 106 | 0 | 16 | 0 | 315 | 0 | 343 | 32 | 30 | 135 | 4 | 16 | 0 | 84 | 30 | 38 | 0 | 100 | 0 | 0 | 0 | 143 | 0.18 | 0.34 | 0 | 5001.66 | 579 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 750 | 0 | 0 | 0 | 822.96 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 38.47 | 70 | 0 | 0 | 5.01 | 0 | 0 | 0 | 0 | 185 | 0 | 343 | 0 | 0.31 | 0 | 48 | 0 | 5 | 0 | 0 | 0 | 0 | 1.8 | 52 | 0.55 | 0 | 140 | 100 | 110 | 0 | 250 | 500 | 0 | 4484.1 | 9485.76 | 77.91
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 2 | 315 | 0 | 0 | 50 | 0 | 0 | 148 | 0 | 0 | 0 | 605 | 0 | 0 | 0 | 220 | 320 | 250 | 51 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 102 | 0 | 26 | 0 | 310 | 0 | 343 | 32 | 30 | 136 | 3 | 16 | 0 | 82 | 30 | 38 | 0 | 100 | 0 | 0 | 0 | 133 | 0.9 | 4.05 | 0 | 4778.95 | 927 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 757 | 0 | 0 | 0 | 822.06 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 49.33 | 104 | 0 | 0 | 14.44 | 0 | 0 | 0 | 0 | 171 | 0 | 350 | 0 | 1.42 | 0 | 48 | 0 | 8 | 0 | 0 | 0 | 0 | 2.4 | 47 | 0.65 | 0 | 140 | 100 | 110 | 0 | 250 | 500 | 0 | 4890.3 | 9669.25 | 77.91
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 19 | 0 | 22 | 0 | 0 | 380 | 0 | 0 | 13 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0.67 | 40 | 0 | 2 | 315 | 0 | 0 | 26 | 0 | 0 | 148 | 0 | 0 | 0 | 605 | 18 | 0 | 0 | 316 | 320 | 250 | 51 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 98 | 0 | 51 | 0 | 315 | 0 | 344 | 32 | 30 | 139 | 0 | 16 | 0 | 83 | 30 | 38 | 0 | 100 | 0 | 0 | 0 | 162 | 2.9 | 39.88 | 0 | 5097.45 | 927 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 758 | 0 | 0 | 0 | 826.29 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 35.33 | 74 | 0 | 0 | 17.31 | 0 | 0 | 0 | 0 | 195 | 0 | 414 | 0 | 1.79 | 0 | 50 | 0 | 11 | 0 | 0 | 0 | 0 | 2.4 | 53 | 0.23 | 0 | 140 | 130 | 110 | 0 | 250 | 500 | 0 | 5014.35 | 10111.8 | 77.91
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 16 | 0 | 23 | 0 | 0 | 450 | 0 | 0 | 20 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 4.76 | 40 | 0 | 2 | 315 | 0 | 0 | 50 | 0 | 0 | 146 | 0 | 0 | 0 | 805 | 0 | 0 | 0 | 328 | 320 | 280 | 51 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 120 | 0 | 51 | 0 | 320 | 0 | 344 | 41 | 30 | 145 | 1 | 16 | 0 | 83 | 30 | 98 | 0 | 100 | 0 | 0 | 0 | 160 | 1.1 | 3.5 | 0 | 5642.36 | 927 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 765 | 0 | 0 | 0 | 835.36 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 40.35 | 45 | 0 | 0 | 0.23 | 0 | 0 | 0 | 0 | 202 | 0 | 414 | 0 | 0.02 | 0 | 50 | 0 | 17 | 0 | 0 | 0 | 0 | 3 | 97 | 0.27 | 0 | 140 | 130 | 110 | 0 | 272 | 515 | 0 | 5112.23 | 10754.59 | 77.91
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 268 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 6 | 0 | 23 | 0 | 0 | 450 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 2.29 | 40 | 0 | 2 | 362 | 0 | 0 | 50 | 0 | 0 | 148 | 0 | 0 | 0 | 825 | 0 | 0 | 0 | 282 | 358 | 320 | 51 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 120 | 0 | 20 | 0 | 310 | 0 | 344 | 41 | 30 | 147 | 1 | 16 | 0 | 84 | 30 | 149 | 0 | 100 | 0 | 0 | 0 | 160 | 1 | 18.72 | 0 | 5655.01 | 927 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 743 | 0 | 0 | 0 | 823.28 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 2.33 | 101 | 0 | 0 | 20.96 | 0 | 0 | 0 | 0 | 199 | 0 | 388 | 0 | 2.45 | 0 | 50 | 0 | 32 | 0 | 0 | 0 | 0 | 3 | 65 | 0.21 | 0 | 140 | 130 | 110 | 0 | 300 | 600 | 0 | 5153.23 | 10808.24 | 77.91
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 1 | 0 | 27 | 0 | 0 | 320 | 0 | 0 | 20 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 4.13 | 40 | 0 | 2 | 450 | 0 | 0 | 46 | 0 | 0 | 131 | 0 | 0 | 0 | 800 | 0 | 0 | 0 | 295 | 359 | 230 | 51 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 124 | 0 | 70 | 0 | 300 | 0 | 344 | 41 | 30 | 137 | 0 | 16 | 0 | 83 | 30 | 142 | 0 | 100 | 0 | 0 | 0 | 160 | 1.3 | 22.18 | 0 | 5404.61 | 927 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 746 | 0 | 0 | 0 | 820.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.61 | 70 | 0 | 0 | 43.75 | 0 | 0 | 0 | 0 | 176 | 0 | 342 | 0 | 4.76 | 0 | 52 | 0 | 7 | 0 | 0 | 0 | 0 | 2.2 | 16 | 0.02 | 0 | 140 | 100 | 110 | 0 | 304 | 500 | 0 | 4777.18 | 10181.79 | 77.91
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 26 | 0 | 22 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 1.13 | 36 | 0 | 2 | 450 | 0 | 0 | 42 | 0 | 0 | 75 | 0 | 0 | 0 | 649 | 0 | 0 | 0 | 285 | 300 | 230 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 25 | 0 | 290 | 0 | 344 | 41 | 30 | 136 | 1 | 16 | 0 | 0 | 20 | 125 | 0 | 100 | 0 | 0 | 0 | 160 | 0.65 | 21.78 | 0 | 4820.56 | 888 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 751 | 0 | 0 | 0 | 822.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.87 | 70 | 0 | 0 | 30.1 | 0 | 0 | 0 | 0 | 158 | 0 | 332 | 0 | 4 | 0 | 52 | 0 | 7 | 0 | 0 | 0 | 0 | 2.2 | 151 | 0.01 | 0 | 140 | 100 | 110 | 0 | 250 | 500 | 0 | 4678.3 | 9498.86 | 77.91
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 12 | 0 | 23 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0.48 | 36 | 0 | 2 | 370 | 0 | 0 | 40 | 0 | 0 | 76 | 0 | 0 | 0 | 611 | 2 | 0 | 0 | 301 | 300 | 260 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 1 | 0 | 240 | 0 | 330 | 41 | 30 | 137 | 1 | 16 | 0 | 0 | 20 | 122 | 0 | 101 | 0 | 0 | 0 | 150 | 0.56 | 10.63 | 0 | 4681.67 | 927 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 763 | 0 | 0 | 0 | 825.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.18 | 34 | 0 | 0 | 16.87 | 0 | 0 | 0 | 0 | 150 | 0 | 337 | 0 | 1.6 | 0 | 52 | 0 | 5 | 0 | 0 | 0 | 0 | 2.5 | 63 | 0.08 | 0 | 140 | 100 | 110 | 0 | 230 | 500 | 0 | 4587.39 | 9269.06 | 77.91
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 5 | 0 | 24 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 611 | 1 | 0 | 0 | 314 | 300 | 300 | 0 | 0 | 202 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 82 | 0 | 1 | 0 | 245 | 0 | 330 | 41 | 30 | 138 | 1 | 17 | 0 | 5 | 20 | 117 | 0 | 101 | 0 | 0 | 0 | 150 | 0.32 | 8.65 | 0 | 4853.97 | 928 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 762 | 0 | 0 | 0 | 825.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7 | 17 | 0 | 0 | 8.91 | 0 | 0 | 0 | 0 | 154 | 0 | 361 | 0 | 0.65 | 0 | 52 | 0 | 7 | 0 | 0 | 0 | 0 | 2.9 | 50 | 0.11 | 0 | 140 | 100 | 110 | 0 | 230 | 530 | 0 | 4604.76 | 9458.73 | 77.91
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 257 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 1 | 0 | 23 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 6 | 370 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 753 | 0 | 0 | 0 | 331 | 300 | 300 | 9 | 0 | 208 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 88 | 0 | 1 | 0 | 315 | 0 | 333 | 42 | 30 | 138 | 0 | 17 | 0 | 5 | 20 | 117 | 0 | 101 | 0 | 2 | 2 | 150 | 0.07 | 2.52 | 0 | 5219.59 | 927 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.46 | 807 | 0 | 0 | 0 | 825.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.18 | 4 | 0 | 0 | 1.86 | 0 | 0 | 0 | 0 | 165 | 0 | 378 | 0 | 0.16 | 0 | 51 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 9 | 0 | 0 | 183 | 100 | 110 | 0 | 240 | 550 | 0 | 4656.94 | 9876.53 | 77.91
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 312 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 3 | 25 | 13 | 0 | 470 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 8 | 450 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 940 | 0 | 0 | 0 | 348 | 338 | 320 | 51 | 0 | 206 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 320 | 0 | 394 | 41 | 30 | 151 | 0 | 17 | 0 | 84 | 30 | 36 | 0 | 101 | 0 | 8 | 8 | 150 | 0 | 0 | 0 | 5928 | 927 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 941 | 0 | 0 | 0 | 1032.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 414 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222 | 130 | 110 | 0 | 300 | 750 | 0 | 5393.86 | 11321.86 | 77.91
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 293 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 25 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 16 | 450 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 970 | 0 | 0 | 0 | 324 | 361 | 320 | 51 | 0 | 195 | 0 | 0 | 102 | 0 | 0 | 5 | 0 | 108 | 0 | 0 | 0 | 310 | 0 | 394 | 41 | 30 | 157 | 0 | 17 | 0 | 84 | 30 | 70 | 0 | 101 | 0 | 8 | 9 | 150 | 0 | 0 | 0 | 5917 | 927 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 958 | 0 | 0 | 0 | 1007.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 130 | 110 | 0 | 300 | 855 | 0 | 5484.16 | 11401.16 | 77.91
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 283 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 24 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 12 | 450 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 970 | 0 | 0 | 0 | 309 | 361 | 320 | 51 | 0 | 190 | 0 | 0 | 102 | 0 | 0 | 7 | 0 | 104 | 0 | 0 | 0 | 310 | 0 | 392 | 41 | 30 | 154 | 0 | 17 | 0 | 84 | 30 | 109 | 0 | 101 | 0 | 19 | 9 | 146 | 0 | 0 | 0 | 5945 | 927 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 956 | 0 | 0 | 0 | 1003.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 130 | 110 | 0 | 300 | 895 | 0 | 5490.13 | 11435.13 | 77.91
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 0 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 450 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 975 | 0 | 0 | 0 | 325 | 361 | 320 | 51 | 0 | 197 | 0 | 0 | 102 | 0 | 0 | 7 | 0 | 98 | 0 | 0 | 0 | 310 | 0 | 392 | 41 | 30 | 154 | 0 | 17 | 0 | 84 | 30 | 110 | 0 | 101 | 0 | 16 | 9 | 147 | 0 | 0 | 0 | 6015 | 927 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 870 | 0 | 0 | 0 | 924.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 130 | 110 | 0 | 250 | 866 | 0 | 5260.7 | 11275.7 | 77.91
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 22 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 18 | 450 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 947 | 0 | 0 | 0 | 311 | 361 | 320 | 51 | 0 | 190 | 0 | 0 | 103 | 0 | 0 | 7 | 0 | 104 | 0 | 0 | 0 | 315 | 0 | 391 | 41 | 30 | 152 | 0 | 17 | 0 | 84 | 30 | 110 | 0 | 101 | 0 | 0 | 9 | 143 | 0 | 0 | 0 | 5964 | 927 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 856 | 0 | 0 | 0 | 908.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 130 | 110 | 0 | 250 | 850 | 0 | 5202.56 | 11166.56 | 77.91
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 22 | 14 | 0 | 460 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 22 | 390 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 905 | 0 | 0 | 0 | 321 | 361 | 345 | 51 | 0 | 201 | 0 | 0 | 103 | 0 | 0 | 13 | 0 | 98 | 0 | 0 | 0 | 310 | 0 | 392 | 41 | 30 | 149 | 0 | 17 | 0 | 84 | 30 | 110 | 0 | 101 | 0 | 0 | 9 | 132 | 0 | 0 | 0 | 5950 | 927 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772 | 0 | 0 | 0 | 816.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 130 | 110 | 0 | 250 | 750 | 0 | 4848.34 | 10798.34 | 77.91
Total KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8506800 | 0 | 6606980 | 0 | 0 | 62496 | 0 | 0 | 0 | 70389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6555839 | 0 | 0 | 160991 | 48000 | 477000 | 205920 | 0 | 9310909.09 | 0 | 0 | 87120 | 0 | 510240 | 0 | 0 | 0 | 0 | 0 | 19927 | 939300 | 0 | 126720 | 8843636.36 | 0 | 0 | 394080 | 0 | 0 | 2659280 | 0 | 0 | 0 | 17176362 | 34965 | 0 | 0 | 6629000 | 8355200 | 6930000 | 710700 | 0 | 4885000 | 0 | 0 | 657832 | 0 | 0 | 243270 | 0 | 2304960 | 0 | 265127 | 0 | 7407000 | 0 | 8664000 | 905000 | 601440 | 3391036.36 | 18596 | 280896 | 0 | 1090560 | 616512 | 1716600 | 0 | 2415800 | 0 | 49200 | 45600 | 3229440 | 8550 | 132690 | 0 | 124350963.81 | 19051636 | 8642304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530640 | 18923637 | 0 | 0 | 0 | 20509091 | 0 | 0 | 0 | 0 | 0 | 0 | 424048 | 0 | 0 | 291992 | 617750 | 0 | 0 | 165008 | 0 | 0 | 0 | 0 | 4366582 | 0 | 9089600 | 0 | 13920 | 0 | 1003636 | 0 | 93506 | 0 | 0 | 0 | 0 | 23022.36 | 588240 | 3501 | 0 | 3797000 | 2741000 | 2691560 | 0 | 6312727 | 14717090.91 | 0 | 114597491.27 | 238948455.08

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 02-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 10754.59 | MW | 12:00 Hr. | Energy Generated |  |  | 238.9485 |  | MKWHr.
| Day Peak Demand |  |  | 10754.59 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 11435.13 | MW | 20:00 Hr. | Energy Demand |  |  | 238.9485 |  | MKWHr.
| Evening Peak Demand |  |  | 11435.13 | MW | 20:00 Hr. | Maximum Temperature |  |  | 32 |  | °C
| Minimum Generation of the Day |  |  | 8208 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 903.22 |  | MMCFD
| Maximum Generation of the Day |  |  | 11435.13 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 5.0327 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.6634 | 0 | 0.18088 | 0 | 0 | 0.16099 | 0 | 0 | 32.0053 | Gas | 120.7098 | Gas | 419284293.7065
| Chattogram Zone |  |  | 2.786 | 26.02 | 0.4812 | 0 | 0.9393 | 0.054892 | 0 | 0.51024 | 30.7916 | Coal | 70.7741 | Coal | 474797964.294
| Cumilla Zone |  |  | 28.411 | 0 | 0 | 0 | 0 | 0.26513 | 2.305 | 0 | 30.9811 | HFO | 1.1809 | HFO | 19736562.75
| Mymensingh Zone |  |  | 3.2294 | 0 | 0.0948 | 0 | 0 | 0.14124 | 0 | 0 | 3.4655 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.0888 | 0 | 0 | 0 | 0 | 0.018596 | 0 | 0 | 27.1074 | Hydro | 0.9393 | Hydro | 93930
| Khulna Zone |  |  | 8.6423 | 18.9236 | 0 | 0 | 0 | 0.53064 | 19.0516 | 0 | 47.1482 | Solar | 2.9684 | Solar | 47039929.12
| Barishal Zone |  |  | 5.4326 | 24.8268 | 0 | 0 | 0 | 0.003501 | 0 | 0 | 30.2629 | Import | 41.8657 | Import | 234107400.59
| Rajshahi Zone |  |  | 13.4562 | 0 | 0.42405 | 0 | 0 | 1.0887 | 20.5091 | 0 | 35.478 | Wind | 0.51024 | Wind | 7505630.4
| Rangpur Zone |  |  | 0 | 1.0036 | 0 | 0 | 0 | 0.70477 | 0 | 0 | 1.7084
| Total |  |  | 120.7098 | 70.7741 | 1.1809 | 0 | 0.9393 | 2.9684 | 41.8657 | 0.51024 | 238.9485
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 419284293.7065 |  | Hydro | 93930
|  |  |  | Coal | 474797964.294 |  | Solar | 47039929.12
|  |  |  | HFO | 19736562.75 |  | Import | 234107400.59
|  |  |  | HSD | 0 |  | Wind | 7505630.4
[5 empty] | Total: | 120,25,65,710 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.0516 | Peak Hr Flow | 927.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 39418400 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 20.5091 | Peak Hr Flow | 1003.13 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1963 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.305 | Peak Hr Flow | 104.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2227 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 41.8657 | Peak Hr Flow | 2034.13 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4480
|  |  |  | Chattogram |  | 0 |  | 921
|  |  |  | Cumilla |  | 0 |  | 930
|  |  |  | Mymensingh |  | 0 |  | 864
|  |  |  | Sylhet |  | 0 |  | 382
|  |  |  | Khulna |  | 0 |  | 1256
|  |  |  | Barishal |  | 0 |  | 186
|  |  |  | Rajshahi |  | 0 |  | 1196
|  |  |  | Rangpur |  | 0 |  | 691
|  |  |  | Total |  | 0 |  | 10906
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:51 | 15:56 | Jhenaidah 132/33kV S/S Jhenaidah-Kushtia 132kV Circuit-1(L1) Scheduled S/D
| 08:52 | 15:53 | Jhenaidah-Kushtia 132kV Ckt-1 Scheduled S/D from Kushtia 132/33kV end.
| 08:52 | 15:54 | Jhenaidah-Kushtia 132kV Ckt-2 Scheduled S/D from Kushtia 132/33kV end.
| 08:52 | 15:56 | Jhenaidah 132/33kV S/S Jhenaidah-Kushtia 132kV Circuit-2(L2) Scheduled S/D
|  | 08:59 | Khulshi-Madunaghat 132kV Ckt-2 is restored.
| 09:24 | 19:11 | Khulna (C) S/S TR-1 425T LT Project Work S/D Due to Tr1 shutdown for project work.
| 09:25 | 19:10 | Khulna (C) S/S TR-1 425T HT Project Work S/D Due to Tr1 shutdown for project work.
| 09:42 |  | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 LT Project Work S/D Due to DFDR testing and
commissioning
| 09:50 | 09:55 | Bagerhat-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end Due to Emergency
tree trimming work.
| 09:54 |  | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 HT Project Work S/D Due to DFDR Testing and
commissioning
|  | 09:58 | Naogaon 132/33kV S/S T-2 33kV BUS is restored.
| 10:07 | 12:53 | Savar 132/33kV S/S T-1 LT Scheduled S/D Due to Painting
| 10:08 | 12:51 | Savar 132/33kV S/S T-1 HT Scheduled S/D Due to Painting
| 10:30 | 12:12 | Kodda 132/33kV S/S Tr-3 (426T) LT Scheduled S/D Due to 33kv (section -2)incomer bus DS | [7 empty] | 25.0MW load
|  |  | change work(work by energypack) | [7 empty] | interrup.
| 10:30 | 12:12 | Kodda 132/33kV S/S Tr-4 (436T) LT Scheduled S/D Due to 33kv (section -2)incomer bus DS | [7 empty] | 25.0MW load
|  |  | change work(work by energypack) | [7 empty] | interrup.
| 10:31 | 12:06 | Kodda 132/33kV S/S Tr-3 (426T) HT Scheduled S/D Due to 33kv (section -2)incomer bus DS
change work(work by energypack)
| 10:32 | 12:10 | Kodda 132/33kV S/S Tr-4 (436T) HT Scheduled S/D Due to 33kv (section -2)incomer bus DS
change work(work by energypack)
| 10:45 |  | Bhola ( Borhanuddin) 230/33 kv Txr Trip ( 33 kv side ) Due to 33 kv Bus PT(B Phase)
Blast .
| 11:25 | 19:00 | Madanganj 132/33kV S/S BUS Coupler Forced S/D Due to 132 KV Basundhara bay equipment test
| 11:26 | 18:07 | Madanganj 132/33kV S/S Madanganj -Bashundhara 132 kv Ckt Forced S/D Due to 132 KV
Basundhara bay equipment test
| 11:29 | 16:36 | Bagerhat 132/33kV S/S Transformer-1 (403T) HT Scheduled S/D
| 11:29 | 16:36 | Bagerhat 132/33kV S/S Transformer-1 (403T) HT Scheduled S/D
| 11:29 | 16:36 | Bagerhat 132/33kV S/S Transformer-1 (403T) HT Scheduled S/D
| 11:29 | 16:37 | Bagerhat 132/33kV S/S Transformer-1 (403T) LT Scheduled S/D
| 11:29 | 16:36 | Bagerhat 132/33kV S/S Transformer-1 (403T) HT Scheduled S/D
| 11:29 | 16:36 | Bagerhat 132/33kV S/S Transformer-1 (403T) HT Scheduled S/D
| 12:00 |  | Day Peak Generation is 10752 MW.
| 12:14 | 12:24 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Overcurrent Relay relays Due to Due to
33Kv Nikra feeder fault.
| 12:19 | 13:25 | Jamalpur 132/33kV S/S Bus-A Project Work S/D Due to 132kv D.S. Upgradation Work purpose.
|  | 12:44 | Baroaulia-Khulshi 132 kV Ckt-1 is restored.
|  | 12:45 | Khulshi 132/33kV S/S Khulshi-Baraulia Circuit-2 is restored.
| 12:55 | 17:20 | Savar 132/33kV S/S T-3 LT Scheduled S/D
| 12:57 | 17:20 | Savar 132/33kV S/S T-3 HT Scheduled S/D
| 13:16 |  | Bhola ( Borhanuddin) 230/33 kv Txr 33 Side Close.
| 13:32 | 16:30 | Jamalpur 132/33kV S/S Bus-B Project Work S/D Due to 132kv D.S. Upgradation Work purpose.
| 13:49 | 14:11 | Feni-PHP 132kV Ckt-1 Tripped from Feni 132/33kV end showing Distance realy: C-phase, | [7 empty] | 12.0MW load
|  |  | zone -1 Autoreclose relay: air fail relays. | [7 empty] | interrup. Feni
132/33kV end
|  | 14:28 | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T HT is restored.
|  | 14:30 | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T LT is restored.
|  | 15:07 | Tangail 132/33kV S/S Kaliakair-1 is restored.
|  | 15:09 | Kaliakoir-Tangail 132kV Ckt-1 is restored.
|  | 15:29 | Baroaulia-Hathazari 132 kV Ckt-1 is restored.
| 15:47 | 22:44 | Baroaulia-Hathazari 132 kV Ckt-1 Tripped from Baroaulia 132/33kV end showing Quadramho
relays Due to The opgw is torn due to the stormy whether
| 16:22 | 18:14 | Naogaon 132/33kV S/S T-2 33kV BUS Project Work S/D Due to 33KV Bus Isolator change. | [7 empty] | 8.0MW load
interrup.
| 17:59 | 20:30 | Cumilla(S) 132/33kV S/S TR-2 LT Scheduled S/D Due to Energypac work.
| 18:00 | 20:29 | Cumilla(S) 132/33kV S/S TR-2 HT Scheduled S/D
|  | 18:50 | Kodda 132/33kV S/S Tr-1 (406T) HT is restored.
|  | 18:51 | Kodda 132/33kV S/S Tr-2 (416T) HT is restored.
|  | 18:52 | Kodda 132/33kV S/S Tr-1 (406T) LT is restored.
|  | 18:53 | Kodda 132/33kV S/S Tr-2 (416T) LT is restored.
| 20:00 |  | Evening Peak Generation: 11435 MW.
| 20:03 | 20:54 | Nawabganj 132/33kV S/S TR-1 HT Forced S/D Due to Emergency red hot maintenance 33kV | [7 empty] | 9.0MW load
|  |  | incomer-01 bus side. | [7 empty] | interrup.
| 20:03 | 20:56 | Nawabganj 132/33kV S/S TR-1 LT Forced S/D Due to Emergency red hot maintenance 33kV | [7 empty] | 9.0MW load
|  |  | incomer-01 bus side. | [7 empty] | interrup.
| 20:20 |  | Shahmirpur 132/33kV S/S 416T HT Tripped showing Differential relays Due to Earth fault
| 05:00 |  | Minimum generation 8931 MW
| 07:10 |  | Jhenaidah 132/33kV S/S Transformer T-2 HT Forced S/D Due to 33kV Y phase(Bus) Loop
Conductor changing.
| 07:11 |  | Jhenaidah 132/33kV S/S Transformer T-1 HT Forced S/D Due to 33kV Y phase(Bus) Loop | [7 empty] | 40.0MW load
|  |  | Conductor changing. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 02-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 351 | 8506800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 6555839 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 70389 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 24 | 477000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 205920 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 14 | 62496 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 160991 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 450 | 9310909.09 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 283 | 6606980 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 17 | 48000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1488 | 32005324.09
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 34965 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 394080 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 939300 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 75 | 2659280 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 12 | 126720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 87120 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19927 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Fuel shortage due to BPDB's payment delay
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 970 | 17176362 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 24 | 510240 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 450 | 8843636.36 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 1571 | 30791630.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 190 | 4885000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 361 | 8355200 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 320 | 6930000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 309 | 6629000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 710700 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 102 | 657832 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 104 | 2304960 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 7 | 243270 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 265127 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1444 | 30981089
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 146 | 3229440 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8550 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 45600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 49200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 132690 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 174 | 3465480
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 18596 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 905000 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 601440 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3391036.36 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 109 | 1716600 | Bad Weather
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 616512 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1090560 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2415800 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 280896 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7407000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 392 | 8664000 | FGMO not available because of Cooling Tower Fan
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1268 | 27107440.36
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 927 | 19051636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 377 | 8642304 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 530640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 956 | 18923637 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2260 | 47148217
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 300 | 6312727 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 2741000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 895 | 14717090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 110 | 2691560 | Plant availability less
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 214 | 3797000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3501 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1649 | 30262878.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 291992 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Plant is standby
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Liquid fuel shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 183 | 4366582 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 395 | 9089600 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 424048 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 13920 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1003.13 | 20509091 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 165008 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 617750 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1581.13 | 35477991
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 1003636 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 23022.36 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 0 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 93506 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 588240 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 0 | 1708404.36
Eastern Grid Total |  |  |  |  | 17418.042 | 5945 | 124350963.81
Western Grid Total |  |  |  |  | 11852.195 | 5490.13 | 114597491.27
National Grid Total |  |  |  |  | 29270.237 | 11435.13 | 238948455.08
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 02-05-2026
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7576.7 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3328.6 | MW
i) Dhaka area |  |  | 4479.7 |  | MW | i) Khulna area |  |  |  | 1256 | MW
ii) Chattogram area |  |  | 921 |  | MW | ii) Barishal area |  |  |  | 186 | MW
iii) Cumilla area |  |  | 930 |  | MW | iii) Rajshahi area |  |  |  | 1195.6 | MW
iv) Mymensingh area |  |  | 864 |  | MW | iv) Rangpur area |  |  |  | 691 | MW
v) Sylhet area |  |  | 382 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10905.3 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 16 | 16:00 | 67 | Hasnabad | 86 | 12:00 | 133 | Natore | 127 | 19:00
2 | AKSML | 161.3 | 07:00 | 68 | Hathazari | 69 | 14:00 | 134 | Nawabganj | 48.2 | 21:00
3 | Aftabnagar | 36 | 13:00 | 69 | Hatirjheel | 33 | 12:00 | 135 | Netrakona | 100 | 19:00
4 | Agargaon | 99 | 13:00 | 70 | Ishurdi | 73 | 19:00 | 136 | New | 72 | 12:00
5 | Agrabad | 42 | 00:00 | 71 | Jaldhaka | 52 | 19:30 | 137 | Niamatpur | 51 | 19:00
6 | Amnura | 24 | 00:00 | 72 | Jamalpur | 92 | 19:30 | 138 | Noapara | 38 | 21:00
7 | Ashuganj | 59 | 00:00 | 73 | Jashore | 127 | 19:00 | 139 | PHP | 12 | 15:00
8 | BSRM | 207 | 18:30 | 74 | Jhenaidah | 89 | 19:00 | 140 | Pabna | 84 | 19:00
9 | Bagerhat | 57 | 00:00 | 75 | Joydebpur | 124 | 19:00 | 141 | Palashbari | 88 | 19:00
10 | Bajitpur | 65 | 18:30 | 76 | Joypurhat | 38 | 16:00 | 142 | Panchagarh | 47 | 19:00
11 | Bakerganj | 9.3 | 21:00 | 77 | Juldah | 15.5 | 15:00 | 143 | Patiya | 8 | 00:00
12 | Bakulia | 78 | 14:00 | 78 | KSRM | 13 | 18:00 | 144 | Patuakhali | 50.9 | 00:00
13 | Banani | 36.6 | 13:00 | 79 | Kabirpur | 234 | 19:00 | 145 | Payra | 26 | 00:00
14 | Bangabhaban | 6 | 11:00 | 80 | Kachua | 61 | 00:00 | 146 | Postogola | 49 | 13:00
15 | Barapukuria | 46 | 19:30 | 81 | Kaliganj | 19 | 19:00 | 147 | Pubail | 41 | 19:30
16 | Barguna | 18 | 00:00 | 82 | Kallyanpur | 93 | 12:00 | 148 | Purbachal | 28 | 11:00
17 | Barishal | 88 | 11:00 | 83 | Kalurghat | 37 | 10:00 | 149 | Purbasadipur | 91 | 19:00
18 | Barishal-230 | 90 | 13:00 | 84 | Kamrangirchar | 74 | 12:00 | 150 | Rahanpur | 28 | 22:00
19 | Baroaulia | 45 | 23:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 34 | 12:00
20 | Baroirhat | 48 | 13:00 | 86 | Kasba | 24 | 22:00 | 152 | Rajbari | 68 | 19:00
21 | Bashundhara | 171 | 13:00 | 87 | Kazla | 106 | 12:00 | 153 | Rajendrapur | 108 | 21:00
22 | BashundharaCement | 3 | 23:00 | 88 | Keranigonj | 75 | 19:00 | 154 | Rajshahi | 122 | 19:00
23 | Beanibazar | 46 | 18:30 | 89 | Khagrachori | 22 | 14:00 | 155 | Rajshahi-230 | 45 | 00:00
24 | Benapole | 48 | 19:30 | 90 | Khulna | 58 | 12:00 | 156 | Ramganj | 76 | 12:00
25 | Bhaluka | 122 | 18:30 | 91 | Khulshi | 173 | 12:00 | 157 | Rampur | 34 | 14:00
26 | Bhandaria | 44 | 00:00 | 92 | Kishoreganj | 91 | 19:30 | 158 | Rangamati | 12 | 11:00
27 | Bhangura | 30 | 19:00 | 93 | Kodda | 255 | 21:00 | 159 | Rangpur | 106 | 12:00
28 | Bheramara(GK) | 57 | 19:00 | 94 | Kulaura | 34 | 18:30 | 160 | Ruppur | 2.2 | 15:00
29 | Bhulta | 190 | 20:00 | 95 | Kurigram | 51 | 19:00 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 60 | 19:00 | 96 | Kushtia | 136 | 19:00 | 162 | Saidpur | 84 | 19:00
31 | Bogura | 128 | 19:30 | 97 | Laksam | 25 | 13:00 | 163 | Santhia | 22 | 00:00
32 | Borhanuddin | 80 | 00:00 | 98 | Lakshmipur | 26 | 00:00 | 164 | Satkhira | 100 | 12:00
33 | Brahmanbaria | 95 | 00:00 | 99 | Lalbag | 61 | 12:00 | 165 | Satmasjid | 89 | 13:00
34 | Cantonment | 94 | 13:00 | 100 | Lalmonirhat | 46 | 20:00 | 166 | Savar | 188 | 18:00
35 | Chandina | 17 | 18:30 | 101 | MI_Cement | 9.2 | 09:00 | 167 | SevenRings | 19.33 | 12:00
36 | Chandpur | 58 | 22:00 | 102 | Madanganj | 38 | 13:00 | 168 | ShahCement | 31 | 10:00
37 | Chandraghona | 25 | 00:00 | 103 | Madaripur | 81 | 13:00 | 169 | Shahjadpur | 74 | 20:00
38 | Chapai | 57 | 00:00 | 104 | Madartek | 69 | 13:00 | 170 | Shahjibazar | 90 | 19:30
39 | Charsaidpur | 30 | 16:00 | 105 | Madunaghat | 52 | 15:00 | 171 | Shahmirpur | 35 | 00:00
40 | Chauddagram | 55 | 13:00 | 106 | Magura | 53 | 19:00 | 172 | Shariatpur | 63 | 19:00
41 | Chhatak | 20 | 00:00 | 107 | Mahasthangarh | 64 | 19:00 | 173 | Sherpur | 106 | 19:00
42 | Chowmuhani | 103 | 13:00 | 108 | Maijdee | 37 | 00:00 | 174 | Shikalbaha | 26 | 15:00
43 | Chuadanga | 98 | 19:00 | 109 | Manikganj | 110 | 21:00 | 175 | Shitalakhya | 79.3 | 12:00
44 | Coxsbazar | 115 | 00:00 | 110 | Maniknagar | 62 | 13:00 | 176 | Sholosohor | 40 | 15:00
45 | Cumilla(N) | 101 | 13:00 | 111 | Matarbari | 42 | 00:00 | 177 | Shyampur | 172 | 10:00
46 | Cumilla(S) | 124 | 14:00 | 112 | Matuail | 72 | 12:00 | 178 | Siddhirganj | 122 | 12:00
47 | Daganbhuiyan | 19 | 02:00 | 113 | Metrorail_Motijheel | 18 | 12:00 | 179 | Sirajganj | 80 | 19:00
48 | Daudkandi | 115 | 19:30 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sonargaon | 109 | 19:30
49 | DhakaUniversity | 70 | 13:00 | 115 | Millgate | 94 | 12:00 | 181 | Sreemongol | 46 | 19:00
50 | Dhamrai | 106 | 19:00 | 116 | Mirpur | 132 | 13:00 | 182 | Sreepur | 101 | 18:30
51 | Dhanmondi | 103 | 13:00 | 117 | Mirsorai | 43 | 08:00 | 183 | Srinagar | 39 | 20:00
52 | Dohazari | 80 | 00:00 | 118 | Mirzapur | 38 | 18:00 | 184 | Sunamganj | 38 | 19:30
53 | Faridpur | 132 | 18:30 | 119 | Mithapukur | 44 | 19:00 | 185 | Sylhet | 23 | 19:00
54 | Fatullah | 82 | 12:00 | 120 | Modern | N/A | N/A | 186 | Sylhet-132 | 88 | 13:00
55 | Fenchuganj | 24 | 13:00 | 121 | Mogbazar | 69.2 | 13:00 | 187 | TK | 18 | 00:00
56 | Feni | 70 | 20:00 | 122 | Mongla | 39 | 19:00 | 188 | Tangail | 122 | 18:30
57 | GPH | 1 | 00:00 | 123 | Motijheel | 38 | 13:00 | 189 | Taraganj | 17 | 19:00
58 | Ghatail | 74 | 18:30 | 124 | Muktagacha | 27 | 19:00 | 190 | Tasnim | 28 | 15:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 92 | 13:00 | 191 | Thakurgaon | 75 | 19:30
60 | Ghorashal-230 | 88 | 18:00 | 126 | Muradnagar | 31 | 21:00 | 192 | Tongi | 134 | 11:00
61 | Goalpara | 30 | 12:00 | 127 | Mymensingh | 142 | 20:00 | 193 | Ullahpara | 29 | 19:30
62 | Gollamari | 84 | 12:00 | 128 | Nabinagar | 35 | 20:00 | 194 | Ullon | 45 | 13:00
63 | Gopalganj | 70.6 | 12:00 | 129 | Naogaon | 111 | 20:00 | 195 | Uttara | 73 | 12:00
64 | Gulshan | 90 | 13:00 | 130 | Narail | 37 | 00:00 | 196 | UttaraNew | 41 | 12:00
65 | Halishahar | 120 | 16:00 | 131 | Narinda | 64 | 13:00 | 197 | Zigatola | 77 | 14:00
66 | HaripurSBU | 121 | 17:00 | 132 | Narshingdi | 147 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 02-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 10234 | 0 |  | 10234
1:00 | 9540 | 0 |  | 9540
2:00 | 9239 | 0 |  | 9239
3:00 | 8873 | 0 |  | 8873
4:00 | 8505 | 0 |  | 8505
5:00 | 8208 | 0 |  | 8208
6:00 | 8254.76 | 0 |  | 8254.76
7:00 | 8836.73 | 0 |  | 8836.73
8:00 | 9221.82 | 0 |  | 9221.82
9:00 | 9485.76 | 0 |  | 9485.76
10:00 | 9669.25 | 0 |  | 9669.25
11:00 | 10111.8 | 0 |  | 10111.8
12:00 | 10754.59 | 0 |  | 10754.59
13:00 | 10808.24 | 0 |  | 10808.24
14:00 | 10181.79 | 0 |  | 10181.79
15:00 | 9498.86 | 0 |  | 9498.86
16:00 | 9269.06 | 0 |  | 9269.06
17:00 | 9458.73 | 0 |  | 9458.73
18:00 | 9876.53 | 0 |  | 9876.53
19:00 | 11321.86 | 0 |  | 11321.86
19:30 | 11401.16 | 0 |  | 11401.16
20:00 | 11435.13 | 0 |  | 11435.13
21:00 | 11275.7 | 0 |  | 11275.7
22:00 | 11166.56 | 0 |  | 11166.56
23:00 | 10798.34 | 0 |  | 10798.34
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 02-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5569 | 4665 | 10234 | DAILY GENERATION CURVE
00:30 | 5296.5 | 4590.5 | 9887
01:00 | 5024 | 4516 | 9540 | 02-05-2026
01:30 | 4877.5 | 4512 | 9389.5
02:00 | 4731 | 4508 | 9239
02:30 | 4597.5 | 4458.5 | 9056
03:00 | 4464 | 4409 | 8873
03:30 | 4461 | 4228 | 8689
04:00 | 4458 | 4047 | 8505
04:30 | 4359.5 | 3997 | 8356.5
05:00 | 4261 | 3947 | 8208
05:30 | 4253.505 | 3977.875 | 8231.38
06:00 | 4246.01 | 4008.75 | 8254.76
06:30 | 4454.36 | 4091.385 | 8545.745
07:00 | 4662.71 | 4174.02 | 8836.73
07:30 | 4797.11 | 4232.165 | 9029.275
08:00 | 4931.51 | 4290.31 | 9221.82
08:30 | 4966.585 | 4387.205 | 9353.79
09:00 | 5001.66 | 4484.1 | 9485.76
09:30 | 4890.305 | 4687.2 | 9577.505
10:00 | 4778.95 | 4890.3 | 9669.25
10:30 | 4938.2 | 4952.325 | 9890.525
11:00 | 5097.45 | 5014.35 | 10111.8
11:30 | 5369.905 | 5063.29 | 10433.195
12:00 | 5642.36 | 5112.23 | 10754.59
12:30 | 5648.685 | 5132.73 | 10781.415
13:00 | 5655.01 | 5153.23 | 10808.24
13:30 | 5529.81 | 4965.205 | 10495.015
14:00 | 5404.61 | 4777.18 | 10181.79
14:30 | 5112.585 | 4727.74 | 9840.325
15:00 | 4820.56 | 4678.3 | 9498.86
15:30 | 4751.115 | 4632.845 | 9383.96
16:00 | 4681.67 | 4587.39 | 9269.06
16:30 | 4767.82 | 4596.075 | 9363.895
17:00 | 4853.97 | 4604.76 | 9458.73
17:30 | 5036.78 | 4630.85 | 9667.63
18:00 | 5219.59 | 4656.94 | 9876.53
18:30 | 5573.795 | 5025.4 | 10599.195
19:00 | 5928 | 5393.86 | 11321.86
19:30 | 5917 | 5484.16 | 11401.16
20:00 | 5945 | 5490.13 | 11435.13
20:30 | 5980 | 5375.415 | 11355.415 |  | Executive Engineer
21:00 | 6015 | 5260.7 | 11275.7 |  | Network Operation Division
21:30 | 5989.5 | 5231.63 | 11221.13
22:00 | 5964 | 5202.56 | 11166.56
22:30 | 5957 | 5025.45 | 10982.45
23:00 | 5950 | 4848.34 | 10798.34

## En-Curve
QF-LDC-12
Date | 02-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3879 | 1441 | 925 | 0 | 92 | 823 | 40 | 3022 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | DAILY ENERGY CURVE
00:30 | 3815 | 1312 | 925 | 0 | 92 | 823 | 40 | 2864 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 02-05-2026
01:00 | 3751 | 1183 | 925 | 0 | 92 | 823 | 40 | 2706 | 0 | 0 | 0 | 0 | 0 | 20 | 0
01:30 | 3636 | 1171 | 925 | 0 | 91 | 823 | 40 | 2681 | 0 | 0 | 0 | 0 | 0 | 22.5 | 0 | Energy Generated | 238.9485 |  | MKWHr
02:00 | 3521 | 1159 | 925 | 0 | 90 | 823 | 40 | 2656 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3399 | 1162.5 | 877.5 | 0 | 88 | 824 | 38.5 | 2644 | 0 | 0 | 0 | 0 | 0 | 22.5 | 0 | Total Energy Requirement | 238.9485 |  | MKWHr
03:00 | 3277 | 1166 | 830 | 0 | 86 | 825 | 37 | 2632 | 0 | 0 | 0 | 0 | 0 | 20 | 0
03:30 | 3278.5 | 1189 | 613.5 | 0 | 82 | 825.5 | 37 | 2636 | 0 | 0 | 0 | 0 | 0 | 27.5 | 0
04:00 | 3280 | 1212 | 397 | 0 | 78 | 826 | 37 | 2640 | 0 | 0 | 0 | 0 | 0 | 35 | 0
04:30 | 3210 | 1168.5 | 379 | 0 | 81 | 825 | 37.5 | 2628.5 | 0 | 0 | 0 | 0 | 0 | 27 | 0
05:00 | 3140 | 1125 | 361 | 0 | 84 | 824 | 38 | 2617 | 0 | 0 | 0 | 0 | 0 | 19 | 0
05:30 | 3120 | 1131 | 361 | 0 | 82 | 831 | 39 | 2613 | 7.58 | 26.8 | 0 | 0 | 0 | 20 | 0
06:00 | 3100 | 1137 | 361 | 0 | 80 | 838 | 40 | 2609 | 15.16 | 53.6 | 0 | 0 | 0 | 21 | 0
06:30 | 3242.5 | 1244.5 | 361 | 0 | 83 | 842 | 40 | 2619.5 | 43.645 | 53.6 | 0 | 0 | 0 | 16 | 0
07:00 | 3385 | 1352 | 361 | 0 | 86 | 846 | 40 | 2630 | 72.13 | 53.6 | 0 | 0 | 0 | 11 | 0
07:30 | 3460.5 | 1406.5 | 361 | 0 | 93 | 836.5 | 40 | 2623.5 | 133.175 | 53.6 | 10.5 | 0 | 0 | 11 | 0
08:00 | 3536 | 1461 | 361 | 0 | 100 | 827 | 40 | 2617 | 194.22 | 53.6 | 21 | 0 | 0 | 11 | 0
08:30 | 3516.5 | 1448.5 | 470 | 0 | 103 | 824.98 | 40 | 2615 | 233.51 | 52.3 | 35.5 | 0 | 0 | 14.5 | 0
09:00 | 3497 | 1436 | 579 | 0 | 106 | 822.96 | 40 | 2613 | 272.8 | 51 | 50 | 0 | 0 | 18 | 0
09:30 | 3434.5 | 1358.5 | 753 | 0 | 104 | 822.51 | 40 | 2614 | 328.495 | 51 | 53 | 0 | 0 | 18.5 | 0
10:00 | 3372 | 1281 | 927 | 0 | 102 | 822.06 | 40 | 2615 | 384.19 | 51 | 56 | 0 | 0 | 19 | 0
10:30 | 3524.5 | 1326 | 927 | 0 | 100 | 824.175 | 40 | 2616.5 | 403.35 | 51 | 56 | 0 | 0 | 22 | 0
11:00 | 3677 | 1371 | 927 | 0 | 98 | 826.29 | 40 | 2618 | 422.51 | 51 | 56 | 0 | 0 | 25 | 0
11:30 | 3784.5 | 1441 | 927 | 0 | 109 | 830.825 | 40 | 2740 | 403.37 | 51.5 | 71.5 | 0 | 0 | 34.5 | 0
12:00 | 3892 | 1511 | 927 | 0 | 120 | 835.36 | 40 | 2862 | 384.23 | 52 | 87 | 0 | 0 | 44 | 0
12:30 | 3899.5 | 1492.5 | 927 | 0 | 120 | 829.32 | 40 | 2941 | 346.095 | 73 | 87 | 0 | 0 | 26 | 0
13:00 | 3907 | 1474 | 927 | 0 | 120 | 823.28 | 40 | 3020 | 307.96 | 94 | 87 | 0 | 0 | 8 | 0
13:30 | 3758.5 | 1382.5 | 927 | 0 | 122 | 822.06 | 40 | 3006 | 297.955 | 47 | 84 | 0 | 0 | 8 | 0
14:00 | 3610 | 1291 | 927 | 0 | 124 | 820.84 | 40 | 2992 | 287.95 | 0 | 81 | 0 | 0 | 8 | 0
14:30 | 3444.5 | 1192 | 907.5 | 0 | 114 | 821.48 | 38 | 2892 | 354.345 | 0 | 61.5 | 0 | 0 | 15 | 0
15:00 | 3279 | 1093 | 888 | 0 | 104 | 822.12 | 36 | 2792 | 420.74 | 0 | 42 | 0 | 0 | 22 | 0
15:30 | 3330.5 | 1093 | 907.5 | 0 | 90 | 823.64 | 36 | 2729 | 320.82 | 0 | 41 | 0 | 0 | 12.5 | 0
16:00 | 3382 | 1093 | 927 | 0 | 76 | 825.16 | 36 | 2666 | 220.9 | 0 | 40 | 0 | 0 | 3 | 0
16:30 | 3480.5 | 1130.5 | 927.5 | 0 | 79 | 825.325 | 36.5 | 2680.5 | 175.07 | 0 | 20 | 0 | 0 | 9 | 0
17:00 | 3579 | 1168 | 928 | 0 | 82 | 825.49 | 37 | 2695 | 129.24 | 0 | 0 | 0 | 0 | 15 | 0
17:30 | 3649.5 | 1224 | 927.5 | 0 | 85 | 825.285 | 38 | 2824.5 | 77.345 | 0 | 5.5 | 0 | 0 | 11 | 0
18:00 | 3720 | 1280 | 927 | 0 | 88 | 825.08 | 39 | 2954 | 25.45 | 0 | 11 | 0 | 0 | 7 | 0
18:30 | 3811 | 1420.5 | 927 | 0 | 92 | 928.97 | 39.5 | 3304.5 | 12.725 | 1.5 | 30 | 0 | 0 | 31.5 | 0
19:00 | 3902 | 1561 | 927 | 0 | 96 | 1032.86 | 40 | 3655 | 0 | 3 | 49 | 0 | 0 | 56 | 0
19:30 | 3984 | 1532 | 927 | 0 | 108 | 1007.16 | 40 | 3750 | 0 | 17 | 36 | 0 | 0 | 0 | 0
20:00 | 3977 | 1516 | 927 | 0 | 104 | 1003.13 | 40 | 3785 | 0 | 17 | 42 | 0 | 0 | 24 | 0
20:30 | 4030.5 | 1518 | 927 | 0 | 101 | 963.915 | 40 | 3706 | 0 | 17 | 33.5 | 0 | 0 | 18.5 | 0
21:00 | 4084 | 1520 | 927 | 0 | 98 | 924.7 | 40 | 3627 | 0 | 17 | 25 | 0 | 0 | 13 | 0
21:30 | 4069.5 | 1523.5 | 927 | 0 | 101 | 916.63 | 40 | 3598 | 0 | 8.5 | 17 | 0 | 0 | 20 | 0
22:00 | 4055 | 1527 | 927 | 0 | 104 | 908.56 | 40 | 3569 | 0 | 0 | 9 | 0 | 0 | 27 | 0
22:30 | 4051 | 1542 | 927 | 0 | 101 | 862.45 | 40 | 3408.5 | 0 | 0 | 9 | 0 | 0 | 41.5 | 0
23:00 | 4047 | 1557 | 927 | 0 | 98 | 816.34 | 40 | 3248 | 0 | 0 | 9 | 0 | 0 | 56 | 0
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 02-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 113 | -33 | 350 | 40 | 984 | 166 | Ishurdi-Ghorashal Ckt-1 | Export | 3514400
1:00 | 125 | -32 | 380 | 32 | 1020 | 168
2:00 | 155 | -32 | 460 | 36 | 1154 | 164 |  | Import | 0
3:00 | 182 | -17 | 464 | 40 | 1270 | 194
4:00 | 118 | -24 | 458 | 36 | 1162 | 186 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 107 | -23 | 432 | 22 | 1128 | 172
6:00 | 105 | -22 | 410 | 26 | 1092 | 174 |  | Import | 0
7:00 | 88 | -20 | 388 | 44 | 982 | 174
8:00 | 97 | -17 | 406 | 58 | 1066 | 206 | Sirajganj-Sreepur Ckt-1 | Export | 2666000
9:00 | 149 | -13 | 384 | 24 | 1272 | 258
10:00 | 214 | -14 | 500 | 48 | 1424 | 266 |  | Import | 0
11:00 | 201 | -13 | 530 | 86 | 1306 | 296
12:00 | 204 | -6 | 544 | 116 | 1350 | 352 | Sirajganj-Sreepur Ckt-2 | Export | 2688000
13:00 | 210 | -1 | 480 | 84 | 1440 | 382
14:00 | 185 | -11 | 472 | 90 | 1516 | 400 |  | Import | 0
15:00 | 183 | -13 | 520 | 92 | 1524 | 322
16:00 | 171 | -21 | 482 | 80 | 1506 | 328 | Gopalganj-Aminbazar Ckt-1 | Export | 15290000
17:00 | 166 | -20 | 480 | 94 | 1388 | 316
18:00 | 147 | -21 | 464 | 108 | 1384 | 314 |  | Import | 0
18:30 | 151 | -21 | 480 | 120 | 1554 | 296
19:00 | 127 | -20 | 428 | 110 | 1468 | 294 | Gopalganj-Aminbazar Ckt-2 | Export | 15260000
19:30 | 120 | -19 | 404 | 96 | 1456 | 282
20:00 | 121 | -18 | 394 | 92 | 1448 | 288 |  | Import | 0
21:00 | 117 | -17 | 390 | 86 | 1276 | 278
22:00 | 118 | -18 | 388 | 80 | 1236 | 274 |  | Total Export | 39418400
23:00 | 114 | -16 | 344 | 74 | 1134 | 272 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 02-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 405 | 05:00 | 387 | 13:00 | Madunaghat | 405 | 06:00 | 398 | 13:00
Amtali | 417 | 03:00 | 411 | 19:30 | Meghnaghat | 403 | 05:00 | 388 | 12:00
Ashuganj | 418 | 5:00 | 397 | 12:00 | Payra | 418 | 05:00 | 412 | 19:30
Bhulta | 413 | 05:00 | 390 | 12:00 | Rahanpur | 420 | 05:00 | 402 | 19:00
Bibiana | 412 | 04:00 | 402 | 19:00 | Rampal | 408 | 05:00 | 394 | 19:30
BIPTC | 407 | 04:00 | 390 | 20:00
Bogura | 413 | 04:00 | 389 | 20:00
Gopalganj | 410 | 05:00 | 396 | 12:00
Kaliakoir | 401 | 05:00 | 380 | 19:30
Korerhat | 410 | 05:00 | 399 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 236 | 04:00 | 221 | 12:00 | Jhenaidah | 235 | 05:00 | 220 | 19:00
AKSML | 238.4 | 06:00 | 228.6 | 00:00 | Kachua | 235 | 15:00 | 225 | 13:00
Aminbazar | 237 | 05:00 | 222 | 13:00 | Kaliakoir | 238 | 04:00 | 222 | 11:00
Ashuganj | 236 | 05:00 | 225 | 12:00 | Keranigonj | 235 | 05:00 | 221 | 12:00
Ashuganj-400 | 236 | 05:00 | 225 | 12:00 | Khulna(S) | 236 | 05:00 | 224 | 19:00
Baghabari | 238 | 03:00 | 226 | 19:00 | Korerhat | 234 | 06:00 | 227 | 12:00
Barapukuria | 234 | 04:00 | 209 | 19:30 | Madunaghat | 237 | 06:00 | 233 | 12:00
Barapukuria-230 | 234 | 04:00 | 209 | 19:30 | Madunaghat-400 | 238 | 06:00 | 233 | 13:00
Barishal | 231 | 03:00 | 225 | 12:00 | Maniknagar | 236 | 02:00 | 221 | 12:00
Bheramara | 235 | 05:00 | 221 | 19:00 | Meghnaghat | 243 | 04:00 | 230 | 12:00
Bhulta | 237 | 05:00 | 222 | 12:00 | Meghnaghat-400 | 238 | 05:00 | 225 | 12:00
Bibiana | 238 | 06:00 | 232 | 19:30 | Mirsorai | 238 | 06:00 | 231 | 12:00
BIPTC | 237 | 03:00 | 221 | 19:00 | Naogaon | 230 | 05:00 | 209 | 19:00
Bogura | 242 | 05:00 | 225 | 19:30 | Purbasadipur | 234 | 05:00 | 208 | 19:30
Bogura-400 | 241 | 04:00 | 225 | 19:30 | Rajshahi | 235 | 04:00 | 220 | 19:30
Borhanuddin | 233 | 16:00 | 230 | 00:00 | Rampal | 234 | 04:00 | 223 | 19:00
BSRM | 234 | 06:00 | 227 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 234 | 06:00 | 229 | 22:00 | Rampura | 236 | 05:00 | 221 | 12:00
Cumilla(N) | 235 | 05:00 | 225 | 12:00 | Shikalbaha | 236 | 07:00 | 231 | 13:00
Faridpur | 230 | 05:00 | 221 | 12:00 | Shyampur | 236 | 05:00 | 221 | 12:00
Fenchuganj | 242 | 08:00 | 237 | 19:30 | Siddhirganj | 237 | 02:00 | 223 | 12:00
Feni | 234 | 06:00 | 225 | 13:00 | Sirajgonj | 244 | 05:00 | 232 | 19:30
Ghorashal | 238 | 08:00 | 220 | 13:00 | Sreepur | 234 | 05:00 | 220 | 19:00
Ghorashal-230 | 234 | 05:00 | 218 | 12:00 | Tongi | 234 | 04:00 | 220 | 18:00
Gopalganj | 229 | 05:00 | 221 | 11:00
GPH | 237 | 06:00 | 230 | 12:00
Haripur | 237 | 05:00 | 223 | 12:00
Hasnabad | 236 | 03:00 | 223 | 13:00
Hathazari | 236 | 06:00 | 231 | 12:00
Ishurdi | 238 | 03:00 | 224 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 04:00 | 124 | 12:00 | Madunaghat | 138 | 06:00 | 135 | 00:00
Agargaon | 137 | 05:00 | 127 | 12:00 | Magura | 138 | 04:00 | 126 | 19:00
Agrabad | 137 | 17:00 | 133 | 00:00 | Mahasthangarh | 139 | 04:00 | 126 | 19:00
AKS | 135 | 05:00 | 131 | 13:00 | Maijdee | 132 | 16:00 | 126 | 12:00
Aminbazar | 136 | 04:00 | 126 | 13:00 | Manikganj | 134 | 04:00 | 122 | 12:00
Amnura | 138 | 05:00 | 127 | 19:00 | Maniknagar | 140 | 04:00 | 129 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 135 | 19:30 | 119 | 00:00
Ashuganj-230 | 141 | 01:00 | 135 | 20:00 | Matuail | 138 | 03:00 | 129.5 | 12:00
Bagerhat | 139 | 14:00 | 127 | 19:00 | Metrorail_Motijheel | 140 | 04:00 | 129 | 12:00
Bajitpur | 136 | 05:00 | 126 | 18:30 | Metrorail_Uttara | 138 | 02:00 | 126 | 13:00
Bakerganj | 136 | 15:00 | 131 | 11:00 | Millgate | 139 | 04:00 | 126 | 12:00
Bakulia | 138 | 19:30 | 134 | 00:00 | Mirpur | 135 | 01:00 | 124 | 12:00
Banani | 134 | 02:00 | 124 | 12:00 | Mirzapur | 139 | 04:00 | 129 | 14:00
Bangabhaban | 140 | 05:00 | 129 | 12:00 | Mithapukur | 137 | 05:00 | 123 | 19:00
Barapukuria | 136 | 04:00 | 120 | 19:30 | MI_Cement | 136 | 04:00 | 123.2 | 12:00
Barguna | 137 | 15:00 | 131 | 10:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 135 | 06:00 | 129 | 12:00 | Mogbazar | 135 | 01:00 | 125 | 12:00
Barishal-230 | 135 | 15:00 | 130 | 12:00 | Mongla | 138 | 14:00 | 127 | 22:00
Baroaulia | 138 | 16:00 | 133 | 00:00 | Motijheel | 140 | 05:00 | 129 | 12:00
Baroirhat | 135 | 05:00 | 131 | 12:00 | Muktagacha | 138 | 05:00 | 125 | 20:00
Bashundhara | 138 | 02:00 | 123 | 13:00 | Munshiganj | 136 | 05:00 | 128 | 12:00
BashundharaCement | 136 | 01:00 | 129 | 12:00 | Muradnagar | 135 | 05:00 | 126 | 13:00
Beanibazar | 134 | 06:00 | 130 | 13:00 | Mymensingh | 138 | 06:00 | 117 | 18:30
Benapole | 137 | 04:00 | 125 | 19:00 | Nabinagar | 137 | 00:00 | 127 | 12:00
Bhaluka | 134 | 09:00 | 121 | 18:30 | Naogaon | 139 | 04:00 | 126 | 19:00
Bhandaria | 136 | 17:00 | 125 | 23:00 | Narail | 138 | 13:00 | 126 | 19:00
Bhangura | 137 | 03:00 | 129 | 19:00 | Narinda | 140 | 04:00 | 129 | 12:00
Bheramara | 138 | 03:00 | 131 | 19:00 | Narshingdi | 134 | 05:00 | 126 | 12:00
Bheramara(GK) | 138 | 03:00 | 131 | 19:00 | Natore | 137 | 03:00 | 127 | 19:00
Bhulta | 131 | 07:00 | 128 | 12:00 | Nawabganj | 139 | 03:00 | 129 | 12:00
Bog-Sherpur | 140 | 04:00 | 129 | 19:00 | Netrakona | 133 | 06:00 | 114 | 19:00
Bogura | 141 | 04:00 | 129 | 19:00 | New | 138 | 04:00 | 127 | 12:00
Bogura-230 | 140 | 04:00 | 129 | 19:30 | Niamatpur | 138 | 01:00 | 132 | 19:00
Brahmanbaria | 135 | 05:00 | 129 | 18:00 | Noapara | 138 | 05:00 | 128 | 18:30
Cantonment | 137 | 04:00 | 126 | 12:00 | Pabna | 138 | 03:00 | 129 | 19:00
Chandina | 137 | 05:00 | 130 | 12:00 | Palashbari | 135 | 04:00 | 121 | 19:00
Chandpur | 133 | 15:00 | 125 | 13:00 | Panchagarh | 138 | 04:00 | 125 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 139 | 17:00 | 134 | 13:00 | Patiya | 137 | 09:00 | 132 | 00:00
Chapai | 139 | 05:00 | 132 | 20:00 | Patuakhali | 135 | 04:00 | 130 | 12:00
Charsaidpur | 137 | 02:00 | 128 | 13:00 | Payra | 136 | 03:00 | 134 | 12:00
Chauddagram | 134 | 04:00 | 128 | 13:00 | PHP | 135 | 05:00 | 130 | 12:00
Chhatak | 134 | 07:00 | 129 | 13:00 | Postogola | 137 | 04:00 | 126 | 12:00
Chowmuhani | 133 | 16:00 | 126 | 12:00 | Pubail | 140 | 03:00 | 130 | 18:30
Chuadanga | 136 | 04:00 | 124 | 19:00 | Purbachal | 138 | 02:00 | 124 | 12:00
Coxsbazar | 133 | 19:30 | 120 | 00:00 | Purbasadipur | 135 | 04:00 | 120 | 19:30
Cumilla(N) | 136 | 05:00 | 130 | 13:00 | Rahanpur | 139 | 03:00 | 133 | 19:30
Cumilla(S) | 136 | 04:00 | 129 | 12:00 | Rahanpur-400 | 140 | 05:00 | 133 | 19:00
Daganbhuiyan | 134 | 06:00 | 128 | 12:00 | Rahim | 138 | 03:00 | 130 | 13:00
Daudkandi | 134 | 05:00 | 125 | 12:00 | Rajbari | 132 | 04:00 | 125 | 19:00
DhakaUniversity | 134 | 02:00 | 124 | 12:00 | Rajendrapur | 134 | 05:00 | 121 | 19:00
Dhamrai | 139 | 04:00 | 127 | 12:00 | Rajshahi | 136 | 03:00 | 125 | 19:00
Dhanmondi | 139 | 03:00 | 130 | 12:00 | Rajshahi-230 | 136 | 04:00 | 127 | 19:00
Dohazari | 137 | 19:30 | 129 | 00:00 | Ramganj | 132 | 15:00 | 123 | 13:00
Faridpur | 133 | 07:00 | 128 | 12:00 | Rampur | 137 | 07:00 | 133 | 00:00
Fatullah | 137 | 05:00 | 124 | 12:00 | Rampura | 134 | 01:00 | 124 | 12:00
Fenchuganj | 138 | 05:00 | 134 | 19:00 | Rangamati | 139 | 17:00 | 134 | 11:00
Feni | 133 | 05:00 | 128 | 12:00 | Rangpur | 136 | 04:00 | 123 | 19:00
Feni-230 | 134 | 05:00 | 128 | 13:00 | Ruppur | 138 | 04:00 | 131 | 19:00
Ghatail | 139 | 05:00 | 124 | 19:00 | Saidpur | 134 | 04:00 | 122 | 19:30
Ghorashal | 141 | 04:00 | 132 | 12:00 | Santhia | 138 | 04:00 | 130 | 19:00
Goalpara | 140 | 05:00 | 131 | 19:00 | Satkhira | 136 | 14:00 | 126 | 12:00
Gollamari | 139 | 05:00 | 131 | 18:30 | Satmasjid | 136 | 03:00 | 126 | 13:00
Gopalganj | 137 | 05:00 | 130 | 19:00 | Savar | 134 | 03:00 | 122 | 12:00
Gopalganj-400 | 136 | 03:00 | 132 | 13:00 | SevenRings | 141 | 04:00 | 132 | 12:00
Gulshan | 134 | 03:00 | 124 | 12:00 | ShahCement | 137 | 03:00 | 128 | 13:00
Halishahar | 137 | 07:00 | 133 | 00:00 | Shahjadpur | 140 | 04:00 | 133 | 19:00
Haripur | 138 | 04:00 | 130 | 12:00 | Shahjibazar | 134 | 03:00 | 128 | 18:00
HaripurSBU | 138 | 04:00 | 132 | 12:00 | Shahmirpur | 138 | 17:00 | 134 | 00:00
Hasnabad | 137 | 04:00 | 125 | 13:00 | Shariatpur | 135 | 04:00 | 129 | 12:00
Hathazari | 140 | 16:00 | 135 | 00:00 | Sherpur | 135 | 06:00 | 115 | 19:00
Hatirjheel | 135 | 05:00 | 124 | 12:00 | Shikalbaha | 127 | 04:00 | 123 | 00:00
Ishurdi | 140 | 03:00 | 132 | 19:00 | Shikalbaha-230 | 139 | 17:00 | 135 | 00:00
Jaldhaka | 133 | 05:00 | 116 | 19:30 | Shitalakhya | 136 | 04:00 | 123.2 | 12:00
Jamalpur | 136 | 06:00 | 121 | 19:00 | Sholosohor | 138 | 06:00 | 134 | 12:00
Jashore | 137 | 05:00 | 125 | 19:00 | Shyampur | 134 | 04:00 | 126 | 12:00
Jhenaidah | 139 | 03:00 | 125 | 19:00 | Shyampur-230 | 136 | 05:00 | 127 | 12:00
Jhenaidah-230 | 139 | 04:00 | 129 | 19:00 | Siddhirganj | 138 | 03:00 | 130 | 12:00
Joydebpur | 138 | 02:00 | 128 | 12:00 | Sirajganj | 139 | 04:00 | 127 | 19:00
Joypurhat | 136 | 05:00 | 124 | 19:00 | Sonargaon | 136 | 03:00 | 128 | 12:00
Juldah | 138 | 16:00 | 133 | 00:00 | Sreemongol | 135 | 11:00 | 130 | 18:00
Kabirpur | 140 | 08:00 | 122 | 12:00 | Sreepur | 135 | 05:00 | 123 | 19:00
Kachua | 134 | 15:00 | 128 | 12:00 | Srinagar | 139 | 03:00 | 129 | 12:00
Kaliakoir | 143 | 04:00 | 130 | 12:00 | SSM | 142 | 08:00 | 139 | 00:00
Kaliganj | 137 | 06:00 | 128 | 19:00 | Sunamganj | 133 | 08:00 | 128 | 19:00
Kallyanpur | 135 | 01:00 | 124 | 12:00 | Sylhet | 135 | 06:00 | 131 | 19:00
Kalurghat | 138 | 06:00 | 135 | 00:00 | Sylhet-132 | 133 | 06:00 | 131 | 13:00
Kamrangirchar | 140 | 04:00 | 122 | 12:00 | Tangail | 138 | 05:00 | 124 | 14:00
Kaptai | 140 | 4:00 | 136 | 13:00 | Taraganj | 134 | 04:00 | 123 | 19:00
Kasba | 135 | 05:00 | 126 | 13:00 | Tasnim | 137 | 04:00 | 128 | 12:00
Kazla | 140 | 05:00 | 128 | 13:00 | Thakurgaon | 136 | 04:00 | 122 | 19:30
Keranigonj | 140 | 05:00 | 130 | 12:00 | TK | 138 | 17:00 | 135 | 00:00
Khagrachori | 139 | 17:00 | 134 | 00:00 | Tongi | 139 | 04:00 | 130 | 13:00
Khulna | 139 | 04:00 | 130 | 19:30 | Ullahpara | 139 | 04:00 | 129 | 19:00
Khulna(S) | 140 | 05:00 | 132 | 12:00 | Ullon | 134 | 04:00 | 125 | 12:00
Khulshi | 136 | 17:00 | 131 | 00:00 | Uttara | 138 | 03:00 | 124 | 12:00
Kishoreganj | 136 | 05:00 | 124 | 18:30 | UttaraNew | 138 | 02:00 | 126 | 12:00
Kodda | 137 | 08:00 | 124 | 20:00 | Zigatola | 140 | 05:00 | 129 | 13:00
Korerhat | 137 | 06:00 | 132 | 12:00
KSRM | 137 | 06:00 | 133 | 12:00
Kulaura | 137 | 06:00 | 134 | 13:00
Kurigram | 133 | 05:00 | 117 | 19:30
Kushtia | 136 | 09:00 | 128 | 19:00
Laksam | 135 | 16:00 | 127 | 12:00
Lakshmipur | 131 | 15:00 | 124 | 13:00
Lalbag | 139 | 02:00 | 130 | 12:00
Lalmonirhat | 133 | 03:00 | 119 | 19:30
Madanganj | 136 | 01:00 | 129 | 12:00
Madaripur | 135 | 03:00 | 130 | 12:00
Madartek | 134 | 05:00 | 124 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division