## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 04-05-2026 | [28 empty] | Date: | 04-05-2026 | [28 empty] | Date: | 04-05-2026 | [28 empty] | Date: | 04-05-2026 | [28 empty] | Date: | 04-05-2026 | [17 empty] | Date: | 04-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [17 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 225 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 0 | 24 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 12 | 800 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 220 | 354 | 345 | 51 | 0 | 198 | 0 | 0 | 83 | 0 | 0 | 20 | 0 | 122 | 0 | 0 | 0 | 310 | 0 | 394 | 0 | 30 | 151 | 0 | 17 | 0 | 83 | 30 | 109 | 0 | 100 | 0 | 9 | 57 | 62 | 0 | 0 | 0 | 6294 | 927 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 895 | 0 | 0 | 0 | 1113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 130 | 220 | 0 | 334 | 940 | 0 | 5633 | 11927 | 77.94
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 220 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 0 | 0 | 25 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 13 | 720 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1110 | 0 | 0 | 0 | 220 | 354 | 345 | 51 | 0 | 200 | 0 | 0 | 82 | 0 | 0 | 20 | 0 | 124 | 0 | 0 | 0 | 305 | 0 | 392 | 0 | 30 | 151 | 0 | 17 | 0 | 83 | 30 | 110 | 0 | 100 | 0 | 9 | 35 | 62 | 0 | 0 | 0 | 6169 | 930 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 0 | 0 | 1038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 130 | 220 | 0 | 334 | 890 | 0 | 5394 | 11563 | 77.95
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 0 | 0 | 25 | 14 | 0 | 410 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 13 | 720 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 955 | 0 | 0 | 0 | 220 | 354 | 345 | 51 | 0 | 200 | 0 | 0 | 81 | 0 | 0 | 20 | 0 | 112 | 0 | 0 | 0 | 305 | 0 | 394 | 0 | 30 | 151 | 0 | 17 | 0 | 83 | 30 | 110 | 0 | 100 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 5943 | 929 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 775 | 0 | 0 | 0 | 861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 130 | 220 | 0 | 297 | 800 | 0 | 5058 | 11001 | 77.95
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 25 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 13 | 720 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 843 | 0 | 0 | 0 | 220 | 353 | 345 | 51 | 0 | 200 | 0 | 0 | 82 | 0 | 0 | 20 | 0 | 114 | 0 | 0 | 0 | 310 | 0 | 394 | 0 | 30 | 147 | 0 | 17 | 0 | 83 | 30 | 110 | 0 | 101 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 5828 | 929 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 766 | 0 | 0 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 130 | 220 | 0 | 252 | 600 | 0 | 4769 | 10597 | 77.95
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 25 | 14 | 0 | 350 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 23 | 720 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 730 | 0 | 0 | 0 | 220 | 354 | 345 | 51 | 0 | 205 | 0 | 0 | 83 | 0 | 0 | 20 | 0 | 104 | 0 | 0 | 0 | 295 | 0 | 394 | 0 | 30 | 135 | 0 | 17 | 0 | 83 | 30 | 110 | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 5598 | 930 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753 | 0 | 0 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 130 | 220 | 0 | 254 | 500 | 0 | 4580 | 10178 | 77.96
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 0 | 0 | 0 | 25 | 14 | 0 | 310 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 25 | 720 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 220 | 355 | 280 | 10 | 0 | 170 | 0 | 0 | 83 | 0 | 0 | 20 | 0 | 112 | 0 | 0 | 0 | 300 | 0 | 332 | 0 | 30 | 137 | 0 | 17 | 0 | 11 | 30 | 110 | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 5334 | 930 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 130 | 180 | 0 | 254 | 500 | 0 | 4475 | 9809 | 77.96
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 1 | 0 | 25 | 14 | 0 | 330 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 26 | 720 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 755 | 1 | 0 | 0 | 220 | 305 | 250 | 10 | 0 | 170 | 0 | 0 | 81 | 0 | 0 | 20 | 0 | 106 | 0 | 3 | 0 | 300 | 0 | 332 | 0 | 30 | 137 | 0 | 17 | 0 | 11 | 30 | 110 | 0 | 100 | 0 | 0 | 0 | 65 | 0 | 0.03 | 0 | 5307.03 | 930 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.82 | 770 | 0 | 0 | 0 | 826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98 | 3 | 0 | 0 | 0.65 | 0 | 0 | 0 | 0 | 167 | 0 | 372 | 0 | 0.01 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 10 | 0 | 0 | 140 | 100 | 180 | 0 | 254 | 500 | 0 | 4509.56 | 9816.59 | 77.96
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 5 | 0 | 25 | 14 | 0 | 375 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 1.1 | 40 | 0 | 22 | 720 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 758 | 6 | 0 | 0 | 260 | 300 | 300 | 10 | 0 | 202 | 0 | 0 | 83 | 0 | 0 | 20 | 0 | 104 | 0 | 17 | 0 | 315 | 0 | 332 | 0 | 30 | 140 | 0 | 17 | 0 | 11 | 30 | 110 | 0 | 100 | 0 | 0 | 0 | 62 | 0.65 | 0.91 | 0 | 5540.66 | 929 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 782 | 0 | 0 | 0 | 819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.92 | 18 | 0 | 0 | 12.09 | 0 | 0 | 0 | 0 | 175 | 0 | 414 | 0 | 1.15 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 1.3 | 27 | 0.14 | 0 | 140 | 100 | 180 | 0 | 255 | 500 | 0 | 4637.6 | 10178.26 | 77.97
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 10 | 14 | 23 | 14 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.13 | 40 | 0 | 6 | 720 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 755 | 7 | 0 | 0 | 260 | 305 | 300 | 10 | 0 | 210 | 0 | 0 | 81 | 0 | 0 | 20 | 0 | 110 | 0 | 35 | 0 | 315 | 0 | 336 | 0 | 30 | 137 | 1 | 17 | 0 | 11 | 30 | 110 | 0 | 100 | 0 | 0 | 35 | 63 | 0.1 | 7.67 | 0 | 5678.9 | 930 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 795 | 0 | 0 | 0 | 835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.04 | 15 | 0 | 0 | 4.93 | 0 | 0 | 0 | 0 | 173 | 0 | 414 | 0 | 0.37 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 3.1 | 78 | 0.35 | 0 | 140 | 100 | 180 | 0 | 254 | 505 | 0 | 4753.79 | 10432.69 | 77.97
09:00 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 17 | 17 | 22 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 2 | 800 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 840 | 16 | 0 | 0 | 296 | 320 | 345 | 21 | 0 | 192 | 0 | 0 | 82 | 0 | 0 | 20 | 0 | 106 | 0 | 46 | 0 | 310 | 0 | 359 | 0 | 30 | 136 | 1 | 17 | 0 | 84 | 30 | 110 | 0 | 101 | 0 | 0 | 35 | 30 | 1.54 | 11 | 0 | 5954.54 | 930 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.35 | 749 | 0 | 0 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.03 | 15 | 0 | 0 | 21.11 | 0 | 0 | 0 | 0 | 189 | 0 | 402 | 0 | 1.6 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 1 | 93 | 0.52 | 0 | 173 | 130 | 220 | 0 | 266 | 550 | 0 | 4989.61 | 10944.15 | 77.98
10:00 | 0 | 4 | 8 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 15 | 17 | 13 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.08 | 40 | 0 | 2 | 800 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 825 | 18 | 0 | 8 | 309 | 320 | 345 | 51 | 0 | 198 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 124 | 0 | 53 | 0 | 310 | 0 | 374 | 0 | 30 | 133 | 1 | 17 | 0 | 83 | 30 | 110 | 0 | 100 | 0 | 0 | 35 | 30 | 1.4 | 22.38 | 0 | 5992.86 | 930 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.91 | 767 | 0 | 0 | 0 | 825.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.1 | 62 | 0 | 0 | 55.35 | 0 | 0 | 0 | 0 | 170 | 0 | 346 | 0 | 2.96 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 7.3 | 163 | 0.69 | 0 | 181 | 130 | 220 | 0 | 300 | 590 | 0 | 5207.57 | 11200.43 | 77.99
11:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 286 | 0 | 0 | 30 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 35 | 40 | 20 | 6 | 0 | 380 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 1.58 | 40 | 0 | 2 | 800 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 850 | 14 | 0 | 8 | 325 | 320 | 320 | 51 | 0 | 208 | 0 | 0 | 96 | 0 | 0 | 14 | 0 | 130 | 0 | 43 | 0 | 305 | 0 | 388 | 0 | 30 | 136 | 1 | 17 | 0 | 84 | 30 | 110 | 0 | 100 | 0 | 0 | 35 | 30 | 1.2 | 46.89 | 0 | 6221.67 | 932 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.72 | 787 | 0 | 0 | 0 | 831.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.83 | 103 | 0 | 0 | 20.93 | 0 | 0 | 0 | 0 | 161 | 0 | 377 | 0 | 3.26 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 7.9 | 173 | 0.75 | 0 | 183 | 120 | 220 | 0 | 300 | 591 | 0 | 5271.92 | 11493.59 | 78
12:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 290 | 0 | 0 | 34 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 35 | 70 | 21 | 14 | 0 | 440 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 1.72 | 40 | 0 | 2 | 850 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 945 | 6 | 0 | 8 | 345 | 320 | 250 | 51 | 0 | 211 | 0 | 0 | 97 | 0 | 0 | 12 | 0 | 144 | 0 | 19 | 0 | 315 | 0 | 388 | 0 | 30 | 155 | 4 | 0 | 0 | 84 | 30 | 110 | 0 | 100 | 22 | 0 | 35 | 29 | 2.1 | 41.2 | 0 | 6502.02 | 932 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.03 | 890 | 0 | 0 | 0 | 932.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.52 | 108 | 0 | 0 | 60.97 | 0 | 0 | 0 | 0 | 190 | 0 | 414 | 0 | 5 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 8 | 159 | 0.47 | 0 | 210 | 130 | 220 | 0 | 337 | 650 | 0 | 5683.23 | 12185.25 | 78.01
13:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 299 | 0 | 0 | 34 | 0 | 45 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 7 | 70 | 21 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 4.54 | 40 | 0 | 5 | 850 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 1030 | 10 | 0 | 8 | 315 | 320 | 270 | 51 | 0 | 201 | 0 | 0 | 98 | 0 | 0 | 12 | 0 | 140 | 0 | 7 | 0 | 315 | 0 | 388 | 0 | 30 | 158 | 5 | 17 | 0 | 84 | 30 | 110 | 0 | 100 | 30 | 0 | 37 | 26 | 1.5 | 37.75 | 0 | 6571.79 | 932 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.8 | 1005 | 0 | 0 | 0 | 1020.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 13.53 | 55 | 0 | 0 | 59.03 | 0 | 0 | 0 | 0 | 188 | 0 | 414 | 0 | 5.22 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 8 | 198 | 0.78 | 0 | 254 | 130 | 220 | 0 | 340 | 736 | 0 | 5940.55 | 12512.34 | 78.03
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 289 | 0 | 0 | 69 | 0 | 15 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 3 | 88 | 21 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 3.86 | 40 | 0 | 5 | 830 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 1050 | 12 | 0 | 8 | 280 | 320 | 270 | 51 | 0 | 202 | 0 | 0 | 97 | 0 | 0 | 12 | 0 | 142 | 0 | 25 | 0 | 310 | 0 | 394 | 0 | 30 | 144 | 11 | 17 | 0 | 83 | 30 | 110 | 0 | 100 | 54.5 | 9 | 66 | 26 | 2.1 | 44.05 | 0 | 6595.51 | 932 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.1 | 1004 | 0 | 0 | 0 | 1016.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 10.68 | 40 | 0 | 0 | 47.23 | 0 | 0 | 0 | 0 | 174 | 0 | 414 | 0 | 4.38 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 4.8 | 168 | 0.08 | 0 | 241 | 130 | 220 | 0 | 326 | 760 | 0 | 5838.6 | 12434.11 | 78.05
15:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 284 | 0 | 0 | 72 | 0 | 15 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 7 | 108 | 20 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 2.62 | 38 | 0 | 0 | 760 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1050 | 3 | 0 | 8 | 280 | 320 | 270 | 51 | 0 | 201 | 0 | 0 | 97 | 0 | 0 | 12 | 0 | 146 | 0 | 28 | 0 | 315 | 0 | 401 | 30 | 30 | 145 | 8 | 17 | 0 | 83 | 30 | 110 | 0 | 100 | 54.5 | 9 | 66 | 26 | 0.69 | 23.05 | 0 | 6557.86 | 930 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.98 | 1000 | 0 | 0 | 0 | 995.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 37.65 | 74 | 0 | 0 | 40.62 | 0 | 0 | 0 | 0 | 174 | 0 | 414 | 0 | 3.4 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 4.5 | 128 | 0.18 | 0 | 222 | 130 | 220 | 0 | 318 | 740 | 0 | 5813.46 | 12371.32 | 78.07
16:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 240 | 0 | 0 | 88 | 0 | 15 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 8 | 90 | 20 | 14 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.79 | 37 | 0 | 0 | 780 | 0 | 0 | 18 | 0 | 0 | 215 | 0 | 0 | 0 | 1050 | 6 | 0 | 8 | 300 | 320 | 270 | 51 | 0 | 196 | 0 | 0 | 100 | 0 | 0 | 9 | 0 | 150 | 0 | 9 | 0 | 305 | 0 | 401 | 30 | 30 | 135 | 5 | 17 | 0 | 83 | 30 | 108 | 0 | 100 | 54.5 | 9 | 65 | 26 | 0.75 | 15.82 | 0 | 6481.86 | 931 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.92 | 992 | 0 | 0 | 0 | 925.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.4 | 52 | 0 | 0 | 26.71 | 0 | 0 | 0 | 0 | 167 | 0 | 405 | 0 | 1.79 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 4.1 | 93 | 0.02 | 0 | 181 | 130 | 220 | 0 | 306 | 720 | 0 | 5507.13 | 11988.99 | 78.09
17:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 285 | 0 | 3 | 88 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 0 | 7 | 88 | 20 | 14 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 37 | 0 | 0 | 780 | 0 | 0 | 19 | 0 | 0 | 213 | 0 | 0 | 0 | 1050 | 3 | 0 | 8 | 280 | 320 | 270 | 51 | 0 | 198 | 0 | 0 | 101 | 0 | 0 | 14 | 0 | 142 | 0 | 3 | 0 | 305 | 0 | 401 | 30 | 30 | 147 | 2 | 17 | 0 | 84 | 30 | 110 | 0 | 100 | 54.5 | 9 | 68 | 28 | 0.4 | 10.4 | 0 | 6521.64 | 932 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.04 | 990 | 0 | 0 | 0 | 936.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.28 | 11 | 0 | 0 | 7.36 | 0 | 0 | 0 | 0 | 175 | 0 | 352 | 0 | 0.71 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 1.7 | 31 | 0.05 | 0 | 191 | 130 | 220 | 0 | 318 | 730 | 0 | 5344.02 | 11865.66 | 78.11
18:00 | 0 | 34 | 12 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 242 | 0 | 17 | 91 | 12 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 1 | 94 | 18 | 14 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 960 | 0 | 0 | 19 | 0 | 0 | 217 | 0 | 0 | 0 | 1050 | 0 | 0 | 63 | 350 | 0 | 342 | 51 | 2 | 197 | 2 | 0 | 101 | 0 | 0 | 14 | 0 | 136 | 0 | 0 | 0 | 310 | 0 | 401 | 30 | 30 | 135 | 0 | 17 | 0 | 84 | 30 | 109 | 0 | 100 | 54.5 | 9 | 68 | 28 | 0.07 | 1.43 | 10 | 6501 | 932 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.21 | 1050 | 0 | 0 | 0 | 1086.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.09 | 6 | 0 | 0 | 1.19 | 0 | 0 | 0 | 0 | 166 | 0 | 347 | 0 | 0.1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 8 | 0.01 | 0 | 176 | 130 | 220 | 0 | 313 | 760 | 0 | 5499.81 | 12000.81 | 78.13
19:00 | 0 | 34 | 36 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 307 | 15.5 | 17 | 96 | 15 | 15 | 8 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 17 | 298 | 0 | 0 | 0 | 123 | 19 | 14 | 0 | 410 | 0 | 0 | 1 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 8 | 8 | 1010 | 0 | 0 | 19 | 0 | 10 | 219 | 0 | 0 | 0 | 1094 | 0 | 13 | 128 | 395 | 0 | 345 | 51 | 13 | 205 | 22 | 13 | 101 | 0 | 0 | 14 | 0 | 130 | 0 | 0 | 0 | 305 | 0 | 401 | 30 | 30 | 136 | 0 | 17 | 0 | 84 | 30 | 110 | 0 | 100 | 54.5 | 9 | 76 | 26 | 0 | 0 | 12 | 7135 | 932 | 301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1215 | 0 | 0 | 0 | 1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 414 | 0 | 0 | 0 | 0 | 50 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259 | 130 | 220 | 0 | 392 | 886 | 0 | 6492 | 13627 | 78.15
19:30 | 0 | 34 | 42 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 290 | 15.6 | 17 | 96 | 15 | 30 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 17 | 290 | 0 | 0 | 0 | 123 | 19 | 14 | 0 | 400 | 0 | 0 | 30 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 15 | 2 | 990 | 0 | 0 | 19 | 0 | 30 | 218 | 0 | 0 | 0 | 1090 | 0 | 30 | 136 | 393 | 0 | 345 | 51 | 20 | 200 | 26 | 32 | 101 | 0 | 0 | 14 | 0 | 146 | 0 | 0 | 0 | 305 | 0 | 401 | 30 | 30 | 148 | 0 | 17 | 0 | 84 | 30 | 110 | 0 | 100 | 35 | 9 | 76 | 26 | 0 | 0 | 12 | 7187.6 | 932 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1222 | 0 | 0 | 0 | 1423.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251 | 130 | 220 | 0 | 446 | 1030 | 0 | 6700.66 | 13888.26 | 0
20:00 | 0 | 34 | 51 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 226 | 15.8 | 17 | 100 | 0 | 30 | 0 | 17 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 123 | 20 | 14 | 0 | 330 | 0 | 0 | 30 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 40 | 16 | 10 | 950 | 0 | 0 | 19 | 0 | 30 | 219 | 0 | 0 | 0 | 1055 | 0 | 30 | 138 | 393 | 0 | 345 | 51 | 25 | 198 | 34 | 32 | 101 | 0 | 0 | 14 | 0 | 136 | 0 | 0 | 0 | 300 | 0 | 399 | 30 | 30 | 140 | 0 | 17 | 0 | 84 | 30 | 109 | 0 | 100 | 35 | 9 | 76 | 26 | 0 | 0 | 12 | 6944.8 | 932 | 289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1222 | 0 | 0 | 0 | 1373.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 130 | 220 | 0 | 461 | 1044 | 0 | 6635.81 | 13580.61 | 78.17
21:00 | 0 | 34 | 51 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 280 | 15.8 | 17 | 112 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 123 | 20 | 14 | 0 | 400 | 0 | 0 | 30 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 8 | 975 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 1060 | 0 | 0 | 55 | 240 | 67 | 345 | 51 | 22 | 188 | 10 | 20 | 102 | 0 | 0 | 14 | 0 | 140 | 0 | 0 | 0 | 300 | 0 | 400 | 30 | 30 | 144 | 0 | 17 | 0 | 84 | 30 | 111 | 0 | 100 | 0 | 9 | 68 | 26 | 0 | 0 | 12 | 6747.8 | 932 | 289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1227 | 0 | 0 | 0 | 1352.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 130 | 220 | 0 | 494 | 1070 | 0 | 6700.57 | 13448.37 | 78.19
22:00 | 0 | 34 | 51 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 257 | 15.8 | 17 | 112 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 123 | 18.5 | 14 | 0 | 380 | 0 | 0 | 28 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 15 | 950 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 1060 | 0 | 0 | 8 | 295 | 27 | 345 | 51 | 0 | 196 | 10 | 0 | 102 | 0 | 0 | 14 | 0 | 138 | 0 | 0 | 0 | 295 | 0 | 399 | 30 | 30 | 147 | 0 | 17 | 0 | 84 | 30 | 109 | 0 | 100 | 0 | 9 | 58 | 26 | 0 | 0 | 0 | 6590.3 | 932 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1215 | 0 | 0 | 0 | 1328.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 345 | 0 | 0 | 0 | 0 | 70 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 130 | 220 | 0 | 484 | 1080 | 0 | 6580.01 | 13170.31 | 78.21
23:00 | 0 | 34 | 51 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 223 | 15.4 | 17 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 106 | 18.5 | 14 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 15 | 965 | 0 | 0 | 19 | 0 | 0 | 222 | 0 | 0 | 0 | 1010 | 0 | 0 | 8 | 340 | 53 | 345 | 51 | 0 | 197 | 10 | 0 | 103 | 0 | 0 | 14 | 0 | 134 | 0 | 0 | 0 | 295 | 0 | 399 | 30 | 30 | 129 | 0 | 17 | 0 | 84 | 30 | 110 | 0 | 100 | 0 | 9 | 58 | 26 | 0 | 0 | 0 | 6442.9 | 931 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1219 | 0 | 0 | 0 | 1219.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 352 | 0 | 0 | 0 | 0 | 50 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 130 | 220 | 0 | 430 | 1030 | 0 | 6266.5 | 12709.4 | 78.23
Total KWH | 0 | 384960 | 351840 | 0 | 0 | 0 | 0 | 0 | 8316000 | 0 | 6406910 | 95760 | 117720 | 1243440 | 36960 | 132982 | 17530 | 232400 | 82080 | 0 | 0 | 0 | 0 | 0 | 31182 | 7090903 | 0 | 0 | 0 | 1448400 | 493200 | 288360 | 0 | 9204090.91 | 0 | 0 | 92160 | 0 | 177600 | 190894 | 0 | 0 | 0 | 0 | 24723 | 939600 | 40981 | 231360 | 19694545.46 | 0 | 0 | 166080 | 0 | 59382 | 5308570 | 0 | 0 | 0 | 22663634 | 94635 | 58545 | 468364 | 6978000 | 6217600 | 7560000 | 1104460 | 69120 | 4880000 | 107640 | 84480 | 2202753 | 0 | 0 | 421650 | 0 | 3113280 | 0 | 331200 | 0 | 7420000 | 0 | 9292000 | 298000 | 715560 | 3392918.18 | 39490 | 396528 | 0 | 1412160 | 714048 | 2600100 | 0 | 2408550 | 491760 | 116400 | 991200 | 898560 | 13000 | 256130 | 47520 | 150759898.55 | 22506182 | 7333344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558720 | 22480000 | 0 | 0 | 0 | 24264932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28070 | 0 | 262504 | 606110 | 0 | 0 | 343488 | 0 | 0 | 0 | 0 | 4421918 | 0 | 9163200 | 0 | 31080 | 0 | 0 | 336798 | 208758 | 481305 | 0 | 0 | 0 | 58599.12 | 1328400 | 3333 | 0 | 4647000 | 2987000 | 5372650 | 0 | 7905454 | 18388363.64 | 0 | 133717208.76 | 284477107.31

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 05-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-05-2026 | during | 05-05-2026 | during | 05-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 364 | 361 | 412 | 412 | 392 | 392 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 450 | 450 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 335 | 335 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 15 | 55 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 313 | 290 | 335 | 335 | 310 | 310 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 32 | 32 | 32 | 32 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 15.6 | 53.97 | 53.97 | 17 | 36 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 15 | 149.36 | 149.36 | 15 | 149 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 19 | 33 | 33 | 28 | 28 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 14 | 14 | 14 | 14 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 42 | 52.19 | 52.19 | 16 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 30 | 300 | 300 | 48 | 294 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 96 | 149 | 149 | 150 | 150 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 34 | 105 | 105 | 17 | 34 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 33 | 162 | 162 | 35 | 88 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 35 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 440 | 400 | 584 | 584 | 450 | 450 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 290 | 290 | 718 | 718 | 290 | 290 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 123 | 160 | 160 | 17 | 160 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1623 | 1813.6 | 5964.22 | 5939.22 | 3290 | 3989
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 0 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 6 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 19 | 50 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 39 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 213 | 218 | 215 | 215 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 30 | 105 | 105 | 34 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 0 | 68 | 0 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 2 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 30 | 108 | 108 | 12 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.72 | 0 | 2.05 | 0 | 2.05 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 15 | 110 | 110 | 54 | 54 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 17 | 54 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 945 | 1090 | 1224 | 1224 | 1204 | 1204 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 19 | 0 | 1 | 2 | 1 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 850 | 990 | 1150 | 1150 | 1150 | 1150 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2076.72 | 2467 | 3934.91 | 4014.86 | 2961.05 | 3160
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 211 | 200 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 320 | 0 | 350.01 | 350.01 | 350.01 | 350.01 | FGMO not available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 250 | 345 | 342.01 | 342.01 | 342.01 | 342.01 | FGMO not available
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 345 | 393 | 393 | 393 | 363 | 363 | FGMO
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 26 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 20 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 136 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 30 | 25 | 150 | 25 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 40 | 40 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 97 | 101 | 163 | 163 | 51 | 51 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 17 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 144 | 146 | 84 | 80 | 148 | 148 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 14 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 17 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 32 | 115 | 115 | 17 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 19 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1457 | 1494 | 2632.44 | 2698.44 | 1702.27 | 2092.27
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-05-2026 | during | 05-05-2026 | during | 05-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 29 | 26 | 157.5 | 157.5 | 65 | 65 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.1 | 0 | 2.3 | 0 | 2.3 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 35 | 76 | 80 | 70 | 10 | 10 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 0 | 9 | 10 | 10 | 10 | 10 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 41.2 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 22 | 35 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 129.3 | 158 | 371.3 | 314 | 149.3 | 114
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 30 | 0 | 0 | 0 | 0 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 148 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 110 | 110 | 110 | 110 | 110 | 110 | Machine Problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 85 | 85 | 85 | 85 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 17 | 25 | 25 | 17 | 17 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 388 | 401 | 380 | 380 | 380 | 380 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1216 | 1255 | 1284 | 1284 | 1206 | 1206
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 932 | 932 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 30 | 30 | 30 | 30 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 300 | 296 | 410 | 410 | 320 | 320 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 72.03 | 0 | 98 | 0 | 98 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 890 | 1222 | 1234.2 | 1234.2 | 1194 | 1194 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2194.03 | 2450 | 3592.2 | 3494.2 | 2689.1 | 2591.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 337 | 446 | 300 | 500 | 300 | 500 | ps availability is less
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 650 | 1030 | 1244 | 1244 | 1184 | 1184 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 210 | 251 | 307 | 307 | 287 | 287 | Bad quality coal
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.47 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1547.47 | 2077 | 2462 | 2661 | 2155 | 2354
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 53.52 | 0 | 48.55 | 0 | 48.55 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 32 | 32 | 32 | 32 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Fuel shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 190 | 173 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0.03 | 0.03 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 92 | 92 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5 | 0 | 3.3 | 0 | 3.3 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 932.24 | 1423.66 | 1435.88 | 1435.88 | 1356 | 1356 | AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 60.97 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 108 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1763.73 | 2010.66 | 3201.72 | 2988.87 | 2750.29 | 2622.44
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 93 | 113 | 113 | 35 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 8 | 0 | 6.5 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 0 | 70 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 11 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 159 | 0 | 200 | 0 | 200 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 178 | 163 | 498.5 | 262 | 271 | 183
System Total |  |  |  |  | 28823.2 | 29270.237 | 12185.25 | 13888.26 | 23941.29 | 23656.59 | 17174.01 | 18311.81
Forecast Scenario (05-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12900 |  | 0 |  | 12900
|  |  |  | 1:00 | 12500 |  | 0 |  | 12500
|  |  |  | 2:00 | 11970 |  | 0 |  | 11970
|  |  |  | 3:00 | 11510 |  | 0 |  | 11510
|  |  |  | 4:00 | 11040 |  | 0 |  | 11040
|  |  |  | 5:00 | 10610 |  | 0 |  | 10610
|  |  |  | 6:00 | 10570 |  | 0 |  | 10570
|  |  |  | 7:00 | 10870 |  | 0 |  | 10870
|  |  |  | 8:00 | 11070 |  | 0 |  | 11070
|  |  |  | 9:00 | 11530 |  | 0 |  | 11530
|  |  |  | 10:00 | 11730 |  | 0 |  | 11730
|  |  |  | 11:00 | 11970 |  | 0 |  | 11970
|  |  |  | 12:00 | 12600 |  | 0 |  | 12600
|  |  |  | 13:00 | 12920 |  | 0 |  | 12920
|  |  |  | 14:00 | 12830 |  | 0 |  | 12830
|  |  |  | 15:00 | 12830 |  | 0 |  | 12830
|  |  |  | 16:00 | 12520 |  | 0 |  | 12520
|  |  |  | 17:00 | 12430 |  | 0 |  | 12430
|  |  |  | 18:00 | 12430 |  | 0 |  | 12430
|  |  |  | 18:30 | 13000 |  | 0 |  | 13000
|  |  |  | 19:00 | 13690 |  | 0 |  | 13690
|  |  |  | 19:30 | 14200 |  | 0 |  | 14200
|  |  |  | 20:00 | 14050 |  | 0 |  | 14050
|  |  |  | 21:00 | 13900 |  | 0 |  | 13900
|  |  |  | 22:00 | 13610 |  | 0 |  | 13610
|  |  |  | 23:00 | 13170 |  | 0 |  | 13170
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 12600.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14200.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14200.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 295.25 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:40 hrs on 05-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 04-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12185.25 | MW | 12:00 Hr. | Energy Generated |  |  | 284.4771 |  | MKWHr.
| Day Peak Demand |  |  | 12185.25 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 13888.26 | MW | 19:30 Hr. | Energy Demand |  |  | 284.4771 |  | MKWHr.
| Evening Peak Demand |  |  | 13888.26 | MW | 19:30 Hr. | Maximum Temperature |  |  | 32.2 |  | °C
| Minimum Generation of the Day |  |  | 9809 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 922.79 |  | MMCFD
| Maximum Generation of the Day |  |  | 13888.26 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.4641 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.7995 | 0 | 4.1753 | 0 | 0 | 0 | 0 | 0 | 35.9747 | Gas | 126.1755 | Gas | 439481492.2503
| Chattogram Zone |  |  | 5.5399 | 42.3582 | 0.5495 | 0 | 0.9396 | 0.11936 | 0 | 0.1776 | 49.6842 | Coal | 95.779 | Coal | 637118400.1666
| Cumilla Zone |  |  | 30.0096 | 0 | 0.14303 | 0 | 0 | 0.3312 | 3.1133 | 0 | 33.5971 | HFO | 7.3608 | HFO | 126663078.06
| Mymensingh Zone |  |  | 0.89856 | 0 | 1.6469 | 0 | 0 | 0.26913 | 0 | 0 | 2.8146 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.6499 | 0 | 0 | 0 | 0 | 0.03949 | 0 | 0 | 28.6894 | Hydro | 0.9396 | Hydro | 93960
| Khulna Zone |  |  | 7.3333 | 22.48 | 0 | 0 | 0 | 0.55872 | 22.5062 | 0 | 52.8782 | Solar | 4.1602 | Solar | 68009151.17
| Barishal Zone |  |  | 8.3597 | 30.9408 | 0 | 0 | 0 | 0.003333 | 0 | 0 | 39.3038 | Import | 49.8844 | Import | 280420621.18
| Rajshahi Zone |  |  | 13.5851 | 0 | 0.02807 | 0 | 0 | 1.2432 | 24.2649 | 0 | 39.1213 | Wind | 0.1776 | Wind | 2612496
| Rangpur Zone |  |  | 0 | 0 | 0.8181 | 0 | 0 | 1.5958 | 0 | 0 | 2.4139
| Total |  |  | 126.1755 | 95.779 | 7.3608 | 0 | 0.9396 | 4.1602 | 49.8844 | 0.1776 | 284.4771
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 439481492.2503 |  | Hydro | 93960
|  |  |  | Coal | 637118400.1666 |  | Solar | 68009151.17
|  |  |  | HFO | 126663078.06 |  | Import | 280420621.18
|  |  |  | HSD | 0 |  | Wind | 2612496
[5 empty] | Total: | 155,43,99,198 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.5062 | Peak Hr Flow | 932.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 35754472.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.2649 | Peak Hr Flow | 1423.66 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2282 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.1133 | Peak Hr Flow | 146.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2448 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.8844 | Peak Hr Flow | 2501.66 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5055
|  |  |  | Chattogram |  | 0 |  | 1469
|  |  |  | Cumilla |  | 0 |  | 1185
|  |  |  | Mymensingh |  | 0 |  | 1015
|  |  |  | Sylhet |  | 0 |  | 457
|  |  |  | Khulna |  | 0 |  | 1552
|  |  |  | Barishal |  | 0 |  | 346
|  |  |  | Rajshahi |  | 0 |  | 1414
|  |  |  | Rangpur |  | 0 |  | 904
|  |  |  | Total |  | 0 |  | 13397
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:12 | 16:42 | Khulna (C) S/S TR-1 425T LT Project Work S/D Due to Painting work
| 08:13 | 16:41 | Khulna (C) S/S TR-1 425T HT Project Work S/D Due to Painting work
|  | 09:38 | Nawabganj 132/33kV S/S TR-1 HT is restored.
|  | 09:40 | Nawabganj 132/33kV S/S TR-1 LT is restored.
| 09:55 | 18:07 | Barishal-Barishal(N) 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to
Shutdown by ALDC and from Barishal 230/132kV end Due to Replace of OPGW
| 10:15 | 13:00 | Mymensingh RPCL -Mymensingh 132kV Ckt-1 Project Work S/D from Mymensingh 132/33kV end
Due to None
| 10:30 | 10:34 | Pabna 132/33kV S/S T-1 LT Forced S/D Due to 132 kv CB Maintenance work.
| 10:30 | 10:34 | Pabna 132/33kV S/S T-1 HT Forced S/D Due to 132 Kv CB maintenance work
| 11:05 | 14:37 | Baghabari-Shahjadpur 132 kV Ckt-2 Scheduled S/D from Shahjadpur 132/33kV end Due to S/D
taken by Baghabari Power Station
|  | 11:15 | Hathazari 230/132/33kV S/S Raojan-02 is restored.
| 11:19 | 13:15 | Mithapukur 132/33kV S/S TR-1(404T) LT Forced S/D Due to Red hot maintenance work | [7 empty] | 15.0MW load
interrup.
| 11:20 | 13:14 | Mithapukur 132/33kV S/S TR-1(404T) HT Forced S/D | [7 empty] | 15.0MW load
interrup.
| 11:42 | 16:44 | Bagerhat 132/33kV S/S Transformer-1 (403T) HT Tripped showing Over current relays.
| 11:42 | 16:44 | Bagerhat 132/33kV S/S Transformer-1 (403T) LT Tripped showing Over current (132 kv
side.) relays.
| 11:59 |  | Goalpara 132/33kV S/S Goalpara-NWPGCL Scheduled S/D Due to BUS-1 PT Test
| 12:00 |  | Day Peak Generation is 12182 MW.
| 12:08 |  | Goalpara 132/33kV S/S Bus 1 Scheduled S/D Due to Bus-1 PT problem testing
| 12:25 | 13:25 | Kishoreganj-Mymensingh 132kV Ckt-1 Forced S/D from Bajitpur 132/33kV end.
| 12:46 | 16:03 | Barguna 132/33kV S/S Transformer-1 HT Scheduled S/D Due to WZPDCL-2(Barguna) Redhot
Maintenance
| 12:46 | 16:04 | Barguna 132/33kV S/S Transformer-1 LT Scheduled S/D Due to WZPDCL-2(Barguna) Redhot
Maintenance
| 13:22 | 14:11 | Niamatpur 132/33kV S/S 132 kV Naogaon ckt-2 Tripped showing SEMENS relays.
| 14:16 | 21:56 | Baghabari-Ishurdi 230 kV Ckt-1 Project Work S/D from Baghabari 230/132kV end Due to
Project Work
| 14:32 | 17:26 | Niamatpur 132/33kV S/S 132 kV Naogaon ckt-2 Tripped showing SEMENS SIPROTEC 7SA612
relays.
| 16:08 | 18:51 | Nawabganj 132/33kV S/S TR-2 LT Forced S/D Due to Due to red hot maintenance(Bay-105,
R-phase DS)
| 16:09 | 18:45 | Nawabganj 132/33kV S/S TR-2 HT Forced S/D Due to Due to red hot maintenance(Bay-105,
R-phase DS)
| 16:45 | 19:54 | Bagerhat 132/33kV S/S Transformer-1 (403T) HT Scheduled S/D Due to CT Cable Change work.
| 16:45 | 19:56 | Bagerhat 132/33kV S/S Transformer-1 (403T) LT Scheduled S/D Due to CT Cable Change work.
| 17:14 | 18:28 | Srinagar 132/33kV S/S Tr-02 LT Scheduled S/D Due to Red Hot Maintenance at Mpbs | [7 empty] | 12.0MW load
|  |  | feeder-05. | [7 empty] | interrup.
| 17:15 | 18:30 | Srinagar 132/33kV S/S Tr-02 HT Scheduled S/D Due to Red Hot Maintenance at Mpbs | [7 empty] | 12.0MW load
|  |  | feeder-05. | [7 empty] | interrup.
| 17:31 |  | Ashuganj 450 MW CCPP(North) Tripped with remarks:- GT
| 17:31 |  | Ashuganj North 360 MW CCPP tripped.
| 20:25 |  | Ashuganj North 360 MW CCPP GT was sync.
| 20:25 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- gt
|  | 20:59 | Khulna(C )-Noapara 132kV Ckt-2 is restored.
| 21:53 | 22:32 | Bhangura 132/33kV S/S Tr-1(403T) LT Forced S/D Due to RED HOT | [7 empty] | 12.0MW load
interrup.
| 21:55 | 22:30 | Bhangura 132/33kV S/S Tr-1(403T) HT Forced S/D Due to RED HOT | [7 empty] | 12.0MW load
interrup.
|  | 00:38 | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) is restored.
| 01:02 | 02:59 | Kishoreganj-Mymensingh 132kV Ckt-1 Forced S/D from Bajitpur 132/33kV end.
| 04:30 | 05:01 | Kushtia 132/33kV S/S T-1 HT Tripped showing Main-1 Relay Operated TR-1 relays Due to | [7 empty] | 30.0MW load
|  |  | Ov/Overflux Trip | [7 empty] | interrup.
| 04:30 | 05:03 | Kushtia 132/33kV S/S T2 HT Tripped showing Main-1 Relay Operated TR-2 relays Due to | [7 empty] | 41.0MW load
|  |  | Ov/Overflux Trip | [7 empty] | interrup.
| 04:30 | 05:01 | Kushtia 132/33kV S/S T-1 LT Tripped showing Main-1 Relay Operated TR-1 relays Due to | [7 empty] | 32.0MW load
|  |  | Lockout-1 Operated Lockout-2 Operated | [7 empty] | interrup.
| 04:30 | 05:03 | Kushtia 132/33kV S/S T2 LT Tripped showing Main-1 Relay Operated TR-2 relays Due to | [7 empty] | 41.0MW load
|  |  | Lockout-1 Operated Lockout-2 Operated | [7 empty] | interrup.
| 04:50 | 05:01 | Kushtia 132/33kV S/S T-3 HT Tripped showing Main-1 Relay Operated TR-3 relays Due to | [7 empty] | 30.0MW load
|  |  | Ov/Overflux Trip | [7 empty] | interrup.
| 04:50 | 05:01 | Kushtia 132/33kV S/S T-3 LT Tripped showing Main-1 Relay Operated TR-3 relays Due to | [7 empty] | 30.0MW load
|  |  | Lockout-1 Operated Lockout-2 Operated | [7 empty] | interrup.
| 05:54 |  | Saidpur 132/33kV S/S TR-3 (424T) LT Scheduled S/D Due to Red hot maintainance. | [7 empty] | 20.0MW load
interrup.
| 05:55 |  | Saidpur 132/33kV S/S TR-3 (424T) HT Scheduled S/D Due to Red hot maintainance. | [7 empty] | 20.0MW load
interrup.
| 06:13 | 07:33 | Khulna(C )-Noapara 132kV Ckt-2 Scheduled S/D from Noapara 132/33kV end Due to By the
instruction of ALDC. and from Khulna (C) end Due to For red hot maintenance.
| 06:58 |  | Sirajganj 132/33kV S/S T2-(425) LT Scheduled S/D Due to NESCO Sirajganj has taken S/D due
to BUSBAR jumping the new puthiyabari feeder
| 06:58 |  | Sirajganj 132/33kV S/S T2-(425) HT Scheduled S/D Due to NESCO Sirajganj has taken S/D due
to BUSBAR jumping the new puthiyabari feeder
| 07:27 |  | Barapukuria-Bogura 230 kV Ckt-1 Scheduled S/D from Barapukuria 230/132/33kV end Due to
ERS erection / conductor stringing work and from Bogura 400/230kVend.
| 07:58 |  | Cumilla(S) 132/33kV S/S TR-2 LT Scheduled S/D Due to T-1 Transformer replacement work | [7 empty] | 12.0MW load
interrup.
| 07:58 |  | Cumilla(S) 132/33kV S/S TR-2 HT Scheduled S/D | [7 empty] | 12.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 04-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 361 | 8316000 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 17530 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 290 | 7090903 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 15.6 | 95760 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 15 | 36960 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 232400 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 31182 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 493200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 288360 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 42 | 351840 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 30 | 132982 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 96 | 1243440 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 384960 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 33 | 82080 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 117720 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 9204090.91 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 290 | 6406910 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 123 | 1448400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1813.6 | 35974717.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 94635 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 166080 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 39 | 939600 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5308570 | STG Under Maintenance
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 30 | 59382 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 190894 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 2 | 231360 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 30 | 92160 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24723 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 15 | 40981 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1090 | 22663634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 177600 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 990 | 19694545.46 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 2467 | 49684164.46
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 200 | 4880000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 0 | 6217600 | FGMO not available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 345 | 7560000 | FGMO not available
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 6978000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 26 | 107640 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 20 | 69120 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 136 | 468364 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1104460 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 30 | 58545 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 101 | 2202753 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 146 | 3113280 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 421650 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 32 | 84480 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 331200 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1494 | 33597092
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 26 | 898560 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 76 | 991200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 116400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 256130 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 47520 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 491760 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 158 | 2814570
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 39490 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 298000 | GT-1 under maint.
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 715560 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 148 | 3392918.18 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 110 | 2600100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 714048 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1412160 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2408550 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 396528 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7420000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 401 | 9292000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1255 | 28689354.18
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 932 | 22506182 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 296 | 7333344 | -
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 558720 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1222 | 22480000 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2450 | 52878246
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 446 | 7905454 | ps availability is less
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 2987000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1030 | 18388363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5372650 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 251 | 4647000 | Bad quality coal
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3333 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2077 | 39303800.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 262504 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 28070 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Fuel shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 173 | 4421918 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9163200 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 31080 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1423.66 | 24264932 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 343488 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 606110 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2010.66 | 39121302
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 93 | 481305 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 58599.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 336798 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 208758 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1328400 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 163 | 2413860.12
Eastern Grid Total |  |  |  |  | 17418.042 | 7187.6 | 150759898.55
Western Grid Total |  |  |  |  | 11852.195 | 6700.66 | 133717208.76
National Grid Total |  |  |  |  | 29270.237 | 13888.26 | 284477107.31
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 04-05-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9181.38 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4215.5 | MW
i) Dhaka area |  |  | 5054.98 |  | MW | i) Khulna area |  |  |  | 1551.5 | MW
ii) Chattogram area |  |  | 1469.4 |  | MW | ii) Barishal area |  |  |  | 345.8 | MW
iii) Cumilla area |  |  | 1185 |  | MW | iii) Rajshahi area |  |  |  | 1414.2 | MW
iv) Mymensingh area |  |  | 1015 |  | MW | iv) Rangpur area |  |  |  | 904 | MW
v) Sylhet area |  |  | 457 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13396.88 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 14 | 16:00 | 67 | Hasnabad | 80 | 18:30 | 133 | Natore | 146 | 19:30
2 | AKSML | 127.7 | 06:00 | 68 | Hathazari | 75 | 20:00 | 134 | Nawabganj | 49.2 | 10:00
3 | Aftabnagar | 36 | 13:00 | 69 | Hatirjheel | 39 | 16:00 | 135 | Netrakona | 114 | 19:30
4 | Agargaon | 104 | 14:00 | 70 | Ishurdi | 79 | 19:00 | 136 | New | 74.6 | 12:00
5 | Agrabad | 50 | 15:00 | 71 | Jaldhaka | 68 | 19:00 | 137 | Niamatpur | 65 | 22:00
6 | Amnura | 30 | 19:00 | 72 | Jamalpur | 99 | 20:00 | 138 | Noapara | 40 | 22:00
7 | Ashuganj | 87.5 | 19:00 | 73 | Jashore | 137 | 19:00 | 139 | PHP | 12 | 11:00
8 | BSRM | 200 | 00:00 | 74 | Jhenaidah | 109 | 19:30 | 140 | Pabna | 91 | 19:00
9 | Bagerhat | 75 | 20:00 | 75 | Joydebpur | 138 | 19:00 | 141 | Palashbari | 104 | 19:30
10 | Bajitpur | 67 | 21:00 | 76 | Joypurhat | 53 | 22:00 | 142 | Panchagarh | 59 | 19:30
11 | Bakerganj | 8.6 | 15:00 | 77 | Juldah | 15 | 10:00 | 143 | Patiya | 10 | 19:30
12 | Bakulia | 83 | 15:00 | 78 | KSRM | 18 | 11:00 | 144 | Patuakhali | 59.5 | 00:00
13 | Banani | 44 | 13:00 | 79 | Kabirpur | 274 | 19:00 | 145 | Payra | 32 | 00:00
14 | Bangabhaban | 16 | 12:00 | 80 | Kachua | 73 | 19:00 | 146 | Postogola | 49 | 13:00
15 | Barapukuria | 56 | 19:30 | 81 | Kaliganj | 22 | 00:00 | 147 | Pubail | 38 | 21:00
16 | Barguna | 20 | 20:00 | 82 | Kallyanpur | 99 | 19:00 | 148 | Purbachal | 29 | 12:00
17 | Barishal | 88 | 13:00 | 83 | Kalurghat | 38 | 16:00 | 149 | Purbasadipur | 110 | 19:30
18 | Barishal-230 | 88 | 12:00 | 84 | Kamrangirchar | 76 | 13:00 | 150 | Rahanpur | 34 | 21:00
19 | Baroaulia | 66 | 11:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 39 | 10:00
20 | Baroirhat | 45 | 18:30 | 86 | Kasba | 33 | 19:30 | 152 | Rajbari | 75 | 19:00
21 | Bashundhara | 173 | 14:00 | 87 | Kazla | 111 | 13:00 | 153 | Rajendrapur | 119 | 19:30
22 | BashundharaCement | 8 | 08:00 | 88 | Keranigonj | 84 | 14:00 | 154 | Rajshahi | 123 | 00:00
23 | Beanibazar | 52 | 21:00 | 89 | Khagrachori | 28 | 19:30 | 155 | Rajshahi-230 | 88 | 13:00
24 | Benapole | 60 | 00:00 | 90 | Khulna | 66 | 13:00 | 156 | Ramganj | 88 | 19:00
25 | Bhaluka | 137 | 19:00 | 91 | Khulshi | 189 | 16:00 | 157 | Rampur | 38 | 18:30
26 | Bhandaria | 48 | 22:00 | 92 | Kishoreganj | 107 | 19:30 | 158 | Rangamati | 16 | 19:00
27 | Bhangura | 37 | 19:00 | 93 | Kodda | 305 | 21:00 | 159 | Rangpur | 133 | 19:30
28 | Bheramara(GK) | 61 | 19:00 | 94 | Kulaura | 35 | 18:30 | 160 | Ruppur | 4 | 10:00
29 | Bhulta | 200 | 00:00 | 95 | Kurigram | 58 | 19:30 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 72 | 23:00 | 96 | Kushtia | 147 | 19:00 | 162 | Saidpur | 97 | 19:00
31 | Bogura | 146 | 19:30 | 97 | Laksam | 28 | 19:00 | 163 | Santhia | 28 | 19:00
32 | Borhanuddin | 80 | 01:00 | 98 | Lakshmipur | 30 | 20:00 | 164 | Satkhira | 125 | 00:00
33 | Brahmanbaria | 108 | 20:00 | 99 | Lalbag | 66 | 13:00 | 165 | Satmasjid | 86 | 14:00
34 | Cantonment | 104 | 13:00 | 100 | Lalmonirhat | 54 | 19:00 | 166 | Savar | 214 | 15:00
35 | Chandina | 29 | 19:00 | 101 | MI_Cement | 15.7 | 13:00 | 167 | SevenRings | 16.89 | 17:00
36 | Chandpur | 64 | 21:00 | 102 | Madanganj | 39 | 14:00 | 168 | ShahCement | 34 | 08:00
37 | Chandraghona | 35 | 19:30 | 103 | Madaripur | 84 | 21:00 | 169 | Shahjadpur | 84 | 20:00
38 | Chapai | 67 | 21:00 | 104 | Madartek | 68 | 13:00 | 170 | Shahjibazar | 100 | 19:00
39 | Charsaidpur | 42 | 08:00 | 105 | Madunaghat | 50 | 18:30 | 171 | Shahmirpur | 45 | 21:00
40 | Chauddagram | 61 | 19:30 | 106 | Magura | 57 | 19:30 | 172 | Shariatpur | 67 | 21:00
41 | Chhatak | 28 | 19:00 | 107 | Mahasthangarh | 67 | 19:30 | 173 | Sherpur | 124 | 20:00
42 | Chowmuhani | 109 | 19:00 | 108 | Maijdee | 37 | 21:00 | 174 | Shikalbaha | 34.5 | 20:00
43 | Chuadanga | 108 | 19:30 | 109 | Manikganj | 122 | 19:30 | 175 | Shitalakhya | 81.2 | 12:00
44 | Coxsbazar | 142 | 19:00 | 110 | Maniknagar | 67 | 13:00 | 176 | Sholosohor | 45 | 22:00
45 | Cumilla(N) | 106 | 19:30 | 111 | Matarbari | 52 | 19:00 | 177 | Shyampur | 166 | 01:00
46 | Cumilla(S) | 154 | 18:30 | 112 | Matuail | 72 | 16:00 | 178 | Siddhirganj | 117 | 12:00
47 | Daganbhuiyan | 21 | 21:00 | 113 | Metrorail_Motijheel | 19 | 13:00 | 179 | Sirajganj | 112 | 19:30
48 | Daudkandi | 110 | 19:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sonargaon | 115 | 04:00
49 | DhakaUniversity | 76 | 12:00 | 115 | Millgate | 96 | 15:00 | 181 | Sreemongol | 58 | 19:00
50 | Dhamrai | 116 | 18:30 | 116 | Mirpur | 130 | 13:00 | 182 | Sreepur | 107 | 15:00
51 | Dhanmondi | 108.7 | 13:00 | 117 | Mirsorai | 61 | 10:00 | 183 | Srinagar | 39.2 | 21:00
52 | Dohazari | 93 | 21:00 | 118 | Mirzapur | 46 | 20:00 | 184 | Sunamganj | 49 | 19:00
53 | Faridpur | 150 | 19:00 | 119 | Mithapukur | 52 | 19:00 | 185 | Sylhet | 31 | 19:00
54 | Fatullah | 85 | 16:00 | 120 | Modern | N/A | N/A | 186 | Sylhet-132 | 98 | 19:00
55 | Fenchuganj | 31 | 18:30 | 121 | Mogbazar | 76.3 | 13:00 | 187 | TK | 23 | 19:00
56 | Feni | 86 | 19:00 | 122 | Mongla | 43 | 19:00 | 188 | Tangail | 154 | 19:30
57 | GPH | 2 | 02:00 | 123 | Motijheel | 42 | 13:00 | 189 | Taraganj | 22 | 19:00
58 | Ghatail | 82 | 19:30 | 124 | Muktagacha | 31 | 19:30 | 190 | Tasnim | 18 | 15:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 92 | 21:00 | 191 | Thakurgaon | 97 | 19:30
60 | Ghorashal-230 | 96 | 15:00 | 126 | Muradnagar | 40 | 22:00 | 192 | Tongi | 145 | 19:00
61 | Goalpara | 39 | 13:00 | 127 | Mymensingh | 160 | 19:00 | 193 | Ullahpara | 40 | 19:00
62 | Gollamari | 100 | 13:00 | 128 | Nabinagar | 47 | 19:00 | 194 | Ullon | 44 | 14:00
63 | Gopalganj | 86 | 19:00 | 129 | Naogaon | 117 | 19:30 | 195 | Uttara | 78 | 13:00
64 | Gulshan | 110 | 13:00 | 130 | Narail | 47 | 19:00 | 196 | UttaraNew | 46 | 13:00
65 | Halishahar | 101.5 | 14:00 | 131 | Narinda | 65 | 13:00 | 197 | Zigatola | 80 | 13:00
66 | HaripurSBU | 134 | 01:00 | 132 | Narshingdi | 157 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 04-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 11927 | 0 |  | 11927
1:00 | 11563 | 0 |  | 11563
2:00 | 11001 | 0 |  | 11001
3:00 | 10597 | 0 |  | 10597
4:00 | 10178 | 0 |  | 10178
5:00 | 9809 | 0 |  | 9809
6:00 | 9816.59 | 0 |  | 9816.59
7:00 | 10178.26 | 0 |  | 10178.26
8:00 | 10432.69 | 0 |  | 10432.69
9:00 | 10944.15 | 0 |  | 10944.15
10:00 | 11200.43 | 0 |  | 11200.43
11:00 | 11493.59 | 0 |  | 11493.59
12:00 | 12185.25 | 0 |  | 12185.25
13:00 | 12512.34 | 0 |  | 12512.34
14:00 | 12434.11 | 0 |  | 12434.11
15:00 | 12371.32 | 0 |  | 12371.32
16:00 | 11988.99 | 0 |  | 11988.99
17:00 | 11865.66 | 0 |  | 11865.66
18:00 | 12000.81 | 0 |  | 12000.81
19:00 | 13627 | 0 |  | 13627
19:30 | 13888.26 | 0 |  | 13888.26
20:00 | 13580.61 | 0 |  | 13580.61
21:00 | 13448.37 | 0 |  | 13448.37
22:00 | 13170.31 | 0 |  | 13170.31
23:00 | 12709.4 | 0 |  | 12709.4
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 04-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6294 | 5633 | 11927 | DAILY GENERATION CURVE
00:30 | 6231.5 | 5513.5 | 11745
01:00 | 6169 | 5394 | 11563 | 04-05-2026
01:30 | 6056 | 5226 | 11282
02:00 | 5943 | 5058 | 11001
02:30 | 5885.5 | 4913.5 | 10799
03:00 | 5828 | 4769 | 10597
03:30 | 5713 | 4674.5 | 10387.5
04:00 | 5598 | 4580 | 10178
04:30 | 5466 | 4527.5 | 9993.5
05:00 | 5334 | 4475 | 9809
05:30 | 5320.515 | 4492.28 | 9812.795
06:00 | 5307.03 | 4509.56 | 9816.59
06:30 | 5423.845 | 4573.58 | 9997.425
07:00 | 5540.66 | 4637.6 | 10178.26
07:30 | 5609.78 | 4695.695 | 10305.475
08:00 | 5678.9 | 4753.79 | 10432.69
08:30 | 5816.72 | 4871.7 | 10688.42
09:00 | 5954.54 | 4989.61 | 10944.15
09:30 | 5973.7 | 5098.59 | 11072.29
10:00 | 5992.86 | 5207.57 | 11200.43
10:30 | 6107.265 | 5239.745 | 11347.01
11:00 | 6221.67 | 5271.92 | 11493.59
11:30 | 6361.845 | 5477.575 | 11839.42
12:00 | 6502.02 | 5683.23 | 12185.25
12:30 | 6536.905 | 5811.89 | 12348.795
13:00 | 6571.79 | 5940.55 | 12512.34
13:30 | 6583.65 | 5889.575 | 12473.225
14:00 | 6595.51 | 5838.6 | 12434.11
14:30 | 6576.685 | 5826.03 | 12402.715
15:00 | 6557.86 | 5813.46 | 12371.32
15:30 | 6519.86 | 5660.295 | 12180.155
16:00 | 6481.86 | 5507.13 | 11988.99
16:30 | 6501.75 | 5425.575 | 11927.325
17:00 | 6521.64 | 5344.02 | 11865.66
17:30 | 6511.32 | 5421.915 | 11933.235
18:00 | 6501 | 5499.81 | 12000.81
18:30 | 6818 | 5995.905 | 12813.905
19:00 | 7135 | 6492 | 13627
19:30 | 7187.6 | 6700.66 | 13888.26
20:00 | 6944.8 | 6635.81 | 13580.61
20:30 | 6846.3 | 6668.19 | 13514.49 |  | Executive Engineer
21:00 | 6747.8 | 6700.57 | 13448.37 |  | Network Operation Division
21:30 | 6669.05 | 6640.29 | 13309.34
22:00 | 6590.3 | 6580.01 | 13170.31
22:30 | 6516.6 | 6423.255 | 12939.855
23:00 | 6442.9 | 6266.5 | 12709.4

## En-Curve
QF-LDC-12
Date | 04-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3756 | 1527 | 927 | 0 | 122 | 1113 | 40 | 4288 | 0 | 0 | 117 | 0 | 0 | 37 | 0 | DAILY ENERGY CURVE
00:30 | 3747 | 1523 | 928.5 | 0 | 123 | 1075.5 | 40 | 4176 | 0 | 0 | 104.5 | 0 | 0 | 27.5 | 0 | 04-05-2026
01:00 | 3738 | 1519 | 930 | 0 | 124 | 1038 | 40 | 4064 | 0 | 0 | 92 | 0 | 0 | 18 | 0
01:30 | 3758 | 1528.5 | 929.5 | 0 | 118 | 949.5 | 40 | 3895.5 | 0 | 0 | 46 | 0 | 0 | 17 | 0 | Energy Generated | 284.4771 |  | MKWHr
02:00 | 3778 | 1538 | 929 | 0 | 112 | 861 | 40 | 3727 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3783.5 | 1532 | 929 | 0 | 113 | 843 | 39 | 3543.5 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | Total Energy Requirement | 284.4771 |  | MKWHr
03:00 | 3789 | 1526 | 929 | 0 | 114 | 825 | 38 | 3360 | 0 | 0 | 0 | 0 | 0 | 16 | 0
03:30 | 3756 | 1489 | 929.5 | 0 | 109 | 825 | 37.5 | 3228.5 | 0 | 0 | 0 | 0 | 0 | 13 | 0
04:00 | 3723 | 1452 | 930 | 0 | 104 | 825 | 37 | 3097 | 0 | 0 | 0 | 0 | 0 | 10 | 0
04:30 | 3607.5 | 1360 | 930 | 0 | 108 | 825.5 | 37 | 3113 | 0 | 0 | 0 | 0 | 0 | 12.5 | 0
05:00 | 3492 | 1268 | 930 | 0 | 112 | 826 | 37 | 3129 | 0 | 0 | 0 | 0 | 0 | 15 | 0
05:30 | 3459.5 | 1285.5 | 930 | 0 | 109 | 826 | 38 | 3134 | 12.795 | 0 | 0 | 0 | 0 | 18 | 0
06:00 | 3427 | 1303 | 930 | 0 | 106 | 826 | 39 | 3139 | 25.59 | 0 | 0 | 0 | 0 | 21 | 0
06:30 | 3503 | 1358.5 | 929.5 | 0 | 105 | 822.5 | 39.5 | 3147 | 74.925 | 0 | 0 | 0 | 0 | 17.5 | 0
07:00 | 3579 | 1414 | 929 | 0 | 104 | 819 | 40 | 3155 | 124.26 | 0 | 0 | 0 | 0 | 14 | 0
07:30 | 3593 | 1433 | 929.5 | 0 | 107 | 827 | 40 | 3162 | 182.475 | 7 | 17.5 | 0 | 0 | 7 | 0
08:00 | 3607 | 1452 | 930 | 0 | 110 | 835 | 40 | 3169 | 240.69 | 14 | 35 | 0 | 0 | 0 | 0
08:30 | 3685 | 1483.5 | 930 | 0 | 108 | 830 | 40 | 3273.5 | 285.92 | 17 | 35 | 0 | 0 | 0.5 | 0
09:00 | 3763 | 1515 | 930 | 0 | 106 | 825 | 40 | 3378 | 331.15 | 20 | 35 | 0 | 0 | 1 | 0
09:30 | 3723 | 1520 | 930 | 0 | 115 | 825.13 | 40 | 3420.5 | 436.66 | 24.5 | 37 | 0 | 0 | 0.5 | 0
10:00 | 3683 | 1525 | 930 | 0 | 124 | 825.26 | 40 | 3463 | 542.17 | 29 | 39 | 0 | 0 | 0 | 0
10:30 | 3729 | 1527 | 931 | 0 | 127 | 828.395 | 40 | 3487 | 567.115 | 47 | 60.5 | 0 | 0 | 3 | 0
11:00 | 3775 | 1529 | 932 | 0 | 130 | 831.53 | 40 | 3511 | 592.06 | 65 | 82 | 0 | 0 | 6 | 0
11:30 | 3804.5 | 1570.5 | 932 | 0 | 137 | 881.885 | 40 | 3696.5 | 589.535 | 80 | 95 | 0 | 0 | 12.5 | 0
12:00 | 3834 | 1612 | 932 | 0 | 144 | 932.24 | 40 | 3882 | 587.01 | 95 | 108 | 0 | 0 | 19 | 0
12:30 | 3812 | 1608 | 932 | 0 | 142 | 976.215 | 40 | 4048.5 | 538.08 | 97.5 | 135.5 | 0 | 0 | 19 | 0
13:00 | 3790 | 1604 | 932 | 0 | 140 | 1020.19 | 40 | 4215 | 489.15 | 100 | 163 | 0 | 0 | 19 | 0
13:30 | 3761.5 | 1587 | 932 | 0 | 141 | 1018.26 | 40 | 4213 | 463.215 | 109 | 196.75 | 0 | 0 | 11.5 | 0
14:00 | 3733 | 1570 | 932 | 0 | 142 | 1016.33 | 40 | 4211 | 437.28 | 118 | 230.5 | 0 | 0 | 4 | 0
14:30 | 3760 | 1562.5 | 931 | 0 | 144 | 1005.73 | 39 | 4150.5 | 435.985 | 138 | 232 | 0 | 0 | 4 | 0
15:00 | 3787 | 1555 | 930 | 0 | 146 | 995.13 | 38 | 4090 | 434.69 | 158 | 233.5 | 0 | 0 | 4 | 0
15:30 | 3778.5 | 1513.5 | 930.5 | 0 | 148 | 960.16 | 37.5 | 4059.5 | 355.495 | 145 | 250 | 0 | 0 | 2 | 0
16:00 | 3770 | 1472 | 931 | 0 | 150 | 925.19 | 37 | 4029 | 276.3 | 132 | 266.5 | 0 | 0 | 0 | 0
16:30 | 3745 | 1513.5 | 931.5 | 0 | 146 | 931.035 | 37 | 4044 | 185.79 | 131 | 262.5 | 0 | 0 | 0 | 0
17:00 | 3720 | 1555 | 932 | 0 | 142 | 936.88 | 37 | 4059 | 95.28 | 130 | 258.5 | 0 | 0 | 0 | 0
17:30 | 3615 | 1542.5 | 932 | 0 | 139 | 1011.895 | 37.5 | 4184 | 58.34 | 141 | 272 | 0 | 0 | 0 | 0
18:00 | 3510 | 1530 | 932 | 0 | 136 | 1086.91 | 38 | 4309 | 21.4 | 152 | 285.5 | 0 | 0 | 0 | 0
18:30 | 3603.5 | 1628 | 932 | 0 | 133 | 1266.955 | 38.5 | 4582.5 | 10.7 | 197 | 421.75 | 0 | 0 | 0 | 0
19:00 | 3697 | 1726 | 932 | 0 | 130 | 1447 | 39 | 4856 | 0 | 242 | 558 | 0 | 0 | 0 | 0
19:30 | 3674 | 1720 | 932 | 0 | 146 | 1423.66 | 39 | 5029 | 0 | 248 | 676.6 | 0 | 0 | 0 | 0
20:00 | 3656 | 1589 | 932 | 0 | 136 | 1373.81 | 40 | 4957 | 0 | 242 | 654.8 | 0 | 0 | 0 | 0
20:30 | 3602 | 1609 | 932 | 0 | 138 | 1363.19 | 40 | 5005 | 0 | 242 | 583.3 | 0 | 0 | 0 | 0
21:00 | 3548 | 1629 | 932 | 0 | 140 | 1352.57 | 40 | 5053 | 0 | 242 | 511.8 | 0 | 0 | 0 | 0
21:30 | 3531 | 1574.75 | 932 | 0 | 139 | 1340.29 | 40 | 5030 | 0 | 242 | 480.3 | 0 | 0 | 0 | 0
22:00 | 3514 | 1520.5 | 932 | 0 | 138 | 1328.01 | 40 | 5007 | 0 | 242 | 448.8 | 0 | 0 | 0 | 0
22:30 | 3532 | 1474.5 | 931.5 | 0 | 136 | 1273.755 | 40 | 4917 | 0 | 233 | 402.1 | 0 | 0 | 0 | 0
23:00 | 3550 | 1428.5 | 931 | 0 | 134 | 1219.5 | 40 | 4827 | 0 | 224 | 355.4 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 04-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 96 | -4 | 364 | 88 | 1238 | 310 | Ishurdi-Ghorashal Ckt-1 | Export | 3074472.73
1:00 | 90 | -10 | 348 | 70 | 1174 | 304
2:00 | 86 | -18 | 312 | 62 | 1180 | 328 |  | Import | 0
3:00 | 93 | -20 | 280 | 36 | 898 | 302
4:00 | 102 | -26 | 270 | 20 | 956 | 308 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 100 | -26 | 268 | 12 | 956 | 300
6:00 | 95 | -26 | 272 | 2 | 898 | 304 |  | Import | 0
7:00 | 83 | -27 | 260 | 6 | 840 | 296
8:00 | 111 | -24 | 360 | 38 | 1018 | 330 | Sirajganj-Sreepur Ckt-1 | Export | 0
9:00 | 144 | -16 | 420 | 50 | 1244 | 364
10:00 | 157 | -18 | 436 | 54 | 1276 | 372 |  | Import | 0
11:00 | 158 | -16 | 450 | 62 | 1240 | 398
12:00 | 155 | -17 | 502 | 94 | 1572 | 450 | Sirajganj-Sreepur Ckt-2 | Export | 0
13:00 | 160 | -13 | 504 | 80 | 1572 | 450
14:00 | 160 | -10 | 478 | 66 | 1564 | 450 |  | Import | 0
15:00 | 165 | -10 | 524 | 88 | 1612 | 482
16:00 | 160 | -8 | 482 | 76 | 1626 | 472 | Gopalganj-Aminbazar Ckt-1 | Export | 16320000
17:00 | 136 | -12 | 420 | 74 | 1526 | 440
18:00 | 141 | -13 | 440 | 64 | 1566 | 428 |  | Import | 0
18:30 | 146 | -17 | 492 | 64 | 1762 | 364
19:00 | 110 | -18 | 454 | 62 | 1726 | 338 | Gopalganj-Aminbazar Ckt-2 | Export | 16360000
19:30 | 110 | -13 | 440 | 76 | 1732 | 366
20:00 | 109 | -15 | 420 | 60 | 1748 | 336 |  | Import | 0
21:00 | 126 | -7 | 484 | 84 | 1752 | 370
22:00 | 129 | -2 | 482 | 96 | 1732 | 380 |  | Total Export | 35754472.73
23:00 | 154 | 3 | 522 | 102 | 1772 | 424 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 04-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 400 | 04:00 | 380 | 19:30 | Madunaghat | 407 | 06:00 | 395 | 19:00
Amtali | 417 | 03:00 | 406 | 18:30 | Meghnaghat | 402 | 05:00 | 383 | 19:30
Ashuganj | 422 | 05:00 | 394 | 20:00 | Payra | 418 | 03:00 | 408 | 19:30
Bhulta | 415 | 05:00 | 389 | 19:30 | Rahanpur | 425 | 05:00 | 400 | 19:00
Bibiana | 409 | 05:00 | 399 | 22:00 | Rampal | 410 | 04:00 | 393 | 19:00
BIPTC | 404 | 06:00 | 396 | 14:00
Bogura | 417 | 05:00 | 387 | 19:00
Gopalganj | 410 | 05:00 | 391 | 19:30
Kaliakoir | 393 | 05:00 | 373 | 13:00
Korerhat | 409 | 05:00 | 393 | 19:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 238 | 05:00 | 223 | 13:00 | Jhenaidah | 230 | 05:00 | 217 | 19:00
AKSML | 238 | 05:00 | 225 | 19:00 | Kachua | 234 | 05:00 | 223 | 19:00
Aminbazar | 238 | 05:00 | 224 | 19:00 | Kaliakoir | 239 | 04:00 | 225 | 19:30
Ashuganj | 237 | 03:00 | 225 | 19:30 | Keranigonj | 236 | 04:00 | 222 | 13:00
Ashuganj-400 | 237 | 03:00 | 225 | 19:30 | Khulna(S) | 236 | 05:00 | 223 | 19:00
Baghabari | 239 | 05:00 | 225 | 19:00 | Korerhat | 235 | 04:00 | 223 | 13:00
Barapukuria | 231 | 05:00 | 205 | 19:00 | Madunaghat | 236 | 06:00 | 227 | 18:30
Barapukuria-230 | 231 | 05:00 | 205 | 19:00 | Madunaghat-400 | 238 | 05:00 | 230 | 13:00
Barishal | 230 | 04:00 | 223 | 19:00 | Maniknagar | 235 | 05:00 | 222 | 13:00
Bheramara | 234 | 00:00 | 222 | 13:00 | Meghnaghat | 242 | 06:00 | 230 | 14:00
Bhulta | 237 | 05:00 | 223 | 13:00 | Meghnaghat-400 | 237 | 04:00 | 225 | 13:00
Bibiana | 241 | 04:00 | 231 | 15:00 | Mirsorai | 237 | 05:00 | 227 | 19:00
BIPTC | 236 | 00:00 | 221 | 19:00 | Naogaon | 228 | 04:00 | 210 | 19:00
Bogura | 242 | 04:00 | 224 | 19:00 | Purbasadipur | 231 | 05:00 | 204 | 19:00
Bogura-400 | 241 | 04:00 | 223 | 19:00 | Rajshahi | 234 | 00:00 | 218 | 19:00
Borhanuddin | 232 | 03:00 | 228 | 18:30 | Rampal | 234 | 04:00 | 222 | 19:00
BSRM | 234 | 05:00 | 224 | 19:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 232 | 08:00 | 223 | 19:00 | Rampura | 236 | 04:00 | 221 | 19:30
Cumilla(N) | 235 | 05:00 | 223 | 19:00 | Shikalbaha | 235 | 03:00 | 225 | 19:00
Faridpur | 229 | 05:00 | 217 | 19:00 | Shyampur | 236 | 05:00 | 223 | 13:00
Fenchuganj | 240 | 07:00 | 234 | 19:30 | Siddhirganj | 236 | 06:00 | 225 | 13:00
Feni | 234 | 05:00 | 223 | 19:00 | Sirajgonj | 245 | 05:00 | 232 | 19:30
Ghorashal | 240 | 02:00 | 223 | 13:00 | Sreepur | 236 | 05:00 | 220 | 19:30
Ghorashal-230 | 235 | 06:00 | 220 | 13:00 | Tongi | 233 | 07:00 | 219 | 19:00
Gopalganj | 228 | 05:00 | 217 | 19:30
GPH | 230 | 00:00 | 225 | 19:00
Haripur | 236 | 05:00 | 223 | 13:00
Hasnabad | 235 | 07:00 | 221 | 13:00
Hathazari | 235 | 05:00 | 224 | 19:00
Ishurdi | 237 | 01:00 | 224 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 03:00 | 125 | 13:00 | Madunaghat | 137 | 04:00 | 131 | 14:00
Agargaon | 137 | 03:00 | 128 | 13:00 | Magura | 135 | 04:00 | 126 | 19:00
Agrabad | 135 | 03:00 | 128 | 12:00 | Mahasthangarh | 137 | 04:00 | 124 | 19:00
AKS | 133 | 05:00 | 126 | 18:30 | Maijdee | 131 | 05:00 | 124 | 19:00
Aminbazar | 136 | 03:00 | 127 | 13:00 | Manikganj | 133 | 04:00 | 120 | 19:00
Amnura | 138 | 10:00 | 126 | 18:30 | Maniknagar | 138 | 04:00 | 128 | 13:00
Ashuganj | 144 | 07:00 | 135 | 19:30 | Matarbari | 125 | 05:00 | 108 | 19:00
Ashuganj-230 | 144 | 07:00 | 135 | 19:30 | Matuail | 137 | 04:00 | 129 | 13:00
Bagerhat | 134 | 04:00 | 124 | 19:00 | Metrorail_Motijheel | 138 | 05:00 | 124 | 07:00
Bajitpur | 137 | 06:00 | 128 | 19:00 | Metrorail_Uttara | 138 | 03:00 | 125 | 19:30
Bakerganj | 135 | 17:00 | 130 | 19:00 | Millgate | 139 | 03:00 | 126 | 19:00
Bakulia | 136 | 01:00 | 127 | 19:00 | Mirpur | 135 | 04:00 | 126 | 13:00
Banani | 135 | 04:00 | 123 | 13:00 | Mirzapur | 136 | 05:00 | 127 | 19:30
Bangabhaban | 139 | 03:00 | 129 | 13:00 | Mithapukur | 134 | 05:00 | 119 | 19:00
Barapukuria | 133 | 04:00 | 117 | 19:00 | MI_Cement | 135 | 04:00 | 124 | 14:00
Barguna | 135 | 04:00 | 129 | 19:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 133 | 04:00 | 127 | 13:00 | Mogbazar | 135 | 03:00 | 125 | 13:00
Barishal-230 | 134 | 8:00 | 129 | 19:00 | Mongla | 134 | 07:00 | 124 | 21:00
Baroaulia | 136 | 05:00 | 129 | 14:00 | Motijheel | 139 | 03:00 | 129 | 13:00
Baroirhat | 135 | 03:00 | 128 | 18:30 | Muktagacha | 131 | 01:00 | 121 | 19:00
Bashundhara | 139 | 04:00 | 123 | 13:00 | Munshiganj | 135 | 05:00 | 127 | 13:00
BashundharaCement | 136 | 05:00 | 129 | 13:00 | Muradnagar | 134 | 04:00 | 125 | 19:00
Beanibazar | 134 | 05:00 | 127 | 19:00 | Mymensingh | 134 | 04:00 | 119 | 19:00
Benapole | 130 | 05:00 | 119 | 12:00 | Nabinagar | 137 | 04:00 | 126 | 19:00
Bhaluka | 135 | 06:00 | 123 | 19:30 | Naogaon | 139 | 05:00 | 126 | 19:00
Bhandaria | 134 | 16:00 | 124 | 13:00 | Narail | 136 | 05:00 | 126 | 19:00
Bhangura | 138 | 06:00 | 128 | 19:00 | Narinda | 138 | 04:00 | 128 | 13:00
Bheramara | 138 | 03:00 | 132 | 19:00 | Narshingdi | 138 | 07:00 | 125 | 13:00
Bheramara(GK) | 137 | 03:00 | 132 | 19:00 | Natore | 135 | 06:00 | 126 | 19:00
Bhulta | 131 | 08:00 | 125 | 12:00 | Nawabganj | 139 | 04:00 | 130 | 13:00
Bog-Sherpur | 139 | 05:00 | 127 | 19:00 | Netrakona | 126 | 13:00 | 117 | 19:30
Bogura | 139 | 05:00 | 128 | 19:00 | New | 138 | 04:00 | 128 | 14:00
Bogura-230 | 140 | 04:00 | 128 | 19:00 | Niamatpur | 139 | 05:00 | 128 | 19:00
Brahmanbaria | 138 | 07:00 | 127 | 19:30 | Noapara | 131 | 05:00 | 120 | 13:00
Cantonment | 137 | 05:00 | 127 | 13:00 | Pabna | 137 | 05:00 | 129 | 19:00
Chandina | 136 | 04:00 | 129 | 19:00 | Palashbari | 133 | 05:00 | 118 | 19:00
Chandpur | 132 | 06:00 | 127 | 13:00 | Panchagarh | 139 | 05:00 | 123 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 137 | 04:00 | 131 | 18:30 | Patiya | 134 | 07:00 | 126 | 19:00
Chapai | 138 | 05:00 | 130 | 20:00 | Patuakhali | 134 | 05:00 | 129 | 19:30
Charsaidpur | 136 | 03:00 | 128 | 13:00 | Payra | 137 | 05:00 | 132 | 19:30
Chauddagram | 134 | 03:00 | 127 | 19:00 | PHP | 134 | 04:00 | 128 | 19:00
Chhatak | 133 | 04:00 | 125 | 19:00 | Postogola | 136 | 04:00 | 127 | 14:00
Chowmuhani | 131 | 06:00 | 125 | 15:00 | Pubail | 139 | 04:00 | 129 | 12:00
Chuadanga | 132 | 05:00 | 123 | 19:00 | Purbachal | 138 | 03:00 | 124 | 13:00
Coxsbazar | 127 | 09:00 | 110 | 19:00 | Purbasadipur | 134 | 05:00 | 119 | 19:00
Cumilla(N) | 136 | 06:00 | 129 | 19:00 | Rahanpur | 140 | 04:00 | 131 | 19:00
Cumilla(S) | 136 | 06:00 | 122 | 15:00 | Rahanpur-400 | 141 | 05:00 | 132 | 19:00
Daganbhuiyan | 133 | 04:00 | 127 | 19:00 | Rahim | 136 | 05:00 | 129 | 13:00
Daudkandi | 132 | 04:00 | 124 | 13:00 | Rajbari | 131 | 04:00 | 123 | 19:00
DhakaUniversity | 135 | 04:00 | 124 | 13:00 | Rajendrapur | 134 | 07:00 | 122 | 19:00
Dhamrai | 137 | 04:00 | 127 | 19:00 | Rajshahi | 132 | 00:00 | 124 | 19:00
Dhanmondi | 138 | 03:00 | 131 | 13:00 | Rajshahi-230 | 135 | 04:00 | 125 | 19:00
Dohazari | 132 | 05:00 | 122 | 19:00 | Ramganj | 129 | 07:00 | 123 | 19:00
Faridpur | 132 | 04:00 | 126 | 19:00 | Rampur | 136 | 06:00 | 127 | 19:00
Fatullah | 136 | 05:00 | 125 | 13:00 | Rampura | 135 | 05:00 | 124 | 13:00
Fenchuganj | 137 | 07:00 | 133 | 13:00 | Rangamati | 137 | 05:00 | 129 | 19:00
Feni | 132 | 04:00 | 128 | 12:00 | Rangpur | 133 | 05:00 | 120 | 19:00
Feni-230 | 134 | 05:00 | 127 | 19:00 | Ruppur | 138 | 03:00 | 131 | 19:00
Ghatail | 132 | 03:00 | 120 | 19:00 | Saidpur | 132 | 03:00 | 116 | 19:00
Ghorashal | 141 | 06:00 | 133 | 18:30 | Santhia | 137 | 02:00 | 129 | 19:30
Goalpara | 139 | 05:00 | 131 | 19:00 | Satkhira | 134 | 04:00 | 126 | 21:00
Gollamari | 138 | 05:00 | 130 | 19:00 | Satmasjid | 137 | 04:00 | 126 | 13:00
Gopalganj | 136 | 05:00 | 128 | 19:00 | Savar | 133 | 04:00 | 123 | 15:00
Gopalganj-400 | 136 | 04:00 | 129 | 19:00 | SevenRings | 141 | 04:00 | 132 | 19:30
Gulshan | 134 | 06:00 | 124 | 13:00 | ShahCement | 136 | 03:00 | 128 | 13:00
Halishahar | 136 | 04:00 | 127 | 19:00 | Shahjadpur | 138 | 01:00 | 132 | 18:30
Haripur | 137 | 04:00 | 130 | 13:00 | Shahjibazar | 137 | 07:00 | 127 | 19:00
HaripurSBU | 137 | 04:00 | 130 | 13:00 | Shahmirpur | 136 | 06:00 | 128 | 18:30
Hasnabad | 135 | 03:00 | 128 | 14:00 | Shariatpur | 134 | 04:00 | 127 | 19:00
Hathazari | 138 | 05:00 | 131 | 19:00 | Sherpur | 125 | 00:00 | 113 | 19:30
Hatirjheel | 135 | 04:00 | 124 | 13:00 | Shikalbaha | 137 | 07:00 | 129 | 19:00
Ishurdi | 139 | 03:00 | 132 | 19:00 | Shikalbaha-230 | 137 | 03:00 | 130 | 19:00
Jaldhaka | 131 | 05:00 | 112 | 19:00 | Shitalakhya | 135 | 04:00 | 124 | 14:00
Jamalpur | 127 | 00:00 | 117 | 19:30 | Sholosohor | 137 | 04:00 | 131 | 13:00
Jashore | 130 | 05:00 | 119 | 19:00 | Shyampur | 135 | 06:00 | 128 | 17:00
Jhenaidah | 136 | 05:00 | 127 | 19:00 | Shyampur-230 | 136 | 04:00 | 129 | 13:00
Jhenaidah-230 | 136 | 05:00 | 127 | 19:00 | Siddhirganj | 138 | 04:00 | 130 | 10:00
Joydebpur | 136 | 05:00 | 129 | 15:00 | Sirajganj | 136 | 05:00 | 125 | 19:00
Joypurhat | 136 | 04:00 | 124 | 19:00 | Sonargaon | 135 | 04:00 | 129 | 13:00
Juldah | 134 | 01:00 | 128 | 19:00 | Sreemongol | 137 | 07:00 | 127 | 19:30
Kabirpur | 135 | 00:00 | 122 | 19:30 | Sreepur | 136 | 04:00 | 125 | 19:00
Kachua | 133 | 06:00 | 127 | 19:00 | Srinagar | 140 | 04:00 | 130 | 13:00
Kaliakoir | 140 | 05:00 | 130 | 14:00 | SSM | 140 | 00:00 | 135 | 12:00
Kaliganj | 135 | 05:00 | 126 | 12:00 | Sunamganj | 133 | 06:00 | 124 | 19:00
Kallyanpur | 135 | 05:00 | 125 | 13:00 | Sylhet | 135 | 06:00 | 129 | 19:00
Kalurghat | 138 | 05:00 | 131 | 13:00 | Sylhet-132 | 134 | 04:00 | 129 | 18:30
Kamrangirchar | 140 | 04:00 | 124 | 12:00 | Tangail | 133 | 04:00 | 121 | 12:00
Kaptai | 139 | 6:00 | 133 | 19:00 | Taraganj | 133 | 05:00 | 115 | 19:30
Kasba | 135 | 07:00 | 125 | 19:00 | Tasnim | 136 | 04:00 | 129 | 13:00
Kazla | 139 | 05:00 | 128 | 13:00 | Thakurgaon | 136 | 04:00 | 121 | 19:00
Keranigonj | 140 | 04:00 | 131 | 13:00 | TK | 138 | 04:00 | 131 | 13:00
Khagrachori | 134 | 09:00 | 129 | 19:00 | Tongi | 139 | 07:00 | 129 | 19:00
Khulna | 138 | 05:00 | 130 | 19:00 | Ullahpara | 137 | 03:00 | 127 | 19:00
Khulna(S) | 139 | 05:00 | 131 | 19:00 | Ullon | 135 | 05:00 | 124 | 14:00
Khulshi | 134 | 05:00 | 126 | 19:00 | Uttara | 138 | 04:00 | 125 | 14:00
Kishoreganj | 136 | 04:00 | 124 | 19:30 | UttaraNew | 138 | 03:00 | 125 | 19:30
Kodda | 132 | 04:00 | 125 | 12:00 | Zigatola | 140 | 04:00 | 131 | 13:00
Korerhat | 136 | 04:00 | 130 | 19:00
KSRM | 136 | 03:00 | 130 | 12:00
Kulaura | 137 | 05:00 | 132 | 18:30
Kurigram | 130 | 23:00 | 111 | 19:30
Kushtia | 136 | 06:00 | 128 | 12:00
Laksam | 132 | 05:00 | 126 | 19:00
Lakshmipur | 131 | 05:00 | 124 | 13:00
Lalbag | 140 | 05:00 | 130 | 13:00
Lalmonirhat | 128 | 04:00 | 118 | 19:00
Madanganj | 136 | 05:00 | 129 | 13:00
Madaripur | 135 | 05:00 | 128 | 19:30
Madartek | 134 | 04:00 | 123 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division