## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 06-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-05-2026 | during | 06-05-2026 | during | 06-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 385 | 368 | 412 | 412 | 412 | 412 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 8 | 55 | 55 | 55 | 15 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 295 | 288 | 335 | 335 | 310 | 310 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 32 | 7 | 32 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 15.2 | 18 | 53.97 | 53.97 | 17 | 17
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 14 | 50 | 149.36 | 149.36 | 46 | 46 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 0 | 33 | 33 | 25 | 25 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 14 | 14 | 14 | 14 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 51 | 52.19 | 52.19 | 16 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 50 | 195 | 300 | 300 | 48 | 294 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 115 | 115 | 149 | 149 | 115 | 115 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 70 | 105 | 105 | 17 | 34 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 90 | 162 | 162 | 35 | 88 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 460 | 475 | 584 | 584 | 470 | 470 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 313 | 293 | 718 | 718 | 335 | 335 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 80 | 142 | 160 | 160 | 123 | 123 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1913.2 | 2293 | 5969.22 | 5914.22 | 2129 | 2484
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 0 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 16 | 0 | 16 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 15 | 19 | 50 | 50 | 19 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 219 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 9 | 31 | 105 | 105 | 34 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 68 | 68 | 50 | 50 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 12 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 18 | 31 | 108 | 108 | 12 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.07 | 0 | 1.71 | 0 | 1.71 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 32 | 163 | 163 | 17 | 54 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1182 | 1126 | 1224 | 1224 | 1204 | 1204 | AGC
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 1 | 0 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1000 | 1000 | 1150 | 1150 | 1150 | 1150 | AGC
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2484.07 | 2593 | 3999.57 | 4013.86 | 3042.71 | 3176
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 203 | 192 | 221.25 | 221.25 | 205.25 | 205.25 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 354 | 356 | 350.01 | 350.01 | 350.01 | 350.01
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 270 | 250 | 342.01 | 342.01 | 342.01 | 342.01 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 215 | 320 | 393 | 393 | 260 | 260 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 150 | 150 | 150 | 25 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 31 | 40 | 40 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 87 | 163 | 163 | 51 | 51 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 4 | 77 | 200 | 200 | 17 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 144 | 126 | 84 | 80 | 148 | 148 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 43 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 14 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 17 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 18 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 2 | 90 | 115 | 115 | 17 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 60 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1391 | 1805 | 2757.44 | 2698.44 | 1599.27 | 1989.27
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-05-2026 | during | 06-05-2026 | during | 06-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 11 | 157.5 | 157.5 | 31 | 31 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.4 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 77 | 67 | 70 | 70 | 10 | 10 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 10 | 10 | 70 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 45.27 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 143.67 | 134 | 361.2 | 314 | 175.2 | 140
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 12 | 42 | 41 | 41 | 30 | 30 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 153 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 110 | 110 | 110 | 110 | Machine Problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 25 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 84 | 85 | 85 | 85 | 85 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 98 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 17 | 17 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 339 | 368 | 380 | 380 | 380 | 380 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1081 | 1132 | 1323 | 1323 | 1236 | 1236
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 932 | 932 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 36 | 36 | 36 | 36 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 246 | 227 | 410 | 410 | 280 | 280 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 97 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1090 | 1160 | 1234.2 | 1234.2 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2365 | 2319 | 3575.2 | 3500.2 | 2632.1 | 2557.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 320 | 401 | 300 | 500 | 300 | 500 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 860 | 1100 | 1244 | 1244 | 1244 | 1244 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 261 | 216 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.65 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1791.65 | 2067 | 2462 | 2661 | 2215 | 2414
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 40.95 | 0 | 48.55 | 0 | 48.55 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 28 | 28 | 28 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 50 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 196 | 140 | 220 | 220 | 200 | 200 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0.03 | 0.03 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 92 | 92 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.38 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1080.01 | 1330.35 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 66.09 | 0 | 63.96 | 0 | 63.96 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 105 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1907.43 | 1934.35 | 3209.23 | 2990.87 | 2381.68 | 2248.32
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 105 | 113 | 113 | 49 | 49 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 8 | 0 | 7.1 | 0 | 7.1 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 108 | 115 | 115 | 35 | 35 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 38 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 132 | 0 | 190.06 | 0 | 190.06 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 212 | 213 | 489.16 | 262 | 311.16 | 84
System Total |  |  |  |  | 28823.2 | 29270.237 | 13289.02 | 14490.35 | 24146.02 | 23677.59 | 15722.12 | 16328.69
Forecast Scenario (06-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12900 |  | 0 |  | 12900
|  |  |  | 1:00 | 12250 |  | 0 |  | 12250
|  |  |  | 2:00 | 11810 |  | 0 |  | 11810
|  |  |  | 3:00 | 11400 |  | 0 |  | 11400
|  |  |  | 4:00 | 11110 |  | 0 |  | 11110
|  |  |  | 5:00 | 10720 |  | 0 |  | 10720
|  |  |  | 6:00 | 11040 |  | 0 |  | 11040
|  |  |  | 7:00 | 11460 |  | 0 |  | 11460
|  |  |  | 8:00 | 11700 |  | 0 |  | 11700
|  |  |  | 9:00 | 11980 |  | 0 |  | 11980
|  |  |  | 10:00 | 12430 |  | 0 |  | 12430
|  |  |  | 11:00 | 13160 |  | 0 |  | 13160
|  |  |  | 12:00 | 13600 |  | 0 |  | 13600
|  |  |  | 13:00 | 13990 |  | 0 |  | 13990
|  |  |  | 14:00 | 13310 |  | 0 |  | 13310
|  |  |  | 15:00 | 13320 |  | 0 |  | 13320
|  |  |  | 16:00 | 12930 |  | 0 |  | 12930
|  |  |  | 17:00 | 12800 |  | 0 |  | 12800
|  |  |  | 18:00 | 12930 |  | 0 |  | 12930
|  |  |  | 18:30 | 13850 |  | 0 |  | 13850
|  |  |  | 19:00 | 14550 |  | 0 |  | 14550
|  |  |  | 19:30 | 14800 |  | 0 |  | 14800
|  |  |  | 20:00 | 14500 |  | 0 |  | 14500
|  |  |  | 21:00 | 14370 |  | 0 |  | 14370
|  |  |  | 22:00 | 14090 |  | 0 |  | 14090
|  |  |  | 23:00 | 13630 |  | 0 |  | 13630
Probable Maximum Temperature: |  |  | 31.70°C
Probable Maximum Demand at Day Peak: |  |  | 13600.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14800.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14800.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 305.98 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:46 hrs on 06-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 05-05-2026 | [28 empty] | Date: | 05-05-2026 | [28 empty] | Date: | 05-05-2026 | [28 empty] | Date: | 05-05-2026 | [28 empty] | Date: | 05-05-2026 | [17 empty] | Date: | 05-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 220 | 15 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 88 | 18.5 | 14 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 15 | 930 | 0 | 0 | 9 | 0 | 0 | 222 | 0 | 0 | 0 | 970 | 0 | 0 | 8 | 300 | 58 | 320 | 0 | 0 | 198 | 10 | 0 | 51 | 0 | 0 | 14 | 0 | 136 | 0 | 0 | 0 | 300 | 0 | 354 | 30 | 30 | 127 | 0 | 17 | 0 | 22 | 30 | 109 | 0 | 100 | 0 | 9 | 58 | 27 | 0 | 0 | 0 | 5959.5 | 932 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1096 | 0 | 0 | 0 | 1193.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 130 | 180 | 0 | 350 | 975 | 0 | 5807.89 | 11767.39 | 78.25
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 282 | 15.4 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 94 | 18.5 | 14 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 27 | 800 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 950 | 0 | 0 | 8 | 300 | 170 | 300 | 0 | 0 | 200 | 10 | 0 | 51 | 0 | 0 | 14 | 0 | 134 | 0 | 0 | 0 | 300 | 0 | 344 | 30 | 30 | 129 | 0 | 17 | 0 | 22 | 30 | 110 | 0 | 100 | 0 | 9 | 58 | 28 | 0 | 0 | 0 | 5988.9 | 932 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 838 | 0 | 0 | 0 | 979.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 130 | 180 | 0 | 350 | 910 | 0 | 5189.47 | 11178.37 | 78.28
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 277 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 106 | 19 | 14 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 22 | 735 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 925 | 0 | 0 | 0 | 300 | 295 | 300 | 0 | 0 | 194 | 0 | 0 | 51 | 0 | 0 | 14 | 0 | 132 | 0 | 0 | 0 | 295 | 0 | 344 | 30 | 30 | 132 | 0 | 17 | 0 | 22 | 30 | 109 | 0 | 100 | 0 | 9 | 8 | 30 | 0 | 0 | 0 | 5909 | 932 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 774 | 0 | 0 | 0 | 917.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 300 | 825 | 0 | 4901.65 | 10810.65 | 78.31
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 19 | 14 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 22 | 735 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 845 | 0 | 0 | 0 | 300 | 355 | 300 | 0 | 0 | 196 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 126 | 0 | 0 | 0 | 300 | 0 | 344 | 30 | 30 | 142 | 0 | 17 | 0 | 22 | 30 | 70 | 0 | 100 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 5717 | 932 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772 | 0 | 0 | 0 | 837.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 300 | 744 | 0 | 4751.46 | 10468.46 | 78.34
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 19 | 14 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 22 | 684 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 845 | 0 | 0 | 0 | 280 | 320 | 300 | 0 | 0 | 193 | 0 | 0 | 51 | 0 | 0 | 14 | 0 | 126 | 0 | 0 | 0 | 300 | 0 | 331 | 30 | 30 | 140 | 0 | 17 | 0 | 22 | 30 | 70 | 0 | 100 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 5543 | 931 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 776 | 0 | 0 | 0 | 839.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 300 | 690 | 0 | 4698.85 | 10241.85 | 78.37
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 19 | 14 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 22 | 644 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 240 | 320 | 250 | 0 | 0 | 193 | 0 | 0 | 51 | 0 | 0 | 14 | 0 | 118 | 0 | 0 | 0 | 300 | 0 | 331 | 30 | 30 | 147 | 0 | 17 | 0 | 22 | 30 | 70 | 0 | 100 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 5333 | 932 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 777 | 0 | 0 | 0 | 839.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 100 | 180 | 0 | 250 | 615 | 0 | 4587.3 | 9920.3 | 78.4
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 19 | 14 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 39 | 0 | 27 | 691 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 802 | 1 | 0 | 0 | 240 | 360 | 250 | 0 | 0 | 210 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 114 | 0 | 4 | 0 | 315 | 0 | 399 | 30 | 30 | 151 | 0 | 17 | 0 | 22 | 30 | 80 | 0 | 100 | 0 | 0 | 0 | 30 | 0.05 | 0.69 | 0 | 5748.94 | 932 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.51 | 779 | 0 | 0 | 0 | 880.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53 | 5 | 0 | 0 | 2.46 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.22 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 7 | 0 | 0 | 140 | 100 | 220 | 0 | 250 | 576 | 0 | 4563.83 | 10312.77 | 78.43
07:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 274 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 5 | 0 | 19 | 14 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.08 | 40 | 0 | 28 | 753 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 890 | 2 | 0 | 0 | 240 | 360 | 300 | 12 | 0 | 194 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 114 | 0 | 19 | 0 | 310 | 0 | 400 | 30 | 30 | 159 | 1 | 17 | 0 | 84 | 30 | 110 | 0 | 100 | 0 | 9 | 56 | 31 | 0.3 | 6.54 | 0 | 6035.92 | 932 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.65 | 778 | 0 | 0 | 0 | 839.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.15 | 29 | 0 | 0 | 15.36 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 2.2 | 28 | 0.15 | 0 | 206 | 130 | 220 | 0 | 250 | 640 | 0 | 4764.91 | 10800.83 | 78.46
08:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 281 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 14 | 35 | 18 | 14 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.13 | 40 | 0 | 6 | 730 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 885 | 5 | 0 | 0 | 240 | 360 | 300 | 51 | 0 | 197 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 108 | 0 | 21 | 0 | 305 | 0 | 401 | 30 | 30 | 148 | 3 | 17 | 0 | 84 | 30 | 110 | 0 | 100 | 0 | 9 | 56 | 28 | 1 | 26.66 | 0 | 6105.79 | 932 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 774 | 0 | 0 | 0 | 841.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.91 | 61 | 0 | 0 | 31.99 | 0 | 0 | 0 | 0 | 20 | 0 | 414 | 0 | 2.89 | 0 | 0 | 0 | 17 | 34 | 0 | 0 | 0 | 5.2 | 115 | 0.11 | 0 | 177 | 130 | 220 | 0 | 250 | 675 | 0 | 5009.26 | 11115.05 | 78.49
09:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 335 | 0 | 0 | 70 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 0 | 0 | 24 | 52 | 21 | 14 | 0 | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.23 | 40 | 0 | 2 | 730 | 0 | 0 | 1 | 0 | 0 | 219 | 0 | 0 | 0 | 986 | 0 | 0 | 0 | 220 | 360 | 300 | 51 | 0 | 200 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 118 | 0 | 33 | 0 | 310 | 0 | 375 | 30 | 30 | 156 | 5 | 17 | 0 | 84 | 30 | 110 | 0 | 100 | 0 | 9 | 56 | 28 | 1.77 | 31.37 | 0 | 6324.37 | 932 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 782 | 0 | 0 | 0 | 835.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.69 | 72 | 0 | 0 | 45.36 | 0 | 0 | 0 | 0 | 43 | 0 | 414 | 0 | 4.06 | 0 | 0 | 0 | 14 | 34 | 0 | 0 | 0 | 6.6 | 108 | 0.26 | 0 | 194 | 130 | 220 | 0 | 250 | 675 | 0 | 5136.86 | 11461.23 | 78.52
10:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 297 | 0 | 0 | 90 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 0 | 30 | 52 | 20 | 14 | 0 | 430 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.69 | 40 | 0 | 2 | 750 | 0 | 0 | 6 | 0 | 0 | 217 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 215 | 360 | 270 | 51 | 0 | 192 | 0 | 0 | 50 | 0 | 0 | 14 | 0 | 134 | 0 | 38 | 0 | 305 | 0 | 356 | 20 | 30 | 155 | 6 | 17 | 0 | 84 | 30 | 111 | 0 | 100 | 0 | 9 | 77 | 10 | 2.1 | 48.03 | 0 | 6414.82 | 932 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 770 | 0 | 0 | 0 | 974.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.67 | 95 | 0 | 0 | 58.82 | 0 | 0 | 0 | 0 | 107 | 0 | 414 | 0 | 5.21 | 0 | 0 | 0 | 25 | 34 | 0 | 0 | 0 | 4.3 | 195 | 0.69 | 0 | 223 | 130 | 220 | 0 | 267 | 715 | 0 | 5561.51 | 11976.33 | 78.55
11:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 313 | 12 | 0 | 105 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 24 | 52 | 20 | 14 | 0 | 440 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.25 | 40 | 0 | 2 | 900 | 0 | 0 | 7 | 0 | 0 | 217 | 0 | 0 | 0 | 1165 | 0 | 0 | 0 | 215 | 358 | 270 | 51 | 0 | 200 | 0 | 0 | 50 | 0 | 0 | 18 | 0 | 138 | 0 | 72 | 0 | 310 | 0 | 357 | 10 | 30 | 153 | 12 | 17 | 0 | 84 | 30 | 111 | 0 | 100 | 0 | 9 | 77 | 10 | 2.4 | 51.09 | 0 | 6796.74 | 932 | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 902 | 0 | 0 | 0 | 1051.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.53 | 100 | 0 | 0 | 62.77 | 0 | 0 | 0 | 0 | 176 | 0 | 414 | 0 | 5.42 | 0 | 0 | 0 | 35 | 34 | 0 | 0 | 0 | 8 | 197 | 0.72 | 0 | 256 | 130 | 220 | 0 | 320 | 752 | 0 | 5975.63 | 12772.37 | 78.58
12:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 313 | 15.2 | 0 | 115 | 14 | 50 | 8 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 17 | 295 | 0 | 0 | 32 | 80 | 20 | 14 | 0 | 460 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.07 | 40 | 0 | 2 | 1000 | 0 | 0 | 15 | 0 | 9 | 215 | 0 | 0 | 0 | 1182 | 0 | 20 | 0 | 215 | 354 | 270 | 51 | 0 | 203 | 0 | 2 | 50 | 4 | 0 | 18 | 0 | 144 | 0 | 60 | 0 | 310 | 0 | 339 | 12 | 30 | 153 | 12 | 17 | 0 | 83 | 25 | 0 | 0 | 100 | 0 | 9 | 77 | 10 | 2.4 | 45.27 | 0 | 7012.94 | 932 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 1090 | 0 | 0 | 0 | 1080.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.95 | 105 | 0 | 0 | 66.09 | 0 | 0 | 0 | 0 | 196 | 0 | 414 | 0 | 5.38 | 0 | 0 | 0 | 38 | 34 | 0 | 0 | 0 | 8 | 132 | 0.65 | 0 | 261 | 130 | 220 | 0 | 320 | 860 | 0 | 6276.08 | 13289.02 | 78.61
13:00 | 7 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 292 | 18 | 0 | 115 | 50 | 160 | 48 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 17 | 275 | 0 | 0 | 26 | 142 | 20 | 14 | 0 | 370 | 0 | 0 | 19 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 3.86 | 40 | 0 | 4 | 1000 | 23 | 0 | 19 | 0 | 30 | 215 | 0 | 0 | 0 | 1192 | 16 | 97 | 0 | 215 | 357 | 250 | 51 | 0 | 205 | 0 | 16 | 50 | 62 | 8 | 18 | 0 | 144 | 1 | 39 | 1 | 320 | 0 | 339 | 12 | 30 | 151 | 11 | 17 | 0 | 83 | 25 | 0 | 0 | 100 | 0 | 9 | 77 | 10 | 2.1 | 41.01 | 0 | 7327.97 | 932 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 1118 | 0 | 0 | 0 | 1103.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.01 | 102 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 172 | 0 | 414 | 0 | 4.6 | 0 | 0 | 25 | 36 | 34 | 0 | 0 | 0 | 8 | 51 | 0.58 | 0 | 255 | 130 | 220 | 0 | 317 | 990 | 0 | 6337.5 | 13665.47 | 78.64
14:00 | 7 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 235 | 17.5 | 0 | 115 | 60 | 160 | 55 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 19 | 142 | 20 | 14 | 0 | 350 | 0 | 0 | 15 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1.93 | 43 | 0 | 0 | 965 | 54 | 0 | 19 | 7 | 30 | 215 | 0 | 0 | 0 | 1114 | 15 | 127 | 0 | 250 | 320 | 250 | 51 | 0 | 202 | 0 | 17 | 50 | 79 | 9 | 18 | 0 | 158 | 1 | 51 | 16 | 300 | 0 | 309 | 15 | 30 | 142 | 6 | 17 | 0 | 80 | 30 | 0 | 0 | 98 | 0 | 9 | 78 | 10 | 1 | 35.07 | 0 | 7118.5 | 932 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.75 | 1026 | 0 | 0 | 0 | 1034.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.36 | 50 | 0 | 0 | 26.33 | 0 | 0 | 0 | 0 | 158 | 0 | 351 | 0 | 2.31 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 7.7 | 148 | 0.47 | 0 | 215 | 100 | 220 | 0 | 308 | 998 | 0 | 5857.76 | 12976.26 | 78.67
15:00 | 7 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 274 | 18 | 0 | 115 | 60 | 160 | 41 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 10 | 142 | 20 | 14 | 0 | 390 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 41 | 0 | 0 | 980 | 49 | 0 | 20 | 8 | 32 | 214 | 0 | 0 | 0 | 1107 | 10 | 135 | 0 | 250 | 320 | 250 | 51 | 0 | 195 | 0 | 31 | 50 | 82 | 9 | 14 | 0 | 142 | 20 | 28 | 19 | 315 | 0 | 326 | 40 | 30 | 150 | 3 | 17 | 0 | 80 | 30 | 0 | 0 | 98 | 0 | 9 | 78 | 10 | 0.86 | 33.4 | 0 | 7236.89 | 931 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 932 | 0 | 0 | 0 | 1034.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.79 | 55 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 165 | 0 | 401 | 0 | 3.29 | 0 | 0 | 64 | 24 | 32 | 0 | 0 | 0 | 6.4 | 179 | 0.21 | 0 | 232 | 130 | 220 | 0 | 313 | 990 | 0 | 6102.27 | 13339.16 | 78.69
16:00 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 229 | 18 | 4 | 115 | 60 | 160 | 41 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 0 | 0 | 8 | 142 | 20 | 14 | 0 | 330 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92 | 38 | 0 | 5 | 965 | 48 | 0 | 22 | 8 | 33 | 219 | 0 | 0 | 0 | 1109 | 6 | 128 | 0 | 250 | 320 | 250 | 51 | 0 | 198 | 0 | 31 | 50 | 80 | 9 | 0 | 0 | 72 | 27 | 17 | 17 | 315 | 0 | 338 | 35 | 30 | 143 | 3 | 17 | 0 | 80 | 30 | 0 | 0 | 98 | 0 | 9 | 68 | 10 | 0.3 | 15.01 | 0 | 7004.23 | 932 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 943 | 0 | 0 | 0 | 951.89 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9 | 0 | 0 | 14.66 | 29 | 0 | 0 | 10 | 17 | 0 | 0 | 0 | 161 | 0 | 405 | 0 | 0.97 | 0 | 0 | 90 | 17 | 58 | 0 | 0 | 0 | 2.3 | 118 | 0.24 | 0 | 192 | 130 | 220 | 0 | 308 | 990 | 0 | 5861.96 | 12866.19 | 78.71
17:00 | 16 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 228 | 18 | 17 | 115 | 60 | 160 | 41 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 274 | 0 | 0 | 7 | 142 | 20 | 14 | 0 | 330 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38 | 37 | 0 | 7 | 945 | 46 | 0 | 19 | 8 | 32 | 219 | 0 | 0 | 0 | 1070 | 0 | 147 | 0 | 250 | 320 | 250 | 51 | 0 | 198 | 0 | 17 | 83 | 78 | 9 | 0 | 0 | 116 | 25 | 10 | 23 | 310 | 0 | 344 | 36 | 30 | 137 | 2 | 17 | 0 | 84 | 30 | 0 | 0 | 98 | 33 | 9 | 67 | 11 | 0.7 | 4.8 | 0 | 7081.88 | 932 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 947 | 0 | 0 | 0 | 887.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.49 | 23 | 0 | 0 | 13 | 7 | 0 | 0 | 0 | 153 | 0 | 404 | 0 | 1.15 | 0 | 0 | 95 | 8 | 71 | 0 | 0 | 0 | 2.3 | 46 | 0.1 | 0 | 172 | 130 | 220 | 0 | 304 | 930 | 0 | 5606.18 | 12688.06 | 78.73
18:00 | 16 | 70 | 51 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 306 | 18 | 17 | 115 | 60 | 160 | 52 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 274 | 0 | 0 | 0 | 142 | 20 | 14 | 0 | 370 | 0 | 0 | 20 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.01 | 38 | 0 | 10 | 945 | 49 | 0 | 19 | 9 | 31 | 219 | 0 | 0 | 0 | 970 | 0 | 145 | 0 | 290 | 340 | 250 | 51 | 0 | 198 | 0 | 21 | 82 | 80 | 15 | 5 | 0 | 120 | 25 | 1 | 31 | 315 | 0 | 356 | 35 | 30 | 140 | 0 | 17 | 0 | 84 | 30 | 0 | 0 | 98 | 35 | 9 | 67 | 11 | 0.05 | 2.69 | 10 | 7327.75 | 932 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.11 | 801 | 0 | 0 | 0 | 836.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.67 | 4 | 0 | 0 | 1.6 | 5 | 0 | 0 | 0 | 142 | 0 | 358 | 0 | 0.15 | 0 | 0 | 92 | 1 | 85 | 0 | 0 | 0 | 0.3 | 8 | 0.02 | 0 | 173 | 130 | 220 | 0 | 305 | 920 | 0 | 5253.03 | 12580.78 | 78.74
19:00 | 24 | 70 | 51 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 305 | 18 | 17 | 115 | 60 | 195 | 55 | 35 | 90 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 142 | 20 | 14 | 0 | 500 | 0 | 0 | 31 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 17 | 1000 | 46 | 0 | 19 | 18 | 32 | 219 | 0 | 0 | 0 | 1095 | 0 | 145 | 0 | 393 | 356 | 250 | 51 | 0 | 202 | 0 | 72 | 85 | 83 | 18 | 14 | 0 | 130 | 43 | 0 | 31 | 310 | 0 | 363 | 42 | 30 | 147 | 0 | 17 | 0 | 84 | 30 | 0 | 0 | 98 | 35 | 9 | 67 | 11 | 0 | 0 | 12 | 8115 | 931 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1026 | 0 | 0 | 0 | 1117.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 0 | 94 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 130 | 220 | 0 | 313 | 960 | 0 | 5876.83 | 13991.83 | 78.75
19:30 | 0 | 70 | 51 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 293 | 18 | 17 | 115 | 50 | 195 | 55 | 35 | 90 | 0 | 0 | 0 | 0 | 0 | 17 | 288 | 0 | 0 | 0 | 142 | 0 | 14 | 0 | 475 | 0 | 0 | 31 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 12 | 1000 | 32 | 0 | 19 | 17 | 31 | 219 | 0 | 0 | 0 | 1126 | 0 | 150 | 0 | 320 | 356 | 250 | 51 | 0 | 192 | 0 | 90 | 87 | 77 | 18 | 14 | 0 | 126 | 43 | 0 | 31 | 310 | 0 | 368 | 42 | 30 | 153 | 0 | 17 | 0 | 84 | 30 | 0 | 0 | 98 | 35 | 9 | 67 | 11 | 0 | 0 | 12 | 7957 | 932 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 1330.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 0 | 108 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 130 | 220 | 0 | 401 | 1100 | 0 | 6533.35 | 14490.35
20:00 | 0 | 34 | 51 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 285 | 18 | 17 | 115 | 30 | 195 | 55 | 35 | 90 | 0 | 0 | 0 | 0 | 0 | 17 | 283 | 0 | 0 | 0 | 123 | 0 | 14 | 0 | 415 | 0 | 0 | 31 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 18 | 1000 | 0 | 0 | 19 | 17.5 | 0 | 220 | 0 | 0 | 0 | 1105 | 0 | 150 | 0 | 295 | 356 | 250 | 51 | 0 | 189 | 0 | 87 | 87 | 0 | 0 | 18 | 0 | 132 | 0 | 0 | 0 | 310 | 0 | 380 | 42 | 30 | 149 | 0 | 17 | 0 | 84 | 30 | 0 | 0 | 98 | 0 | 9 | 67 | 11 | 0 | 0 | 12 | 7517.5 | 932 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1170 | 0 | 0 | 0 | 1450.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 140 | 0 | 405 | 0 | 0 | 0 | 0 | 111 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 130 | 220 | 0 | 402 | 1100 | 0 | 6669.08 | 14186.58 | 78.76
21:00 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 300 | 18 | 17 | 115 | 30 | 45 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 123 | 20 | 14 | 0 | 500 | 0 | 0 | 30 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 19 | 1000 | 0 | 0 | 19 | 21 | 0 | 220 | 0 | 0 | 0 | 1141 | 0 | 80 | 0 | 240 | 356 | 250 | 51 | 0 | 205 | 0 | 90 | 86 | 0 | 0 | 18 | 0 | 134 | 0 | 0 | 0 | 305 | 0 | 394 | 42 | 30 | 152 | 0 | 17 | 0 | 84 | 28 | 0 | 0 | 100 | 0 | 9 | 67 | 11 | 0 | 0 | 12 | 7271 | 932 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1181 | 0 | 0 | 0 | 1448.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 0 | 108 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 130 | 220 | 0 | 495 | 1110 | 0 | 6859.88 | 14130.88 | 78.77
22:00 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 304 | 18 | 17 | 115 | 30 | 45 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 123 | 19 | 14 | 0 | 480 | 0 | 0 | 35 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 24 | 970 | 0 | 0 | 19 | 25.5 | 0 | 221 | 0 | 0 | 0 | 1133 | 0 | 80 | 0 | 225 | 356 | 250 | 51 | 0 | 218 | 0 | 71 | 86 | 0 | 0 | 18 | 0 | 136 | 0 | 0 | 0 | 300 | 0 | 401 | 42 | 30 | 149 | 0 | 17 | 0 | 84 | 30 | 0 | 0 | 100 | 0 | 9 | 58 | 11 | 0 | 0 | 12 | 7190.5 | 932 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1171 | 0 | 0 | 0 | 1374.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 141 | 0 | 414 | 0 | 0 | 0 | 0 | 107 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 130 | 220 | 0 | 477 | 1100 | 0 | 6748.36 | 13938.86 | 78.78
23:00 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 302 | 18 | 17 | 115 | 30 | 45 | 0 | 30 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 123 | 19 | 14 | 0 | 480 | 0 | 0 | 39 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 28 | 950 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 1130 | 0 | 40 | 0 | 240 | 355 | 250 | 51 | 0 | 212 | 0 | 65 | 87 | 0 | 0 | 18 | 0 | 124 | 0 | 0 | 0 | 305 | 0 | 389 | 42 | 30 | 149 | 0 | 17 | 0 | 84 | 28 | 0 | 0 | 100 | 0 | 9 | 58 | 11 | 0 | 0 | 0 | 7086 | 932 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1175 | 0 | 0 | 0 | 1364.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 142 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 130 | 220 | 0 | 452 | 1080 | 0 | 6600.72 | 13686.72 | 78.79
Total KWH | 102002 | 314880 | 389280 | 0 | 0 | 0 | 0 | 0 | 8899200 | 0 | 7191390 | 258840 | 151200 | 2048976 | 610560 | 1559651 | 419171 | 295989 | 509760 | 0 | 0 | 0 | 0 | 0 | 121019 | 6962103 | 0 | 0 | 213692 | 2194800 | 454800 | 344520 | 0 | 10110000 | 0 | 0 | 357120 | 0 | 12960 | 442723 | 0 | 0 | 0 | 0 | 26277 | 980400 | 0 | 344640 | 20807272.73 | 346255 | 0 | 261120 | 126082.8 | 271818 | 5138560 | 0 | 0 | 0 | 24447270 | 64260 | 1369963 | 16727 | 6232500 | 8353000 | 6592000 | 898208 | 0 | 4970000 | 16848 | 568320 | 1458133 | 604800 | 94920 | 420460 | 0 | 2995200 | 169200 | 412745 | 140240 | 7425000 | 0 | 8729000 | 713000 | 726840 | 3535936.36 | 72535 | 400320 | 0 | 1593600 | 701184 | 1117200 | 0 | 2388810 | 132480 | 182400 | 1281600 | 384000 | 14050 | 326630 | 60240 | 161876680.89 | 22453818 | 5872032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 529200 | 22414550 | 0 | 0 | 0 | 24521521 | 0 | 0 | 0 | 0 | 0 | 0 | 15072 | 0 | 0 | 374880 | 792698 | 0 | 0 | 402752 | 662818 | 0 | 0 | 0 | 3441491 | 0 | 9420800 | 0 | 34200 | 0 | 0 | 941126 | 211775 | 1010371 | 0 | 0 | 0 | 50089.32 | 1372320 | 4176 | 0 | 4778000 | 2904000 | 5297090 | 0 | 7927273 | 21389090.91 | 0 | 136821143.23 | 298697824.12

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 05-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13289.02 | MW | 12:00 Hr. | Energy Generated |  |  | 298.6978 |  | MKWHr.
| Day Peak Demand |  |  | 13289.02 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.603 |  | MKWHr.
| Evening Peak Generation |  |  | 14490.35 | MW | 19:30 Hr. | Energy Demand |  |  | 299.3008 |  | MKWHr.
| Evening Peak Demand |  |  | 14620.35 | MW | 19:30 Hr. | Maximum Temperature |  |  | 33.3 |  | °C
| Minimum Generation of the Day |  |  | 9920.3 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 915.41 |  | MMCFD
| Maximum Generation of the Day |  |  | 14490.35 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.8784 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.962 | 0 | 8.9761 | 0 | 0 | 0.21369 | 0 | 0 | 43.1518 | Gas | 123.7162 | Gas | 429635398.7312
| Chattogram Zone |  |  | 5.4832 | 45.2545 | 1.8051 | 0 | 0.9804 | 0.090537 | 0 | 0.01296 | 53.6268 | Coal | 101.7635 | Coal | 675432695.1501
| Cumilla Zone |  |  | 28.9579 | 0 | 2.9474 | 0 | 0 | 0.41274 | 2.9952 | 0 | 35.3133 | HFO | 17.352 | HFO | 290380997.79
| Mymensingh Zone |  |  | 0.384 | 0 | 1.6567 | 0 | 0 | 0.34068 | 0 | 0 | 2.3814 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.3309 | 0 | 0 | 0 | 0 | 0.072535 | 0 | 0 | 27.4034 | Hydro | 0.9804 | Hydro | 98040
| Khulna Zone |  |  | 5.872 | 22.4145 | 0 | 0 | 0 | 0.5292 | 22.4538 | 0 | 51.2696 | Solar | 4.9023 | Solar | 79224204.83
| Barishal Zone |  |  | 8.2011 | 34.0944 | 0 | 0 | 0 | 0.004176 | 0 | 0 | 42.2996 | Import | 49.9705 | Import | 280913453.31
| Rajshahi Zone |  |  | 13.5251 | 0 | 0.015072 | 0 | 0 | 1.6045 | 24.5215 | 0 | 39.6662 | Wind | 0.01296 | Wind | 190641.6
| Rangpur Zone |  |  | 0 | 0 | 1.9515 | 0 | 0 | 1.6342 | 0 | 0 | 3.5857
| Total |  |  | 123.7162 | 101.7635 | 17.352 | 0 | 0.9804 | 4.9023 | 49.9705 | 0.01296 | 298.6978
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 429635398.7312 |  | Hydro | 98040
|  |  |  | Coal | 675432695.1501 |  | Solar | 79224204.83
|  |  |  | HFO | 290380997.79 |  | Import | 280913453.31
|  |  |  | HSD | 0 |  | Wind | 190641.6
[5 empty] | Total: | 175,58,75,431 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.4538 | Peak Hr Flow | 932.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 38215600 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.5215 | Peak Hr Flow | 1330.35 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1734 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.9952 | Peak Hr Flow | 126.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2559 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.9705 | Peak Hr Flow | 2388.35 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 15 |  | 5118
|  |  |  | Chattogram |  | 0 |  | 1497
|  |  |  | Cumilla |  | 0 |  | 1187
|  |  |  | Mymensingh |  | 109 |  | 1143
|  |  |  | Sylhet |  | 0 |  | 565
|  |  |  | Khulna |  | 0 |  | 1774
|  |  |  | Barishal |  | 0 |  | 437
|  |  |  | Rajshahi |  | 0 |  | 1446
|  |  |  | Rangpur |  | 0 |  | 950
|  |  |  | Total |  | 124 |  | 14117
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:14 | 18:38 | Barishal-Barishal(N) 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to OPGW
Upgration Work of OFCN and from Barishal 230/132kV end Due to OPGW Replace
|  | 08:15 | Saidpur 132/33kV S/S TR-3 (424T) LT is restored.
|  | 08:15 | Saidpur 132/33kV S/S TR-3 (424T) HT is restored.
|  | 08:44 | Sirajganj 132/33kV S/S T2-(425) HT is restored.
|  | 08:45 | Sirajganj 132/33kV S/S T2-(425) LT is restored.
|  | 09:38 | Cumilla(S) 132/33kV S/S TR-2 HT is restored.
|  | 09:38 | Cumilla(S) 132/33kV S/S TR-2 LT is restored.
| 10:31 | 11:02 | Rajshahi-Rajshahi(New) 132kV Ckt-1 Forced S/D from Rajshahi 132/33kV end Due to The Work
Of Remove a Kite
| 12:00 |  | Day peak generation 13346 MW
| 12:02 |  | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D Due to Instructed by ALDC
| 13:03 | 15:10 | Chandina 132/33kV S/S TR-2 LT Forced S/D Due to For Rectification of Red Hot Issue at
33kV Bus DS.
| 13:04 | 15:10 | Chandina 132/33kV S/S TR-2 HT Forced S/D Due to For Rectification of Red Hot Issue at
33kV Bus DS.
| 13:05 |  | Full interruption occurred under entire Rangpur zone (Except Palashbari) due to tripping
of Barapukuria-Bogura 230 kV ckt-2 showing distance relay and Palashbari-Mithapukur 132
kV both ckt showing overcurrent relay. Barapukuria-Bogura 230 kV ckt-1 was in shutdown
condition.
| 13:06 | 13:18 | Mithapukur-Palashbari 132kV Ckt-2 Tripped from Mithapukur 132/33kV end showing 21M2, | [7 empty] | 34.0MW load interrup.
86A, 86B relays Due to None
| 13:07 | 13:57 | Barapukuria-Bogura 230 kV Ckt-2 Tripped from Barapukuria 230/132/33kV end showing REL | [7 empty] | 333.0MW load interrup.
521, REL 511 relays.
| 13:08 | 13:19 | Mithapukur-Palashbari 132kV Ckt-1 Tripped from Palashbari 132/33kV end showing Over
Current. relays Due to Unknown.
| 13:18 |  | Power restoration was started by closing Palashbari-Mithapukur both ckt.
|  | 14:42 | Barapukuria-Bogura 230 kV Ckt-1 is restored.
| 15:45 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- GT
| 16:50 | 17:28 | Chandina 132/33kV S/S TR-3 HT Forced S/D Due to For rectification of red hot. | [7 empty] | 5.0MW load interrup.
| 16:50 | 17:29 | Chandina 132/33kV S/S TR-3 LT Forced S/D Due to For rectification of Red hot . | [7 empty] | 4.0MW load interrup.
| 17:28 | 18:12 | Niamatpur 132/33kV S/S 132 kV Naogaon ckt-2 Project Work S/D Due to Project work
| 18:33 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- ST
| 19:30 |  | Evening Peak Generation is 14490 MW.
|  | 20:37 | Goalpara 132/33kV S/S Bus 1 is restored.
|  | 20:46 | Goalpara 132/33kV S/S Goalpara-NWPGCL is restored.
| 23:22 | 00:58 | Chowmuhani 230/132/33kV S/S TR2-425T HT Forced S/D Due to 33 kV BUS Jumper R phase & Y | [7 empty] | 30.0MW load
|  |  | Phase red-hot Maintenance. | [7 empty] | interrup.
| 23:22 | 00:58 | Chowmuhani 230/132/33kV S/S TR2-425T LT Forced S/D Due to 33 kV BUS Jumper R phase & Y | [7 empty] | 30.0MW load
|  |  | Phase red-hot Maintenance. | [7 empty] | interrup.
| 06:24 |  | Cumilla(S) 132/33kV S/S TR-2 HT Scheduled S/D Due to Tr-01 replacing work by energypac.
| 06:24 |  | Cumilla(S) 132/33kV S/S TR-2 LT Scheduled S/D Due to Tr-01 replacing work by energypac.
| 07:07 |  | Khulna (C) S/S TR-1 425T HT Scheduled S/D Due to Hot spot Maintenance | [7 empty] | 12.0MW load interrup.
| 07:07 |  | Khulna (C) S/S TR-1 425T LT Scheduled S/D Due to Hot spot Maintenance | [7 empty] | 12.0MW load interrup.
| 07:07 |  | Khulna (C) S/S TR-1 425T LT Scheduled S/D Due to Hot spot Maintenance | [7 empty] | 12.0MW load interrup.
| 07:10 |  | Mymensingh 132/33kV S/S Transformer-1 (404T) LT Scheduled S/D
| 07:14 |  | Mymensingh 132/33kV S/S Transformer-1 (404T) HT Scheduled S/D
| 07:28 |  | Mymensingh 132/33kV S/S T-1 Bus Scheduled S/D Due to 33kV Bhal -1 Feeder, Raiser Change
on source side
| 07:47 |  | Barapukuria-Bogura 230 kV Ckt-1 Scheduled S/D from Bogura 400/230kV end Due to Due to
Conductor stringing at Barapukuria site. and from Barapukuria 230/132/33kV end Due to
Tower errection
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 05-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 368 | 8899200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 419171 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 288 | 6962103 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 102002 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 18 | 258840 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 50 | 610560 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 295989 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 121019 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 0 | 454800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 344520 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 51 | 389280 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 1559651 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 115 | 2048976 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 314880 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 509760 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 213692 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 151200 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 475 | 10110000 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 293 | 7191390 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 2194800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2293 | 43151833
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 126082.8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 64260 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 261120 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 980400 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 5138560 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 31 | 271818 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 442723 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 12 | 344640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 31 | 357120 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 26277 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 32 | 346255 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1126 | 24447270 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 12960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1000 | 20807272.73 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 2593 | 53626758.53
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 192 | 4970000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 356 | 8353000 | FGMO not available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 250 | 6592000 | FGMO not available
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 320 | 6232500 | FGMO
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 16848 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 16727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 898208 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 1369963 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 31 | 140240 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 87 | 1458133 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 77 | 604800 | -
| Import (Tripura) |  | Import | 0 | 160 | 126 | 2995200 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 169200 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 420460 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 18 | 94920 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 568320 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 412745 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1805 | 35313264
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 11 | 384000 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 67 | 1281600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 182400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 326630 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 60240 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 132480 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 134 | 2381400
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 72535 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 713000 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 726840 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 153 | 3535936.36 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 1117200 | Machine Problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 701184 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1593600 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 98 | 2388810 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 400320 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7425000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 368 | 8729000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1132 | 27403425.36
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 932 | 22453818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 227 | 5872032 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 529200 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1160 | 22414550 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2319 | 51269600
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 401 | 7927273 | ps availability is less
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 2904000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1100 | 21389090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5297090 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 216 | 4778000 | Bad quality coal
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4176 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2067 | 42299629.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 374880 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 50 | 662818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Fuel shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 140 | 3441491 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9420800 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 15072 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 34200 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1330.35 | 24521521 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 402752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 792698 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1934.35 | 39666232
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 105 | 1010371 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 50089.32 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 108 | 941126 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 211775 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1372320 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 213 | 3585681.32
Eastern Grid Total |  |  |  |  | 17418.042 | 7957 | 161876680.89
Western Grid Total |  |  |  |  | 11852.195 | 6533.35 | 136821143.23
National Grid Total |  |  |  |  | 29270.237 | 14490.35 | 298697824.12
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 05-05-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9385.99 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4606.9 | MW
i) Dhaka area |  |  | 5102.79 |  | MW | i) Khulna area |  |  |  | 1773.5 | MW
ii) Chattogram area |  |  | 1497.2 |  | MW | ii) Barishal area |  |  |  | 437.2 | MW
iii) Cumilla area |  |  | 1187 |  | MW | iii) Rajshahi area |  |  |  | 1446.2 | MW
iv) Mymensingh area |  |  | 1034 |  | MW | iv) Rangpur area |  |  |  | 950 | MW
v) Sylhet area |  |  | 565 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13992.89 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 15 | 04:00 | 67 | Hasnabad | 96 | 13:00 | 133 | Natore | 148 | 19:30
2 | AKSML | 118 | 08:00 | 68 | Hathazari | 84 | 19:30 | 134 | Nawabganj | 52 | 19:00
3 | Aftabnagar | 36 | 12:00 | 69 | Hatirjheel | 31 | 12:00 | 135 | Netrakona | 143 | 19:30
4 | Agargaon | 113 | 13:00 | 70 | Ishurdi | 80 | 19:30 | 136 | New | 80 | 12:00
5 | Agrabad | 68 | 18:30 | 71 | Jaldhaka | 74 | 19:30 | 137 | Niamatpur | 59 | 19:30
6 | Amnura | 28 | 21:00 | 72 | Jamalpur | 96 | 18:00 | 138 | Noapara | 44 | 19:30
7 | Ashuganj | 77 | 13:00 | 73 | Jashore | 138 | 19:00 | 139 | PHP | 12 | 11:00
8 | BSRM | 205 | 04:00 | 74 | Jhenaidah | 112 | 19:30 | 140 | Pabna | 97 | 21:00
9 | Bagerhat | 82 | 22:00 | 75 | Joydebpur | 142 | 19:00 | 141 | Palashbari | 114 | 19:30
10 | Bajitpur | 75 | 20:00 | 76 | Joypurhat | 56 | 21:00 | 142 | Panchagarh | 59 | 20:00
11 | Bakerganj | 10.2 | 19:00 | 77 | Juldah | 17 | 13:00 | 143 | Patiya | 10.6 | 22:00
12 | Bakulia | 89 | 15:00 | 78 | KSRM | 17 | 06:00 | 144 | Patuakhali | 60 | 19:00
13 | Banani | 48.4 | 12:00 | 79 | Kabirpur | 268 | 15:00 | 145 | Payra | 30 | 21:00
14 | Bangabhaban | 17 | 10:00 | 80 | Kachua | 70 | 19:00 | 146 | Postogola | 52 | 12:00
15 | Barapukuria | 63 | 19:30 | 81 | Kaliganj | 19 | 19:30 | 147 | Pubail | 34 | 13:00
16 | Barguna | 18 | 00:00 | 82 | Kallyanpur | 102 | 13:00 | 148 | Purbachal | 31 | 13:00
17 | Barishal | 102 | 13:00 | 83 | Kalurghat | 40 | 11:00 | 149 | Purbasadipur | 121 | 19:30
18 | Barishal-230 | 92 | 20:00 | 84 | Kamrangirchar | 84 | 13:00 | 150 | Rahanpur | 32 | 21:00
19 | Baroaulia | 60 | 13:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 42 | 10:00
20 | Baroirhat | 50 | 19:00 | 86 | Kasba | 30 | 21:00 | 152 | Rajbari | 85 | 19:00
21 | Bashundhara | 193 | 13:00 | 87 | Kazla | 116 | 12:00 | 153 | Rajendrapur | 126 | 19:30
22 | BashundharaCement | 8 | 18:00 | 88 | Keranigonj | 86 | 13:00 | 154 | Rajshahi | 104 | 19:30
23 | Beanibazar | 72 | 19:00 | 89 | Khagrachori | 26 | 19:30 | 155 | Rajshahi-230 | 90 | 13:00
24 | Benapole | 62 | 23:00 | 90 | Khulna | 71 | 13:00 | 156 | Ramganj | 96 | 19:00
25 | Bhaluka | 161 | 19:00 | 91 | Khulshi | 198 | 12:00 | 157 | Rampur | 40 | 22:00
26 | Bhandaria | 51 | 22:00 | 92 | Kishoreganj | 123 | 19:00 | 158 | Rangamati | 16 | 18:30
27 | Bhangura | 41 | 19:00 | 93 | Kodda | 309 | 21:00 | 159 | Rangpur | 140 | 19:30
28 | Bheramara(GK) | 63 | 19:30 | 94 | Kulaura | 50 | 20:00 | 160 | Ruppur | 4 | 15:00
29 | Bhulta | 203 | 11:00 | 95 | Kurigram | 64 | 19:00 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 72 | 21:00 | 96 | Kushtia | 154 | 20:00 | 162 | Saidpur | 97 | 15:00
31 | Bogura | 157 | 21:00 | 97 | Laksam | 29 | 19:30 | 163 | Santhia | 38 | 19:00
32 | Borhanuddin | 94 | 19:30 | 98 | Lakshmipur | 35 | 19:00 | 164 | Satkhira | 136 | 19:30
33 | Brahmanbaria | 115 | 21:00 | 99 | Lalbag | 68 | 13:00 | 165 | Satmasjid | 96 | 13:00
34 | Cantonment | 112 | 13:00 | 100 | Lalmonirhat | 58 | 19:00 | 166 | Savar | 218 | 12:00
35 | Chandina | 24 | 23:00 | 101 | MI_Cement | 14.7 | 19:30 | 167 | SevenRings | 15.24 | 04:00
36 | Chandpur | 69 | 14:00 | 102 | Madanganj | 40 | 20:00 | 168 | ShahCement | 40 | 23:00
37 | Chandraghona | 36 | 21:00 | 103 | Madaripur | 97 | 20:00 | 169 | Shahjadpur | 84 | 21:00
38 | Chapai | 63 | 21:00 | 104 | Madartek | 66 | 19:00 | 170 | Shahjibazar | 115 | 19:30
39 | Charsaidpur | 42 | 11:00 | 105 | Madunaghat | 53 | 18:30 | 171 | Shahmirpur | 45 | 21:00
40 | Chauddagram | 58 | 15:00 | 106 | Magura | 67 | 19:30 | 172 | Shariatpur | 75 | 19:30
41 | Chhatak | 34 | 22:00 | 107 | Mahasthangarh | 71 | 19:30 | 173 | Sherpur | 110 | 00:00
42 | Chowmuhani | 124 | 21:00 | 108 | Maijdee | 43 | 21:00 | 174 | Shikalbaha | 37 | 21:00
43 | Chuadanga | 116 | 19:30 | 109 | Manikganj | 138 | 19:00 | 175 | Shitalakhya | 86.5 | 12:00
44 | Coxsbazar | 145 | 19:00 | 110 | Maniknagar | 75 | 13:00 | 176 | Sholosohor | 44 | 15:00
45 | Cumilla(N) | 99 | 12:00 | 111 | Matarbari | 50 | 21:00 | 177 | Shyampur | 194 | 12:00
46 | Cumilla(S) | 158 | 14:00 | 112 | Matuail | 78 | 12:00 | 178 | Siddhirganj | 129 | 12:00
47 | Daganbhuiyan | 27 | 14:00 | 113 | Metrorail_Motijheel | 26 | 19:30 | 179 | Sirajganj | 116 | 19:30
48 | Daudkandi | 128 | 00:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sonargaon | 128 | 16:00
49 | DhakaUniversity | 86 | 13:00 | 115 | Millgate | 100 | 15:00 | 181 | Sreemongol | 62 | 22:00
50 | Dhamrai | 114 | 15:00 | 116 | Mirpur | 142 | 13:00 | 182 | Sreepur | 113 | 18:30
51 | Dhanmondi | 97.5 | 13:00 | 117 | Mirsorai | 54 | 01:00 | 183 | Srinagar | 40.6 | 15:00
52 | Dohazari | 99 | 23:00 | 118 | Mirzapur | 43 | 19:00 | 184 | Sunamganj | 56 | 20:00
53 | Faridpur | 161 | 19:30 | 119 | Mithapukur | 54 | 19:00 | 185 | Sylhet | 41 | 19:30
54 | Fatullah | 89 | 12:00 | 120 | Modern | N/A | N/A | 186 | Sylhet-132 | 120 | 18:30
55 | Fenchuganj | 44 | 19:00 | 121 | Mogbazar | 84.1 | 13:00 | 187 | TK | 24 | 19:00
56 | Feni | 100 | 19:30 | 122 | Mongla | 40 | 16:00 | 188 | Tangail | 154 | 21:00
57 | GPH | 3 | 14:00 | 123 | Motijheel | 47 | 13:00 | 189 | Taraganj | 24 | 19:00
58 | Ghatail | 80 | 17:00 | 124 | Muktagacha | 35 | 18:30 | 190 | Tasnim | 19 | 18:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 99 | 14:00 | 191 | Thakurgaon | 98 | 19:30
60 | Ghorashal-230 | 108 | 22:00 | 126 | Muradnagar | 40 | 19:00 | 192 | Tongi | 149 | 15:00
61 | Goalpara | 39 | 19:30 | 127 | Mymensingh | 171 | 19:00 | 193 | Ullahpara | 40 | 19:00
62 | Gollamari | 98 | 20:00 | 128 | Nabinagar | 52 | 19:00 | 194 | Ullon | 48 | 12:00
63 | Gopalganj | 99 | 20:00 | 129 | Naogaon | 117 | 19:30 | 195 | Uttara | 84 | 12:00
64 | Gulshan | 118 | 12:00 | 130 | Narail | 58 | 19:00 | 196 | UttaraNew | 50 | 13:00
65 | Halishahar | 104.5 | 15:00 | 131 | Narinda | 73 | 13:00 | 197 | Zigatola | 86 | 13:00
66 | HaripurSBU | 133 | 01:00 | 132 | Narshingdi | 169 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 05-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 11767.39 | 0 |  | 11767.39
1:00 | 11178.37 | 0 |  | 11178.37
2:00 | 10810.65 | 0 |  | 10810.65
3:00 | 10468.46 | 0 |  | 10468.46
4:00 | 10241.85 | 0 |  | 10241.85
5:00 | 9920.3 | 0 |  | 9920.3
6:00 | 10312.77 | 0 |  | 10312.77
7:00 | 10800.83 | 0 |  | 10800.83
8:00 | 11115.05 | 0 |  | 11115.05
9:00 | 11461.23 | 0 |  | 11461.23
10:00 | 11976.33 | 0 |  | 11976.33
11:00 | 12772.37 | 0 |  | 12772.37
12:00 | 13289.02 | 0 |  | 13289.02
13:00 | 13665.47 | 0 |  | 13665.47
14:00 | 12976.26 | 0 |  | 12976.26
15:00 | 13339.16 | 0 |  | 13339.16
16:00 | 12866.19 | 0 |  | 12866.19
17:00 | 12688.06 | 0 |  | 12688.06
18:00 | 12580.78 | 0 |  | 12580.78
19:00 | 13991.83 | 95 |  | 14090.83
19:30 | 14490.35 | 124 |  | 14620.35
20:00 | 14186.58 | 109 |  | 14300.58
21:00 | 14130.88 | 125 |  | 14261.88
22:00 | 13938.86 | 136 |  | 14080.86
23:00 | 13686.72 | 138 |  | 13830.72
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 05-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5959.5 | 5807.89 | 11767.39 | DAILY GENERATION CURVE
00:30 | 5974.2 | 5498.68 | 11472.88
01:00 | 5988.9 | 5189.47 | 11178.37 | 05-05-2026
01:30 | 5948.95 | 5045.56 | 10994.51
02:00 | 5909 | 4901.65 | 10810.65
02:30 | 5813 | 4826.555 | 10639.555
03:00 | 5717 | 4751.46 | 10468.46
03:30 | 5630 | 4725.155 | 10355.155
04:00 | 5543 | 4698.85 | 10241.85
04:30 | 5438 | 4643.075 | 10081.075
05:00 | 5333 | 4587.3 | 9920.3
05:30 | 5540.97 | 4575.565 | 10116.535
06:00 | 5748.94 | 4563.83 | 10312.77
06:30 | 5892.43 | 4664.37 | 10556.8
07:00 | 6035.92 | 4764.91 | 10800.83
07:30 | 6070.855 | 4887.085 | 10957.94
08:00 | 6105.79 | 5009.26 | 11115.05
08:30 | 6215.08 | 5073.06 | 11288.14
09:00 | 6324.37 | 5136.86 | 11461.23
09:30 | 6369.595 | 5349.185 | 11718.78
10:00 | 6414.82 | 5561.51 | 11976.33
10:30 | 6605.78 | 5768.57 | 12374.35
11:00 | 6796.74 | 5975.63 | 12772.37
11:30 | 6904.84 | 6125.855 | 13030.695
12:00 | 7012.94 | 6276.08 | 13289.02
12:30 | 7170.455 | 6306.79 | 13477.245
13:00 | 7327.97 | 6337.5 | 13665.47
13:30 | 7223.235 | 6097.63 | 13320.865
14:00 | 7118.5 | 5857.76 | 12976.26
14:30 | 7177.695 | 5980.015 | 13157.71
15:00 | 7236.89 | 6102.27 | 13339.16
15:30 | 7120.56 | 5982.115 | 13102.675
16:00 | 7004.23 | 5861.96 | 12866.19
16:30 | 7043.055 | 5734.07 | 12777.125
17:00 | 7081.88 | 5606.18 | 12688.06
17:30 | 7204.815 | 5429.605 | 12634.42
18:00 | 7327.75 | 5253.03 | 12580.78
18:30 | 7721.375 | 5564.93 | 13286.305
19:00 | 8115 | 5876.83 | 13991.83
19:30 | 7957 | 6533.35 | 14490.35
20:00 | 7517.5 | 6669.08 | 14186.58
20:30 | 7394.25 | 6764.48 | 14158.73 |  | Executive Engineer
21:00 | 7271 | 6859.88 | 14130.88 |  | Network Operation Division
21:30 | 7230.75 | 6804.12 | 14034.87
22:00 | 7190.5 | 6748.36 | 13938.86
22:30 | 7138.25 | 6674.54 | 13812.79
23:00 | 7086 | 6600.72 | 13686.72

## En-Curve
QF-LDC-12
Date | 05-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3371 | 1265.5 | 932 | 0 | 136 | 1193.89 | 40 | 4489 | 0 | 137 | 203 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3387.5 | 1316 | 932 | 0 | 135 | 1086.68 | 40 | 4248 | 0 | 132 | 195.7 | 0 | 0 | 0 | 0 | 05-05-2026
01:00 | 3404 | 1366.5 | 932 | 0 | 134 | 979.47 | 40 | 4007 | 0 | 127 | 188.4 | 0 | 0 | 0 | 0
01:30 | 3456.5 | 1366.75 | 932 | 0 | 133 | 948.56 | 40 | 3853 | 0 | 133 | 131.7 | 0 | 0 | 0 | 0 | Energy Generated | 298.6978 |  | MKWHr
02:00 | 3509 | 1367 | 932 | 0 | 132 | 917.65 | 40 | 3699 | 0 | 139 | 75 | 0 | 0 | 0 | 0 | Energy not Served | 0.603 |  | MKWHr
02:30 | 3533.5 | 1403 | 932 | 0 | 129 | 877.555 | 40 | 3617.5 | 0 | 69.5 | 37.5 | 0 | 0 | 0 | 0 | Total Energy Requirement | 299.3008 |  | MKWHr
03:00 | 3558 | 1439 | 932 | 0 | 126 | 837.46 | 40 | 3536 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 3520 | 1414 | 931.5 | 0 | 126 | 838.655 | 39.5 | 3485.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 3482 | 1389 | 931 | 0 | 126 | 839.85 | 39 | 3435 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 3439 | 1395 | 931.5 | 0 | 122 | 839.575 | 38.5 | 3315.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 3396 | 1401 | 932 | 0 | 118 | 839.3 | 38 | 3196 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 3429.5 | 1511.5 | 932 | 0 | 116 | 859.655 | 38.5 | 3217 | 12.38 | 0 | 0 | 0 | 0 | 0 | 0
06:00 | 3463 | 1622 | 932 | 0 | 114 | 880.01 | 39 | 3238 | 24.76 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 3509.5 | 1599 | 932 | 0 | 114 | 859.705 | 39.5 | 3377.5 | 81.595 | 4 | 40 | 0 | 0 | 0 | 0
07:00 | 3556 | 1576 | 932 | 0 | 114 | 839.4 | 40 | 3517 | 138.43 | 8 | 80 | 0 | 0 | 0 | 0
07:30 | 3570 | 1574.5 | 932 | 0 | 111 | 840.28 | 40 | 3504 | 239.16 | 25.5 | 121.5 | 0 | 0 | 0 | 0
08:00 | 3584 | 1573 | 932 | 0 | 108 | 841.16 | 40 | 3491 | 339.89 | 43 | 163 | 0 | 0 | 0 | 0
08:30 | 3577 | 1618.5 | 932 | 0 | 113 | 838.525 | 40 | 3554 | 395.115 | 51.5 | 168.5 | 0 | 0 | 0 | 0
09:00 | 3570 | 1664 | 932 | 0 | 118 | 835.89 | 40 | 3617 | 450.34 | 60 | 174 | 0 | 0 | 0 | 0
09:30 | 3550 | 1636.5 | 932 | 0 | 126 | 905.355 | 40 | 3711 | 544.425 | 68.5 | 205 | 0 | 0 | 0 | 0
10:00 | 3530 | 1609 | 932 | 0 | 134 | 974.82 | 40 | 3805 | 638.51 | 77 | 236 | 0 | 0 | 0 | 0
10:30 | 3566 | 1625.5 | 932 | 0 | 136 | 1013.005 | 40 | 4050 | 668.345 | 77 | 266.5 | 0 | 0 | 0 | 0
11:00 | 3602 | 1642 | 932 | 0 | 138 | 1051.19 | 40 | 4295 | 698.18 | 77 | 297 | 0 | 0 | 0 | 0
11:30 | 3545.5 | 1651.5 | 932 | 0 | 141 | 1065.6 | 40 | 4504 | 672.995 | 98 | 380.1 | 0 | 0 | 0 | 0
12:00 | 3489 | 1661 | 932 | 0 | 144 | 1080.01 | 40 | 4713 | 647.81 | 119 | 463.2 | 0 | 0 | 0 | 0
12:30 | 3451.5 | 1610.5 | 932 | 0 | 144 | 1091.66 | 40 | 4792.5 | 587.485 | 164.5 | 659.1 | 0 | 0 | 4 | 0
13:00 | 3414 | 1560 | 932 | 0 | 144 | 1103.31 | 40 | 4872 | 527.16 | 210 | 855 | 0 | 0 | 8 | 0
13:30 | 3333.5 | 1503.5 | 932 | 0 | 151 | 1069.075 | 41.5 | 4749 | 465.04 | 222.5 | 848.75 | 0 | 0 | 5 | 0
14:00 | 3253 | 1447 | 932 | 0 | 158 | 1034.84 | 43 | 4626 | 402.92 | 235 | 842.5 | 0 | 0 | 2 | 0
14:30 | 3317 | 1496 | 931.5 | 0 | 150 | 1034.71 | 42 | 4590 | 456.25 | 236.5 | 902.75 | 0 | 0 | 1 | 0
15:00 | 3381 | 1545 | 931 | 0 | 142 | 1034.58 | 41 | 4554 | 509.58 | 238 | 963 | 0 | 0 | 0 | 0
15:30 | 3394.5 | 1484.5 | 931.5 | 0 | 107 | 993.235 | 39.5 | 4530.5 | 389.99 | 241.45 | 990.5 | 0 | 0 | 0 | 0
16:00 | 3408 | 1424 | 932 | 0 | 72 | 951.89 | 38 | 4507 | 270.4 | 244.9 | 1018 | 0 | 0 | 0 | 0
16:30 | 3415.5 | 1421 | 932 | 0 | 94 | 919.515 | 37.5 | 4437.5 | 207.16 | 247.45 | 1065.5 | 0 | 0 | 0 | 0
17:00 | 3423 | 1418 | 932 | 0 | 116 | 887.14 | 37 | 4368 | 143.92 | 250 | 1113 | 0 | 0 | 0 | 0
17:30 | 3426 | 1485 | 932 | 0 | 118 | 861.66 | 37.5 | 4241 | 84.26 | 303 | 1146 | 0 | 0 | 0 | 0
18:00 | 3429 | 1552 | 932 | 0 | 120 | 836.18 | 38 | 4114 | 24.6 | 356 | 1179 | 0 | 0 | 0 | 0
18:30 | 3558 | 1625.5 | 931.5 | 0 | 125 | 977.005 | 38.5 | 4353 | 12.3 | 388.5 | 1277 | 0 | 0 | 0 | 47.5
19:00 | 3687 | 1699 | 931 | 0 | 130 | 1117.83 | 39 | 4592 | 0 | 421 | 1375 | 0 | 0 | 0 | 95
19:30 | 3620 | 1643 | 932 | 0 | 126 | 1330.35 | 40 | 5003 | 0 | 410 | 1386 | 0 | 0 | 0 | 124
20:00 | 3607 | 1581 | 932 | 0 | 132 | 1450.08 | 41 | 4992 | 0 | 304 | 1147.5 | 0 | 0 | 0 | 109
20:30 | 3620.5 | 1640.5 | 932 | 0 | 133 | 1449.48 | 41.5 | 5086.5 | 0 | 287 | 968.25 | 0 | 0 | 0 | 117
21:00 | 3634 | 1700 | 932 | 0 | 134 | 1448.88 | 42 | 5181 | 0 | 270 | 789 | 0 | 0 | 0 | 125
21:30 | 3646.5 | 1690 | 932 | 0 | 135 | 1411.62 | 42.5 | 5131.5 | 0 | 266.5 | 779.25 | 0 | 0 | 0 | 130.5
22:00 | 3659 | 1680 | 932 | 0 | 136 | 1374.36 | 43 | 5082 | 0 | 263 | 769.5 | 0 | 0 | 0 | 136
22:30 | 3654.5 | 1683.5 | 932 | 0 | 130 | 1369.54 | 43.5 | 5042.5 | 0 | 266.5 | 690.75 | 0 | 0 | 0 | 137
23:00 | 3650 | 1687 | 932 | 0 | 124 | 1364.72 | 44 | 5003 | 0 | 270 | 612 | 0 | 0 | 0 | 138
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 05-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 194 | 12 | 646 | 122 | 1560 | 352 | Ishurdi-Ghorashal Ckt-1 | Export | 3385600
1:00 | 181 | -3 | 600 | 90 | 1566 | 386
2:00 | 156 | -12 | 572 | 74 | 0 | 360 |  | Import | 0
3:00 | 137 | -15 | 452 | 56 | 1238 | 358
4:00 | 146 | -13 | 468 | 60 | 1242 | 358 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 166 | -11 | 500 | 58 | 1272 | 352
6:00 | 140 | -12 | 420 | 50 | 1163 | 360 |  | Import | 0
7:00 | 110 | -19 | 340 | 44 | 1148 | 346
8:00 | 146 | -15 | 424 | 46 | 1230 | 354 | Sirajganj-Sreepur Ckt-1 | Export | 0
9:00 | 178 | -2 | 510 | 76 | 1478 | 454
10:00 | 204 | 3 | 616 | 104 | 1674 | 498 |  | Import | 0
11:00 | 201 | 0 | 624 | 134 | 1734 | 506
12:00 | 179 | 7 | 560 | 130 | 1792 | 574 | Sirajganj-Sreepur Ckt-2 | Export | 0
13:00 | 157 | -1 | 480 | 90 | 1714 | 493
14:00 | 175 | 1 | 594 | 112 | 1714 | 468 |  | Import | 0
15:00 | 140 | -6 | 476 | 80 | 1554 | 428
16:00 | 139 | -4 | 454 | 76 | 1498 | 438 | Gopalganj-Aminbazar Ckt-1 | Export | 17420000
17:00 | 127 | -8 | 408 | 62 | 1400 | 396
18:00 | 104 | -8 | 326 | 52 | 1228 | 358 |  | Import | 0
18:30 | 91 | -11 | 328 | 64 | 1146 | 318
19:00 | 63 | -21 | 306 | 68 | 1172 | 250 | Gopalganj-Aminbazar Ckt-2 | Export | 17410000
19:30 | 56 | -29 | 350 | 88 | 1328 | 202
20:00 | 79 | -17 | 448 | 110 | 1580 | 292 |  | Import | 0
21:00 | 103 | -6 | 490 | 128 | 1612 | 304
22:00 | 106 | -2 | 484 | 120 | 1572 | 336 |  | Total Export | 38215600
23:00 | 110 | -2 | 480 | 110 | 1580 | 340 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 05-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 397 | 05:00 | 374 | 15:00 | Madunaghat | 403 | 05:00 | 390 | 13:00
Amtali | 415 | 05:00 | 405 | 21:00 | Meghnaghat | 398 | 05:00 | 376 | 12:00
Ashuganj | 418 | 3:00 | 391 | 12:00 | Payra | 416 | 05:00 | 407 | 21:00
Bhulta | 410 | 03:00 | 381 | 12:00 | Rahanpur | 422 | 00:00 | 397 | 20:00
Bibiana | 407 | 02:00 | 395 | 12:00 | Rampal | 409 | 04:00 | 309 | 13:00
BIPTC | 405 | 03:00 | 395 | 20:00
Bogura | 410 | 00:00 | 387 | 20:00
Gopalganj | 407 | 05:00 | 388 | 12:00
Kaliakoir | 390 | 05:00 | 368 | 12:00
Korerhat | 405 | 05:00 | 387 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 234 | 04:00 | 216 | 12:00 | Jhenaidah | 234 | 05:00 | 214 | 19:30
AKSML | 235 | 05:00 | 222 | 12:00 | Kachua | 231 | 18:30 | 219 | 12:00
Aminbazar | 229 | 17:00 | 217 | 12:00 | Kaliakoir | 237 | 05:00 | 220 | 12:00
Ashuganj | 235 | 05:00 | 220 | 12:00 | Keranigonj | 234 | 05:00 | 215 | 12:00
Ashuganj-400 | 235 | 5:00 | 220 | 12:00 | Khulna(S) | 237 | 04:00 | 218 | 20:00
Baghabari | 236 | 00:00 | 225 | 12:00 | Korerhat | 231 | 05:00 | 219 | 12:00
Barapukuria | 236 | 14:00 | 208 | 12:00 | Madunaghat | 232 | 17:00 | 225 | 12:00
Barapukuria-230 | 236 | 14:00 | 210 | 12:00 | Madunaghat-400 | 235 | 05:00 | 227 | 12:00
Barishal | 231 | 05:00 | 221 | 21:00 | Maniknagar | 232 | 04:00 | 216 | 11:00
Bheramara | 235 | 05:00 | 221 | 19:30 | Meghnaghat | 239 | 06:00 | 223 | 12:00
Bhulta | 234 | 05:00 | 214 | 12:00 | Meghnaghat-400 | 235 | 05:00 | 218 | 12:00
Bibiana | 239 | 05:00 | 227 | 12:00 | Mirsorai | 235 | 05:00 | 224 | 12:00
BIPTC | 238 | 05:00 | 222 | 11:00 | Naogaon | 232 | 00:00 | 208 | 19:30
Bogura | 240 | 05:00 | 223 | 19:30 | Purbasadipur | 234 | 01:00 | 205 | 19:30
Bogura-400 | 239 | 01:00 | 224 | 19:30 | Rajshahi | 235 | 05:00 | 220 | 12:00
Borhanuddin | 233 | 04:00 | 227 | 20:00 | Rampal | 235 | 05:00 | 220 | 19:00
BSRM | 232 | 05:00 | 219 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 230 | 02:00 | 222 | 23:00 | Rampura | 234 | 05:00 | 213 | 12:00
Cumilla(N) | 232 | 05:00 | 218 | 12:00 | Shikalbaha | 232 | 07:00 | 224 | 12:00
Faridpur | 229 | 05:00 | 216 | 12:00 | Shyampur | 234 | 05:00 | 215 | 12:00
Fenchuganj | 240 | 03:00 | 231 | 12:00 | Siddhirganj | 232 | 05:00 | 226 | 19:30
Feni | 231 | 05:00 | 218 | 12:00 | Sirajgonj | 242 | 04:00 | 232 | 11:00
Ghorashal | 238 | 01:00 | 218 | 13:00 | Sreepur | 231 | 05:00 | 216 | 12:00
Ghorashal-230 | 232 | 05:00 | 214 | 12:00 | Tongi | 232 | 07:00 | 212 | 11:00
Gopalganj | 229 | 14:00 | 216 | 20:00
GPH | 232 | 07:00 | 226 | 14:00
Haripur | 234 | 05:00 | 216 | 12:00
Hasnabad | 233 | 07:00 | 215 | 12:00
Hathazari | 232 | 06:00 | 222 | 12:00
Ishurdi | 239 | 05:00 | 224 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 18:00 | 122 | 11:00 | Madunaghat | 134 | 06:00 | 130 | 12:00
Agargaon | 135 | 04:00 | 123 | 12:00 | Magura | 138 | 06:00 | 122 | 19:30
Agrabad | 134 | 07:00 | 127 | 11:00 | Mahasthangarh | 138 | 01:00 | 124 | 19:30
AKS | 131 | 04:00 | 126 | 12:00 | Maijdee | 129 | 05:00 | 122 | 12:00
Aminbazar | 134 | 03:00 | 123 | 12:00 | Manikganj | 130 | 02:00 | 118 | 12:00
Amnura | 138 | 00:00 | 126 | 19:00 | Maniknagar | 137 | 04:00 | 123 | 12:00
Ashuganj | 140 | 0:00 | 132 | 12:00 | Matarbari | 123 | 16:00 | 111 | 23:00
Ashuganj-230 | 140 | 03:00 | 132 | 12:00 | Matuail | 136 | 04:00 | 125 | 12:00
Bagerhat | 135 | 05:00 | 119 | 19:30 | Metrorail_Motijheel | 137 | 04:00 | 123 | 12:00
Bajitpur | 133 | 02:00 | 120 | 12:00 | Metrorail_Uttara | 135 | 03:00 | 121 | 12:00
Bakerganj | 135 | 04:00 | 128 | 19:30 | Millgate | 136 | 02:00 | 122 | 12:00
Bakulia | 134 | 18:30 | 128 | 11:00 | Mirpur | 134 | 04:00 | 122 | 12:00
Banani | 134 | 18:00 | 122 | 10:00 | Mirzapur | 134 | 03:00 | 125 | 12:00
Bangabhaban | 138 | 05:00 | 123 | 12:00 | Mithapukur | 137 | 01:00 | 123 | 19:30
Barapukuria | 137 | 14:00 | 121 | 12:00 | MI_Cement | 133 | 04:00 | 119 | 12:00
Barguna | 134 | 05:00 | 127 | 19:30 | Modern | N/A | N/A | N/A | N/A
Barishal | 135 | 04:00 | 128 | 13:00 | Mogbazar | 135 | 05:00 | 123 | 11:00
Barishal-230 | 135 | 05:00 | 127 | 21:00 | Mongla | 134 | 05:00 | 120 | 19:30
Baroaulia | 135 | 04:00 | 128 | 11:00 | Motijheel | 138 | 05:00 | 123 | 12:00
Baroirhat | 133 | 05:00 | 125 | 12:00 | Muktagacha | 131 | 08:00 | 116 | 22:00
Bashundhara | 135 | 02:00 | 122 | 11:00 | Munshiganj | 134 | 18:00 | 124 | 12:00
BashundharaCement | 135 | 06:00 | 125 | 12:00 | Muradnagar | 132 | 18:00 | 121 | 12:00
Beanibazar | 131 | 06:00 | 122 | 20:00 | Mymensingh | 131 | 08:00 | 111 | 19:00
Benapole | 136 | 04:00 | 119 | 19:30 | Nabinagar | 135 | 03:00 | 121 | 12:00
Bhaluka | 131 | 02:00 | 120 | 19:30 | Naogaon | 139 | 00:00 | 124 | 19:30
Bhandaria | 131 | 07:00 | 128 | 18:00 | Narail | 138 | 06:00 | 124 | 19:30
Bhangura | 137 | 01:00 | 128 | 12:00 | Narinda | 137 | 4:00 | 123 | 12:00
Bheramara | 140 | 05:00 | 131 | 19:30 | Narshingdi | 131 | 07:00 | 119 | 11:00
Bheramara(GK) | 138 | 00:00 | 131 | 19:30 | Natore | 136 | 00:00 | 125 | 19:30
Bhulta | 129 | 08:00 | 120 | 12:00 | Nawabganj | 138 | 04:00 | 125 | 13:00
Bog-Sherpur | 138 | 01:00 | 126 | 19:30 | Netrakona | 128 | 05:00 | 109 | 20:00
Bogura | 139 | 01:00 | 128 | 19:00 | New | 135 | 04:00 | 122 | 12:00
Bogura-230 | 139 | 01:00 | 128 | 19:30 | Niamatpur | 138 | 00:00 | 128 | 19:30
Brahmanbaria | 137 | 15:00 | 132 | 12:00 | Noapara | 138 | 05:00 | 121 | 19:30
Cantonment | 136 | 05:00 | 123 | 12:00 | Pabna | 138 | 05:00 | 128 | 19:30
Chandina | 134 | 05:00 | 126 | 12:00 | Palashbari | 135 | 01:00 | 118 | 19:30
Chandpur | 135 | 18:30 | 124 | 11:00 | Panchagarh | 139 | 01:00 | 124 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 139 | 06:00 | 129 | 12:00 | Patiya | 133 | 18:30 | 127 | 12:00
Chapai | 138 | 01:00 | 130 | 19:30 | Patuakhali | 133 | 03:00 | 127 | 20:00
Charsaidpur | 135 | 04:00 | 124 | 12:00 | Payra | 136 | 03:00 | 132 | 19:30
Chauddagram | 132 | 02:00 | 124 | 12:00 | PHP | 135 | 13:00 | 125 | 12:00
Chhatak | 131 | 04:00 | 121 | 19:30 | Postogola | 135 | 03:00 | 122 | 12:00
Chowmuhani | 128 | 07:00 | 122 | 11:00 | Pubail | 138 | 05:00 | 126 | 12:00
Chuadanga | 138 | 05:00 | 119 | 19:30 | Purbachal | 135 | 03:00 | 121 | 12:00
Coxsbazar | 124 | 16:00 | 113 | 19:00 | Purbasadipur | 136 | 01:00 | 119 | 12:00
Cumilla(N) | 134 | 05:00 | 125 | 12:00 | Rahanpur | 139 | 00:00 | 131 | 19:30
Cumilla(S) | 134 | 05:00 | 121 | 12:00 | Rahanpur-400 | 140 | 00:00 | 131 | 19:30
Daganbhuiyan | 132 | 05:00 | 124 | 12:00 | Rahim | 135 | 06:00 | 126 | 12:00
Daudkandi | 130 | 05:00 | 119 | 12:00 | Rajbari | 131 | 04:00 | 122 | 19:30
DhakaUniversity | 135 | 18:30 | 122 | 11:00 | Rajendrapur | 129 | 03:00 | 118 | 11:00
Dhamrai | 136 | 04:00 | 123 | 12:00 | Rajshahi | 136 | 04:00 | 125 | 19:30
Dhanmondi | 136 | 05:00 | 126 | 12:00 | Rajshahi-230 | 136 | 05:00 | 125 | 19:30
Dohazari | 129 | 04:00 | 124 | 12:00 | Ramganj | 129 | 18:00 | 122 | 12:00
Faridpur | 133 | 06:00 | 125 | 12:00 | Rampur | 133 | 05:00 | 128 | 11:00
Fatullah | 134 | 05:00 | 120 | 12:00 | Rampura | 134 | 18:00 | 121 | 11:00
Fenchuganj | 136 | 06:00 | 130 | 12:00 | Rangamati | 135 | 03:00 | 128 | 12:00
Feni | 131 | 03:00 | 125 | 12:00 | Rangpur | 136 | 01:00 | 120 | 19:30
Feni-230 | 132 | 05:00 | 124 | 12:00 | Ruppur | 139 | 05:00 | 131 | 19:30
Ghatail | 132 | 04:00 | 119 | 12:00 | Saidpur | 135 | 01:00 | 118 | 19:30
Ghorashal | 139 | 01:00 | 129 | 12:00 | Santhia | 137 | 03:00 | 129 | 12:00
Goalpara | 140 | 04:00 | 125 | 19:30 | Satkhira | 136 | 05:00 | 118 | 19:30
Gollamari | 139 | 05:00 | 126 | 19:30 | Satmasjid | 136 | 05:00 | 123 | 12:00
Gopalganj | 136 | 05:00 | 125 | 19:30 | Savar | 133 | 05:00 | 121 | 12:00
Gopalganj-400 | 136 | 05:00 | 128 | 12:00 | SevenRings | 139 | 03:00 | 128 | 12:00
Gulshan | 134 | 18:00 | 121 | 11:00 | ShahCement | 135 | 04:00 | 124 | 12:00
Halishahar | 133 | 04:00 | 126 | 12:00 | Shahjadpur | 140 | 02:00 | 132 | 12:00
Haripur | 136 | 05:00 | 126 | 12:00 | Shahjibazar | 132 | 07:00 | 124 | 12:00
HaripurSBU | 135 | 04:00 | 128 | 11:00 | Shahmirpur | 134 | 05:00 | 128 | 11:00
Hasnabad | 135 | 04:00 | 122 | 12:00 | Shariatpur | 134 | 04:00 | 126 | 12:00
Hathazari | 136 | 06:00 | 129 | 12:00 | Sherpur | 127 | 08:00 | 111 | 22:00
Hatirjheel | 134 | 18:00 | 122 | 11:00 | Shikalbaha | 124 | 05:00 | 117 | 12:00
Ishurdi | 141 | 05:00 | 131 | 19:30 | Shikalbaha-230 | 136 | 18:30 | 130 | 12:00
Jaldhaka | 134 | 14:00 | 114 | 19:30 | Shitalakhya | 133 | 05:00 | 119 | 12:00
Jamalpur | 130 | 08:00 | 113 | 22:00 | Sholosohor | 135 | 05:00 | 128 | 12:00
Jashore | 136 | 05:00 | 119 | 19:30 | Shyampur | 133 | 02:00 | 120 | 12:00
Jhenaidah | 138 | 04:00 | 125 | 19:30 | Shyampur-230 | 135 | 05:00 | 122 | 12:00
Jhenaidah-230 | 140 | 05:00 | 125 | 19:30 | Siddhirganj | 135 | 03:00 | 125 | 12:00
Joydebpur | 135 | 07:00 | 124 | 12:00 | Sirajganj | 136 | 01:00 | 124 | 19:00
Joypurhat | 138 | 00:00 | 122 | 19:30 | Sonargaon | 133 | 18:00 | 123 | 12:00
Juldah | 133 | 07:00 | 129 | 11:00 | Sreemongol | 133 | 07:00 | 125 | 12:00
Kabirpur | 136 | 18:00 | 118 | 12:00 | Sreepur | 132 | 02:00 | 122 | 12:00
Kachua | 132 | 18:00 | 125 | 12:00 | Srinagar | 138 | 05:00 | 126 | 12:00
Kaliakoir | 138 | 02:00 | 126 | 12:00 | SSM | 136 | 18:30 | 134 | 12:00
Kaliganj | 138 | 05:00 | 124 | 19:30 | Sunamganj | 130 | 06:00 | 119 | 20:00
Kallyanpur | 133 | 04:00 | 123 | 12:00 | Sylhet | 133 | 06:00 | 126 | 13:00
Kalurghat | 136 | 05:00 | 129 | 12:00 | Sylhet-132 | 132 | 04:00 | 126 | 22:00
Kamrangirchar | 139 | 06:00 | 120 | 12:00 | Tangail | 132 | 03:00 | 121 | 12:00
Kaptai | 138 | 5:00 | 133 | 12:00 | Taraganj | 133 | 04:00 | 117 | 19:30
Kasba | 132 | 18:00 | 120 | 12:00 | Tasnim | 134 | 05:00 | 123 | 12:00
Kazla | 137 | 05:00 | 123 | 13:00 | Thakurgaon | 138 | 17:00 | 122 | 11:00
Keranigonj | 139 | 05:00 | 126 | 12:00 | TK | 135 | 04:00 | 129 | 12:00
Khagrachori | 135 | 05:00 | 127 | 12:00 | Tongi | 135 | 07:00 | 125 | 11:00
Khulna | 138 | 06:00 | 126 | 19:30 | Ullahpara | 137 | 02:00 | 126 | 19:30
Khulna(S) | 139 | 03:00 | 126 | 19:30 | Ullon | 134 | 18:30 | 122 | 11:00
Khulshi | 133 | 05:00 | 125 | 12:00 | Uttara | 137 | 05:00 | 120 | 12:00
Kishoreganj | 133 | 05:00 | 120 | 20:00 | UttaraNew | 135 | 03:00 | 121 | 12:00
Kodda | 135 | 18:00 | 126 | 06:00 | Zigatola | 138 | 04:00 | 126 | 13:00
Korerhat | 134 | 03:00 | 128 | 12:00
KSRM | 134 | 03:00 | 127 | 12:00
Kulaura | 135 | 04:00 | 129 | 12:00
Kurigram | 135 | 02:00 | 115 | 19:30
Kushtia | 141 | 05:00 | 130 | 13:00
Laksam | 132 | 18:00 | 124 | 12:00
Lakshmipur | 129 | 05:00 | 122 | 12:00
Lalbag | 138 | 06:00 | 126 | 12:00
Lalmonirhat | 131 | 14:00 | 115 | 19:30
Madanganj | 135 | 05:00 | 125 | 12:00
Madaripur | 134 | 04:00 | 128 | 12:00
Madartek | 135 | 18:00 | 122 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division