## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 06-05-2026 | [28 empty] | Date: | 06-05-2026 | [28 empty] | Date: | 06-05-2026 | [28 empty] | Date: | 06-05-2026 | [28 empty] | Date: | 06-05-2026 | [17 empty] | Date: | 06-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 306 | 18 | 17 | 115 | 0 | 45 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 88 | 20.5 | 14 | 0 | 470 | 0 | 0 | 37 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 28 | 940 | 0 | 0 | 6 | 0 | 0 | 220 | 0 | 0 | 0 | 1123 | 0 | 24 | 0 | 240 | 355 | 250 | 51 | 0 | 212 | 0 | 36 | 87 | 0 | 0 | 18 | 0 | 114 | 0 | 0 | 0 | 300 | 0 | 381 | 42 | 30 | 150 | 0 | 17 | 0 | 84 | 30 | 0 | 0 | 100 | 0 | 9 | 58 | 11 | 0 | 0 | 0 | 6886.5 | 932 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1170 | 0 | 0 | 0 | 1278.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 151 | 0 | 414 | 0 | 0 | 0 | 0 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 130 | 220 | 0 | 440 | 1080 | 0 | 6448.65 | 13335.15 | 78.8
01:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 299 | 18 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 70 | 21 | 14 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 28 | 940 | 0 | 0 | 6 | 0 | 0 | 220 | 0 | 0 | 0 | 1155 | 0 | 0 | 0 | 240 | 355 | 250 | 51 | 0 | 213 | 0 | 0 | 87 | 0 | 0 | 18 | 0 | 112 | 0 | 0 | 0 | 295 | 0 | 389 | 42 | 30 | 149 | 0 | 17 | 0 | 84 | 30 | 0 | 0 | 100 | 0 | 32 | 9 | 11 | 0 | 0 | 0 | 6651 | 931 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1033 | 0 | 0 | 0 | 1257.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 156 | 0 | 410 | 0 | 0 | 0 | 0 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 130 | 220 | 0 | 347 | 1065 | 0 | 6153.53 | 12804.53 | 78.82
02:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 303 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 52 | 21 | 14 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 29 | 910 | 0 | 0 | 6 | 0 | 0 | 220 | 0 | 0 | 0 | 1055 | 0 | 0 | 0 | 240 | 355 | 250 | 51 | 0 | 216 | 0 | 0 | 87 | 0 | 0 | 18 | 0 | 108 | 0 | 0 | 0 | 300 | 0 | 381 | 42 | 30 | 151 | 0 | 17 | 0 | 84 | 30 | 0 | 0 | 100 | 0 | 56 | 9 | 17 | 0 | 0 | 0 | 6486 | 932 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 870 | 0 | 0 | 0 | 1237.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 156 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 130 | 220 | 0 | 300 | 1050 | 0 | 5860.93 | 12346.93 | 78.84
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 300 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 52 | 21 | 14 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 29 | 784 | 0 | 0 | 6 | 0 | 0 | 220 | 0 | 0 | 0 | 1060 | 0 | 0 | 0 | 245 | 355 | 250 | 51 | 0 | 199 | 0 | 0 | 87 | 0 | 0 | 18 | 0 | 106 | 0 | 0 | 0 | 305 | 0 | 381 | 42 | 30 | 152 | 0 | 17 | 0 | 84 | 30 | 0 | 0 | 100 | 0 | 56 | 9 | 17 | 0 | 0 | 0 | 6303 | 932 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 1234.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 161 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207 | 130 | 220 | 0 | 300 | 1060 | 0 | 5734.89 | 12037.89 | 78.86
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 293 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 0 | 0 | 35 | 21 | 14 | 0 | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 738 | 0 | 0 | 6 | 0 | 0 | 220 | 0 | 0 | 0 | 970 | 0 | 0 | 0 | 300 | 355 | 250 | 51 | 0 | 195 | 0 | 0 | 87 | 0 | 0 | 18 | 0 | 106 | 0 | 0 | 0 | 305 | 0 | 381 | 42 | 30 | 149 | 0 | 17 | 0 | 84 | 30 | 0 | 0 | 100 | 0 | 56 | 9 | 17 | 0 | 0 | 0 | 6128 | 931 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764 | 0 | 0 | 0 | 1112.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 163 | 0 | 406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 130 | 220 | 0 | 300 | 1030 | 0 | 5558.02 | 11686.02 | 78.88
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 294 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 35 | 21 | 14 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 30 | 732 | 0 | 0 | 6 | 0 | 0 | 220 | 0 | 0 | 0 | 966 | 0 | 0 | 0 | 280 | 355 | 250 | 51 | 0 | 195 | 0 | 0 | 87 | 0 | 0 | 18 | 0 | 106 | 0 | 0 | 0 | 305 | 0 | 381 | 42 | 30 | 149 | 0 | 17 | 0 | 84 | 30 | 0 | 0 | 100 | 0 | 56 | 9 | 17 | 0 | 0 | 0 | 6118 | 932 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765 | 0 | 0 | 0 | 1012.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 163 | 0 | 406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 100 | 180 | 0 | 300 | 1000 | 0 | 5351.83 | 11469.83 | 78.9
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 302 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 2 | 35 | 21 | 14 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46 | 39 | 0 | 32 | 739 | 0 | 0 | 6 | 0 | 0 | 223 | 0 | 0 | 0 | 957 | 0 | 0 | 0 | 270 | 355 | 250 | 51 | 0 | 196 | 0 | 0 | 87 | 0 | 0 | 16 | 0 | 100 | 0 | 4 | 0 | 300 | 0 | 400 | 42 | 30 | 149 | 1 | 17 | 0 | 84 | 30 | 0 | 0 | 100 | 0 | 9 | 56 | 17 | 0.1 | 3.59 | 0 | 6165.15 | 932 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.15 | 760 | 0 | 0 | 0 | 977.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.33 | 2 | 0 | 0 | 1.83 | 140 | 0 | 0 | 0 | 163 | 0 | 414 | 0 | 0.17 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.25 | 9 | 0.03 | 0 | 181 | 100 | 180 | 0 | 300 | 965 | 0 | 5312.48 | 11477.63 | 78.92
07:00 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 300 | 0 | 0 | 91 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 5 | 35 | 21 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 40 | 0 | 29 | 749 | 0 | 0 | 6 | 0 | 0 | 222 | 0 | 0 | 0 | 1042 | 5 | 0 | 0 | 270 | 355 | 250 | 51 | 0 | 192 | 0 | 0 | 87 | 0 | 0 | 16 | 0 | 96 | 0 | 16 | 0 | 305 | 0 | 394 | 42 | 30 | 152 | 2 | 17 | 0 | 84 | 30 | 0 | 0 | 100 | 0 | 9 | 55 | 11 | 0.5 | 9.12 | 0 | 6289.32 | 932 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.06 | 852 | 0 | 0 | 0 | 947.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.82 | 18 | 0 | 0 | 7.38 | 140 | 0 | 0 | 0 | 163 | 0 | 410 | 0 | 0.69 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 32 | 0.22 | 0 | 180 | 130 | 220 | 0 | 300 | 976 | 0 | 5522.55 | 11811.87 | 78.94
08:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 305 | 0 | 0 | 96 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 10 | 35 | 18 | 14 | 0 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.35 | 41 | 0 | 8 | 740 | 0 | 0 | 6 | 0 | 0 | 220 | 0 | 0 | 0 | 985 | 10 | 0 | 0 | 245 | 356 | 250 | 51 | 0 | 194 | 0 | 0 | 85 | 0 | 0 | 14 | 0 | 110 | 0 | 42 | 0 | 305 | 0 | 388 | 42 | 30 | 146 | 6 | 8 | 0 | 84 | 30 | 0 | 0 | 100 | 0 | 9 | 58 | 9 | 0.6 | 22.32 | 0 | 6243.27 | 932 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 806 | 0 | 0 | 0 | 891.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.35 | 51 | 0 | 0 | 12.44 | 140 | 0 | 0 | 0 | 167 | 0 | 414 | 0 | 1.08 | 0 | 0 | 30 | 14 | 33 | 0 | 0 | 0 | 2.7 | 55 | 0.42 | 0 | 178 | 130 | 220 | 0 | 300 | 945 | 0 | 5550.52 | 11793.79 | 78.95
09:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 310 | 0 | 0 | 96 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 19 | 35 | 18 | 14 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.19 | 43 | 0 | 2 | 765 | 0 | 0 | 6 | 0 | 0 | 220 | 0 | 0 | 0 | 1106 | 16 | 0 | 0 | 245 | 356 | 250 | 51 | 0 | 196 | 0 | 0 | 86 | 0 | 0 | 14 | 0 | 104 | 0 | 37 | 0 | 310 | 0 | 382 | 42 | 30 | 151 | 5 | 17 | 0 | 84 | 30 | 0 | 0 | 100 | 0 | 9 | 58 | 7 | 1.88 | 21.71 | 0 | 6431.78 | 932 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.92 | 922 | 0 | 0 | 0 | 947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.56 | 38 | 0 | 0 | 21 | 140 | 0 | 0 | 0 | 169 | 0 | 414 | 0 | 2.43 | 0 | 0 | 35 | 17 | 33 | 0 | 0 | 0 | 1.3 | 105 | 0.29 | 0 | 193 | 130 | 220 | 0 | 300 | 960 | 0 | 5863.5 | 12295.28 | 78.96
10:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 300 | 0 | 0 | 96 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 31 | 35 | 18 | 14 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.55 | 43 | 0 | 4 | 815 | 0 | 0 | 6 | 0 | 0 | 219 | 0 | 0 | 0 | 1130 | 14 | 0 | 0 | 245 | 356 | 250 | 51 | 0 | 197 | 0 | 0 | 85 | 0 | 0 | 14 | 0 | 114 | 0 | 47 | 0 | 300 | 0 | 375 | 42 | 30 | 153 | 6 | 17 | 0 | 84 | 30 | 0 | 0 | 101 | 0 | 9 | 67 | 7 | 0.7 | 33 | 0 | 6560.25 | 932 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 1002 | 0 | 0 | 0 | 970 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.59 | 100 | 0 | 0 | 34 | 145 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 4.64 | 0 | 0 | 35 | 18 | 34 | 0 | 0 | 0 | 0.6 | 117 | 0.24 | 0 | 216 | 130 | 220 | 0 | 300 | 966 | 0 | 6067.07 | 12627.32 | 78.96
11:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 313 | 0 | 0 | 96 | 15 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 31 | 35 | 18 | 14 | 0 | 510 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.22 | 60 | 0 | 5 | 900 | 0 | 0 | 6 | 0 | 0 | 217 | 0 | 0 | 0 | 1160 | 6 | 0 | 0 | 245 | 356 | 250 | 51 | 0 | 201 | 0 | 0 | 83 | 0 | 0 | 14 | 0 | 118 | 0 | 65 | 0 | 300 | 0 | 370 | 42 | 30 | 154 | 5 | 17 | 0 | 83 | 30 | 0 | 0 | 101 | 0 | 9 | 67 | 5 | 2.26 | 49.39 | 0 | 6800.87 | 932 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 1004 | 0 | 0 | 0 | 1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.93 | 103 | 0 | 0 | 40 | 180 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 5.24 | 0 | 0 | 35 | 11 | 34 | 0 | 0 | 0 | 0.8 | 96 | 0.55 | 0 | 249 | 128 | 220 | 0 | 300 | 1010 | 0 | 6241.52 | 13042.39 | 78.96
12:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 313 | 12 | 0 | 96 | 15 | 70 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 34 | 70 | 18 | 14 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.99 | 45 | 0 | 3 | 920 | 0 | 0 | 6 | 1 | 0 | 216 | 0 | 0 | 0 | 1162 | 9 | 0 | 0 | 235 | 356 | 250 | 51 | 0 | 196 | 0 | 0 | 87 | 0 | 0 | 14 | 0 | 110 | 0 | 49 | 0 | 310 | 0 | 357 | 42 | 30 | 155 | 12 | 17 | 0 | 83 | 28 | 0 | 0 | 100 | 0 | 9 | 68 | 5 | 1.78 | 22.32 | 0 | 6856.09 | 932 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 1090 | 0 | 0 | 0 | 1087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.79 | 104 | 0 | 0 | 60 | 180 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 5.72 | 0 | 0 | 35 | 8 | 34 | 0 | 0 | 0 | 3.9 | 43 | 0.44 | 0 | 259 | 128 | 220 | 0 | 314 | 1063 | 0 | 6404.85 | 13260.94 | 78.97
13:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 297 | 16.6 | 2 | 96 | 15 | 130 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 31 | 70 | 18 | 14 | 0 | 440 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2.75 | 46 | 0 | 10 | 980 | 0 | 0 | 6 | 0 | 0 | 216 | 0 | 0 | 0 | 1145 | 18 | 0 | 0 | 225 | 356 | 250 | 51 | 0 | 200 | 0 | 16 | 88 | 0 | 0 | 19 | 0 | 110 | 0 | 64 | 0 | 310 | 0 | 357 | 42 | 30 | 153 | 12 | 17 | 0 | 83 | 25 | 0 | 0 | 101 | 0 | 9 | 68 | 5 | 0.3 | 33.86 | 0 | 6949.51 | 932 | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 1085 | 0 | 0 | 0 | 1151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.63 | 105 | 0 | 0 | 51 | 180 | 0 | 0 | 0 | 140 | 0 | 347 | 0 | 5.14 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 2.5 | 1 | 0.73 | 0 | 234 | 128 | 220 | 0 | 359 | 1100 | 0 | 6363 | 13312.51 | 78.97
14:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 303 | 15.5 | 17 | 96 | 15 | 145 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 17 | 295 | 0 | 0 | 27 | 70 | 18 | 14 | 0 | 400 | 0 | 0 | 13 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 2.5 | 45 | 0 | 5 | 920 | 0 | 0 | 6 | 0 | 0 | 214 | 0 | 0 | 0 | 1111 | 17 | 0 | 0 | 225 | 356 | 250 | 51 | 0 | 207 | 0 | 33 | 87 | 0 | 0 | 19 | 0 | 120 | 0 | 62 | 0 | 310 | 0 | 310 | 42 | 30 | 145 | 7 | 17 | 0 | 84 | 30 | 0 | 0 | 100 | 0 | 9 | 68 | 5 | 0 | 34.52 | 0 | 6860.52 | 932 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 1095 | 0 | 0 | 0 | 1093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 88 | 0 | 0 | 50 | 180 | 0 | 0 | 0 | 140 | 0 | 357 | 0 | 5.22 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 12 | 0.15 | 0 | 210 | 100 | 180 | 0 | 350 | 1060 | 0 | 6116.37 | 12976.89 | 78.97
15:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 314 | 15.9 | 17 | 96 | 0 | 145 | 0 | 17 | 70 | 0 | 0 | 0 | 0 | 0 | 17 | 310 | 0 | 0 | 21 | 70 | 18 | 14 | 0 | 470 | 0 | 0 | 18 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 2.67 | 42 | 0 | 2 | 946 | 0 | 0 | 6 | 0 | 0 | 214 | 0 | 0 | 0 | 1132 | 13 | 0 | 0 | 225 | 356 | 250 | 51 | 0 | 214 | 0 | 34 | 87 | 0 | 0 | 19 | 0 | 114 | 0 | 50 | 0 | 315 | 0 | 307 | 42 | 30 | 150 | 8 | 17 | 0 | 80 | 25 | 0 | 0 | 100 | 0 | 9 | 45 | 5 | 0 | 8.78 | 0 | 6951.35 | 932 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 1060 | 0 | 0 | 0 | 1111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.83 | 30 | 0 | 0 | 11 | 130 | 0 | 0 | 0 | 130 | 0 | 320 | 0 | 1.05 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 6.1 | 44 | 0.27 | 0 | 228 | 100 | 180 | 0 | 340 | 1030 | 0 | 5823.25 | 12774.6 | 78.98
16:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 292 | 16.2 | 17 | 96 | 0 | 175 | 0 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 6 | 70 | 18 | 14 | 0 | 360 | 0 | 0 | 22 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 1.79 | 40 | 0 | 2 | 884 | 0 | 0 | 6 | 0 | 0 | 216 | 0 | 0 | 0 | 1137 | 8 | 0 | 0 | 225 | 356 | 250 | 51 | 0 | 209 | 0 | 34 | 87 | 0 | 0 | 19 | 0 | 110 | 0 | 33 | 0 | 315 | 0 | 332 | 42 | 30 | 147 | 2 | 17 | 0 | 80 | 25 | 0 | 0 | 100 | 0 | 9 | 24 | 0 | 0 | 0 | 0 | 6736.99 | 932 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 910 | 0 | 0 | 0 | 1014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.69 | 1 | 0 | 0 | 0.9 | 130 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 4.4 | 19 | 0.27 | 0 | 177 | 100 | 220 | 0 | 326 | 1046 | 0 | 5561.26 | 12298.25 | 78.98
17:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 298 | 16.2 | 17 | 82 | 0 | 125 | 0 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 17 | 296 | 0 | 0 | 0 | 17 | 0 | 14 | 0 | 360 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92 | 39 | 0 | 4 | 845 | 0 | 0 | 6 | 0 | 0 | 216 | 0 | 0 | 0 | 1096 | 4 | 0 | 0 | 225 | 356 | 250 | 51 | 0 | 213 | 0 | 17 | 87 | 0 | 0 | 19 | 0 | 120 | 0 | 14 | 0 | 310 | 0 | 332 | 42 | 30 | 140 | 1 | 17 | 0 | 84 | 25 | 0 | 0 | 100 | 0 | 9 | 8 | 0 | 0 | 0.52 | 0 | 6443.64 | 931 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 770 | 0 | 0 | 0 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 6 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 2.3 | 5 | 0.01 | 0 | 174 | 100 | 220 | 0 | 305 | 940 | 0 | 5193.52 | 11637.16 | 78.98
18:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 276 | 15 | 17 | 54 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 380 | 0 | 0 | 37 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0.01 | 38 | 0 | 9 | 744 | 0 | 0 | 10 | 1 | 0 | 218 | 0 | 0 | 0 | 940 | 0 | 0 | 0 | 225 | 320 | 220 | 20 | 0 | 140 | 0 | 0 | 87 | 0 | 0 | 19 | 0 | 126 | 0 | 1 | 0 | 305 | 0 | 344 | 42 | 30 | 136 | 0 | 17 | 0 | 44 | 20 | 0 | 0 | 100 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 5690.01 | 932 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 768 | 0 | 0 | 0 | 831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0.22 | 130 | 0 | 0 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.5 | 3 | 0.01 | 0 | 144 | 130 | 180 | 0 | 273 | 892 | 0 | 4834.73 | 10524.74 | 78.98
19:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 288 | 35 | 0 | 17 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 445 | 0 | 0 | 35 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 767 | 0 | 0 | 18 | 7 | 0 | 220 | 0 | 0 | 0 | 1050 | 0 | 0 | 0 | 250 | 320 | 250 | 20 | 0 | 196 | 0 | 0 | 87 | 0 | 0 | 19 | 0 | 148 | 0 | 0 | 6 | 310 | 0 | 354 | 42 | 30 | 150 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 100 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 6031 | 932 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 885 | 0 | 0 | 0 | 966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 130 | 220 | 0 | 285 | 810 | 0 | 5139 | 11170 | 78.98
19:30 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 258 | 18 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 18 | 12 | 0 | 410 | 0 | 0 | 38 | 0 | 1 | 49 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 7 | 740 | 0 | 0 | 19 | 8 | 0 | 220 | 0 | 0 | 0 | 1050 | 0 | 0 | 0 | 250 | 320 | 280 | 20 | 0 | 197 | 0 | 0 | 87 | 0 | 0 | 19 | 0 | 156 | 0 | 0 | 16 | 310 | 0 | 377 | 42 | 30 | 148 | 0 | 0 | 0 | 84 | 30 | 0 | 0 | 100 | 0 | 9 | 65 | 0 | 0 | 0 | 0 | 6136 | 932 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 883 | 0 | 0 | 0 | 932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 130 | 220 | 0 | 306 | 895 | 0 | 5264 | 11400 | 0
20:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 278 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 0 | 18 | 14 | 0 | 440 | 0 | 0 | 38 | 0 | 1 | 47 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 3 | 750 | 0 | 0 | 19 | 8 | 0 | 220 | 0 | 0 | 0 | 1048 | 0 | 0 | 0 | 280 | 320 | 305 | 20 | 0 | 199 | 0 | 0 | 87 | 0 | 0 | 5 | 0 | 146 | 0 | 0 | 0 | 305 | 0 | 381 | 42 | 30 | 145 | 0 | 0 | 0 | 84 | 30 | 0 | 0 | 100 | 0 | 9 | 84 | 0 | 0 | 0 | 0 | 6205 | 933 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 816 | 0 | 0 | 0 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 130 | 220 | 0 | 310 | 900 | 0 | 5249 | 11454 | 78.99
21:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 315 | 0 | 1 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 18 | 14 | 0 | 490 | 0 | 0 | 37 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 10 | 815 | 0 | 0 | 19 | 8 | 0 | 220 | 0 | 0 | 0 | 1092 | 0 | 0 | 0 | 280 | 320 | 320 | 35 | 0 | 206 | 0 | 0 | 87 | 0 | 0 | 2 | 0 | 116 | 0 | 0 | 0 | 305 | 0 | 381 | 42 | 30 | 154 | 0 | 0 | 0 | 84 | 30 | 40 | 0 | 100 | 0 | 9 | 84 | 0 | 0 | 0 | 0 | 6489 | 931 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 792 | 0 | 0 | 0 | 1069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 130 | 220 | 0 | 321 | 920 | 0 | 5449 | 11938 | 78.99
22:00 | 0 | 24 | 43 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 247 | 0 | 17 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 9 | 0 | 14 | 0 | 400 | 0 | 0 | 38 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 15 | 835 | 0 | 0 | 19 | 8 | 0 | 221 | 0 | 0 | 0 | 1088 | 0 | 0 | 0 | 240 | 320 | 320 | 40 | 0 | 185 | 0 | 0 | 87 | 0 | 0 | 5 | 0 | 120 | 0 | 0 | 0 | 305 | 0 | 381 | 42 | 30 | 154 | 0 | 8 | 0 | 81 | 30 | 100 | 0 | 100 | 0 | 9 | 78 | 0 | 0 | 0 | 2 | 6434 | 932 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 1099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224 | 130 | 220 | 0 | 371 | 990 | 0 | 5575 | 12009 | 78.99
23:00 | 0 | 34 | 43 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 305 | 0 | 17 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 17 | 16 | 14 | 0 | 460 | 0 | 0 | 38 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 21 | 850 | 0 | 0 | 19 | 0 | 0 | 219 | 0 | 0 | 0 | 1110 | 0 | 0 | 0 | 215 | 320 | 320 | 51 | 0 | 195 | 0 | 0 | 87 | 0 | 0 | 6 | 0 | 120 | 0 | 0 | 0 | 310 | 0 | 380 | 42 | 30 | 151 | 0 | 0 | 0 | 81 | 30 | 70 | 0 | 100 | 0 | 9 | 78 | 0 | 0 | 0 | 12 | 6616 | 932 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772 | 0 | 0 | 0 | 1104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 130 | 220 | 0 | 370 | 990 | 0 | 5591 | 12207 | 78.99
Total KWH | 0 | 566400 | 360480 | 0 | 0 | 0 | 0 | 0 | 8942400 | 0 | 7394550 | 160920 | 158760 | 1993248 | 144960 | 846065 | 0 | 126231 | 404640 | 0 | 0 | 0 | 0 | 0 | 95181 | 7217403 | 0 | 0 | 212699 | 948000 | 393600 | 333360 | 0 | 10853181.82 | 0 | 0 | 360000 | 0 | 24960 | 335601 | 0 | 0 | 0 | 0 | 27602 | 1012800 | 0 | 352320 | 20741818.18 | 0 | 0 | 224160 | 40968 | 0 | 5382414 | 0 | 0 | 0 | 25783634 | 135000 | 10036 | 0 | 5925500 | 8672800 | 6398000 | 1204216 | 0 | 4936000 | 0 | 174720 | 2081365 | 0 | 0 | 361870 | 0 | 2728320 | 0 | 470664 | 12608 | 7393000 | 0 | 8920000 | 993000 | 723720 | 3599918.18 | 63327 | 300336 | 0 | 1863360 | 687744 | 247800 | 0 | 2406710 | 0 | 434400 | 1132800 | 146880 | 8950 | 278590 | 26640 | 157776630.18 | 22533091 | 3486816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 678240 | 21258180 | 0 | 0 | 0 | 25211435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338944 | 638571 | 0 | 0 | 297760 | 3592182 | 0 | 0 | 0 | 3769055 | 0 | 9631564 | 0 | 31560 | 0 | 0 | 398905 | 119137 | 459897 | 0 | 0 | 0 | 28535.4 | 558000 | 4662 | 0 | 4866000 | 2930000 | 5336380 | 0 | 7767273 | 24282181.82 | 0 | 138218369.22 | 295994999.4

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 07-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-05-2026 | during | 07-05-2026 | during | 07-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 380 | 374 | 412 | 412 | 412 | 412 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 15 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 310 | 310 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 32 | 7 | 32 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 12 | 0 | 53.97 | 53.97 | 17 | 36 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 0 | 149.36 | 149.36 | 46 | 46 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 18 | 18 | 33 | 33 | 21 | 21 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 14 | 14 | 14 | 14 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 8 | 52.19 | 52.19 | 16 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 70 | 0 | 300 | 300 | 48 | 294 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 96 | 25 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 17 | 105 | 105 | 17 | 34 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 31 | 0 | 162 | 162 | 35 | 88 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 1 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 480 | 490 | 584 | 584 | 515 | 515 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 313 | 315 | 718 | 718 | 335 | 335 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 0 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1902 | 1572 | 5946.22 | 5939.22 | 2187 | 2627
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 1 | 8 | 25.5 | 25.5 | 0 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 9 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 0 | 0 | 19 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 45 | 42 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 220 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 34 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 49 | 0 | 68 | 0 | 68 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 10 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 37 | 108 | 108 | 12 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.99 | 0 | 3.89 | 0 | 3.89 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 17 | 54 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1162 | 1092 | 1224 | 1224 | 1204 | 1204 | U2 on AGC
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 920 | 815 | 1150 | 1150 | 1150 | 1150 | AGC
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2365.99 | 2292 | 3885.75 | 3962.86 | 2996.89 | 3193
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 196 | 206 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 356 | 320 | 350.01 | 350.01 | 350.01 | 350.01 | FGMO not available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 250 | 320 | 342.01 | 342.01 | 342.01 | 342.01 | FGMO not available
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 235 | 280 | 393 | 393 | 301 | 301 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 35 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 25 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 87 | 87 | 163 | 163 | 87 | 87 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 17 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 110 | 116 | 84 | 80 | 148 | 148 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 20 | 52 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 2 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 17 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 17 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 49 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1348 | 1366 | 2749.44 | 2690.44 | 1696.27 | 2118.27
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-05-2026 | during | 07-05-2026 | during | 07-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 0 | 157.5 | 157.5 | 17 | 17 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.78 | 0 | 2.4 | 0 | 2.4 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 68 | 84 | 90 | 90 | 80 | 80 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 10 | 10 | 80 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 22.32 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 106.1 | 93 | 381.4 | 334 | 241.4 | 196
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 41 | 41 | 41 | 41 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 154 | 163 | 163 | 147 | 147 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 40 | 100 | 100 | 0 | 0 | Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 28 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 0 | 25 | 25 | 17 | 17 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 357 | 381 | 360 | 360 | 360 | 360 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1134 | 1166 | 1274 | 1274 | 1116 | 1116
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 932 | 931 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 36 | 36 | 36 | 36 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 135 | 109 | 410 | 410 | 180 | 180 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 100 | 0 | 99 | 0 | 99 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1090 | 792 | 1234.2 | 1234.2 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2257 | 1832 | 3599.2 | 3500.2 | 2556.1 | 2457.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 314 | 321 | 350 | 500 | 350 | 500 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 128 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1063 | 920 | 1244 | 1244 | 1184 | 1184 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 259 | 214 | 307 | 307 | 307 | 307 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.44 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1984.44 | 1805 | 2512 | 2661 | 2225 | 2374
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 48.79 | 0 | 48.55 | 0 | 48.55 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 180 | 130 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Fuel shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 130 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0.03 | 0.03 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 92 | 92 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.72 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1087 | 1069 | 1435.88 | 1435.88 | 1356 | 1356 | AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 60 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 104 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2039.51 | 1743 | 3210.27 | 2994.87 | 2536.84 | 2406.44
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 34 | 113 | 113 | 35 | 113 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.9 | 0 | 5.4 | 0 | 5.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 35 | 115 | 115 | 0 | 70 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 8 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 43 | 0 | 189.31 | 0 | 189.31 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 123.9 | 69 | 472.71 | 248 | 259.71 | 183
System Total |  |  |  |  | 28823.2 | 29270.237 | 13260.94 | 11938 | 24030.99 | 23604.59 | 15815.21 | 16670.81
Forecast Scenario (07-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12250 |  | 0 |  | 12250
|  |  |  | 1:00 | 11600 |  | 0 |  | 11600
|  |  |  | 2:00 | 11170 |  | 0 |  | 11170
|  |  |  | 3:00 | 10760 |  | 0 |  | 10760
|  |  |  | 4:00 | 10470 |  | 0 |  | 10470
|  |  |  | 5:00 | 10090 |  | 0 |  | 10090
|  |  |  | 6:00 | 10410 |  | 0 |  | 10410
|  |  |  | 7:00 | 10840 |  | 0 |  | 10840
|  |  |  | 8:00 | 11090 |  | 0 |  | 11090
|  |  |  | 9:00 | 11370 |  | 0 |  | 11370
|  |  |  | 10:00 | 11920 |  | 0 |  | 11920
|  |  |  | 11:00 | 12650 |  | 0 |  | 12650
|  |  |  | 12:00 | 13100 |  | 0 |  | 13100
|  |  |  | 13:00 | 13500 |  | 0 |  | 13500
|  |  |  | 14:00 | 12830 |  | 0 |  | 12830
|  |  |  | 15:00 | 12800 |  | 0 |  | 12800
|  |  |  | 16:00 | 12770 |  | 0 |  | 12770
|  |  |  | 17:00 | 12610 |  | 0 |  | 12610
|  |  |  | 18:00 | 12520 |  | 0 |  | 12520
|  |  |  | 18:30 | 13300 |  | 0 |  | 13300
|  |  |  | 19:00 | 14050 |  | 0 |  | 14050
|  |  |  | 19:30 | 14600 |  | 0 |  | 14600
|  |  |  | 20:00 | 14290 |  | 0 |  | 14290
|  |  |  | 21:00 | 14250 |  | 0 |  | 14250
|  |  |  | 22:00 | 14070 |  | 0 |  | 14070
|  |  |  | 23:00 | 13820 |  | 0 |  | 13820
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 13100.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14600.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14600.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 295.23 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:44 hrs on 07-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 06-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13260.94 | MW | 12:00 Hr. | Energy Generated |  |  | 295.995 |  | MKWHr.
| Day Peak Demand |  |  | 13291.94 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.702 |  | MKWHr.
| Evening Peak Generation |  |  | 11938 | MW | 21:00 Hr. | Energy Demand |  |  | 296.697 |  | MKWHr.
| Evening Peak Demand |  |  | 11938 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33.5 |  | °C
| Minimum Generation of the Day |  |  | 11170 | MW | 19:00 Hr. | Total Gas Supplied |  |  | 903.66 |  | MMCFD
| Maximum Generation of the Day |  |  | 13335.15 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.5284 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 35.1345 | 0 | 5.8049 | 0 | 0 | 0.2127 | 0 | 0 | 41.1521 | Gas | 126.4774 | Gas | 441954249.275
| Chattogram Zone |  |  | 5.7347 | 46.5255 | 0.96073 | 0 | 1.0128 | 0.1626 | 0 | 0.02496 | 54.4213 | Coal | 104.6991 | Coal | 693036279.2318
| Cumilla Zone |  |  | 29.5798 | 0 | 0.19736 | 0 | 0 | 0.47066 | 2.7283 | 0 | 32.9761 | HFO | 9.4156 | HFO | 156354354.18
| Mymensingh Zone |  |  | 0.14688 | 0 | 1.5938 | 0 | 0 | 0.28754 | 0 | 0 | 2.0283 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.1356 | 0 | 0 | 0 | 0 | 0.063327 | 0 | 0 | 27.1989 | Hydro | 1.0128 | Hydro | 101280
| Khulna Zone |  |  | 3.4868 | 21.2582 | 0 | 0 | 0 | 0.67824 | 22.5331 | 0 | 47.9563 | Solar | 3.8922 | Solar | 61041702.88
| Barishal Zone |  |  | 8.2664 | 36.9155 | 0 | 0 | 0 | 0.004662 | 0 | 0 | 45.1865 | Import | 50.4728 | Import | 283522688.96
| Rajshahi Zone |  |  | 16.9928 | 0 | 0 | 0 | 0 | 1.3068 | 25.2114 | 0 | 43.5111 | Wind | 0.02496 | Wind | 367161.6
| Rangpur Zone |  |  | 0 | 0 | 0.8588 | 0 | 0 | 0.70567 | 0 | 0 | 1.5645
| Total |  |  | 126.4774 | 104.6991 | 9.4156 | 0 | 1.0128 | 3.8922 | 50.4728 | 0.02496 | 295.995
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 441954249.275 |  | Hydro | 101280
|  |  |  | Coal | 693036279.2318 |  | Solar | 61041702.88
|  |  |  | HFO | 156354354.18 |  | Import | 283522688.96
|  |  |  | HSD | 0 |  | Wind | 367161.6
[5 empty] | Total: | 163,63,77,716 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.5331 | Peak Hr Flow | 931.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 46735509.09 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.2114 | Peak Hr Flow | 1069.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1755 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.7283 | Peak Hr Flow | 116.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2830 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.4728 | Peak Hr Flow | 2116.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4457
|  |  |  | Chattogram |  | 0 |  | 1540
|  |  |  | Cumilla |  | 0 |  | 877
|  |  |  | Mymensingh |  | 0 |  | 797
|  |  |  | Sylhet |  | 0 |  | 341
|  |  |  | Khulna |  | 0 |  | 1425
|  |  |  | Barishal |  | 0 |  | 419
|  |  |  | Rajshahi |  | 0 |  | 1091
|  |  |  | Rangpur |  | 0 |  | 696
|  |  |  | Total |  | 0 |  | 11643
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:25 | 18:34 | Barishal-Barishal(N) 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to OPGW
Upgration work of OFCN and from Barishal 230/132kV end Due to Repalace of OPGW
| 09:08 | 09:30 | Brahmanbaria 132/33kV S/S 402T LT Tripped showing O/C & E/F relays. | [7 empty] | 55.0MW load
interrup.
| 09:13 | 09:58 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to S/D Taken by PBS for Red Hot
maintenance.
| 09:13 | 09:56 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D
|  | 09:28 | Mymensingh 132/33kV S/S Transformer-1 (404T) HT is restored.
|  | 09:28 | Khulna (C) S/S TR-1 425T HT is restored.
|  | 09:29 | Khulna (C) S/S TR-1 425T LT is restored.
|  | 09:30 | Mymensingh 132/33kV S/S Transformer-1 (404T) LT is restored.
|  | 10:10 | Barapukuria-Rangpur 132 kV Ckt-1 is restored.
| 10:25 | 12:30 | Bheramara-GK 132kV Ckt-2 Forced S/D from Bheramara 230/132kV end Due to Hotspot
| 10:38 | 12:42 | Bheramara 230/132kV S/S Bus-B (132) Forced S/D Due to Hotspot in Bus DS
| 10:40 | 15:03 | Bhandaria 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Shutdown for 33 kv Bus PT | [7 empty] | 10.0MW load
|  |  | change given by Pirojpur PBS | [7 empty] | interrup.
| 10:40 | 15:03 | Bhandaria 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Shutdown for 33 kv Bus PT | [7 empty] | 10.0MW load
|  |  | change given by Pirojpur PBS | [7 empty] | interrup.
|  | 11:58 | Daganbhuiyan 132/33kV S/S Transformer-1 HT is restored.
| 12:00 |  | Day Peak Generation: 13256 MW.
| 12:01 | 21:02 | Baghabari-Roppur 230kV Ckt-1 Project Work S/D from Baghabari 230/132kV end Due to DFDR
Commissioning.
| 12:08 | 12:46 | Purbasadipur 230/132/33kV S/S TR-1 (H01R22) LT Tripped showing SIMENS SIPROTEC 7SJ81 | [7 empty] | 20.0MW load
|  |  | Relay relays Due to Cable blast of 33 kV Khansama Feeder (PBS) | [7 empty] | interrup.
| 12:24 | 12:48 | Muradnagar 132/33kV S/S 132KV Transformar-01 HT Project Work S/D Due to kite remove
| 13:19 | 14:55 | Sreepur 230/132/33kV S/S 132/33 kV T-1 HT Forced S/D Due to CCCC's project measurement | [7 empty] | 48.0MW load
|  |  | work | [7 empty] | interrup.
| 15:48 | 20:22 | Kushtia 132/33kV S/S T-3 HT Forced S/D Due to A fire incident occurred in the Y-phase | [7 empty] | 30.0MW load
|  |  | control cable under the CT terminal box of the 132 kV CT of T-3 transformer. | [7 empty] | interrup.
| 15:48 | 20:24 | Kushtia 132/33kV S/S T-3 LT Forced S/D Due to A fire incident occurred in the Y-phase | [7 empty] | 35.0MW load
|  |  | control cable under the CT terminal box of the 132 kV CT of T-3 transformer. | [7 empty] | interrup.
| 15:57 | 17:43 | Lalmonirhat 132/33kV S/S T-2 (415T) HT Project Work S/D Due to 132Kv circuit breaker
replace work
| 15:57 | 17:43 | Lalmonirhat 132/33kV S/S T-2 (415T) LT Project Work S/D Due to 132kv Circuit Breaker
Replace work
| 17:20 |  | Kushtia 132/33kV S/S T-1 HT Forced S/D Due to Due to burning of the closing coil of the | [7 empty] | 16.0MW load
|  |  | 33 kV circuit breaker and the closing relay of the 33 kV relay and control panel, the | [7 empty] | interrup.
circuit breaker could not be operated.
| 17:20 |  | Kushtia 132/33kV S/S T-1 LT Forced S/D | [7 empty] | 22.0MW load
interrup.
|  | 17:53 | Cumilla(S) 132/33kV S/S TR-2 LT is restored.
|  | 17:53 | Cumilla(S) 132/33kV S/S TR-2 HT is restored.
|  | 18:10 | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) is restored.
|  | 18:13 | Barapukuria-Bogura 230 kV Ckt-1 is restored.
| 18:27 |  | Chandina 132/33kV S/S TR-2 LT Tripped showing F51, 86L-1&2 relays Due to Diff Trip | [7 empty] | 17.0MW load
interrup.
| 18:27 |  | Chandina 132/33kV S/S TR-2 HT Tripped showing F87T2, 86L1&2 relays Due to Differential | [7 empty] | 17.0MW load
|  |  | Trip | [7 empty] | interrup.
| 18:28 | 18:36 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Tripped from Shahjibazar 132/33kV end showing
Distance relay relays Due to Stormy weather
| 20:20 | 22:57 | Bhangura 132/33kV S/S Tr-2(413T) LT Forced S/D Due to Ct y phase redhot | [7 empty] | 15.0MW load
interrup.
| 20:20 | 22:57 | Bhangura 132/33kV S/S Tr-2(413T) HT Forced S/D Due to Redhot | [7 empty] | 15.0MW load
interrup.
| 21:00 |  | Evening Peak Generation is 11938 MW.
| 22:27 | 23:58 | Daganbhuiyan 132/33kV S/S Transformer-1 LT Forced S/D Due to 33 kv bus red hot | [7 empty] | 10.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 22:40 | 23:58 | Daganbhuiyan 132/33kV S/S Transformer-1 HT Forced S/D Due to 33 kv bus red hot | [7 empty] | 10.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 05:00 |  | Minimum Generation is 10508 MW.
| 05:23 | 06:39 | Magura 132/33kV S/S T-2 (415T) LT Tripped showing Oil temp. Tripping relays Due to
Differential prot.-1
| 05:23 | 06:36 | Magura 132/33kV S/S T-2 (415T) HT Tripped showing Oli temp. Tripping relays Due to
Differential protection-1
| 07:20 |  | Khulna(C )-Noapara 132kV Ckt-2 Project Work S/D from Khulna (C) end Due to Project work.
and from Noapara 132/33kV end Due to According to ALDC's instructions.
| 07:41 |  | Barishal-Barishal(N) 132 kV Ckt-1 Project Work S/D from Barishal 230/132kV end Due to
OPGW Replament work and from Barishal 132/33kV end Due to Optical Fiber upgraded work.
| 07:50 |  | Barapukuria-Bogura 230 kV Ckt-1 Project Work S/D from Bogura 400/230kV end Due to Project
work (Conductor Stringing ).As per ALDCs instruction. and from Barapukuria 230/132/33kV
end Due to project work
| 07:51 |  | Barapukuria-Bogura 230 kV Ckt-1 Scheduled S/D from Barapukuria 230/132/33kV end Due to
project work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 06-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 374 | 8942400 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 310 | 7217403 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 160920 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 144960 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 126231 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 95181 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 393600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 333360 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 360480 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 846065 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 25 | 1993248 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 566400 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 404640 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 212699 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 1 | 158760 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 490 | 10853181.82 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 315 | 7394550 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 0 | 948000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1572 | 41152078.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 40968 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 135000 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 224160 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 42 | 1012800 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5382414 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 49 | 335601 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 10 | 352320 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 37 | 360000 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 27602 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1092 | 25783634 | AGC
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 24960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 815 | 20741818.18 | AGC
Chattogram Area Total |  |  |  |  | 4898.863 | 2292 | 54421277.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 206 | 4936000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 320 | 8672800 | FGMO not available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 320 | 6398000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 280 | 5925500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 35 | 1204216 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 10036 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 12608 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 87 | 2081365 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 116 | 2728320 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 2 | 361870 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 174720 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 470664 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1366 | 32976099
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 146880 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 84 | 1132800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 434400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 278590 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 26640 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 93 | 2028260
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 63327 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 993000 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 723720 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3599918.18 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 40 | 247800 | Machine Problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 687744 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1863360 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2406710 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 300336 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7393000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 381 | 8920000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1166 | 27198915.18
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 931 | 22533091 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 109 | 3486816 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 678240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 792 | 21258180 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1832 | 47956327
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 321 | 7767273 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 2930000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 920 | 24282181.82 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5336380 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 214 | 4866000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4662 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1805 | 45186496.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 338944 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 130 | 3592182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 130 | 3769055 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9631564 | Gas shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 31560 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1069 | 25211435 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 297760 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 638571 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1743 | 43511071
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 459897 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 28535.4 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 398905 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 119137 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 558000 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 69 | 1564474.4
Eastern Grid Total |  |  |  |  | 17418.042 | 6489 | 157776630.18
Western Grid Total |  |  |  |  | 11852.195 | 5449 | 138218369.22
National Grid Total |  |  |  |  | 29270.237 | 11938 | 295994999.4
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 06-05-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8012.8 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3630.7 | MW
i) Dhaka area |  |  | 4457.3 |  | MW | i) Khulna area |  |  |  | 1425 | MW
ii) Chattogram area |  |  | 1540.5 |  | MW | ii) Barishal area |  |  |  | 418.7 | MW
iii) Cumilla area |  |  | 877 |  | MW | iii) Rajshahi area |  |  |  | 1091 | MW
iv) Mymensingh area |  |  | 797 |  | MW | iv) Rangpur area |  |  |  | 696 | MW
v) Sylhet area |  |  | 341 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11643.5 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 18 | 19:00 | 67 | Hasnabad | 86 | 15:00 | 133 | Natore | 132 | 00:00
2 | AKSML | 107 | 03:00 | 68 | Hathazari | 84 | 18:30 | 134 | Nawabganj | 46.8 | 16:00
3 | Aftabnagar | 40 | 14:00 | 69 | Hatirjheel | 41 | 13:00 | 135 | Netrakona | 122 | 00:00
4 | Agargaon | 116 | 13:00 | 70 | Ishurdi | 75 | 13:00 | 136 | New | 82 | 12:00
5 | Agrabad | 72 | 15:00 | 71 | Jaldhaka | 58 | 19:30 | 137 | Niamatpur | 56 | 00:00
6 | Amnura | 27 | 00:00 | 72 | Jamalpur | 97 | 08:00 | 138 | Noapara | 44 | 19:00
7 | Ashuganj | 74 | 13:00 | 73 | Jashore | 132 | 13:00 | 139 | PHP | 13 | 12:00
8 | BSRM | 206 | 21:00 | 74 | Jhenaidah | 98 | 19:00 | 140 | Pabna | 91 | 14:00
9 | Bagerhat | 75 | 00:00 | 75 | Joydebpur | 142 | 17:00 | 141 | Palashbari | 98 | 00:00
10 | Bajitpur | 71 | 00:00 | 76 | Joypurhat | 53 | 00:00 | 142 | Panchagarh | 51 | 19:30
11 | Bakerganj | 10.9 | 19:00 | 77 | Juldah | 15.5 | 17:00 | 143 | Patiya | 10 | 00:00
12 | Bakulia | 91 | 18:30 | 78 | KSRM | 11.5 | 18:00 | 144 | Patuakhali | 66.5 | 23:00
13 | Banani | 48 | 15:00 | 79 | Kabirpur | 277 | 15:00 | 145 | Payra | 32 | 23:00
14 | Bangabhaban | 18 | 10:00 | 80 | Kachua | 86 | 19:30 | 146 | Postogola | 54 | 13:00
15 | Barapukuria | 54 | 00:00 | 81 | Kaliganj | 18 | 00:00 | 147 | Pubail | 22 | 12:00
16 | Barguna | 22 | 22:00 | 82 | Kallyanpur | 105 | 13:00 | 148 | Purbachal | 30 | 18:00
17 | Barishal | 102 | 13:00 | 83 | Kalurghat | 40 | 12:00 | 149 | Purbasadipur | 108 | 00:00
18 | Barishal-230 | 96 | 19:00 | 84 | Kamrangirchar | 87 | 13:00 | 150 | Rahanpur | 28 | 00:00
19 | Baroaulia | 63 | 22:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 38 | 18:00
20 | Baroirhat | 52 | 19:30 | 86 | Kasba | 33 | 18:30 | 152 | Rajbari | 73 | 00:00
21 | Bashundhara | 174 | 13:00 | 87 | Kazla | 116 | 12:00 | 153 | Rajendrapur | 120 | 15:00
22 | BashundharaCement | 7 | 00:00 | 88 | Keranigonj | 82 | 14:00 | 154 | Rajshahi | 99 | 00:00
23 | Beanibazar | 64 | 00:00 | 89 | Khagrachori | 36 | 20:00 | 155 | Rajshahi-230 | 96 | 13:00
24 | Benapole | 59 | 00:00 | 90 | Khulna | 67 | 13:00 | 156 | Ramganj | 106 | 19:00
25 | Bhaluka | 135 | 11:00 | 91 | Khulshi | 178 | 18:00 | 157 | Rampur | 40 | 20:00
26 | Bhandaria | 55 | 22:00 | 92 | Kishoreganj | 106 | 00:00 | 158 | Rangamati | 19 | 19:00
27 | Bhangura | 38 | 14:00 | 93 | Kodda | 298 | 16:00 | 159 | Rangpur | 120 | 11:00
28 | Bheramara(GK) | 58 | 00:00 | 94 | Kulaura | 51 | 19:00 | 160 | Ruppur | 4 | 10:00
29 | Bhulta | 213 | 15:00 | 95 | Kurigram | 48 | 07:00 | 161 | SSM | 10 | 23:00
30 | Bog-Sherpur | 72 | 00:00 | 96 | Kushtia | 144 | 00:00 | 162 | Saidpur | 99 | 11:00
31 | Bogura | 137 | 19:30 | 97 | Laksam | 32 | 19:30 | 163 | Santhia | 28 | 00:00
32 | Borhanuddin | 91 | 19:00 | 98 | Lakshmipur | 39 | 19:00 | 164 | Satkhira | 126 | 19:00
33 | Brahmanbaria | 107 | 01:00 | 99 | Lalbag | 72 | 13:00 | 165 | Satmasjid | 99 | 14:00
34 | Cantonment | 113 | 13:00 | 100 | Lalmonirhat | 46 | 19:00 | 166 | Savar | 216 | 15:00
35 | Chandina | 35 | 15:00 | 101 | MI_Cement | 17.4 | 10:00 | 167 | SevenRings | 3.83 | 16:00
36 | Chandpur | 75 | 19:00 | 102 | Madanganj | 42 | 12:00 | 168 | ShahCement | 41 | 00:00
37 | Chandraghona | 37 | 18:30 | 103 | Madaripur | 92 | 18:30 | 169 | Shahjadpur | 88 | 12:00
38 | Chapai | 60 | 00:00 | 104 | Madartek | 69 | 14:00 | 170 | Shahjibazar | 102 | 00:00
39 | Charsaidpur | 41 | 17:00 | 105 | Madunaghat | 56 | 15:00 | 171 | Shahmirpur | 46 | 22:00
40 | Chauddagram | 84 | 19:00 | 106 | Magura | 58 | 00:00 | 172 | Shariatpur | 69 | 14:00
41 | Chhatak | 32 | 00:00 | 107 | Mahasthangarh | 64 | 00:00 | 173 | Sherpur | 106 | 07:00
42 | Chowmuhani | 143 | 20:00 | 108 | Maijdee | 48 | 21:00 | 174 | Shikalbaha | 35.5 | 00:00
43 | Chuadanga | 109 | 19:00 | 109 | Manikganj | 131 | 16:00 | 175 | Shitalakhya | 83.5 | 11:00
44 | Coxsbazar | 141 | 19:00 | 110 | Maniknagar | 71 | 13:00 | 176 | Sholosohor | 44 | 19:30
45 | Cumilla(N) | 122 | 19:00 | 111 | Matarbari | 53 | 19:30 | 177 | Shyampur | 176 | 10:00
46 | Cumilla(S) | 156 | 19:30 | 112 | Matuail | 78 | 15:00 | 178 | Siddhirganj | 129 | 12:00
47 | Daganbhuiyan | 32 | 19:00 | 113 | Metrorail_Motijheel | 20 | 11:00 | 179 | Sirajganj | 96 | 12:00
48 | Daudkandi | 138 | 18:30 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sonargaon | 131 | 16:00
49 | DhakaUniversity | 90 | 13:00 | 115 | Millgate | 103 | 15:00 | 181 | Sreemongol | 58 | 01:00
50 | Dhamrai | 112 | 16:00 | 116 | Mirpur | 142 | 15:00 | 182 | Sreepur | 117 | 16:00
51 | Dhanmondi | 126 | 14:00 | 117 | Mirsorai | 56 | 09:00 | 183 | Srinagar | 40 | 14:00
52 | Dohazari | 103 | 21:00 | 118 | Mirzapur | 41 | 13:00 | 184 | Sunamganj | 53 | 00:00
53 | Faridpur | 145 | 00:00 | 119 | Mithapukur | 44 | 00:00 | 185 | Sylhet | 42 | 21:00
54 | Fatullah | 92 | 11:00 | 120 | Modern | N/A | N/A | 186 | Sylhet-132 | 124 | 15:00
55 | Fenchuganj | 34 | 15:00 | 121 | Mogbazar | 86.1 | 13:00 | 187 | TK | 23 | 00:00
56 | Feni | 105 | 18:30 | 122 | Mongla | 41 | 15:00 | 188 | Tangail | 154 | 13:00
57 | GPH | 72 | 22:00 | 123 | Motijheel | 48 | 13:00 | 189 | Taraganj | 21 | 19:00
58 | Ghatail | 72 | 14:00 | 124 | Muktagacha | 28 | 13:00 | 190 | Tasnim | 23 | 19:30
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 106 | 15:00 | 191 | Thakurgaon | 86 | 19:30
60 | Ghorashal-230 | 101 | 00:00 | 126 | Muradnagar | 39 | 19:00 | 192 | Tongi | 144 | 15:00
61 | Goalpara | 39 | 13:00 | 127 | Mymensingh | 157 | 00:00 | 193 | Ullahpara | 34 | 07:00
62 | Gollamari | 100 | 13:00 | 128 | Nabinagar | 76 | 21:00 | 194 | Ullon | 50 | 14:00
63 | Gopalganj | 88 | 21:00 | 129 | Naogaon | 110 | 00:00 | 195 | Uttara | 84 | 14:00
64 | Gulshan | 114 | 12:00 | 130 | Narail | 51 | 00:00 | 196 | UttaraNew | 50 | 13:00
65 | Halishahar | 100 | 15:00 | 131 | Narinda | 76 | 13:00 | 197 | Zigatola | 88 | 13:00
66 | HaripurSBU | 139 | 12:00 | 132 | Narshingdi | 163 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 06-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13335.15 | 120 |  | 13460.15
1:00 | 12804.53 | 82 |  | 12890.53
2:00 | 12346.93 | 80 |  | 12430.93
3:00 | 12037.89 | 79 |  | 12120.89
4:00 | 11686.02 | 71 |  | 11760.02
5:00 | 11469.83 | 44 |  | 11515.83
6:00 | 11477.63 | 44 |  | 11523.63
7:00 | 11811.87 | 50 |  | 11864.12
8:00 | 11793.79 | 0 |  | 11793.79
9:00 | 12295.28 | 0 |  | 12295.28
10:00 | 12627.32 | 0 |  | 12627.32
11:00 | 13042.39 | 25 |  | 13068.39
12:00 | 13260.94 | 30 |  | 13291.94
13:00 | 13312.51 | 45 |  | 13359.51
14:00 | 12976.89 | 0 |  | 12976.89
15:00 | 12774.6 | 32 |  | 12807.6
16:00 | 12298.25 | 0 |  | 12298.25
17:00 | 11637.16 | 0 |  | 11637.16
18:00 | 10524.74 | 0 |  | 10524.74
19:00 | 11170 | 0 |  | 11170
19:30 | 11400 | 0 |  | 11400
20:00 | 11454 | 0 |  | 11454
21:00 | 11938 | 0 |  | 11938
22:00 | 12009 | 0 |  | 12009
23:00 | 12207 | 0 |  | 12207
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 06-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6886.5 | 6448.65 | 13335.15 | DAILY GENERATION CURVE
00:30 | 6768.75 | 6301.09 | 13069.84
01:00 | 6651 | 6153.53 | 12804.53 | 06-05-2026
01:30 | 6568.5 | 6007.23 | 12575.73
02:00 | 6486 | 5860.93 | 12346.93
02:30 | 6394.5 | 5797.91 | 12192.41
03:00 | 6303 | 5734.89 | 12037.89
03:30 | 6215.5 | 5646.455 | 11861.955
04:00 | 6128 | 5558.02 | 11686.02
04:30 | 6123 | 5454.925 | 11577.925
05:00 | 6118 | 5351.83 | 11469.83
05:30 | 6141.575 | 5332.155 | 11473.73
06:00 | 6165.15 | 5312.48 | 11477.63
06:30 | 6227.235 | 5417.515 | 11644.75
07:00 | 6289.32 | 5522.55 | 11811.87
07:30 | 6266.295 | 5536.535 | 11802.83
08:00 | 6243.27 | 5550.52 | 11793.79
08:30 | 6337.525 | 5707.01 | 12044.535
09:00 | 6431.78 | 5863.5 | 12295.28
09:30 | 6496.015 | 5965.285 | 12461.3
10:00 | 6560.25 | 6067.07 | 12627.32
10:30 | 6680.56 | 6154.295 | 12834.855
11:00 | 6800.87 | 6241.52 | 13042.39
11:30 | 6828.48 | 6323.185 | 13151.665
12:00 | 6856.09 | 6404.85 | 13260.94
12:30 | 6902.8 | 6383.925 | 13286.725
13:00 | 6949.51 | 6363 | 13312.51
13:30 | 6905.015 | 6239.685 | 13144.7
14:00 | 6860.52 | 6116.37 | 12976.89
14:30 | 6905.935 | 5969.81 | 12875.745
15:00 | 6951.35 | 5823.25 | 12774.6
15:30 | 6844.17 | 5692.255 | 12536.425
16:00 | 6736.99 | 5561.26 | 12298.25
16:30 | 6590.315 | 5377.39 | 11967.705
17:00 | 6443.64 | 5193.52 | 11637.16
17:30 | 6066.825 | 5014.125 | 11080.95
18:00 | 5690.01 | 4834.73 | 10524.74
18:30 | 5860.505 | 4986.865 | 10847.37
19:00 | 6031 | 5139 | 11170
19:30 | 6136 | 5264 | 11400
20:00 | 6205 | 5249 | 11454
20:30 | 6347 | 5349 | 11696 |  | Executive Engineer
21:00 | 6489 | 5449 | 11938 |  | Network Operation Division
21:30 | 6461.5 | 5512 | 11973.5
22:00 | 6434 | 5575 | 12009
22:30 | 6525 | 5583 | 12108
23:00 | 6616 | 5591 | 12207

## En-Curve
QF-LDC-12
Date | 06-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3639 | 1678.5 | 932 | 0 | 114 | 1278.65 | 44 | 4963 | 0 | 205 | 481 | 0 | 0 | 0 | 120 | DAILY ENERGY CURVE
00:30 | 3641 | 1677.25 | 931.5 | 0 | 113 | 1268.09 | 44 | 4851.5 | 0 | 171 | 372.5 | 0 | 0 | 0 | 101 | 06-05-2026
01:00 | 3643 | 1676 | 931 | 0 | 112 | 1257.53 | 44 | 4740 | 0 | 137 | 264 | 0 | 0 | 0 | 82
01:30 | 3647 | 1682 | 931.5 | 0 | 110 | 1247.73 | 43 | 4564.5 | 0 | 111.5 | 238.5 | 0 | 0 | 0 | 81 | Energy Generated | 295.995 |  | MKWHr
02:00 | 3651 | 1688 | 932 | 0 | 108 | 1237.93 | 42 | 4389 | 0 | 86 | 213 | 0 | 0 | 0 | 80 | Energy not Served | 0.702 |  | MKWHr
02:30 | 3646.5 | 1689.5 | 932 | 0 | 107 | 1236.41 | 41.5 | 4280 | 0 | 69 | 190.5 | 0 | 0 | 0 | 79.5 | Total Energy Requirement | 296.697 |  | MKWHr
03:00 | 3642 | 1691 | 932 | 0 | 106 | 1234.89 | 41 | 4171 | 0 | 52 | 168 | 0 | 0 | 0 | 79
03:30 | 3660 | 1666.5 | 931.5 | 0 | 106 | 1173.455 | 40.5 | 4077.5 | 0 | 43.5 | 163 | 0 | 0 | 0 | 75
04:00 | 3678 | 1642 | 931 | 0 | 106 | 1112.02 | 40 | 3984 | 0 | 35 | 158 | 0 | 0 | 0 | 71
04:30 | 3652.5 | 1635 | 931.5 | 0 | 106 | 1062.425 | 39.5 | 3962.5 | 0 | 35 | 153.5 | 0 | 0 | 0 | 57.5
05:00 | 3627 | 1628 | 932 | 0 | 106 | 1012.83 | 39 | 3941 | 0 | 35 | 149 | 0 | 0 | 0 | 44
05:30 | 3639 | 1642 | 932 | 0 | 103 | 995.275 | 39 | 3921.5 | 17.955 | 35 | 149 | 0 | 0 | 0 | 44
06:00 | 3651 | 1656 | 932 | 0 | 100 | 977.72 | 39 | 3902 | 35.91 | 35 | 149 | 0 | 0 | 0 | 44
06:30 | 3652.5 | 1657.5 | 932 | 0 | 98 | 962.55 | 39.5 | 4000.5 | 88.7 | 58.5 | 155 | 0 | 0 | 0 | 47
07:00 | 3654 | 1659 | 932 | 0 | 96 | 947.38 | 40 | 4099 | 141.49 | 82 | 161 | 0 | 0 | 0 | 50
07:30 | 3633.5 | 1651 | 932 | 0 | 103 | 919.455 | 40.5 | 4026.5 | 213.375 | 87 | 196.5 | 0 | 0 | 0 | 25
08:00 | 3613 | 1643 | 932 | 0 | 110 | 891.53 | 41 | 3954 | 285.26 | 92 | 232 | 0 | 0 | 0 | 0
08:30 | 3621 | 1647 | 932 | 0 | 107 | 919.265 | 42 | 4100 | 349.77 | 92 | 234.5 | 0 | 0 | 0 | 0
09:00 | 3629 | 1651 | 932 | 0 | 104 | 947 | 43 | 4246 | 414.28 | 92 | 237 | 0 | 0 | 0 | 0
09:30 | 3612.5 | 1658 | 932 | 0 | 109 | 958.5 | 43 | 4337.5 | 476.8 | 92 | 242 | 0 | 0 | 0 | 0
10:00 | 3596 | 1665 | 932 | 0 | 114 | 970 | 43 | 4429 | 539.32 | 92 | 247 | 0 | 0 | 0 | 0
10:30 | 3614.5 | 1682 | 932 | 0 | 116 | 999 | 51.5 | 4526 | 557.855 | 100.5 | 255.5 | 0 | 0 | 0 | 12.5
11:00 | 3633 | 1699 | 932 | 0 | 118 | 1028 | 60 | 4623 | 576.39 | 109 | 264 | 0 | 0 | 0 | 25
11:30 | 3611 | 1688.5 | 932 | 0 | 114 | 1057.5 | 52.5 | 4715.5 | 541.165 | 126.5 | 313 | 0 | 0 | 0 | 27.5
12:00 | 3589 | 1678 | 932 | 0 | 110 | 1087 | 45 | 4808 | 505.94 | 144 | 362 | 0 | 0 | 0 | 30
12:30 | 3542.5 | 1655 | 932 | 0 | 110 | 1119 | 45.5 | 4855.5 | 492.425 | 144 | 389.8 | 0 | 0 | 1 | 37.5
13:00 | 3496 | 1632 | 932 | 0 | 110 | 1151 | 46 | 4903 | 478.91 | 144 | 417.6 | 0 | 0 | 2 | 45
13:30 | 3455.5 | 1589 | 932 | 0 | 115 | 1122 | 45.5 | 4824.5 | 463.15 | 144 | 451.55 | 0 | 0 | 2.5 | 22.5
14:00 | 3415 | 1546 | 932 | 0 | 120 | 1093 | 45 | 4746 | 447.39 | 144 | 485.5 | 0 | 0 | 3 | 0
14:30 | 3376.5 | 1588 | 932 | 0 | 117 | 1102 | 43.5 | 4741 | 346.545 | 136.5 | 487.7 | 0 | 0 | 5 | 16
15:00 | 3338 | 1630 | 932 | 0 | 114 | 1111 | 42 | 4736 | 245.7 | 129 | 489.9 | 0 | 0 | 7 | 32
15:30 | 3386 | 1582.5 | 932 | 0 | 112 | 1062.5 | 41 | 4608 | 170.375 | 129 | 506.55 | 0 | 0 | 6.5 | 16
16:00 | 3434 | 1535 | 932 | 0 | 110 | 1014 | 40 | 4480 | 95.05 | 129 | 523.2 | 0 | 0 | 6 | 0
16:30 | 3425.5 | 1526 | 931.5 | 0 | 115 | 970 | 39.5 | 4305 | 77.005 | 94 | 481.2 | 0 | 0 | 3 | 0
17:00 | 3417 | 1517 | 931 | 0 | 120 | 926 | 39 | 4130 | 58.96 | 59 | 439.2 | 0 | 0 | 0 | 0
17:30 | 3310 | 1458.5 | 931.5 | 0 | 123 | 878.5 | 38.5 | 3945.5 | 36.85 | 46 | 307.1 | 0 | 0 | 5.5 | 0
18:00 | 3203 | 1400 | 932 | 0 | 126 | 831 | 38 | 3761 | 14.74 | 33 | 175 | 0 | 0 | 11 | 0
18:30 | 3304 | 1435 | 932 | 0 | 137 | 898.5 | 38.5 | 3869.5 | 7.37 | 56.5 | 163.5 | 0 | 0 | 5.5 | 0
19:00 | 3405 | 1470 | 932 | 0 | 148 | 966 | 39 | 3978 | 0 | 80 | 152 | 0 | 0 | 0 | 0
19:30 | 3489 | 1506 | 932 | 0 | 156 | 932 | 40 | 4046 | 0 | 90 | 208 | 0 | 0 | 1 | 0
20:00 | 3574 | 1532 | 933 | 0 | 146 | 908 | 41 | 4003 | 0 | 72 | 244 | 0 | 0 | 1 | 0
20:30 | 3613.5 | 1589.5 | 932 | 0 | 131 | 988.5 | 41.5 | 4078.5 | 0 | 73 | 248 | 0 | 0 | 0.5 | 0
21:00 | 3653 | 1647 | 931 | 0 | 116 | 1069 | 42 | 4154 | 0 | 74 | 252 | 0 | 0 | 0 | 0
21:30 | 3643.5 | 1568 | 931.5 | 0 | 118 | 1084 | 42.5 | 4211 | 0 | 99.5 | 275.5 | 0 | 0 | 0 | 0
22:00 | 3634 | 1489 | 932 | 0 | 120 | 1099 | 43 | 4268 | 0 | 125 | 299 | 0 | 0 | 0 | 0
22:30 | 3607 | 1562 | 932 | 0 | 120 | 1101.5 | 43 | 4294.5 | 0 | 134 | 314 | 0 | 0 | 0 | 0
23:00 | 3580 | 1635 | 932 | 0 | 120 | 1104 | 43 | 4321 | 0 | 143 | 329 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 06-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 105 | 0 | 476 | 118 | 1560 | 352 | Ishurdi-Ghorashal Ckt-1 | Export | 3360509.09
1:00 | 104 | 4 | 478 | 124 | 1416 | 380
2:00 | 107 | 6 | 484 | 118 | 1348 | 378 |  | Import | 0
3:00 | 118 | 0 | 500 | 106 | 1364 | 374
4:00 | 116 | -3 | 486 | 100 | 1360 | 354 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 111 | -11 | 458 | 88 | 1272 | 346
6:00 | 108 | -10 | 440 | 96 | 1250 | 372 |  | Import | 0
7:00 | 99 | -13 | 416 | 94 | 1296 | 344
8:00 | 127 | -8 | 490 | 116 | 1412 | 410 | Sirajganj-Sreepur Ckt-1 | Export | 3274000
9:00 | 164 | 3 | 582 | 152 | 1650 | 492
10:00 | 173 | 1 | 588 | 152 | 1738 | 522 |  | Import | 0
11:00 | 182 | 8 | 656 | 196 | 1864 | 590
12:00 | 186 | 9 | 674 | 210 | 1962 | 604 | Sirajganj-Sreepur Ckt-2 | Export | 3261000
13:00 | 181 | 13 | 660 | 190 | 1902 | 568
14:00 | 192 | 8 | 704 | 178 | 1934 | 564 |  | Import | 0
15:00 | 197 | 20 | 680 | 192 | 1872 | 558
16:00 | 230 | 38 | 708 | 174 | 1768 | 536 | Gopalganj-Aminbazar Ckt-1 | Export | 18390000
17:00 | 209 | 30 | 596 | 128 | 1682 | 542
18:00 | 154 | -11 | 390 | 26 | 1416 | 418 |  | Import | 0
18:30 | 114 | -26 | 322 | 14 | 1240 | 318
19:00 | 66 | -39 | 276 | 20 | 1094 | 234 | Gopalganj-Aminbazar Ckt-2 | Export | 18450000
19:30 | 61 | -41 | 280 | 30 | 1146 | 248
20:00 | 72 | -35 | 320 | 52 | 1196 | 296 |  | Import | 0
21:00 | 93 | -25 | 402 | 82 | 1260 | 360
22:00 | 112 | -25 | 454 | 86 | 1348 | 328 |  | Total Export | 46735509.09
23:00 | 119 | -23 | 490 | 104 | 1364 | 338 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 06-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 394 | 19:00 | 369 | 13:00 | Madunaghat | 399 | 06:00 | 387 | 13:00
Amtali | 413 | 18:00 | 404 | 13:00 | Meghnaghat | 396 | 19:00 | 373 | 13:00
Ashuganj | 415 | 5:00 | 389 | 13:00 | Payra | 414 | 18:00 | 407 | 12:00
Bhulta | 407 | 05:00 | 379 | 12:00 | Rahanpur | 419 | 18:00 | 405 | 19:30
Bibiana | 409 | 19:00 | 393 | 12:00 | Rampal | 408 | 18:00 | 393 | 12:00
BIPTC | 402 | 05:00 | 396 | 00:00
Bogura | 410 | 18:00 | 393 | 19:30
Gopalganj | 404 | 18:30 | 385 | 12:00
Kaliakoir | 390 | 18:30 | 362 | 12:00
Korerhat | 400 | 07:00 | 385 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 234 | 19:00 | 215 | 12:00 | Jhenaidah | 231 | 17:00 | 217 | 12:00
AKSML | 231 | 05:00 | 221 | 12:00 | Kachua | 228 | 05:00 | 217 | 15:00
Aminbazar | 234 | 19:00 | 215 | 13:00 | Kaliakoir | 238 | 18:30 | 218 | 12:00
Ashuganj | 234 | 18:30 | 220 | 12:00 | Keranigonj | 232 | 18:30 | 213 | 12:00
Ashuganj-400 | 234 | 18:30 | 220 | 12:00 | Khulna(S) | 234 | 17:00 | 220 | 12:00
Baghabari | 236 | 16:00 | 226 | 12:00 | Korerhat | 228 | 05:00 | 217 | 13:00
Barapukuria | 223 | 03:00 | 209 | 19:00 | Madunaghat | 232 | 06:00 | 224 | 12:00
Barapukuria-230 | 223 | 03:00 | 209 | 19:00 | Madunaghat-400 | 233 | 05:00 | 225 | 13:00
Barishal | 229 | 18:00 | 221 | 12:00 | Maniknagar | 230 | 19:00 | 213 | 12:00
Bheramara | 235 | 04:00 | 221 | 12:00 | Meghnaghat | 236 | 04:00 | 224 | 15:00
Bhulta | 231 | 05:00 | 213 | 12:00 | Meghnaghat-400 | 233 | 19:00 | 217 | 12:00
Bibiana | 236 | 06:00 | 226 | 12:00 | Mirsorai | 232 | 05:00 | 223 | 12:00
BIPTC | 237 | 04:00 | 221 | 12:00 | Naogaon | 225 | 14:00 | 214 | 00:00
Bogura | 238 | 18:00 | 228 | 19:30 | Purbasadipur | 222 | 12:00 | 212 | 15:00
Bogura-400 | 237 | 18:00 | 227 | 19:30 | Rajshahi | 234 | 04:00 | 220 | 12:00
Borhanuddin | 232 | 18:00 | 227 | 13:00 | Rampal | 233 | 18:00 | 221 | 13:00
BSRM | 228 | 05:00 | 218 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 228 | 06:00 | 218 | 14:00 | Rampura | 231 | 19:00 | 212 | 13:00
Cumilla(N) | 230 | 19:30 | 217 | 12:00 | Shikalbaha | 230 | 02:00 | 222 | 12:00
Faridpur | 228 | 18:00 | 215 | 12:00 | Shyampur | 232 | 19:00 | 213 | 13:00
Fenchuganj | 242 | 19:30 | 230 | 12:00 | Siddhirganj | 233 | 19:00 | 213 | 12:00
Feni | 228 | 05:00 | 217 | 12:00 | Sirajgonj | 244 | 03:00 | 234 | 12:00
Ghorashal | 238 | 18:30 | 218 | 15:00 | Sreepur | 234 | 18:00 | 215 | 12:00
Ghorashal-230 | 231 | 18:30 | 211 | 13:00 | Tongi | 234 | 19:00 | 212 | 11:00
Gopalganj | 226 | 18:30 | 215 | 12:00
GPH | 229 | 12:00 | 222 | 14:00
Haripur | 232 | 19:30 | 214 | 13:00
Hasnabad | 231 | 18:30 | 212 | 13:00
Hathazari | 230 | 05:00 | 221 | 12:00
Ishurdi | 237 | 02:00 | 224 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 05:00 | 124 | 12:00 | Madunaghat | 134 | 06:00 | 129 | 12:00
Agargaon | 134 | 04:00 | 122 | 12:00 | Magura | 137 | 18:00 | 127 | 13:00
Agrabad | 131 | 03:00 | 126 | 12:00 | Mahasthangarh | 135 | 14:00 | 128 | 19:00
AKS | 130 | 04:00 | 125 | 12:00 | Maijdee | 128 | 05:00 | 120 | 15:00
Aminbazar | 135 | 19:00 | 121 | 12:00 | Manikganj | 137 | 18:00 | 116 | 12:00
Amnura | 137 | 14:00 | 124 | 07:00 | Maniknagar | 135 | 06:00 | 122 | 13:00
Ashuganj | 140 | 18:00 | 132 | 12:00 | Matarbari | 123 | 18:30 | 109 | 23:00
Ashuganj-230 | 140 | 18:00 | 132 | 12:00 | Matuail | 135 | 19:30 | 124 | 12:00
Bagerhat | 134 | 17:00 | 122 | 00:00 | Metrorail_Motijheel | 135 | 06:00 | 122 | 13:00
Bajitpur | 138 | 18:30 | 125 | 11:00 | Metrorail_Uttara | 136 | 18:30 | 120 | 12:00
Bakerganj | 133 | 18:00 | 128 | 12:00 | Millgate | 137 | 18:30 | 121 | 12:00
Bakulia | 133 | 06:00 | 126 | 13:00 | Mirpur | 134 | 18:30 | 121 | 12:00
Banani | 137 | 05:00 | 123 | 12:00 | Mirzapur | 137 | 18:00 | 123 | 13:00
Bangabhaban | 135 | 05:00 | 123 | 12:00 | Mithapukur | 133 | 14:00 | 125 | 19:00
Barapukuria | 130 | 03:00 | 120 | 19:00 | MI_Cement | 132.5 | 19:30 | 118 | 13:00
Barguna | 133 | 06:00 | 128 | 12:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 133 | 06:00 | 126 | 13:00 | Mogbazar | 138 | 05:00 | 125 | 12:00
Barishal-230 | 133 | 18:00 | 127 | 12:00 | Mongla | 134 | 17:00 | 121 | 13:00
Baroaulia | 133 | 06:00 | 127 | 12:00 | Motijheel | 135 | 05:00 | 123 | 12:00
Baroirhat | 132 | 05:00 | 124 | 13:00 | Muktagacha | 135 | 16:00 | 117 | 13:00
Bashundhara | 137 | 05:00 | 120 | 12:00 | Munshiganj | 135 | 02:00 | 122 | 12:00
BashundharaCement | 135 | 19:30 | 123 | 12:00 | Muradnagar | 134 | 20:00 | 120 | 13:00
Beanibazar | 134 | 19:30 | 121 | 15:00 | Mymensingh | 136 | 18:00 | 116 | 00:00
Benapole | 134 | 18:00 | 121 | 13:00 | Nabinagar | 141 | 18:00 | 122 | 15:00
Bhaluka | 137 | 18:00 | 122 | 11:00 | Naogaon | 137 | 14:00 | 129 | 00:00
Bhandaria | 130 | 05:00 | 120 | 22:00 | Narail | 138 | 18:00 | 125 | 13:00
Bhangura | 136 | 18:00 | 128 | 11:00 | Narinda | 135 | 06:00 | 122 | 13:00
Bheramara | 138 | 04:00 | 131 | 12:00 | Narshingdi | 136 | 19:00 | 120 | 12:00
Bheramara(GK) | 137 | 16:00 | 131 | 12:00 | Natore | 136 | 16:00 | 128 | 12:00
Bhulta | 132 | 19:30 | 120 | 12:00 | Nawabganj | 138 | 19:00 | 123 | 13:00
Bog-Sherpur | 137 | 16:00 | 130 | 11:00 | Netrakona | 135 | 18:00 | 115 | 11:00
Bogura | 137 | 16:00 | 132 | 00:00 | New | 138 | 18:30 | 122 | 12:00
Bogura-230 | 138 | 16:00 | 132 | 00:00 | Niamatpur | 137 | 14:00 | 131 | 00:00
Brahmanbaria | 138 | 19:30 | 123 | 12:00 | Noapara | 136 | 18:00 | 124 | 13:00
Cantonment | 134 | 05:00 | 122 | 12:00 | Pabna | 137 | 16:00 | 129 | 11:00
Chandina | 133 | 20:00 | 124 | 12:00 | Palashbari | 133 | 14:00 | 125 | 19:00
Chandpur | 129 | 06:00 | 122 | 12:00 | Panchagarh | 136 | 21:00 | 123 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 134 | 07:00 | 129 | 12:00 | Patiya | 131 | 07:00 | 125 | 12:00
Chapai | 137 | 05:00 | 132 | 00:00 | Patuakhali | 132 | 18:00 | 128 | 00:00
Charsaidpur | 135 | 19:30 | 123 | 13:00 | Payra | 136 | 18:30 | 132 | 12:00
Chauddagram | 130 | 04:00 | 123 | 12:00 | PHP | 131 | 05:00 | 125 | 12:00
Chhatak | 133 | 19:00 | 121 | 00:00 | Postogola | 134 | 19:00 | 121 | 12:00
Chowmuhani | 126 | 04:00 | 122 | 12:00 | Pubail | 141 | 18:30 | 126 | 12:00
Chuadanga | 136 | 17:00 | 124 | 12:00 | Purbachal | 137 | 19:00 | 120 | 12:00
Coxsbazar | 121 | 09:00 | 111 | 23:00 | Purbasadipur | 131 | 12:00 | 121 | 19:00
Cumilla(N) | 133 | 20:00 | 124 | 12:00 | Rahanpur | 139 | 18:00 | 133 | 00:00
Cumilla(S) | 132 | 04:00 | 122 | 19:00 | Rahanpur-400 | 139 | 17:00 | 134 | 00:00
Daganbhuiyan | 130 | 05:00 | 123 | 12:00 | Rahim | 135 | 19:30 | 124 | 12:00
Daudkandi | 132 | 20:00 | 117 | 15:00 | Rajbari | 132 | 18:30 | 121 | 13:00
DhakaUniversity | 137 | 04:00 | 124 | 12:00 | Rajendrapur | 138 | 18:00 | 120 | 12:00
Dhamrai | 141 | 18:00 | 123 | 15:00 | Rajshahi | 134 | 15:00 | 125 | 12:00
Dhanmondi | 136 | 04:00 | 124 | 13:00 | Rajshahi-230 | 135 | 04:00 | 126 | 12:00
Dohazari | 127 | 05:00 | 121 | 12:00 | Ramganj | 127 | 05:00 | 120 | 12:00
Faridpur | 132 | 18:00 | 125 | 00:00 | Rampur | 132 | 05:00 | 125 | 12:00
Fatullah | 134 | 19:30 | 119 | 12:00 | Rampura | 136 | 04:00 | 121 | 13:00
Fenchuganj | 138 | 19:30 | 129 | 13:00 | Rangamati | 133 | 05:00 | 127 | 13:00
Feni | 130 | 05:00 | 122 | 12:00 | Rangpur | 131 | 04:00 | 123 | 19:00
Feni-230 | 130 | 05:00 | 123 | 13:00 | Ruppur | 139 | 02:00 | 131 | 12:00
Ghatail | 134 | 17:00 | 116 | 13:00 | Saidpur | 132 | 12:00 | 122 | 10:00
Ghorashal | 141 | 18:30 | 128 | 12:00 | Santhia | 138 | 17:00 | 129 | 12:00
Goalpara | 137 | 17:00 | 127 | 13:00 | Satkhira | 134 | 17:00 | 123 | 00:00
Gollamari | 137 | 18:00 | 127 | 13:00 | Satmasjid | 133 | 06:00 | 120 | 13:00
Gopalganj | 134 | 18:00 | 126 | 12:00 | Savar | 134 | 18:30 | 118 | 12:00
Gopalganj-400 | 134 | 18:00 | 127 | 12:00 | SevenRings | 140 | 18:30 | 128 | 12:00
Gulshan | 136 | 05:00 | 124 | 12:00 | ShahCement | 135 | 19:30 | 123 | 13:00
Halishahar | 132 | 04:00 | 126 | 12:00 | Shahjadpur | 141 | 17:00 | 133 | 10:00
Haripur | 135 | 19:30 | 124 | 12:00 | Shahjibazar | 138 | 19:30 | 124 | 15:00
HaripurSBU | 136 | 11:00 | 124 | 12:00 | Shahmirpur | 131 | 01:00 | 126 | 12:00
Hasnabad | 133 | 20:00 | 121 | 12:00 | Shariatpur | 132 | 05:00 | 125 | 13:00
Hathazari | 135 | 05:00 | 128 | 12:00 | Sherpur | 137 | 16:00 | 110 | 00:00
Hatirjheel | 137 | 05:00 | 123 | 13:00 | Shikalbaha | 123 | 07:00 | 117 | 12:00
Ishurdi | 139 | 04:00 | 132 | 12:00 | Shikalbaha-230 | 134 | 06:00 | 128 | 12:00
Jaldhaka | 128 | 12:00 | 118 | 19:00 | Shitalakhya | 132.5 | 19:30 | 118 | 13:00
Jamalpur | 136 | 16:00 | 114 | 00:00 | Sholosohor | 133 | 04:00 | 128 | 12:00
Jashore | 135 | 18:00 | 121 | 13:00 | Shyampur | 133 | 19:30 | 122 | 12:00
Jhenaidah | 139 | 17:00 | 127 | 13:00 | Shyampur-230 | 134 | 19:00 | 122 | 12:00
Jhenaidah-230 | 138 | 17:00 | 127 | 13:00 | Siddhirganj | 136 | 19:30 | 124 | 12:00
Joydebpur | 141 | 18:30 | 124 | 12:00 | Sirajganj | 136 | 17:00 | 127 | 12:00
Joypurhat | 134 | 14:00 | 127 | 00:00 | Sonargaon | 135 | 19:30 | 122 | 12:00
Juldah | 132 | 08:00 | 127 | 12:00 | Sreemongol | 138 | 19:30 | 124 | 12:00
Kabirpur | 142 | 18:00 | 117 | 12:00 | Sreepur | 138 | 18:00 | 124 | 11:00
Kachua | 130 | 05:00 | 123 | 15:00 | Srinagar | 138 | 18:00 | 124 | 13:00
Kaliakoir | 142 | 18:00 | 127 | 11:00 | SSM | 138 | 05:00 | 130 | 15:00
Kaliganj | 137 | 17:00 | 126 | 13:00 | Sunamganj | 132 | 19:00 | 120 | 00:00
Kallyanpur | 134 | 18:30 | 120 | 12:00 | Sylhet | 135 | 19:30 | 125 | 13:00
Kalurghat | 134 | 06:00 | 128 | 14:00 | Sylhet-132 | 133 | 19:00 | 126 | 15:00
Kamrangirchar | 138 | 19:00 | 118 | 13:00 | Tangail | 134 | 17:00 | 119 | 13:00
Kaptai | 137 | 7:00 | 132 | 11:00 | Taraganj | 130 | 12:00 | 122 | 10:00
Kasba | 133 | 19:30 | 119 | 15:00 | Tasnim | 135 | 19:30 | 122 | 12:00
Kazla | 135 | 06:00 | 121 | 13:00 | Thakurgaon | 133 | 12:00 | 122 | 19:00
Keranigonj | 138 | 19:00 | 125 | 12:00 | TK | 134 | 04:00 | 129 | 14:00
Khagrachori | 133 | 06:00 | 127 | 12:00 | Tongi | 140 | 19:00 | 125 | 11:00
Khulna | 136 | 17:00 | 126 | 13:00 | Ullahpara | 138 | 17:00 | 128 | 11:00
Khulna(S) | 137 | 17:00 | 128 | 12:00 | Ullon | 137 | 05:00 | 123 | 12:00
Khulshi | 131 | 06:00 | 124 | 12:00 | Uttara | 137 | 18:30 | 120 | 12:00
Kishoreganj | 137 | 18:00 | 122 | 12:00 | UttaraNew | 136 | 18:30 | 120 | 12:00
Kodda | 140 | 18:00 | 122 | 12:00 | Zigatola | 138 | 19:00 | 124 | 12:00
Korerhat | 132 | 03:00 | 127 | 12:00
KSRM | 133 | 02:00 | 127 | 12:00
Kulaura | 137 | 19:30 | 128 | 13:00
Kurigram | 130 | 12:00 | 119 | 19:00
Kushtia | 138 | 17:00 | 128 | 13:00
Laksam | 130 | 05:00 | 122 | 13:00
Lakshmipur | 126 | 04:00 | 120 | 15:00
Lalbag | 138 | 19:00 | 125 | 12:00
Lalmonirhat | 130 | 12:00 | 120 | 18:00
Madanganj | 135 | 19:30 | 123 | 12:00
Madaripur | 134 | 18:00 | 128 | 12:00
Madartek | 136 | 06:00 | 124 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division