## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 08-05-2026 | [28 empty] | Date: | 08-05-2026 | [28 empty] | Date: | 08-05-2026 | [28 empty] | Date: | 08-05-2026 | [28 empty] | Date: | 08-05-2026 | [17 empty] | Date: | 08-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [17 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 294 | 0 | 0 | 71 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 68 | 19 | 14 | 0 | 485 | 0 | 0 | 31 | 0 | 4 | 49 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 4 | 840 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1060 | 0 | 0 | 0 | 240 | 357 | 240 | 51 | 0 | 196 | 0 | 0 | 104 | 0 | 0 | 5 | 0 | 140 | 0 | 0 | 0 | 305 | 0 | 369 | 42 | 30 | 156 | 0 | 17 | 0 | 86 | 25 | 100 | 0 | 100 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 6567 | 879 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 915 | 0 | 0 | 0 | 1353.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 50 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 128 | 220 | 0 | 351 | 864 | 0 | 5750.2 | 12317.2 | 79.09
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 295 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 51 | 20 | 14 | 0 | 490 | 0 | 0 | 21 | 0 | 2 | 49 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 12 | 680 | 0 | 0 | 6 | 0 | 0 | 220 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 240 | 356 | 240 | 51 | 0 | 198 | 0 | 0 | 150 | 0 | 0 | 19 | 0 | 144 | 0 | 0 | 0 | 300 | 0 | 369 | 42 | 30 | 154 | 0 | 17 | 0 | 86 | 25 | 100 | 0 | 100 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 6476 | 880 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1009 | 0 | 0 | 0 | 1400.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 370 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211 | 128 | 220 | 0 | 380 | 930 | 0 | 5907.58 | 12383.58 | 79.09
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 257 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 51 | 0 | 14 | 0 | 420 | 0 | 0 | 18 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 590 | 0 | 0 | 6 | 0 | 0 | 221 | 0 | 0 | 0 | 1085 | 0 | 0 | 0 | 260 | 356 | 240 | 51 | 0 | 190 | 0 | 0 | 152 | 0 | 0 | 19 | 0 | 142 | 0 | 0 | 0 | 305 | 0 | 369 | 42 | 30 | 149 | 0 | 17 | 0 | 86 | 25 | 100 | 0 | 100 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 6212 | 880 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 0 | 0 | 0 | 1335.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 370 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 128 | 220 | 0 | 380 | 901 | 0 | 5782.92 | 11994.92 | 79.09
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 264 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 34 | 0 | 14 | 0 | 425 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 540 | 0 | 0 | 6 | 0 | 0 | 223 | 0 | 0 | 0 | 1065 | 0 | 0 | 0 | 315 | 356 | 88 | 51 | 0 | 195 | 0 | 0 | 154 | 0 | 0 | 19 | 0 | 134 | 0 | 0 | 0 | 295 | 0 | 369 | 42 | 30 | 146 | 0 | 17 | 0 | 86 | 25 | 100 | 0 | 100 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 5983 | 880 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 0 | 0 | 0 | 1291.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 370 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 128 | 220 | 0 | 363 | 850 | 0 | 5660.2 | 11643.2 | 79.09
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 239 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 34 | 21 | 14 | 0 | 400 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 540 | 0 | 0 | 6 | 0 | 0 | 223 | 0 | 0 | 0 | 1057 | 0 | 0 | 0 | 370 | 355 | 55 | 51 | 0 | 192 | 0 | 0 | 154 | 0 | 0 | 19 | 0 | 126 | 0 | 0 | 0 | 300 | 0 | 375 | 42 | 30 | 141 | 0 | 17 | 0 | 86 | 25 | 100 | 0 | 100 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 5941 | 880 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 0 | 0 | 0 | 1176.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 370 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 128 | 220 | 0 | 336 | 757 | 0 | 5429.63 | 11370.63 | 79.1
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 265 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 17 | 22 | 14 | 0 | 460 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 18 | 540 | 0 | 0 | 6 | 0 | 0 | 223 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 340 | 356 | 0 | 51 | 0 | 197 | 0 | 0 | 153 | 0 | 0 | 19 | 0 | 130 | 0 | 0 | 0 | 300 | 0 | 375 | 42 | 30 | 144 | 0 | 17 | 0 | 86 | 25 | 100 | 0 | 100 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 5893 | 879 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 901 | 0 | 0 | 0 | 1121.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 370 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 128 | 220 | 0 | 310 | 664 | 0 | 5158.26 | 11051.26 | 79.1
06:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 247 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 2 | 50 | 22 | 14 | 0 | 425 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 41 | 0 | 15 | 540 | 0 | 0 | 6 | 0 | 0 | 223 | 0 | 0 | 0 | 860 | 0 | 0 | 0 | 330 | 355 | 0 | 51 | 0 | 201 | 0 | 0 | 151 | 0 | 0 | 19 | 0 | 114 | 0 | 4 | 0 | 300 | 0 | 367 | 42 | 30 | 141 | 1 | 17 | 0 | 86 | 30 | 100 | 0 | 101 | 0 | 9 | 78 | 0 | 0.1 | 2.95 | 0 | 5717.21 | 879 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 795 | 0 | 0 | 0 | 986.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.28 | 5 | 0 | 0 | 1.83 | 130 | 0 | 0 | 0 | 130 | 0 | 370 | 0 | 0.21 | 0 | 48 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 11 | 0.04 | 0 | 173 | 128 | 220 | 0 | 304 | 622 | 0 | 4893.53 | 10610.74 | 79.1
07:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 284 | 0 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 9 | 86 | 22 | 14 | 0 | 480 | 0 | 0 | 11 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.89 | 41 | 0 | 10 | 540 | 0 | 0 | 6 | 0 | 0 | 223 | 0 | 0 | 0 | 795 | 2 | 0 | 0 | 337 | 356 | 0 | 51 | 0 | 199 | 0 | 0 | 152 | 0 | 0 | 19 | 0 | 114 | 0 | 19 | 0 | 310 | 0 | 367 | 42 | 30 | 151 | 3 | 17 | 0 | 86 | 30 | 101 | 0 | 101 | 0 | 9 | 78 | 0 | 0.35 | 9.97 | 0 | 5912.21 | 880 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 777 | 0 | 0 | 0 | 985.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.47 | 22 | 0 | 0 | 12 | 130 | 0 | 0 | 0 | 130 | 0 | 370 | 0 | 1.17 | 0 | 48 | 0 | 7 | 0 | 0 | 0 | 0 | 1.2 | 37 | 0.16 | 0 | 190 | 128 | 220 | 0 | 311 | 636 | 0 | 5012.11 | 10924.32 | 79.1
08:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 253 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 0 | 15 | 86 | 22 | 14 | 0 | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.22 | 41 | 0 | 2 | 530 | 0 | 0 | 6 | 0 | 0 | 222 | 0 | 0 | 0 | 770 | 3 | 0 | 0 | 335 | 356 | 0 | 51 | 0 | 199 | 0 | 0 | 148 | 0 | 0 | 19 | 0 | 116 | 0 | 39 | 0 | 305 | 0 | 367 | 42 | 30 | 145 | 6 | 17 | 0 | 86 | 30 | 101 | 0 | 100 | 0 | 9 | 78 | 0 | 0.89 | 17.43 | 0 | 5813.54 | 880 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 779 | 0 | 0 | 0 | 929.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.59 | 45 | 0 | 0 | 31.13 | 130 | 0 | 0 | 0 | 130 | 0 | 350 | 0 | 2.73 | 0 | 49 | 0 | 16 | 0 | 0 | 0 | 0 | 0.2 | 78 | 0.35 | 0 | 178 | 110 | 180 | 0 | 308 | 635 | 0 | 5002.67 | 10816.21 | 79.11
09:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 280 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 86 | 22 | 0 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.33 | 42 | 0 | 3 | 535 | 0 | 0 | 6 | 0 | 0 | 219 | 0 | 0 | 0 | 740 | 10 | 0 | 0 | 320 | 357 | 0 | 20 | 0 | 202 | 0 | 0 | 147 | 0 | 0 | 19 | 0 | 116 | 0 | 54 | 0 | 305 | 0 | 357 | 42 | 30 | 148 | 9 | 17 | 0 | 53 | 30 | 100 | 0 | 20 | 0 | 9 | 78 | 0 | 1.7 | 36.96 | 0 | 5694.99 | 880 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 776 | 0 | 0 | 0 | 924.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.47 | 79 | 0 | 0 | 47.71 | 130 | 0 | 0 | 0 | 130 | 0 | 350 | 0 | 4.24 | 0 | 50 | 0 | 24 | 0 | 0 | 0 | 0 | 0.5 | 113 | 0.52 | 0 | 182 | 100 | 180 | 0 | 310 | 620 | 0 | 5108.71 | 10803.7 | 79.11
10:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 277 | 0 | 0 | 82 | 0 | 45 | 0 | 8 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 31 | 86 | 22 | 0 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.93 | 43 | 0 | 2 | 540 | 0 | 0 | 6 | 0 | 0 | 217 | 0 | 0 | 0 | 745 | 11 | 0 | 8 | 320 | 356 | 0 | 20 | 0 | 200 | 0 | 0 | 145 | 0 | 0 | 19 | 0 | 124 | 0 | 51 | 0 | 305 | 0 | 345 | 42 | 30 | 149 | 11 | 17 | 0 | 53 | 30 | 100 | 0 | 20 | 0 | 9 | 87 | 0 | 1.9 | 37.1 | 0 | 5800.93 | 879 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 777 | 0 | 0 | 0 | 927.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 94 | 0 | 0 | 62.35 | 130 | 0 | 0 | 0 | 130 | 0 | 350 | 0 | 5.39 | 0 | 47 | 0 | 18 | 0 | 0 | 0 | 0 | 1.2 | 147 | 0.61 | 0 | 180 | 100 | 180 | 0 | 315 | 610 | 0 | 5187.98 | 10988.91 | 79.11
11:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 295 | 0 | 0 | 88 | 0 | 45 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 28 | 86 | 22 | 7 | 0 | 495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.05 | 43 | 0 | 3 | 560 | 0 | 0 | 6 | 0 | 0 | 214 | 0 | 0 | 0 | 942 | 14 | 0 | 8 | 335 | 355 | 0 | 25 | 0 | 201 | 23 | 0 | 144 | 0 | 0 | 19 | 0 | 134 | 0 | 51 | 0 | 310 | 0 | 346 | 42 | 30 | 153 | 12 | 17 | 0 | 83 | 30 | 100 | 0 | 17 | 0 | 9 | 87 | 0 | 2.1 | 24.02 | 0 | 6168.17 | 879 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 863 | 0 | 0 | 0 | 997.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.31 | 65 | 0 | 0 | 59.79 | 130 | 0 | 0 | 0 | 130 | 0 | 350 | 0 | 5.71 | 0 | 51 | 0 | 4 | 0 | 0 | 0 | 0 | 3.1 | 123 | 0.73 | 0 | 210 | 127 | 220 | 0 | 332 | 640 | 0 | 5417.93 | 11586.1 | 79.11
12:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 285 | 0 | 0 | 90 | 0 | 65 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 36 | 104 | 22 | 14 | 0 | 470 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2.43 | 43 | 0 | 3 | 550 | 0 | 0 | 6 | 0 | 0 | 213 | 0 | 0 | 0 | 1020 | 9 | 0 | 80 | 335 | 354 | 0 | 45 | 1 | 201 | 30 | 0 | 144 | 0 | 0 | 19 | 0 | 144 | 0 | 65 | 0 | 310 | 0 | 347 | 42 | 30 | 151 | 12 | 17 | 0 | 83 | 30 | 100 | 0 | 20 | 0 | 9 | 87 | 0 | 2.29 | 42.3 | 0 | 6382.02 | 880 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.75 | 917 | 0 | 0 | 0 | 1021.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.99 | 100 | 0 | 0 | 64.1 | 130 | 0 | 0 | 0 | 130 | 0 | 350 | 0 | 5.69 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 184 | 0.23 | 0 | 211 | 127 | 220 | 0 | 354 | 780 | 0 | 5782.98 | 12165 | 79.12
13:00 | 0 | 34 | 28 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 247 | 15 | 0 | 103 | 0 | 125 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 33 | 123 | 22 | 14 | 0 | 415 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 3.77 | 43 | 0 | 14 | 558 | 0 | 0 | 6 | 0 | 0 | 213 | 0 | 0 | 0 | 1130 | 8 | 1 | 120 | 320 | 356 | 0 | 51 | 14 | 201 | 39 | 0 | 143 | 0 | 0 | 19 | 0 | 150 | 0 | 51 | 0 | 305 | 0 | 346 | 40 | 30 | 150 | 12 | 17 | 0 | 83 | 28 | 100 | 0 | 20 | 0 | 9 | 86 | 0 | 1.35 | 32.73 | 0 | 6575.85 | 879 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 1030 | 0 | 0 | 0 | 1255.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.14 | 92 | 0 | 0 | 30.95 | 130 | 0 | 0 | 0 | 130 | 0 | 350 | 0 | 4.2 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1 | 0.69 | 0 | 233 | 127 | 180 | 0 | 378 | 890 | 0 | 6001.46 | 12577.31 | 79.12
14:00 | 0 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 243 | 15.5 | 0 | 98 | 0 | 60 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 20 | 105 | 22 | 14 | 0 | 425 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 3.3 | 43 | 0 | 10 | 558 | 0 | 0 | 6 | 0 | 0 | 211 | 0 | 0 | 0 | 910 | 14 | 24 | 120 | 310 | 320 | 0 | 51 | 29 | 198 | 39 | 0 | 142 | 0 | 0 | 19 | 0 | 126 | 0 | 55 | 0 | 305 | 0 | 321 | 39 | 30 | 138 | 6 | 17 | 0 | 83 | 28 | 101 | 0 | 20 | 0 | 9 | 87 | 0 | 2.14 | 30.89 | 0 | 6148.83 | 879 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 956 | 0 | 0 | 0 | 1117.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.15 | 95 | 0 | 0 | 53.63 | 130 | 0 | 0 | 0 | 130 | 0 | 260 | 0 | 4.73 | 0 | 48 | 0 | 32 | 0 | 0 | 0 | 0 | 7.3 | 83 | 0.63 | 0 | 222 | 100 | 180 | 0 | 363 | 950 | 0 | 5838.31 | 11987.14 | 79.12
15:00 | 0 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 300 | 16.3 | 0 | 77 | 0 | 60 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 26 | 105 | 23 | 14 | 0 | 485 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 2.64 | 43 | 0 | 5 | 610 | 0 | 0 | 6 | 0 | 0 | 212 | 0 | 0 | 0 | 975 | 10 | 24 | 120 | 320 | 349 | 0 | 51 | 30 | 201 | 36 | 0 | 142 | 0 | 0 | 19 | 0 | 130 | 0 | 41 | 0 | 310 | 0 | 321 | 39 | 30 | 149 | 9 | 17 | 0 | 82 | 28 | 100 | 0 | 20 | 0 | 9 | 87 | 0 | 1.6 | 22.73 | 0 | 6438.27 | 879 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 904 | 0 | 0 | 0 | 1118.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.37 | 80 | 0 | 0 | 43.9 | 130 | 0 | 0 | 0 | 130 | 0 | 300 | 0 | 3.88 | 0 | 48 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 151 | 0.25 | 0 | 248 | 100 | 180 | 0 | 355 | 960 | 0 | 5864.36 | 12302.63 | 79.12
16:00 | 0 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 231 | 16.3 | 0 | 77 | 0 | 60 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 15 | 105 | 22 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1.72 | 43 | 0 | 5 | 740 | 0 | 0 | 6 | 0 | 0 | 212 | 0 | 0 | 0 | 955 | 9 | 24 | 122 | 295 | 351 | 0 | 51 | 30 | 193 | 38 | 0 | 143 | 0 | 0 | 19 | 0 | 122 | 0 | 28 | 0 | 310 | 0 | 321 | 42 | 30 | 145 | 5 | 17 | 0 | 82 | 28 | 100 | 0 | 95 | 0 | 9 | 88 | 20 | 1 | 22.81 | 0 | 6409.83 | 879 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 905 | 0 | 0 | 0 | 1064.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.37 | 50 | 0 | 0 | 23.86 | 130 | 0 | 0 | 0 | 130 | 0 | 300 | 0 | 1.95 | 0 | 49 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 98 | 0.34 | 0 | 219 | 100 | 180 | 0 | 370 | 985 | 0 | 5687.18 | 12097.01 | 79.13
17:00 | 0 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 242 | 15.2 | 0 | 77 | 0 | 60 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 7 | 105 | 22 | 14 | 0 | 420 | 0 | 0 | 0 | 0 | 3 | 17 | 0 | 0 | 0 | 0 | 0.78 | 42 | 0 | 6 | 770 | 0 | 0 | 6 | 0 | 0 | 214 | 0 | 0 | 0 | 893 | 2 | 24 | 122 | 314 | 350 | 0 | 51 | 30 | 199 | 40 | 0 | 143 | 0 | 0 | 19 | 0 | 136 | 0 | 12 | 0 | 310 | 0 | 321 | 42 | 30 | 140 | 2 | 17 | 0 | 82 | 28 | 100 | 0 | 93 | 0 | 9 | 88 | 20 | 0.4 | 9.65 | 0 | 6384.03 | 879 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 904 | 0 | 0 | 0 | 988.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.01 | 7 | 0 | 0 | 13.55 | 130 | 0 | 0 | 0 | 130 | 0 | 300 | 0 | 1.3 | 0 | 47 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 47 | 0.17 | 0 | 223 | 100 | 180 | 0 | 336 | 895 | 0 | 5335.59 | 11719.62 | 79.13
18:00 | 0 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 285 | 15.5 | 0 | 77 | 0 | 60 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 1 | 105 | 22 | 14 | 0 | 480 | 0 | 0 | 0 | 0 | 1 | 17 | 0 | 0 | 0 | 0 | 0.06 | 40 | 0 | 2 | 800 | 0 | 0 | 10 | 1 | 0 | 215 | 0 | 0 | 0 | 884 | 0 | 24 | 122 | 319 | 300 | 0 | 51 | 30 | 204 | 42 | 0 | 143 | 0 | 0 | 19 | 0 | 134 | 0 | 2 | 0 | 275 | 0 | 334 | 42 | 30 | 141 | 0 | 17 | 0 | 53 | 30 | 102 | 0 | 93 | 0 | 9 | 88 | 18 | 0.1 | 1.28 | 10 | 6406.94 | 880 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 908 | 0 | 0 | 0 | 967.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97 | 5 | 0 | 0 | 2.3 | 130 | 0 | 0 | 0 | 130 | 0 | 250 | 0 | 0.19 | 0 | 47 | 0 | 1 | 0 | 0 | 0 | 0 | 0.4 | 9 | 0.02 | 0 | 229 | 100 | 180 | 0 | 309 | 790 | 0 | 5063.34 | 11470.28 | 79.13
19:00 | 0 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 285 | 17 | 1 | 83 | 0 | 140 | 4 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 105 | 22.5 | 14 | 0 | 460 | 0 | 0 | 0 | 0 | 5 | 50 | 0 | 0 | 0 | 0 | 0 | 40 | 4 | 16 | 980 | 0 | 0 | 19 | 15 | 14 | 215 | 0 | 0 | 0 | 1160 | 0 | 30 | 155 | 325 | 356 | 0 | 51 | 32 | 198 | 42 | 2 | 145 | 1 | 4 | 19 | 0 | 150 | 0 | 0 | 23 | 260 | 0 | 334 | 42 | 30 | 153 | 0 | 17 | 0 | 84 | 25 | 100 | 0 | 100 | 0 | 9 | 87 | 18 | 0 | 0 | 12 | 7248.5 | 879 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1130 | 0 | 0 | 0 | 1357.29 | 0 | 0 | 0 | 7 | 1 | 0 | 93 | 21 | 0 | 0 | 0 | 20 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 48 | 48 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 128 | 220 | 0 | 349 | 820 | 0 | 6196.29 | 13444.79 | 79.13
19:30 | 0 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 239 | 17 | 17 | 113 | 0 | 145 | 30 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 35 | 303 | 0 | 0 | 0 | 105 | 22.5 | 14 | 0 | 420 | 0 | 0 | 30 | 0 | 11 | 50 | 0 | 0 | 0 | 0 | 0 | 39 | 32 | 16 | 895 | 0 | 0 | 19 | 17 | 48 | 215 | 0 | 0 | 0 | 1160 | 0 | 70 | 158 | 340 | 356 | 0 | 51 | 43 | 195 | 40 | 40 | 146 | 51 | 18 | 19 | 0 | 146 | 0 | 0 | 0 | 320 | 0 | 334 | 42 | 30 | 147 | 0 | 17 | 0 | 84 | 25 | 100 | 0 | 102 | 0 | 9 | 88 | 18 | 0 | 0 | 12 | 7446.5 | 879 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1225 | 0 | 0 | 0 | 1322.36 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 47 | 45 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222 | 128 | 220 | 0 | 410 | 1005 | 0 | 6408.36 | 13854.86
20:00 | 0 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 248 | 17 | 17 | 113 | 0 | 145 | 30 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 105 | 22.5 | 14 | 0 | 415 | 0 | 0 | 37 | 0 | 8 | 50 | 0 | 0 | 0 | 0 | 0 | 40 | 33 | 19 | 825 | 0 | 0 | 19 | 17 | 48 | 215 | 0 | 0 | 0 | 1160 | 0 | 70 | 157 | 385 | 356 | 0 | 51 | 39 | 198 | 43 | 58 | 146 | 45 | 18 | 19 | 0 | 144 | 0 | 0 | 0 | 320 | 0 | 334 | 42 | 30 | 141 | 0 | 17 | 0 | 84 | 25 | 101 | 0 | 102 | 0 | 9 | 86 | 18 | 0 | 0 | 12 | 7440.5 | 879 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 0 | 0 | 0 | 1263.15 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 47 | 43 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 128 | 220 | 0 | 434 | 1030 | 0 | 6353.15 | 13793.65 | 79.13
21:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 264 | 17 | 0 | 113 | 0 | 145 | 30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 51 | 22.5 | 14 | 0 | 500 | 0 | 0 | 58 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 41 | 32 | 21 | 983 | 0 | 0 | 19 | 17 | 50 | 215 | 0 | 0 | 0 | 1160 | 0 | 70 | 120 | 315 | 356 | 0 | 51 | 27 | 217 | 40 | 68 | 147 | 51 | 18 | 19 | 0 | 156 | 0 | 0 | 0 | 310 | 0 | 334 | 42 | 30 | 151 | 0 | 17 | 0 | 84 | 20 | 100 | 0 | 102 | 0 | 37 | 115 | 18 | 0 | 0 | 12 | 7569.5 | 879 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1210 | 0 | 0 | 0 | 1330.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 48 | 33 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 128 | 220 | 0 | 432 | 1102 | 0 | 6417.47 | 13986.97 | 79.13
22:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 290 | 0 | 0 | 113 | 0 | 145 | 30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 35 | 303 | 0 | 0 | 0 | 51 | 22.5 | 14 | 0 | 520 | 0 | 0 | 56 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 42 | 33 | 24 | 925 | 0 | 0 | 19 | 17 | 47 | 216 | 0 | 0 | 0 | 1160 | 0 | 70 | 71 | 335 | 356 | 0 | 51 | 12 | 200 | 40 | 69 | 146 | 47 | 18 | 19 | 0 | 158 | 0 | 0 | 0 | 310 | 0 | 334 | 42 | 30 | 149 | 0 | 17 | 0 | 84 | 20 | 100 | 0 | 102 | 0 | 37 | 117 | 16 | 0 | 0 | 12 | 7459.5 | 879 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1214 | 0 | 0 | 0 | 1333.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 49 | 31 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 127 | 220 | 0 | 438 | 1080 | 0 | 6413.45 | 13872.95 | 79.13
23:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 306 | 0 | 0 | 113 | 0 | 145 | 30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 303 | 0 | 0 | 0 | 51 | 22.5 | 14 | 0 | 555 | 0 | 0 | 52 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 43 | 32 | 26 | 905 | 0 | 0 | 19 | 0 | 49 | 216 | 0 | 0 | 0 | 1160 | 0 | 70 | 26 | 393 | 356 | 0 | 51 | 5 | 204 | 40 | 56 | 147 | 48 | 18 | 19 | 0 | 160 | 0 | 0 | 0 | 305 | 0 | 334 | 42 | 30 | 150 | 0 | 17 | 0 | 84 | 20 | 98 | 0 | 102 | 0 | 37 | 117 | 10 | 0 | 0 | 12 | 7444.5 | 879 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1213 | 0 | 0 | 0 | 1323.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 50 | 32 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 127 | 220 | 0 | 433 | 1050 | 0 | 6380.91 | 13825.41 | 79.13
Total KWH | 0 | 530880 | 589920 | 0 | 0 | 0 | 0 | 0 | 8481600 | 0 | 6817010 | 139320 | 25200 | 2198736 | 7200 | 1367204 | 157254 | 78382 | 424800 | 0 | 0 | 0 | 0 | 0 | 139699 | 7274067 | 0 | 0 | 243599 | 1966800 | 481200 | 312840 | 0 | 11161818.18 | 0 | 0 | 381120 | 0 | 64800 | 375599 | 0 | 0 | 0 | 0 | 27719 | 1012380 | 178100 | 333600 | 16138181.82 | 0 | 0 | 222240 | 71575.2 | 265127 | 5118415 | 0 | 0 | 0 | 23803634 | 91125 | 550327 | 1354909 | 7886500 | 8783700 | 744000 | 1190428 | 287520 | 4944000 | 495072 | 290880 | 3492480 | 245760 | 96600 | 455050 | 0 | 3231360 | 0 | 474636 | 24304 | 7350000 | 0 | 8479000 | 989000 | 724800 | 3543463.64 | 85983 | 390960 | 0 | 1882560 | 617280 | 2314500 | 0 | 1797920 | 0 | 301200 | 2073600 | 128640 | 15500 | 314910 | 71280 | 156109267.84 | 21261818 | 2476224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 776160 | 23105450 | 0 | 0 | 0 | 27566546 | 0 | 0 | 0 | 23712 | 43200 | 0 | 54198 | 9729 | 0 | 419640 | 774720 | 13181 | 0 | 436512 | 3268091 | 0 | 0 | 0 | 3413068 | 0 | 8445600 | 0 | 39060 | 0 | 1134109 | 242830 | 133308 | 367536 | 0 | 0 | 0 | 18428.64 | 104112 | 5301 | 0 | 5061000 | 2849000 | 5265800 | 0 | 8676364 | 20762181.82 | 0 | 136746879.46 | 292856147.3

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 09-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-05-2026 | during | 09-05-2026 | during | 09-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 366 | 346 | 412 | 412 | 380 | 380 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55 | 15 | 55 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 304 | 300 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 7 | 7 | 32 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17 | 53.97 | 53.97 | 17 | 36 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 46 | 46 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 22 | 22.5 | 33 | 33 | 21 | 21 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 14 | 14 | 14 | 14 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 16 | 52 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 65 | 145 | 300 | 300 | 48 | 294 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 90 | 113 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 17 | 105 | 105 | 17 | 34 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 17 | 162 | 162 | 35 | 88 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 36 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 470 | 500 | 584 | 584 | 491 | 491 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 285 | 264 | 718 | 718 | 335 | 335 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 104 | 51 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1833 | 1896.5 | 5754.22 | 5724.22 | 2129 | 2571
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 0 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 9 | 0 | 15 | 0 | 15 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 50 | 50 | 19 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 43 | 41 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 213 | 215 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 50 | 105 | 105 | 34 | 51 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 21 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 58 | 108 | 108 | 12 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.43 | 0 | 4.04 | 0 | 4.04 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 32 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 17 | 54 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1020 | 1160 | 1224 | 1224 | 1204 | 1204 | AGC
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 2 | 0 | 1 | 2 | 1 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 550 | 983 | 730 | 1150 | 670 | 1090 | AGC
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1848.43 | 2646 | 3513.9 | 4006.86 | 2515.04 | 3144
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 201 | 217 | 221.25 | 221.25 | 205.25 | 205.25 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 354 | 356 | 350.01 | 350.01 | 350.01 | 350.01 | FGMO not available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 335 | 315 | 393 | 393 | 340 | 340 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 30 | 40 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 1 | 27 | 52.82 | 52.82 | 31 | 31 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 80 | 120 | 195 | 195 | 121 | 121 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 45 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 70 | 150 | 150 | 25 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 42 | 42 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 144 | 147 | 163 | 163 | 87 | 87 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 51 | 200 | 200 | 17 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 144 | 156 | 84 | 76 | 84 | 76 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 20 | 52 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 17 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 18 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 68 | 115 | 115 | 17 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 65 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1418 | 1655 | 2422.43 | 2354.43 | 1486.26 | 1895.26
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-05-2026 | during | 09-05-2026 | during | 09-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 18 | 157.5 | 157.5 | 0 | 0 | Under Maintenance
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.29 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 87 | 115 | 90 | 90 | 10 | 10 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 37 | 10 | 10 | 10 | 10 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 42.3 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 140.59 | 182 | 380.9 | 334 | 121.4 | 49
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 41 | 41 | 41 | 41 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 0 | 0 | 30 | 30 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 151 | 151 | 163 | 163 | 147 | 147 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 100 | 100 | 100 | 100 | 100 | 100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 20 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 84 | 86 | 86 | 81 | 81 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 20 | 102 | 100 | 100 | 100 | 100 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 17 | 17 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 347 | 334 | 360 | 370 | 350 | 350 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1142 | 1190 | 1266 | 1276 | 1203 | 1203
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 880 | 879 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 36 | 36 | 36 | 36 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 92 | 140 | 410 | 410 | 80 | 80 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 101.75 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 917 | 1210 | 1234.2 | 1234.2 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1990.75 | 2229 | 3590.2 | 3500.2 | 2447.1 | 2357.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 354 | 432 | 400 | 500 | 380 | 480 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 127 | 128 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 780 | 1102 | 1244 | 1244 | 1184 | 1184 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 211 | 236 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.23 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1692.23 | 2118 | 2562 | 2661 | 2235 | 2334
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 59.99 | 0 | 62.55 | 0 | 62.55 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 130 | 130 | 214 | 214 | 131 | 131 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Fuel shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 130 | 220 | 220 | 131 | 131 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 350 | 350 | 413.79 | 413.79 | 370 | 370 | Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 25 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0.03 | 0.03 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 92 | 92 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.69 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1021.52 | 1330.47 | 1435.88 | 1435.88 | 1356 | 1356 | AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 64.1 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1861.3 | 1940.47 | 3224.27 | 2994.87 | 2379.43 | 2235.03
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 53 | 48 | 50 | 50 | 50 | 50 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 49 | 113 | 113 | 35 | 113 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.7 | 0 | 5.4 | 0 | 5.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 33 | 115 | 115 | 0 | 70 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 0 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 184 | 0 | 195.88 | 0 | 195.88 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 238.7 | 130 | 543.28 | 312 | 316.28 | 233
System Total |  |  |  |  | 28823.2 | 29270.237 | 12165 | 13986.97 | 23257.2 | 23163.58 | 14832.51 | 16021.39
Forecast Scenario (09-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13400 |  | 0 |  | 13400
|  |  |  | 1:00 | 13110 |  | 0 |  | 13110
|  |  |  | 2:00 | 12950 |  | 0 |  | 12950
|  |  |  | 3:00 | 12480 |  | 0 |  | 12480
|  |  |  | 4:00 | 12320 |  | 0 |  | 12320
|  |  |  | 5:00 | 11910 |  | 0 |  | 11910
|  |  |  | 6:00 | 11880 |  | 0 |  | 11880
|  |  |  | 7:00 | 12140 |  | 0 |  | 12140
|  |  |  | 8:00 | 12150 |  | 0 |  | 12150
|  |  |  | 9:00 | 12270 |  | 0 |  | 12270
|  |  |  | 10:00 | 12130 |  | 0 |  | 12130
|  |  |  | 11:00 | 12470 |  | 0 |  | 12470
|  |  |  | 12:00 | 13100 |  | 0 |  | 13100
|  |  |  | 13:00 | 13340 |  | 0 |  | 13340
|  |  |  | 14:00 | 13360 |  | 0 |  | 13360
|  |  |  | 15:00 | 13340 |  | 0 |  | 13340
|  |  |  | 16:00 | 13280 |  | 0 |  | 13280
|  |  |  | 17:00 | 13160 |  | 0 |  | 13160
|  |  |  | 18:00 | 13300 |  | 0 |  | 13300
|  |  |  | 18:30 | 13700 |  | 0 |  | 13700
|  |  |  | 19:00 | 14180 |  | 0 |  | 14180
|  |  |  | 19:30 | 14220 |  | 0 |  | 14220
|  |  |  | 20:00 | 14300 |  | 0 |  | 14300
|  |  |  | 21:00 | 14300 |  | 0 |  | 14300
|  |  |  | 22:00 | 14100 |  | 0 |  | 14100
|  |  |  | 23:00 | 13980 |  | 0 |  | 13980
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 13100.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14300.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14300.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 312.95 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:52 hrs on 09-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 08-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12165 | MW | 12:00 Hr. | Energy Generated |  |  | 292.8561 |  | MKWHr.
| Day Peak Demand |  |  | 12165 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.429 |  | MKWHr.
| Evening Peak Generation |  |  | 13986.97 | MW | 21:00 Hr. | Energy Demand |  |  | 293.2851 |  | MKWHr.
| Evening Peak Demand |  |  | 13986.97 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35 |  | °C
| Minimum Generation of the Day |  |  | 10610.74 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 925.81 |  | MMCFD
| Maximum Generation of the Day |  |  | 13986.97 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 5.7306 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.5285 | 0 | 7.6254 | 0 | 0 | 0.2436 | 0 | 0 | 42.3975 | Gas | 123.5501 | Gas | 433712084.2494
| Chattogram Zone |  |  | 5.452 | 39.9418 | 1.4938 | 0 | 1.0124 | 0.11884 | 0 | 0.0648 | 48.0836 | Coal | 98.6809 | Coal | 658565978.831
| Cumilla Zone |  |  | 29.6337 | 0 | 1.2079 | 0 | 0 | 0.47464 | 3.2314 | 0 | 34.5475 | HFO | 13.5275 | HFO | 224736212.72
| Mymensingh Zone |  |  | 0.12864 | 0 | 2.4461 | 0 | 0 | 0.33041 | 0 | 0 | 2.9051 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.0895 | 0 | 0 | 0 | 0 | 0.085983 | 0 | 0 | 28.1755 | Hydro | 1.0124 | Hydro | 101238
| Khulna Zone |  |  | 2.4762 | 23.1055 | 0 | 0 | 0 | 0.77616 | 21.2618 | 0 | 47.6197 | Solar | 3.9607 | Solar | 60408138.03
| Barishal Zone |  |  | 8.1148 | 34.4995 | 0 | 0 | 0 | 0.005301 | 0 | 0 | 42.6196 | Import | 52.0597 | Import | 299775274.96
| Rajshahi Zone |  |  | 15.1268 | 0 | 0.14402 | 0 | 0 | 1.6699 | 27.5665 | 0 | 44.5073 | Wind | 0.0648 | Wind | 953208
| Rangpur Zone |  |  | 0 | 1.1341 | 0.61037 | 0 | 0 | 0.25585 | 0 | 0 | 2.0003
| Total |  |  | 123.5501 | 98.6809 | 13.5275 | 0 | 1.0124 | 3.9607 | 52.0597 | 0.0648 | 292.8561
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 433712084.2494 |  | Hydro | 101238
|  |  |  | Coal | 658565978.831 |  | Solar | 60408138.03
|  |  |  | HFO | 224736212.72 |  | Import | 299775274.96
|  |  |  | HSD | 0 |  | Wind | 953208
[5 empty] | Total: | 167,82,52,134 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.2618 | Peak Hr Flow | 879.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 46889400.05 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.5665 | Peak Hr Flow | 1330.47 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2106 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.2314 | Peak Hr Flow | 156.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2508 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.0597 | Peak Hr Flow | 2365.47 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4886
|  |  |  | Chattogram |  | 0 |  | 1421
|  |  |  | Cumilla |  | 0 |  | 1434
|  |  |  | Mymensingh |  | 0 |  | 1013
|  |  |  | Sylhet |  | 0 |  | 600
|  |  |  | Khulna |  | 0 |  | 1644
|  |  |  | Barishal |  | 0 |  | 425
|  |  |  | Rajshahi |  | 0 |  | 1334
|  |  |  | Rangpur |  | 0 |  | 738
|  |  |  | Total |  | 0 |  | 13495
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:18 | 00:01 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Project Work S/D Due to CT & Loop Conductor | [7 empty] | 50.0MW load
|  |  | change by CCCE | [7 empty] | interrup.
| 08:18 | 00:00 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Project Work S/D Due to CT & Loop Conductor
change by CCCE
| 08:43 | 16:30 | Maniknagar 132/33kV S/S Transformer GT-1 HT Scheduled S/D Due to DPDC-PDSD project works
by DPDC
| 08:54 | 13:17 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T LT Scheduled S/D Due to emergency | [7 empty] | 25.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 08:55 | 13:15 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T HT Scheduled S/D Due to emergency | [7 empty] | 25.0MW load
|  |  | maintenance | [7 empty] | interrup.
|  | 09:13 | Nabinagar 132/33kV S/S Nabinagar-Dhamrai Ckt-1 is restored.
|  | 09:13 | Nabinagar 132/33kV S/S Nabinagar-Dhamrai Ckt-2 is restored.
| 09:41 | 11:15 | Kabirpur 132/33kV S/S XFR, T-3 HT Forced S/D Due to High Temperature maintenance work.
| 09:41 | 11:19 | Kabirpur 132/33kV S/S XFR, T-3 LT Forced S/D Due to High Temperature Maintenance Work
| 09:50 | 18:04 | Purbasadipur-Saidpur 132kV Ckt-2 Project Work S/D from Saidpur 132/33kV end Due to For
project work.
|  | 11:16 | Faridpur 132/33kV S/S Transformer-1 HT is restored.
|  | 11:17 | Faridpur 132/33kV S/S Transformer-1 LT is restored.
| 11:47 | 12:48 | Taraganj 132/33kV S/S Taraganj-Rangpur CKT-02 Tripped showing Y Phase
Pickup Zone-1(14.72km) AR Lockout relays Due to heavy rain and strom
| 11:48 | 12:44 | Rangpur-Saidpur 132kV Ckt-2 Tripped from Rangpur 132/33kV end showing Distance relays
Due to heavy Storm
| 13:15 | 14:49 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-2 Tripped showing over current relay
relays.
| 13:15 | 16:13 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 Tripped showing Distance relay relays.
| 13:16 |  | Jashore 132/33kV S/S Cap. Bank-1 Tripped showing 86 relays Due to Grid failed
|  | 13:59 | Khulna(C )-Noapara 132kV Ckt-1 is restored.
|  | 14:00 | Khulna(C )-Noapara 132kV Ckt-2 is restored.
| 15:03 | 18:02 | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T LT Scheduled S/D Due to emergency | [7 empty] | 15.0MW load
|  |  | maintenance work | [7 empty] | interrup.
| 15:05 | 18:00 | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T HT Scheduled S/D Due to emergency | [7 empty] | 15.0MW load
|  |  | maintenance work | [7 empty] | interrup.
|  | 18:01 | Kishoreganj-Mymensingh 132kV Ckt-2 is restored.
|  | 18:18 | Kishoreganj-Mymensingh 132kV Ckt-1 is restored.
|  | 18:51 | Barishal-Barishal(N) 132 kV Ckt-1 is restored.
|  | 18:51 | Barishal-Barishal(N) 132 kV Ckt-1 is restored.
|  | 19:40 | Barapukuria-Bogura 230 kV Ckt-1 is restored.
| 21:00 |  | Evening Peak Generation is 13986 MW.
| 02:05 | 03:24 | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-1 Tripped from Bogura 230/132kV end showing
Distance PROTN. Relay: LO Recloser, Fault type C to G, Zone 1, A/R in PROGRESS, Carrier
send, Carrier Receive, relays Due to Storm and from Bog-Sherpur 132/33kV end showing
Micom-P443 relays.
|  | 04:19 | Chandina 132/33kV S/S TR-2 HT is restored.
|  | 04:21 | Chandina 132/33kV S/S TR-2 LT is restored.
| 04:55 |  | Haripur 412 MW CCPP Shutdown with remarks:- ST
| 05:05 |  | Haripur 412 MW CCPP Synchronized
| 06:00 |  | Minimum Generation: 11065 MW.
| 06:26 |  | Baroaulia-Hathazari 132 kV Ckt-1 Scheduled S/D from Baroaulia 132/33kV end Due to | [7 empty] | 28.0MW load
|  |  | Baraulia-Hathazari ckt-01 165 no tower to 166no tower and 166no tower to Gentry. OPGW | [7 empty] | interrup. Baroaulia
|  |  | Wire Pulling Work | [7 empty] | 132/33kV end
| 06:32 |  | Chandpur 132/33kV S/S 402T (T-01) HT Scheduled S/D Due to Maintainace
| 06:32 |  | Chandpur 132/33kV S/S 402T (T-01) LT Scheduled S/D Due to Maintainace | [7 empty] | 10.0MW load
interrup.
| 06:33 |  | Coxsbazar 132/33kV S/S 415T-T2 HT Project Work S/D Due to Commission the new CRP of | [7 empty] | 90.0MW load
|  |  | Transformer-3 & 33kv Incomer-3 at New Control Room. | [7 empty] | interrup.
| 06:54 |  | Barishal-Barishal(N) 132 kV Ckt-1 Project Work S/D from Barishal 230/132kV end Due to
OPGW change
| 07:25 |  | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) LT Scheduled S/D | [7 empty] | 40.0MW load
interrup.
| 07:25 |  | Chuadanga 132/33kV S/S 132kV Tr. T3 LT Scheduled S/D | [7 empty] | 40.0MW load
interrup.
| 07:26 |  | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) HT Scheduled S/D | [7 empty] | 45.0MW load
interrup.
| 07:27 |  | Chuadanga 132/33kV S/S 132kV Tr. T3 HT Scheduled S/D | [7 empty] | 40.0MW load
interrup.
| 07:35 |  | Feni 132/33kV S/S T-1(405T) HT Scheduled S/D Due to Shutdown taken for PDB 33 KV bus loop | [7 empty] | 40.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 07:36 |  | Feni 132/33kV S/S T-1(405T) LT Scheduled S/D Due to Shutdown taken for PDB 33 KV bus loop | [7 empty] | 40.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 07:45 |  | Barishal-Barishal(N) 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to OPGW
upgration work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 08-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 346 | 8481600 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 157254 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7274067 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 139320 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 7200 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 78382 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 139699 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22.5 | 481200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 312840 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 589920 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 1367204 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 113 | 2198736 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 530880 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 424800 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 243599 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 25200 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 500 | 11161818.18 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 264 | 6817010 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 51 | 1966800 | Engine Problem
Dhaka Area Total |  |  |  |  | 6668.974 | 1896.5 | 42397529.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 71575.2 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 91125 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 222240 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 41 | 1012380 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 215 | 5118415 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 50 | 265127 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 375599 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 21 | 333600 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 58 | 381120 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 27719 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 32 | 178100 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 23803634 | U2 on AGC
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 64800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 983 | 16138181.82 | AGC
Chattogram Area Total |  |  |  |  | 4898.863 | 2646 | 48083616.02
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 217 | 4944000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 356 | 8783700 | FGMO not available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 0 | 744000 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 315 | 7886500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 40 | 495072 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 27 | 287520 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 120 | 1354909 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1190428 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 70 | 550327 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 24304 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 147 | 3492480 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 245760 | -
| Import (Tripura) |  | Import | 0 | 160 | 156 | 3231360 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 455050 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 18 | 96600 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 68 | 290880 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 474636 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1655 | 34547526
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 18 | 128640 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15500 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 115 | 2073600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 37 | 301200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 314910 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 71280 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 182 | 2905130
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 85983 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 989000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 724800 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3543463.64 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 100 | 2314500 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 617280 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1882560 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 102 | 1797920 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 390960 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7350000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 334 | 8479000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1190 | 28175466.64
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 879 | 21261818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 140 | 2476224 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 776160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1210 | 23105450 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2229 | 47619652
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 432 | 8676364 | plant availability zero
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 128 | 2849000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1102 | 20762181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5265800 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 236 | 5061000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 5301 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2118 | 42619646.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 419640 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 9729 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 130 | 3268091 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Fuel shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 130 | 3413068 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 350 | 8445600 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 13181 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 54198 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 43200 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 23712 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 39060 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1330.47 | 27566546 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 436512 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 774720 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1940.47 | 44507257
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 48 | 1134109 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 367536 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 18428.64 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 33 | 242830 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 133308 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 104112 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 130 | 2000323.64
Eastern Grid Total |  |  |  |  | 17418.042 | 7569.5 | 156109267.84
Western Grid Total |  |  |  |  | 11852.195 | 6417.47 | 136746879.46
National Grid Total |  |  |  |  | 29270.237 | 13986.97 | 292856147.3
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 08-05-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9353.94 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4141.6 | MW
i) Dhaka area |  |  | 4885.84 |  | MW | i) Khulna area |  |  |  | 1644.3 | MW
ii) Chattogram area |  |  | 1421.1 |  | MW | ii) Barishal area |  |  |  | 425.3 | MW
iii) Cumilla area |  |  | 1434 |  | MW | iii) Rajshahi area |  |  |  | 1334 | MW
iv) Mymensingh area |  |  | 1013 |  | MW | iv) Rangpur area |  |  |  | 738 | MW
v) Sylhet area |  |  | 600 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13495.54 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 15 | 23:00 | 67 | Hasnabad | 87 | 13:00 | 133 | Natore | 140 | 19:30
2 | AKSML | 110.5 | 01:00 | 68 | Hathazari | 87 | 20:00 | 134 | Nawabganj | 55.8 | 22:00
3 | Aftabnagar | 38 | 19:30 | 69 | Hatirjheel | 30 | 17:00 | 135 | Netrakona | 120 | 19:00
4 | Agargaon | 105 | 13:00 | 70 | Ishurdi | 73 | 19:30 | 136 | New | 66 | 11:00
5 | Agrabad | 58 | 18:30 | 71 | Jaldhaka | 68 | 19:00 | 137 | Niamatpur | 60 | 19:30
6 | Amnura | 25 | 21:00 | 72 | Jamalpur | 106 | 21:00 | 138 | Noapara | 40 | 19:30
7 | Ashuganj | 86 | 23:00 | 73 | Jashore | 135 | 19:30 | 139 | PHP | 12 | 18:30
8 | BSRM | 205 | 23:00 | 74 | Jhenaidah | 106 | 19:30 | 140 | Pabna | 87 | 19:30
9 | Bagerhat | 79.1 | 23:00 | 75 | Joydebpur | 142 | 19:00 | 141 | Palashbari | 110 | 19:00
10 | Bajitpur | 89 | 19:30 | 76 | Joypurhat | 56 | 17:00 | 142 | Panchagarh | 45 | 00:00
11 | Bakerganj | 10 | 19:00 | 77 | Juldah | 15.5 | 22:00 | 143 | Patiya | 10.7 | 19:00
12 | Bakulia | 85 | 21:00 | 78 | KSRM | 10 | 00:00 | 144 | Patuakhali | 67 | 22:00
13 | Banani | 32.2 | 18:30 | 79 | Kabirpur | 214 | 09:00 | 145 | Payra | 36 | 20:00
14 | Bangabhaban | 4 | 10:00 | 80 | Kachua | 92 | 18:30 | 146 | Postogola | 45 | 13:00
15 | Barapukuria | 49 | 20:00 | 81 | Kaliganj | 19 | 19:00 | 147 | Pubail | 22 | 18:30
16 | Barguna | 20 | 19:00 | 82 | Kallyanpur | 111 | 13:00 | 148 | Purbachal | 31 | 12:00
17 | Barishal | 91 | 22:00 | 83 | Kalurghat | 33 | 01:00 | 149 | Purbasadipur | 115 | 19:30
18 | Barishal-230 | 98 | 19:00 | 84 | Kamrangirchar | 67 | 00:00 | 150 | Rahanpur | 32 | 22:00
19 | Baroaulia | 63 | 15:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 31 | 02:00
20 | Baroirhat | 45 | 00:00 | 86 | Kasba | 36 | 20:00 | 152 | Rajbari | 75 | 19:00
21 | Bashundhara | 174 | 13:00 | 87 | Kazla | 108 | 13:00 | 153 | Rajendrapur | 125 | 19:00
22 | BashundharaCement | 7 | 00:00 | 88 | Keranigonj | 71 | 22:00 | 154 | Rajshahi | 107 | 21:00
23 | Beanibazar | 74 | 19:00 | 89 | Khagrachori | 34 | 18:30 | 155 | Rajshahi-230 | 70 | 22:00
24 | Benapole | 70 | 22:00 | 90 | Khulna | 59 | 19:30 | 156 | Ramganj | 110 | 19:00
25 | Bhaluka | 148 | 19:00 | 91 | Khulshi | 176 | 19:00 | 157 | Rampur | 42 | 23:00
26 | Bhandaria | 52 | 23:00 | 92 | Kishoreganj | 114 | 21:00 | 158 | Rangamati | 17 | 19:00
27 | Bhangura | 37 | 19:30 | 93 | Kodda | 271 | 09:00 | 159 | Rangpur | 120 | 20:00
28 | Bheramara(GK) | 62 | 19:00 | 94 | Kulaura | 54 | 22:00 | 160 | Ruppur | 3.8 | 10:00
29 | Bhulta | 205 | 04:00 | 95 | Kurigram | 52 | 19:00 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 68 | 01:00 | 96 | Kushtia | 135 | 19:30 | 162 | Saidpur | 76 | 19:30
31 | Bogura | 148 | 22:00 | 97 | Laksam | 34 | 21:00 | 163 | Santhia | 32 | 19:00
32 | Borhanuddin | 93 | 19:00 | 98 | Lakshmipur | 37 | 19:00 | 164 | Satkhira | 119 | 23:00
33 | Brahmanbaria | 130 | 21:00 | 99 | Lalbag | 59 | 00:00 | 165 | Satmasjid | 87 | 13:00
34 | Cantonment | 104 | 12:00 | 100 | Lalmonirhat | 54 | 19:00 | 166 | Savar | 188 | 11:00
35 | Chandina | 16 | 23:00 | 101 | MI_Cement | 18.2 | 15:00 | 167 | SevenRings | 16.92 | 05:00
36 | Chandpur | 79 | 19:30 | 102 | Madanganj | 37 | 08:00 | 168 | ShahCement | 44 | 00:00
37 | Chandraghona | 37 | 19:30 | 103 | Madaripur | 99 | 23:00 | 169 | Shahjadpur | 76 | 20:00
38 | Chapai | 65 | 21:00 | 104 | Madartek | 76 | 13:00 | 170 | Shahjibazar | 114 | 19:30
39 | Charsaidpur | 44 | 07:00 | 105 | Madunaghat | 53 | 22:00 | 171 | Shahmirpur | 53 | 00:00
40 | Chauddagram | 80 | 19:30 | 106 | Magura | 62 | 19:00 | 172 | Shariatpur | 81 | 20:00
41 | Chhatak | 34 | 19:00 | 107 | Mahasthangarh | 67 | 19:00 | 173 | Sherpur | 120 | 21:00
42 | Chowmuhani | 138 | 19:00 | 108 | Maijdee | 45 | 22:00 | 174 | Shikalbaha | 33 | 23:00
43 | Chuadanga | 113 | 22:00 | 109 | Manikganj | 132 | 21:00 | 175 | Shitalakhya | 61.1 | 13:00
44 | Coxsbazar | 144 | 21:00 | 110 | Maniknagar | 63 | 22:00 | 176 | Sholosohor | 48 | 13:00
45 | Cumilla(N) | 118 | 18:30 | 111 | Matarbari | 55 | 20:00 | 177 | Shyampur | 162 | 00:00
46 | Cumilla(S) | 160 | 23:00 | 112 | Matuail | 68 | 00:00 | 178 | Siddhirganj | 110 | 13:00
47 | Daganbhuiyan | 40 | 15:00 | 113 | Metrorail_Motijheel | 24 | 21:00 | 179 | Sirajganj | 88 | 19:00
48 | Daudkandi | 141 | 21:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sonargaon | 136 | 23:00
49 | DhakaUniversity | 46 | 12:00 | 115 | Millgate | 73 | 15:00 | 181 | Sreemongol | 79 | 21:00
50 | Dhamrai | 114 | 18:30 | 116 | Mirpur | 131 | 12:00 | 182 | Sreepur | 94 | 02:00
51 | Dhanmondi | 92 | 18:30 | 117 | Mirsorai | 42 | 03:00 | 183 | Srinagar | 45.4 | 22:00
52 | Dohazari | 107 | 20:00 | 118 | Mirzapur | 40 | 21:00 | 184 | Sunamganj | 54 | 22:00
53 | Faridpur | 152 | 20:00 | 119 | Mithapukur | 46 | 19:30 | 185 | Sylhet | 41 | 19:30
54 | Fatullah | 74 | 12:00 | 120 | Modern | N/A | N/A | 186 | Sylhet-132 | 119 | 19:00
55 | Fenchuganj | 41 | 19:00 | 121 | Mogbazar | 65.5 | 13:00 | 187 | TK | 25 | 19:00
56 | Feni | 109 | 21:00 | 122 | Mongla | 35 | 00:00 | 188 | Tangail | 170 | 21:00
57 | GPH | 73 | 22:00 | 123 | Motijheel | 34 | 13:00 | 189 | Taraganj | 30 | 19:00
58 | Ghatail | 84 | 21:00 | 124 | Muktagacha | 32 | 21:00 | 190 | Tasnim | 19 | 23:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 106 | 21:00 | 191 | Thakurgaon | 90 | 19:30
60 | Ghorashal-230 | 104 | 00:00 | 126 | Muradnagar | 47 | 19:30 | 192 | Tongi | 141 | 00:00
61 | Goalpara | 36 | 12:00 | 127 | Mymensingh | 143 | 19:30 | 193 | Ullahpara | 38 | 19:00
62 | Gollamari | 92 | 22:00 | 128 | Nabinagar | 59 | 00:00 | 194 | Ullon | 65 | 13:00
63 | Gopalganj | 103 | 19:30 | 129 | Naogaon | 116 | 19:30 | 195 | Uttara | 78 | 12:00
64 | Gulshan | 82 | 12:00 | 130 | Narail | 56 | 19:00 | 196 | UttaraNew | 51 | 13:00
65 | Halishahar | 71 | 19:30 | 131 | Narinda | 50 | 13:00 | 197 | Zigatola | 82 | 13:00
66 | HaripurSBU | 131 | 23:00 | 132 | Narshingdi | 171 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 08-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 12317.2 | 70 |  | 12390.35
1:00 | 12383.58 | 59 |  | 12445.58
2:00 | 11994.92 | 58 |  | 12055.92
3:00 | 11643.2 | 45 |  | 11690.2
4:00 | 11370.63 | 33 |  | 11404.63
5:00 | 11051.26 | 18 |  | 11070.26
6:00 | 10610.74 | 0 |  | 10610.74
7:00 | 10924.32 | 0 |  | 10924.32
8:00 | 10816.21 | 0 |  | 10816.21
9:00 | 10803.7 | 0 |  | 10803.7
10:00 | 10988.91 | 0 |  | 10988.91
11:00 | 11586.1 | 0 |  | 11586.1
12:00 | 12165 | 0 |  | 12165
13:00 | 12577.31 | 0 |  | 12577.31
14:00 | 11987.14 | 0 |  | 11987.14
15:00 | 12302.63 | 0 |  | 12302.63
16:00 | 12097.01 | 0 |  | 12097.01
17:00 | 11719.62 | 0 |  | 11719.62
18:00 | 11470.28 | 0 |  | 11470.28
19:00 | 13444.79 | 73 |  | 13520.79
19:30 | 13854.86 | 77 |  | 13934.86
20:00 | 13793.65 | 73 |  | 13869.65
21:00 | 13986.97 | 0 |  | 13986.97
22:00 | 13872.95 | 0 |  | 13872.95
23:00 | 13825.41 | 0 |  | 13825.41
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 08-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6567 | 5750.2 | 12317.2 | DAILY GENERATION CURVE
00:30 | 6521.5 | 5828.89 | 12350.39
01:00 | 6476 | 5907.58 | 12383.58 | 08-05-2026
01:30 | 6344 | 5845.25 | 12189.25
02:00 | 6212 | 5782.92 | 11994.92
02:30 | 6097.5 | 5721.56 | 11819.06
03:00 | 5983 | 5660.2 | 11643.2
03:30 | 5962 | 5544.915 | 11506.915
04:00 | 5941 | 5429.63 | 11370.63
04:30 | 5917 | 5293.945 | 11210.945
05:00 | 5893 | 5158.26 | 11051.26
05:30 | 5805.105 | 5025.895 | 10831
06:00 | 5717.21 | 4893.53 | 10610.74
06:30 | 5814.71 | 4952.82 | 10767.53
07:00 | 5912.21 | 5012.11 | 10924.32
07:30 | 5862.875 | 5007.39 | 10870.265
08:00 | 5813.54 | 5002.67 | 10816.21
08:30 | 5754.265 | 5055.69 | 10809.955
09:00 | 5694.99 | 5108.71 | 10803.7
09:30 | 5747.96 | 5148.345 | 10896.305
10:00 | 5800.93 | 5187.98 | 10988.91
10:30 | 5984.55 | 5302.955 | 11287.505
11:00 | 6168.17 | 5417.93 | 11586.1
11:30 | 6275.095 | 5600.455 | 11875.55
12:00 | 6382.02 | 5782.98 | 12165
12:30 | 6478.935 | 5892.22 | 12371.155
13:00 | 6575.85 | 6001.46 | 12577.31
13:30 | 6362.34 | 5919.885 | 12282.225
14:00 | 6148.83 | 5838.31 | 11987.14
14:30 | 6293.55 | 5851.335 | 12144.885
15:00 | 6438.27 | 5864.36 | 12302.63
15:30 | 6424.05 | 5775.77 | 12199.82
16:00 | 6409.83 | 5687.18 | 12097.01
16:30 | 6396.93 | 5511.385 | 11908.315
17:00 | 6384.03 | 5335.59 | 11719.62
17:30 | 6395.485 | 5199.465 | 11594.95
18:00 | 6406.94 | 5063.34 | 11470.28
18:30 | 6827.72 | 5629.815 | 12457.535
19:00 | 7248.5 | 6196.29 | 13444.79
19:30 | 7446.5 | 6408.36 | 13854.86
20:00 | 7440.5 | 6353.15 | 13793.65
20:30 | 7505 | 6385.31 | 13890.31 |  | Executive Engineer
21:00 | 7569.5 | 6417.47 | 13986.97 |  | Network Operation Division
21:30 | 7514.5 | 6415.46 | 13929.96
22:00 | 7459.5 | 6413.45 | 13872.95
22:30 | 7452 | 6397.18 | 13849.18
23:00 | 7444.5 | 6380.91 | 13825.41

## En-Curve
QF-LDC-12
Date | 08-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3563 | 1656 | 879 | 0 | 140 | 1353.2 | 43 | 4300 | 0 | 165 | 214 | 0 | 0 | 4 | 70 | DAILY ENERGY CURVE
00:30 | 3564.5 | 1667 | 879.5 | 0 | 142 | 1376.89 | 43 | 4330.5 | 0 | 145 | 199 | 0 | 0 | 3 | 64.5 | 08-05-2026
01:00 | 3566 | 1678 | 880 | 0 | 144 | 1400.58 | 43 | 4361 | 0 | 125 | 184 | 0 | 0 | 2 | 59
01:30 | 3563 | 1620.5 | 880 | 0 | 143 | 1368.25 | 43 | 4279 | 0 | 109 | 182.5 | 0 | 0 | 1 | 58.5 | Energy Generated | 292.8561 |  | MKWHr
02:00 | 3560 | 1563 | 880 | 0 | 142 | 1335.92 | 43 | 4197 | 0 | 93 | 181 | 0 | 0 | 0 | 58 | Energy not Served | 0.429 |  | MKWHr
02:30 | 3515.5 | 1562.5 | 880 | 0 | 138 | 1313.56 | 43 | 4122 | 0 | 63.5 | 181 | 0 | 0 | 0 | 51.5 | Total Energy Requirement | 293.2851 |  | MKWHr
03:00 | 3471 | 1562 | 880 | 0 | 134 | 1291.2 | 43 | 4047 | 0 | 34 | 181 | 0 | 0 | 0 | 45
03:30 | 3474 | 1547.5 | 880 | 0 | 130 | 1233.915 | 43 | 3983 | 0 | 34 | 181.5 | 0 | 0 | 0 | 39
04:00 | 3477 | 1533 | 880 | 0 | 126 | 1176.63 | 43 | 3919 | 0 | 34 | 182 | 0 | 0 | 0 | 33
04:30 | 3450.5 | 1574.5 | 879.5 | 0 | 128 | 1148.945 | 42.5 | 3780 | 0 | 25.5 | 181.5 | 0 | 0 | 0 | 25.5
05:00 | 3424 | 1616 | 879 | 0 | 130 | 1121.26 | 42 | 3641 | 0 | 17 | 181 | 0 | 0 | 0 | 18
05:30 | 3409.5 | 1586.5 | 879 | 0 | 122 | 1053.715 | 41.5 | 3491.5 | 19.785 | 41.5 | 186 | 0 | 0 | 0 | 9
06:00 | 3395 | 1557 | 879 | 0 | 114 | 986.17 | 41 | 3342 | 39.57 | 66 | 191 | 0 | 0 | 0 | 0
06:30 | 3412.5 | 1610.5 | 879.5 | 0 | 114 | 985.64 | 41 | 3319.5 | 102.39 | 101 | 201 | 0 | 0 | 0.5 | 0
07:00 | 3430 | 1664 | 880 | 0 | 114 | 985.11 | 41 | 3297 | 165.21 | 136 | 211 | 0 | 0 | 1 | 0
07:30 | 3407 | 1599 | 880 | 0 | 115 | 957.39 | 41 | 3273 | 251.875 | 136 | 209.5 | 0 | 0 | 0.5 | 0
08:00 | 3384 | 1534 | 880 | 0 | 116 | 929.67 | 41 | 3249 | 338.54 | 136 | 208 | 0 | 0 | 0 | 0
08:30 | 3333 | 1520.5 | 880 | 0 | 116 | 926.97 | 41.5 | 3231 | 419.485 | 136 | 205.5 | 0 | 0 | 0 | 0
09:00 | 3282 | 1507 | 880 | 0 | 116 | 924.27 | 42 | 3213 | 500.43 | 136 | 203 | 0 | 0 | 0 | 0
09:30 | 3273 | 1512 | 879.5 | 0 | 120 | 925.75 | 42.5 | 3213.5 | 559.055 | 136 | 235 | 0 | 0 | 0 | 0
10:00 | 3264 | 1517 | 879 | 0 | 124 | 927.23 | 43 | 3214 | 617.68 | 136 | 267 | 0 | 0 | 0 | 0
10:30 | 3303.5 | 1587 | 879 | 0 | 129 | 962.26 | 43 | 3406 | 575.245 | 136 | 266.5 | 0 | 0 | 0 | 0
11:00 | 3343 | 1657 | 879 | 0 | 134 | 997.29 | 43 | 3598 | 532.81 | 136 | 266 | 0 | 0 | 0 | 0
11:30 | 3344 | 1688.5 | 879.5 | 0 | 139 | 1009.405 | 43 | 3741.5 | 609.645 | 141 | 279 | 0 | 0 | 1 | 0
12:00 | 3345 | 1720 | 880 | 0 | 144 | 1021.52 | 43 | 3885 | 686.48 | 146 | 292 | 0 | 0 | 2 | 0
12:30 | 3339 | 1685.5 | 879.5 | 0 | 147 | 1138.5 | 43 | 4076.5 | 553.155 | 165.5 | 336 | 0 | 0 | 7.5 | 0
13:00 | 3333 | 1651 | 879 | 0 | 150 | 1255.48 | 43 | 4268 | 419.83 | 185 | 380 | 0 | 0 | 13 | 0
13:30 | 3219 | 1653.5 | 879 | 0 | 138 | 1186.675 | 43 | 4137.5 | 480.3 | 178 | 357.25 | 0 | 0 | 10 | 0
14:00 | 3105 | 1656 | 879 | 0 | 126 | 1117.87 | 43 | 4007 | 540.77 | 171 | 334.5 | 0 | 0 | 7 | 0
14:30 | 3167.5 | 1720.5 | 879 | 0 | 128 | 1118.415 | 43 | 4053.5 | 533.57 | 171 | 324.4 | 0 | 0 | 6 | 0
15:00 | 3230 | 1785 | 879 | 0 | 130 | 1118.96 | 43 | 4100 | 526.37 | 171 | 314.3 | 0 | 0 | 5 | 0
15:30 | 3260 | 1706.5 | 879 | 0 | 126 | 1091.81 | 43 | 4161.5 | 440.21 | 171 | 314.8 | 0 | 0 | 6 | 0
16:00 | 3290 | 1628 | 879 | 0 | 122 | 1064.66 | 43 | 4223 | 354.05 | 171 | 315.3 | 0 | 0 | 7 | 0
16:30 | 3294.5 | 1641.5 | 879 | 0 | 129 | 1026.61 | 42.5 | 4145.5 | 250.455 | 179.5 | 314.75 | 0 | 0 | 5 | 0
17:00 | 3299 | 1655 | 879 | 0 | 136 | 988.56 | 42 | 4068 | 146.86 | 188 | 314.2 | 0 | 0 | 3 | 0
17:30 | 3272.5 | 1673 | 879.5 | 0 | 135 | 978.01 | 41 | 4017.5 | 86.59 | 188 | 321.85 | 0 | 0 | 2 | 0
18:00 | 3246 | 1691 | 880 | 0 | 134 | 967.46 | 40 | 3967 | 26.32 | 188 | 329.5 | 0 | 0 | 1 | 0
18:30 | 3351 | 1739.75 | 879.5 | 0 | 142 | 1162.375 | 40 | 4348 | 13.16 | 283 | 495.75 | 0 | 0 | 3 | 36.5
19:00 | 3456 | 1788.5 | 879 | 0 | 150 | 1357.29 | 40 | 4729 | 0 | 378 | 662 | 0 | 0 | 5 | 73
19:30 | 3449 | 1770.5 | 879 | 0 | 146 | 1322.36 | 39 | 4964 | 0 | 221 | 1053 | 0 | 0 | 11 | 77
20:00 | 3503 | 1766.5 | 879 | 0 | 144 | 1263.15 | 40 | 4939 | 0 | 221 | 1030 | 0 | 0 | 8 | 73
20:30 | 3481.5 | 1793.5 | 879 | 0 | 150 | 1296.81 | 40.5 | 5055 | 0 | 182 | 1008 | 0 | 0 | 4 | 36.5
21:00 | 3460 | 1820.5 | 879 | 0 | 156 | 1330.47 | 41 | 5171 | 0 | 143 | 986 | 0 | 0 | 0 | 0
21:30 | 3459 | 1812 | 879 | 0 | 157 | 1331.96 | 41.5 | 5132.5 | 0 | 143 | 974 | 0 | 0 | 0 | 0
22:00 | 3458 | 1803.5 | 879 | 0 | 158 | 1333.45 | 42 | 5094 | 0 | 143 | 962 | 0 | 0 | 0 | 0
22:30 | 3490.5 | 1802 | 879 | 0 | 159 | 1328.68 | 42.5 | 5067 | 0 | 143 | 937.5 | 0 | 0 | 0 | 0
23:00 | 3523 | 1800.5 | 879 | 0 | 160 | 1323.91 | 43 | 5040 | 0 | 143 | 913 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 08-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 130 | -4 | 536 | 126 | 1622 | 446 | Ishurdi-Ghorashal Ckt-1 | Export | 3330400.05
1:00 | 142 | -7 | 554 | 130 | 1724 | 440
2:00 | 149 | -5 | 556 | 126 | 1710 | 430 |  | Import | 0
3:00 | 155 | -2 | 586 | 134 | 1688 | 438
4:00 | 152 | -3 | 574 | 146 | 1590 | 440 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 154 | 0 | 432 | 74 | 1508 | 452
6:00 | 147 | -1 | 516 | 98 | 1418 | 420 |  | Import | 0
7:00 | 127 | -3 | 486 | 126 | 1352 | 380
8:00 | 137 | -5 | 510 | 122 | 1362 | 382 | Sirajganj-Sreepur Ckt-1 | Export | 3287000
9:00 | 167 | -1 | 580 | 118 | 1478 | 432
10:00 | 189 | 2 | 638 | 136 | 1476 | 392 |  | Import | 0
11:00 | 180 | 2 | 604 | 140 | 1580 | 377
12:00 | 190 | 0 | 630 | 122 | 1632 | 420 | Sirajganj-Sreepur Ckt-2 | Export | 3312000
13:00 | 153 | -17 | 590 | 134 | 1728 | 328
14:00 | 191 | -5 | 640 | 140 | 1668 | 334 |  | Import | 0
15:00 | 186 | -3 | 660 | 172 | 1662 | 346
16:00 | 173 | -5 | 600 | 126 | 1538 | 336 | Gopalganj-Aminbazar Ckt-1 | Export | 18460000
17:00 | 148 | -8 | 500 | 80 | 1436 | 340
18:00 | 125 | -11 | 450 | 92 | 1268 | 320 |  | Import | 0
18:30 | 146 | -3 | 520 | 88 | 1418 | 340
19:00 | 102 | -20 | 480 | 108 | 1458 | 268 | Gopalganj-Aminbazar Ckt-2 | Export | 18500000
19:30 | 85 | -25 | 430 | 90 | 1518 | 252
20:00 | 84 | -23 | 420 | 86 | 1514 | 246 |  | Import | 0
21:00 | 94 | -18 | 460 | 114 | 1552 | 304
22:00 | 101 | -18 | 490 | 126 | 1526 | 292 |  | Total Export | 46889400.05
23:00 | 107 | -15 | 500 | 130 | 1564 | 322 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 08-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 393 | 07:00 | 379 | 23:00 | Madunaghat | 402 | 08:00 | 394 | 01:00
Amtali | 415 | 08:00 | 406 | 23:00 | Meghnaghat | 394 | 07:00 | 383 | 23:00
Ashuganj | 409 | 8:00 | 396 | 0:00 | Payra | 415 | 06:00 | 408 | 21:00
Bhulta | 403 | 08:00 | 390 | 23:00 | Rahanpur | 415 | 06:00 | 400 | 19:00
Bibiana | 406 | 08:00 | 394 | 12:00 | Rampal | 407 | 06:00 | 391 | 23:00
BIPTC | 401 | 03:00 | 393 | 15:00
Bogura | 406 | 06:00 | 389 | 19:30
Gopalganj | 404 | 08:00 | 390 | 21:00
Kaliakoir | 391 | 19:00 | 366 | 12:00
Korerhat | 403 | 08:00 | 391 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 06:00 | 224 | 12:00 | Jhenaidah | 231 | 06:00 | 216 | 13:00
AKSML | 233.7 | 07:00 | 223 | 13:00 | Kachua | 228 | 07:00 | 221 | 00:00
Aminbazar | 232 | 06:00 | 224 | 23:00 | Kaliakoir | 234 | 08:00 | 223 | 12:00
Ashuganj | 230 | 18:00 | 222 | 22:00 | Keranigonj | 230 | 06:00 | 222 | 12:00
Ashuganj-400 | 230 | 18:00 | 222 | 22:00 | Khulna(S) | 234 | 11:00 | 219 | 21:00
Baghabari | 236 | 07:00 | 226 | 21:00 | Korerhat | 229 | 08:00 | 222 | 00:00
Barapukuria | 227 | 18:00 | 214 | 00:00 | Madunaghat | 233 | 07:00 | 227 | 00:00
Barapukuria-230 | 227 | 18:00 | 214 | 00:00 | Madunaghat-400 | 234 | 07:00 | 228 | 01:00
Barishal | 230 | 06:00 | 221 | 22:00 | Maniknagar | 228 | 06:00 | 222 | 00:00
Bheramara | 233 | 05:00 | 222 | 13:00 | Meghnaghat | 235 | 07:00 | 229 | 23:00
Bhulta | 230 | 08:00 | 223 | 00:00 | Meghnaghat-400 | 231 | 07:00 | 223 | 23:00
Bibiana | 236 | 07:00 | 227 | 12:00 | Mirsorai | 233 | 06:00 | 227 | 00:00
BIPTC | 236 | 08:00 | 222 | 13:00 | Naogaon | 225 | 07:00 | 212 | 19:30
Bogura | 236 | 06:00 | 227 | 01:00 | Purbasadipur | 225 | 06:00 | 212 | 00:00
Bogura-400 | 236 | 06:00 | 226 | 01:00 | Rajshahi | 233 | 06:00 | 219 | 21:00
Borhanuddin | 233 | 06:00 | 226 | 22:00 | Rampal | 232 | 06:00 | 219 | 22:00
BSRM | 229 | 08:00 | 221 | 23:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 229 | 06:00 | 220 | 22:00 | Rampura | 230 | 08:00 | 222 | 12:00
Cumilla(N) | 229 | 08:00 | 221 | 23:00 | Shikalbaha | 231 | 07:00 | 224 | 00:00
Faridpur | 227 | 06:00 | 216 | 21:00 | Shyampur | 230 | 06:00 | 223 | 12:00
Fenchuganj | 235 | 06:00 | 230 | 12:00 | Siddhirganj | 233 | 04:00 | 223 | 23:00
Feni | 228 | 07:00 | 221 | 23:00 | Sirajgonj | 244 | 07:00 | 234 | 21:00
Ghorashal | 232 | 08:00 | 225 | 00:00 | Sreepur | 229 | 17:00 | 219 | 15:00
Ghorashal-230 | 228 | 08:00 | 220 | 12:00 | Tongi | 228 | 04:00 | 220 | 11:00
Gopalganj | 226 | 06:00 | 217 | 21:00
GPH | 230 | 09:00 | 225 | 00:00
Haripur | 230 | 08:00 | 223 | 12:00
Hasnabad | 231 | 07:00 | 222 | 12:00
Hathazari | 231 | 05:00 | 225 | 00:00
Ishurdi | 236 | 06:00 | 224 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 07:00 | 130 | 10:00 | Madunaghat | 135 | 07:00 | 131 | 00:00
Agargaon | 134 | 06:00 | 128 | 12:00 | Magura | 136 | 05:00 | 124 | 13:00
Agrabad | 133 | 06:00 | 127 | 13:00 | Mahasthangarh | 135 | 06:00 | 127 | 00:00
AKS | 130 | 05:00 | 126 | 00:00 | Maijdee | 127 | 07:00 | 122 | 23:00
Aminbazar | 133 | 06:00 | 127 | 23:00 | Manikganj | 128 | 7:00 | 120 | 00:00
Amnura | 135 | 05:00 | 126 | 19:30 | Maniknagar | 135 | 08:00 | 130 | 13:00
Ashuganj | 137 | 07:00 | 134 | 00:00 | Matarbari | 121 | 08:00 | 109 | 00:00
Ashuganj-230 | 137 | 07:00 | 134 | 00:00 | Matuail | 133 | 08:00 | 129 | 00:00
Bagerhat | 134 | 09:00 | 119 | 23:00 | Metrorail_Motijheel | 135 | 08:00 | 130 | 13:00
Bajitpur | 134 | 17:00 | 127 | 00:00 | Metrorail_Uttara | 132 | 05:00 | 126 | 13:00
Bakerganj | 134 | 09:00 | 128 | 21:00 | Millgate | 133 | 06:00 | 126 | 13:00
Bakulia | 133 | 07:00 | 128 | 00:00 | Mirpur | 132 | 04:00 | 126 | 12:00
Banani | 136 | 06:00 | 130 | 12:00 | Mirzapur | 132 | 08:00 | 123 | 12:00
Bangabhaban | 135 | 06:00 | 130 | 12:00 | Mithapukur | 133 | 06:00 | 125 | 01:00
Barapukuria | 132 | 04:00 | 124 | 00:00 | MI_Cement | 131 | 06:00 | 126 | 13:00
Barguna | 134 | 07:00 | 127 | 21:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 134 | 05:00 | 127 | 19:00 | Mogbazar | 136 | 05:00 | 124 | 14:00
Barishal-230 | 134 | 06:00 | 127 | 22:00 | Mongla | 133 | 07:00 | 121 | 23:00
Baroaulia | 134 | 09:00 | 129 | 12:00 | Motijheel | 135 | 06:00 | 130 | 00:00
Baroirhat | 132 | 06:00 | 127 | 12:00 | Muktagacha | 131 | 16:00 | 117 | 12:00
Bashundhara | 136 | 06:00 | 127 | 12:00 | Munshiganj | 131 | 08:00 | 127 | 00:00
BashundharaCement | 132 | 01:00 | 127 | 13:00 | Muradnagar | 129 | 08:00 | 122 | 21:00
Beanibazar | 125 | 08:00 | 119 | 00:00 | Mymensingh | 130 | 16:00 | 115 | 13:00
Benapole | 134 | 03:00 | 116 | 13:00 | Nabinagar | 132 | 05:00 | 124 | 15:00
Bhaluka | 133 | 05:00 | 123 | 15:00 | Naogaon | 135 | 07:00 | 127 | 21:00
Bhandaria | 133 | 04:00 | 121 | 19:30 | Narail | 136 | 05:00 | 124 | 13:00
Bhangura | 136 | 06:00 | 129 | 21:00 | Narinda | 135 | 08:00 | 130 | 13:00
Bheramara | 137 | 05:00 | 130 | 21:00 | Narshingdi | 129 | 08:00 | 121 | 21:00
Bheramara(GK) | 137 | 05:00 | 129 | 21:00 | Natore | 135 | 05:00 | 127 | 21:00
Bhulta | 129 | 09:00 | 123 | 02:00 | Nawabganj | 136 | 06:00 | 130 | 12:00
Bog-Sherpur | 136 | 05:00 | 129 | 21:00 | Netrakona | 130 | 17:00 | 114 | 13:00
Bogura | 137 | 04:00 | 130 | 01:00 | New | 133 | 05:00 | 128 | 12:00
Bogura-230 | 137 | 06:00 | 131 | 00:00 | Niamatpur | 136 | 06:00 | 130 | 19:00
Brahmanbaria | 129 | 07:00 | 123 | 21:00 | Noapara | 134 | 05:00 | 118 | 13:00
Cantonment | 133 | 05:00 | 127 | 12:00 | Pabna | 135 | 06:00 | 128 | 21:00
Chandina | 132 | 06:00 | 127 | 01:00 | Palashbari | 130 | 05:00 | 123 | 00:00
Chandpur | 128 | 08:00 | 124 | 00:00 | Panchagarh | 138 | 06:00 | 128 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 135 | 08:00 | 131 | 00:00 | Patiya | 132 | 08:00 | 126 | 00:00
Chapai | 135 | 07:00 | 130 | 19:30 | Patuakhali | 134 | 03:00 | 127 | 21:00
Charsaidpur | 132 | 08:00 | 2:00 | 15:00 | Payra | 136 | 10:00 | 132 | 22:00
Chauddagram | 130 | 08:00 | 125 | 00:00 | PHP | 131 | 07:00 | 127 | 00:00
Chhatak | 124 | 06:00 | 117 | 12:00 | Postogola | 133 | 02:00 | 127 | 12:00
Chowmuhani | 128 | 06:00 | 123 | 00:00 | Pubail | 135 | 04:00 | 131 | 12:00
Chuadanga | 136 | 05:00 | 120 | 22:00 | Purbachal | 136 | 06:00 | 127 | 12:00
Coxsbazar | 123 | 08:00 | 111 | 00:00 | Purbasadipur | 134 | 06:00 | 124 | 13:00
Cumilla(N) | 132 | 07:00 | 126 | 23:00 | Rahanpur | 137 | 05:00 | 131 | 21:00
Cumilla(S) | 131 | 05:00 | 122 | 11:00 | Rahanpur-400 | 138 | 06:00 | 132 | 19:00
Daganbhuiyan | 130 | 07:00 | 124 | 03:00 | Rahim | 133 | 09:00 | 129 | 00:00
Daudkandi | 127 | 06:00 | 120 | 21:00 | Rajbari | 131 | 06:00 | 122 | 21:00
DhakaUniversity | 135 | 03:00 | 130 | 12:00 | Rajendrapur | 131 | 06:00 | 125 | 01:00
Dhamrai | 134 | 08:00 | 126 | 15:00 | Rajshahi | 133 | 01:00 | 124 | 21:00
Dhanmondi | 136 | 06:00 | 131 | 01:00 | Rajshahi-230 | 134 | 06:00 | 126 | 21:00
Dohazari | 129 | 09:00 | 122 | 00:00 | Ramganj | 126 | 09:00 | 122 | 00:00
Faridpur | 132 | 06:00 | 125 | 19:30 | Rampur | 133 | 07:00 | 127 | 12:00
Fatullah | 133 | 18:00 | 126 | 12:00 | Rampura | 136 | 06:00 | 130 | 12:00
Fenchuganj | 132 | 06:00 | 128 | 13:00 | Rangamati | 133 | 06:00 | 129 | 00:00
Feni | 130 | 09:00 | 125 | 13:00 | Rangpur | 132 | 05:00 | 125 | 1:00
Feni-230 | 130 | 06:00 | 125 | 23:00 | Ruppur | 137 | 05:00 | 130 | 21:00
Ghatail | 127 | 18:00 | 117 | 12:00 | Saidpur | 131 | 06:00 | 123 | 00:00
Ghorashal | 137 | 08:00 | 133 | 11:00 | Santhia | 137 | 06:00 | 129 | 19:30
Goalpara | 137 | 06:00 | 126 | 21:00 | Satkhira | 133 | 05:00 | 120 | 23:00
Gollamari | 136 | 05:00 | 127 | 21:00 | Satmasjid | 133 | 07:00 | 127 | 13:00
Gopalganj | 134 | 05:00 | 126 | 21:00 | Savar | 130 | 05:00 | 124 | 09:00
Gopalganj-400 | 135 | 08:00 | 128 | 22:00 | SevenRings | 137 | 07:00 | 132 | 13:00
Gulshan | 135 | 06:00 | 130 | 12:00 | ShahCement | 132 | 08:00 | 128 | 00:00
Halishahar | 133 | 07:00 | 128 | 00:00 | Shahjadpur | 138 | 03:00 | 132 | 21:00
Haripur | 133 | 08:00 | 129 | 01:00 | Shahjibazar | 128 | 08:00 | 121 | 23:00
HaripurSBU | 133 | 08:00 | 129 | 01:00 | Shahmirpur | 134 | 07:00 | 129 | 00:00
Hasnabad | 133 | 04:00 | 127 | 12:00 | Shariatpur | 134 | 06:00 | 125 | 21:00
Hathazari | 135 | 09:00 | 131 | 00:00 | Sherpur | 131 | 15:00 | 113 | 07:00
Hatirjheel | 136 | 06:00 | 130 | 12:00 | Shikalbaha | 124 | 08:00 | 118 | 00:00
Ishurdi | 138 | 06:00 | 131 | 21:00 | Shikalbaha-230 | 134 | 07:00 | 129 | 00:00
Jaldhaka | 130 | 04:00 | 122 | 00:00 | Shitalakhya | 131 | 06:00 | 125.8 | 13:00
Jamalpur | 130 | 15:00 | 117 | 00:00 | Sholosohor | 134 | 06:00 | 130 | 00:00
Jashore | 135 | 04:00 | 118 | 13:00 | Shyampur | 132 | 18:00 | 127 | 00:00
Jhenaidah | 137 | 05:00 | 126 | 13:00 | Shyampur-230 | 133 | 06:00 | 128 | 01:00
Jhenaidah-230 | 138 | 06:00 | 126 | 13:00 | Siddhirganj | 133 | 06:00 | 129 | 01:00
Joydebpur | 134 | 06:00 | 128 | 15:00 | Sirajganj | 133 | 01:00 | 127 | 21:00
Joypurhat | 133 | 06:00 | 125 | 21:00 | Sonargaon | 133 | 03:00 | 127 | 00:00
Juldah | 133 | 07:00 | 128 | 12:00 | Sreemongol | 128 | 07:00 | 122 | 21:00
Kabirpur | 136 | 08:00 | 122 | 21:00 | Sreepur | 134 | 17:00 | 126 | 15:00
Kachua | 129 | 07:00 | 124 | 01:00 | Srinagar | 136 | 06:00 | 130 | 13:00
Kaliakoir | 138 | 08:00 | 129 | 12:00 | SSM | 138 | 05:00 | 126 | 04:00
Kaliganj | 137 | 04:00 | 120 | 15:00 | Sunamganj | 122 | 06:00 | 115 | 13:00
Kallyanpur | 132 | 05:00 | 126 | 12:00 | Sylhet | 127 | 06:00 | 122 | 13:00
Kalurghat | 135 | 07:00 | 131 | 00:00 | Sylhet-132 | 126 | 06:00 | 122 | 13:00
Kamrangirchar | 137 | 07:00 | 124 | 13:00 | Tangail | 128 | 08:00 | 120 | 12:00
Kaptai | 137 | 9:00 | 133 | 13:00 | Taraganj | 132 | 04:00 | 124 | 19:00
Kasba | 129 | 07:00 | 121 | 21:00 | Tasnim | 132 | 08:00 | 127 | 00:00
Kazla | 134 | 06:00 | 128 | 14:00 | Thakurgaon | 135 | 05:00 | 126 | 00:00
Keranigonj | 136 | 06:00 | 131 | 12:00 | TK | 135 | 06:00 | 131 | 12:00
Khagrachori | 133 | 06:00 | 128 | 13:00 | Tongi | 135 | 04:00 | 130 | 11:00
Khulna | 136 | 06:00 | 126 | 21:00 | Ullahpara | 135 | 05:00 | 128 | 19:30
Khulna(S) | 137 | 06:00 | 127 | 21:00 | Ullon | 135 | 06:00 | 130 | 12:00
Khulshi | 131 | 06:00 | 126 | 00:00 | Uttara | 133 | 07:00 | 126 | 12:00
Kishoreganj | 134 | 17:00 | 125 | 22:00 | UttaraNew | 132 | 05:00 | 126 | 13:00
Kodda | 135 | 08:00 | 127 | 12:00 | Zigatola | 136 | 06:00 | 130 | 13:00
Korerhat | 133 | 06:00 | 129 | 00:00
KSRM | 134 | 05:00 | 129 | 13:00
Kulaura | 131 | 06:00 | 126 | 00:00
Kurigram | 130 | 06:00 | 121 | 00:00
Kushtia | 137 | 02:00 | 127 | 22:00
Laksam | 128 | 06:00 | 124 | 01:00
Lakshmipur | 127 | 07:00 | 122 | 23:00
Lalbag | 136 | 05:00 | 131 | 00:00
Lalmonirhat | 130 | 06:00 | 122 | 00:00
Madanganj | 132 | 01:00 | 127 | 13:00
Madaripur | 134 | 04:00 | 128 | 19:00
Madartek | 138 | 15:00 | 128 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division