## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 10-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-05-2026 | during | 10-05-2026 | during | 10-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 274 | 320 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 15 | 55 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 302 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 36 | 53.97 | 53.97 | 17 | 36 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 105 | 149.36 | 149.36 | 46 | 46 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 17 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 0 | 19 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 14 | 14 | 14 | 14 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 12 | 48 | 52.19 | 52.19 | 16 | 52 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 286 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 75 | 106 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 105 | 105 | 105 | 70 | 70 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 90 | 162 | 162 | 35 | 88 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 495 | 496 | 584 | 584 | 584 | 584 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 305 | 277 | 718 | 718 | 335 | 335 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 37 | 134 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1627 | 2465 | 5754.22 | 5724.22 | 2591 | 2745
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 16 | 25.5 | 25.5 | 0 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 50 | 50 | 19 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 43 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 141 | 144 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 8 | 49 | 105 | 105 | 68 | 68 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 7 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 5 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 24 | 46 | 108 | 108 | 12 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.46 | 0 | 4.04 | 0 | 4.04 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 3 | 50 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 32 | 163 | 163 | 17 | 90 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1130 | 1161 | 1224 | 1224 | 1204 | 1204 | U2 on AGC
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 4 | 0 | 4 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 595 | 935 | 1150 | 1150 | 1150 | 1150 | AGC
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1955.46 | 2554 | 3873.9 | 3935.86 | 2969.04 | 3186
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 200 | 201 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 355 | 356 | 350.01 | 350.01 | 350.01 | 350.01 | FGMO not available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 0 | 0 | 342.01 | 342.01 | 270 | 270 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 300 | 393 | 393 | 393 | 240 | 240 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 39 | 40 | 41.65 | 41.65 | 40 | 40 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 5 | 20 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 73 | 102 | 195 | 195 | 50 | 50 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 150 | 150 | 150 | 25 | 140 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 9 | 23 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 144 | 147 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 100 | 200 | 200 | 17 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 152 | 144 | 84 | 78 | 84 | 78 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 17 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 18 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 89 | 115 | 115 | 17 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 71 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1416 | 1861 | 2754.44 | 2688.44 | 1654.76 | 2023.76
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-05-2026 | during | 10-05-2026 | during | 10-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 0 | 157.5 | 157.5 | 0 | 0 | Gas shortage
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 85 | 87 | 90 | 90 | 10 | 10 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 10 | 10 | 10 | 10 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 51.67 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 152.87 | 125 | 381.2 | 334 | 121.7 | 49
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 41 | 41 | 41 | 41 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 154 | 147 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 101 | 100 | 100 | 100 | 100 | 100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 28 | 20 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 102 | 100 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 332 | 334 | 370 | 370 | 370 | 370 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1216 | 1188 | 1304 | 1304 | 1234 | 1234
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 879 | 880 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 36 | 36 | 36 | 36 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 223 | 173 | 410 | 410 | 410 | 410 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 98 | 0 | 100 | 0 | 100 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1002 | 1204 | 1234.2 | 1234.2 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2202 | 2257 | 3600.2 | 3500.2 | 2772.1 | 2672.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 360 | 403 | 400 | 500 | 380 | 480 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 32 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 126 | 124 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 750 | 1100 | 1244 | 1244 | 1184 | 1184 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 247 | 227 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.61 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1703.61 | 2141 | 2562 | 2661 | 2235 | 2334
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 57.4 | 0 | 61.55 | 0 | 61.55 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 32 | 32 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 137 | 160 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 197 | 160 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 25 | 25 | 28 | 28 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0.03 | 0.03 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 51 | 93 | 93 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 110 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.5 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1048 | 1452 | 1435.88 | 1435.88 | 1365 | 1365 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 62.13 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 108 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2029.03 | 2441 | 3232.27 | 3003.87 | 2717.84 | 2574.44
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 49 | 50 | 50 | 50 | 50 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 97 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 8 | 0 | 5.4 | 0 | 5.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 110 | 115 | 115 | 0 | 70 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 37 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 206 | 0 | 200 | 0 | 200 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 300 | 256 | 533.4 | 298 | 398.4 | 233
System Total |  |  |  |  | 28823.2 | 29270.237 | 12601.97 | 15288 | 23995.63 | 23449.59 | 16693.84 | 17051.3
Forecast Scenario (10-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14750 |  | 0 |  | 14750
|  |  |  | 1:00 | 13850 |  | 0 |  | 13850
|  |  |  | 2:00 | 13320 |  | 0 |  | 13320
|  |  |  | 3:00 | 12840 |  | 0 |  | 12840
|  |  |  | 4:00 | 12610 |  | 0 |  | 12610
|  |  |  | 5:00 | 12270 |  | 0 |  | 12270
|  |  |  | 6:00 | 12080 |  | 0 |  | 12080
|  |  |  | 7:00 | 12480 |  | 0 |  | 12480
|  |  |  | 8:00 | 12420 |  | 0 |  | 12420
|  |  |  | 9:00 | 12570 |  | 0 |  | 12570
|  |  |  | 10:00 | 12810 |  | 0 |  | 12810
|  |  |  | 11:00 | 13310 |  | 0 |  | 13310
|  |  |  | 12:00 | 13800 |  | 0 |  | 13800
|  |  |  | 13:00 | 14100 |  | 0 |  | 14100
|  |  |  | 14:00 | 14340 |  | 0 |  | 14340
|  |  |  | 15:00 | 14420 |  | 0 |  | 14420
|  |  |  | 16:00 | 14310 |  | 0 |  | 14310
|  |  |  | 17:00 | 14100 |  | 0 |  | 14100
|  |  |  | 18:00 | 14280 |  | 0 |  | 14280
|  |  |  | 18:30 | 14650 |  | 0 |  | 14650
|  |  |  | 19:00 | 15180 |  | 0 |  | 15180
|  |  |  | 19:30 | 15370 |  | 0 |  | 15370
|  |  |  | 20:00 | 15360 |  | 0 |  | 15360
|  |  |  | 21:00 | 15800 |  | 0 |  | 15800
|  |  |  | 22:00 | 15400 |  | 0 |  | 15400
|  |  |  | 23:00 | 15200 |  | 0 |  | 15200
Probable Maximum Temperature: |  |  | 35.30°C
Probable Maximum Demand at Day Peak: |  |  | 13800.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15800.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15800.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 331.30 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:14 hrs on 10-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 09-05-2026 | [28 empty] | Date: | 09-05-2026 | [28 empty] | Date: | 09-05-2026 | [28 empty] | Date: | 09-05-2026 | [28 empty] | Date: | 09-05-2026 | [17 empty] | Date: | 09-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 288 | 0 | 0 | 113 | 0 | 45 | 30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 51 | 22.5 | 14 | 0 | 520 | 0 | 0 | 49 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 43 | 32 | 26 | 800 | 0 | 0 | 6 | 0 | 48 | 218 | 0 | 0 | 0 | 1060 | 0 | 70 | 26 | 393 | 356 | 0 | 51 | 5 | 199 | 40 | 34 | 149 | 50 | 18 | 19 | 0 | 158 | 0 | 0 | 0 | 305 | 0 | 355 | 42 | 30 | 153 | 0 | 17 | 0 | 84 | 20 | 100 | 0 | 100 | 0 | 9 | 78 | 11 | 0 | 0 | 0 | 6974.5 | 879 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1213 | 0 | 0 | 0 | 1360.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 50 | 33 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 127 | 220 | 0 | 444 | 1060 | 0 | 6467.56 | 13442.06 | 79.13
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 255 | 0 | 0 | 113 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 51 | 22 | 14 | 0 | 475 | 0 | 0 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 43 | 32 | 28 | 620 | 0 | 0 | 0 | 0 | 47 | 220 | 0 | 0 | 0 | 1160 | 0 | 0 | 55 | 393 | 356 | 0 | 51 | 5 | 196 | 40 | 0 | 151 | 0 | 0 | 19 | 0 | 146 | 0 | 0 | 0 | 300 | 0 | 360 | 42 | 30 | 147 | 0 | 17 | 0 | 84 | 20 | 100 | 0 | 102 | 0 | 9 | 78 | 11 | 0 | 0 | 0 | 6467 | 879 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1162 | 0 | 0 | 0 | 1328.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 51 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 127 | 220 | 0 | 400 | 1043 | 0 | 6328.3 | 12795.3 | 79.13
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 245 | 0 | 0 | 113 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 0 | 51 | 22 | 14 | 0 | 470 | 0 | 0 | 18 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 32 | 36 | 530 | 0 | 0 | 0 | 0 | 46 | 220 | 0 | 0 | 0 | 1073 | 0 | 0 | 73 | 393 | 356 | 0 | 51 | 5 | 191 | 40 | 0 | 149 | 0 | 0 | 19 | 0 | 144 | 0 | 0 | 0 | 300 | 0 | 360 | 42 | 30 | 140 | 0 | 17 | 0 | 84 | 20 | 100 | 0 | 102 | 0 | 9 | 78 | 11 | 0 | 0 | 0 | 6254 | 879 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 1107.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 128 | 220 | 0 | 360 | 910 | 0 | 5797.42 | 12051.42 | 79.13
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 267 | 0 | 0 | 80 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 51 | 23 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 17 | 36 | 530 | 0 | 0 | 0 | 0 | 33 | 220 | 0 | 0 | 0 | 1050 | 0 | 0 | 73 | 393 | 356 | 0 | 51 | 5 | 202 | 40 | 0 | 149 | 0 | 0 | 19 | 0 | 144 | 0 | 0 | 0 | 305 | 0 | 356 | 42 | 30 | 142 | 0 | 17 | 0 | 84 | 20 | 100 | 0 | 102 | 0 | 9 | 78 | 11 | 0 | 0 | 0 | 6227 | 880 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 996 | 0 | 0 | 0 | 912.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 128 | 220 | 0 | 330 | 850 | 0 | 5361.34 | 11588.34 | 79.13
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 262 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 34 | 23 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 36 | 530 | 0 | 0 | 0 | 0 | 31 | 221 | 0 | 0 | 0 | 1010 | 0 | 0 | 73 | 393 | 356 | 0 | 51 | 5 | 198 | 40 | 0 | 150 | 0 | 0 | 19 | 0 | 144 | 0 | 0 | 0 | 305 | 0 | 356 | 42 | 30 | 144 | 0 | 17 | 0 | 84 | 20 | 100 | 0 | 102 | 0 | 0 | 35 | 17 | 0 | 0 | 0 | 6065 | 879 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 0 | 0 | 0 | 910.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 128 | 220 | 0 | 313 | 780 | 0 | 5291.59 | 11356.59 | 79.13
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 21 | 14 | 0 | 530 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 36 | 530 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 1050 | 0 | 0 | 73 | 393 | 356 | 0 | 51 | 5 | 203 | 40 | 0 | 150 | 0 | 0 | 19 | 0 | 130 | 0 | 0 | 0 | 300 | 0 | 356 | 42 | 30 | 154 | 0 | 17 | 0 | 84 | 20 | 100 | 0 | 102 | 0 | 0 | 16 | 17 | 0 | 0 | 0 | 5846 | 879 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1009 | 0 | 0 | 0 | 903.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 128 | 220 | 0 | 321 | 770 | 0 | 5316.9 | 11162.9 | 79.13
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 1 | 0 | 21 | 14 | 0 | 480 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0.23 | 43 | 0 | 38 | 530 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 980 | 0 | 0 | 73 | 393 | 356 | 0 | 51 | 5 | 199 | 40 | 0 | 149 | 0 | 0 | 19 | 0 | 134 | 0 | 4 | 0 | 305 | 0 | 344 | 42 | 30 | 139 | 1 | 17 | 0 | 84 | 20 | 100 | 0 | 102 | 0 | 0 | 18 | 17 | 0.08 | 1.63 | 0 | 5779.94 | 879 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62 | 1008 | 0 | 0 | 0 | 922.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 4 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 350 | 0 | 0.04 | 0 | 51 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6 | 0.04 | 0 | 177 | 128 | 220 | 0 | 314 | 740 | 0 | 5288.14 | 11068.08 | 79.13
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 270 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 9 | 0 | 21 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1.11 | 42 | 0 | 33 | 530 | 0 | 0 | 6 | 0 | 0 | 221 | 0 | 0 | 0 | 1025 | 0 | 0 | 73 | 393 | 356 | 0 | 51 | 5 | 199 | 40 | 0 | 149 | 0 | 0 | 19 | 0 | 128 | 0 | 18 | 0 | 300 | 0 | 344 | 42 | 30 | 147 | 2 | 17 | 0 | 84 | 20 | 100 | 0 | 102 | 0 | 9 | 53 | 17 | 0.52 | 8.78 | 0 | 6001.41 | 879 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.03 | 1007 | 0 | 0 | 0 | 922.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.94 | 19 | 0 | 0 | 8.13 | 130 | 0 | 0 | 0 | 130 | 0 | 350 | 0 | 0.84 | 0 | 51 | 0 | 3 | 0 | 0 | 0 | 0 | 2.4 | 52 | 0.1 | 0 | 177 | 128 | 220 | 0 | 310 | 680 | 0 | 5318.98 | 11320.39 | 79.13
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 250 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 13 | 0 | 21 | 14 | 0 | 470 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2.15 | 41 | 0 | 11 | 525 | 0 | 0 | 6 | 0 | 0 | 220 | 0 | 0 | 0 | 985 | 0 | 0 | 73 | 350 | 356 | 0 | 51 | 5 | 192 | 40 | 0 | 149 | 0 | 0 | 12 | 0 | 128 | 0 | 15 | 8 | 310 | 0 | 344 | 42 | 30 | 139 | 3 | 17 | 0 | 84 | 20 | 101 | 0 | 102 | 0 | 9 | 75 | 9 | 0.93 | 16.85 | 0 | 5923.93 | 879 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.01 | 931 | 0 | 0 | 0 | 911.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.85 | 47 | 0 | 0 | 19.87 | 130 | 0 | 0 | 0 | 130 | 0 | 300 | 0 | 1.56 | 0 | 49 | 0 | 15 | 0 | 0 | 0 | 0 | 2 | 98 | 0.27 | 0 | 169 | 100 | 180 | 0 | 303 | 680 | 0 | 5260.14 | 11184.07 | 79.13
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 243 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 0 | 16 | 0 | 0 | 14 | 0 | 510 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1.54 | 42 | 0 | 3 | 525 | 0 | 0 | 6 | 0 | 0 | 216 | 0 | 0 | 0 | 923 | 0 | 0 | 73 | 300 | 335 | 0 | 51 | 5 | 188 | 40 | 0 | 148 | 0 | 0 | 19 | 0 | 134 | 0 | 53 | 9 | 305 | 0 | 344 | 42 | 30 | 138 | 8 | 17 | 0 | 84 | 30 | 101 | 0 | 102 | 0 | 9 | 78 | 7 | 1 | 48.73 | 0 | 5864.27 | 880 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.3 | 775 | 0 | 0 | 0 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.17 | 76 | 0 | 0 | 45.48 | 130 | 0 | 0 | 0 | 130 | 0 | 250 | 0 | 4.1 | 0 | 51 | 0 | 24 | 0 | 0 | 0 | 0 | 3.7 | 139 | 0.16 | 0 | 165 | 100 | 180 | 0 | 304 | 680 | 0 | 5157.91 | 11022.18 | 79.12
10:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 316 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 0 | 0 | 28 | 0 | 19 | 14 | 0 | 555 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 3.66 | 42 | 0 | 9 | 535 | 0 | 0 | 6 | 0 | 0 | 213 | 0 | 0 | 0 | 905 | 0 | 0 | 73 | 300 | 320 | 0 | 51 | 5 | 208 | 43 | 0 | 147 | 0 | 0 | 17 | 0 | 138 | 0 | 63 | 9 | 300 | 0 | 344 | 42 | 30 | 148 | 7 | 17 | 0 | 42 | 30 | 100 | 0 | 102 | 0 | 9 | 87 | 5 | 1.9 | 42.31 | 0 | 5975.87 | 879 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 790 | 0 | 0 | 0 | 933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.58 | 93 | 0 | 0 | 55.03 | 130 | 0 | 0 | 0 | 130 | 0 | 250 | 0 | 4.93 | 0 | 50 | 0 | 30 | 0 | 0 | 0 | 0 | 8 | 164 | 0.63 | 0 | 192 | 100 | 180 | 0 | 306 | 660 | 0 | 5275.17 | 11251.04 | 79.12
11:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 295 | 17 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 32 | 1 | 19 | 14 | 0 | 510 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.79 | 43 | 0 | 4 | 580 | 0 | 0 | 6 | 0 | 0 | 143 | 0 | 0 | 0 | 1050 | 0 | 0 | 73 | 300 | 356 | 0 | 51 | 5 | 200 | 43 | 0 | 145 | 0 | 0 | 17 | 0 | 150 | 0 | 68 | 9 | 310 | 0 | 344 | 42 | 30 | 154 | 12 | 17 | 0 | 83 | 30 | 99 | 0 | 102 | 0 | 9 | 87 | 5 | 2.2 | 44.92 | 0 | 6178.91 | 880 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 813 | 0 | 0 | 0 | 961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.37 | 106 | 0 | 0 | 61.08 | 130 | 0 | 0 | 0 | 160 | 0 | 414 | 0 | 5.37 | 0 | 48 | 0 | 34 | 0 | 0 | 0 | 0 | 8 | 199 | 0.64 | 0 | 241 | 126 | 220 | 0 | 335 | 700 | 0 | 5816.46 | 11995.37 | 79.12
12:00 | 0 | 50 | 12 | 0 | 0 | 0 | 0 | 0 | 274 | 0 | 305 | 17 | 0 | 75 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 33 | 37 | 0 | 14 | 0 | 495 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.46 | 43 | 3 | 2 | 595 | 0 | 0 | 6 | 0 | 8 | 141 | 0 | 0 | 0 | 1130 | 0 | 0 | 73 | 300 | 355 | 0 | 51 | 5 | 200 | 39 | 0 | 144 | 0 | 0 | 17 | 0 | 152 | 0 | 71 | 9 | 315 | 0 | 332 | 42 | 30 | 154 | 12 | 17 | 0 | 83 | 28 | 101 | 0 | 102 | 0 | 9 | 85 | 5 | 2.2 | 51.67 | 0 | 6367.33 | 879 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 1002 | 0 | 0 | 0 | 1048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.4 | 108 | 0 | 0 | 62.13 | 137 | 0 | 0 | 0 | 197 | 0 | 414 | 0 | 5.5 | 0 | 49 | 0 | 37 | 0 | 0 | 0 | 0 | 8 | 206 | 0.61 | 0 | 247 | 126 | 220 | 0 | 360 | 750 | 0 | 6234.64 | 12601.97 | 79.12
13:00 | 0 | 50 | 32 | 0 | 0 | 0 | 0 | 0 | 258 | 0 | 298 | 33 | 0 | 109 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 32 | 68 | 19 | 14 | 0 | 505 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.64 | 43 | 29 | 6 | 595 | 0 | 0 | 9 | 0 | 35 | 140 | 0 | 0 | 0 | 1155 | 0 | 0 | 73 | 300 | 354 | 0 | 51 | 5 | 198 | 39 | 0 | 143 | 0 | 0 | 17 | 0 | 154 | 0 | 65 | 9 | 315 | 0 | 333 | 42 | 30 | 152 | 7 | 17 | 0 | 83 | 28 | 75 | 0 | 102 | 0 | 9 | 86 | 5 | 2.1 | 49.14 | 0 | 6515.88 | 880 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 1150 | 0 | 0 | 0 | 1123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.54 | 105 | 0 | 0 | 60.26 | 160 | 0 | 0 | 0 | 207 | 0 | 414 | 0 | 5.3 | 0 | 49 | 0 | 35 | 0 | 0 | 0 | 0 | 7.7 | 199 | 0.55 | 0 | 251 | 122 | 220 | 0 | 377 | 860 | 0 | 6592.35 | 13108.23 | 79.11
14:00 | 0 | 50 | 32 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 271 | 21.6 | 0 | 113 | 15 | 145 | 14 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 17 | 301 | 0 | 0 | 29 | 68 | 0 | 14 | 0 | 522 | 0 | 0 | 24 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 3.3 | 43 | 45 | 2 | 560 | 0 | 0 | 6 | 0 | 50 | 140 | 0 | 0 | 0 | 1135 | 0 | 43 | 73 | 300 | 353 | 0 | 51 | 5 | 201 | 37 | 8 | 143 | 0 | 0 | 17 | 0 | 152 | 0 | 59 | 4 | 305 | 0 | 334 | 42 | 30 | 143 | 10 | 17 | 0 | 82 | 28 | 0 | 0 | 102 | 0 | 9 | 87 | 0 | 1.96 | 44.18 | 0 | 6587.04 | 879 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 1180 | 0 | 0 | 0 | 1115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.12 | 94 | 0 | 0 | 53.22 | 160 | 0 | 0 | 0 | 203 | 0 | 414 | 0 | 4.56 | 0 | 49 | 0 | 27 | 0 | 0 | 0 | 0 | 7 | 174 | 0.51 | 0 | 221 | 122 | 220 | 0 | 392 | 920 | 0 | 6574.41 | 13161.45 | 79.11
15:00 | 0 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 309 | 0 | 0 | 109 | 28 | 145 | 30 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 17 | 308 | 0 | 0 | 23 | 68 | 19 | 14 | 0 | 540 | 0 | 0 | 24 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 2.63 | 43 | 50 | 2 | 630 | 0 | 0 | 6 | 0 | 50 | 140 | 0 | 0 | 0 | 1165 | 0 | 56 | 73 | 350 | 348 | 0 | 51 | 5 | 206 | 35 | 30 | 145 | 0 | 0 | 19 | 0 | 140 | 0 | 34 | 0 | 305 | 0 | 334 | 42 | 30 | 149 | 8 | 17 | 0 | 80 | 20 | 20 | 0 | 102 | 0 | 9 | 87 | 0 | 1.51 | 34.97 | 0 | 6806.11 | 879 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 1190 | 0 | 0 | 0 | 1225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.33 | 74 | 0 | 0 | 41.27 | 160 | 0 | 0 | 0 | 201 | 0 | 414 | 0 | 3.77 | 0 | 49 | 0 | 21 | 0 | 0 | 0 | 0 | 5.6 | 137 | 0.42 | 0 | 245 | 122 | 220 | 0 | 390 | 910 | 0 | 6594.39 | 13400.5 | 79.11
16:00 | 0 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 284 | 0 | 1 | 106 | 30 | 175 | 30 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 17 | 298 | 0 | 0 | 16 | 68 | 19 | 14 | 0 | 490 | 0 | 0 | 24 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 1.8 | 43 | 49 | 2 | 780 | 0 | 0 | 6 | 0 | 49 | 140 | 0 | 0 | 0 | 1145 | 0 | 86 | 100 | 389 | 350 | 0 | 51 | 15 | 200 | 38 | 34 | 144 | 0 | 0 | 19 | 0 | 120 | 0 | 27 | 0 | 310 | 0 | 334 | 42 | 30 | 147 | 5 | 16 | 0 | 82 | 25 | 98 | 0 | 100 | 0 | 9 | 87 | 0 | 1.03 | 21.45 | 0 | 6884.28 | 879 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 1191 | 0 | 0 | 0 | 1259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.91 | 49 | 0 | 0 | 27.15 | 160 | 0 | 0 | 0 | 192 | 0 | 414 | 0 | 2.47 | 0 | 51 | 0 | 16 | 0 | 0 | 0 | 0 | 3.6 | 93 | 0.14 | 0 | 235 | 123 | 220 | 0 | 398 | 960 | 0 | 6501.27 | 13385.55 | 79.11
17:00 | 0 | 43 | 32 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 287 | 0 | 12 | 106 | 60 | 175 | 37 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 17 | 303 | 0 | 0 | 7 | 71 | 19 | 14 | 0 | 500 | 0 | 0 | 26 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0.84 | 43 | 50 | 2 | 775 | 0 | 0 | 6 | 0 | 48 | 140 | 0 | 0 | 0 | 1140 | 0 | 100 | 102 | 392 | 352 | 0 | 51 | 20 | 198 | 38 | 34 | 144 | 0 | 0 | 0 | 0 | 92 | 0 | 7 | 0 | 310 | 0 | 334 | 42 | 30 | 143 | 2 | 16 | 0 | 82 | 25 | 101 | 0 | 100 | 0 | 9 | 86 | 0 | 0.5 | 9.8 | 0 | 6898.14 | 879 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1192 | 0 | 0 | 0 | 1262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2 | 17 | 0 | 0 | 11.32 | 160 | 0 | 0 | 0 | 179 | 0 | 414 | 0 | 1.07 | 0 | 49 | 0 | 7 | 0 | 0 | 0 | 0 | 2 | 46 | 0.06 | 0 | 230 | 123 | 220 | 0 | 386 | 940 | 0 | 6312.65 | 13210.79 | 79.1
18:00 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 290 | 0 | 17 | 106 | 68 | 145 | 40 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 1 | 89 | 19 | 14 | 0 | 500 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 42 | 50 | 5 | 835 | 0 | 0 | 10 | 1 | 33 | 142 | 0 | 0 | 0 | 1094 | 0 | 70 | 102 | 393 | 354 | 0 | 51 | 20 | 201 | 38 | 34 | 145 | 0 | 4 | 19 | 0 | 94 | 0 | 1 | 0 | 310 | 0 | 334 | 42 | 30 | 143 | 0 | 16 | 0 | 83 | 25 | 100 | 0 | 100 | 0 | 9 | 86 | 0 | 0.1 | 1.74 | 9 | 7108.91 | 879 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1097 | 0 | 0 | 0 | 1275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99 | 7 | 12 | 0 | 3.26 | 160 | 0 | 0 | 0 | 160 | 0 | 350 | 0 | 0.26 | 0 | 49 | 18 | 1 | 34 | 0 | 0 | 0 | 0.5 | 10 | 0 | 13 | 230 | 100 | 180 | 0 | 381 | 910 | 0 | 6054.01 | 13162.92 | 79.1
19:00 | 0 | 82 | 43 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 295 | 35 | 17 | 106 | 105 | 220 | 40 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 55 | 303 | 0 | 0 | 0 | 123 | 19 | 14 | 0 | 510 | 5 | 15 | 42 | 0 | 0 | 50 | 7 | 0 | 0 | 0 | 0 | 40 | 51 | 2 | 980 | 12 | 0 | 19 | 8 | 45 | 143 | 0 | 0 | 0 | 1167 | 0 | 107 | 102 | 393 | 353 | 0 | 51 | 20 | 202 | 39 | 61 | 146 | 34 | 18 | 19 | 0 | 152 | 4 | 0 | 20 | 305 | 0 | 334 | 42 | 30 | 146 | 0 | 16 | 0 | 84 | 20 | 99 | 0 | 100 | 4 | 9 | 86 | 0 | 0 | 0 | 12 | 7974 | 879 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1212 | 0 | 0 | 0 | 1435 | 0 | 0 | 0 | 30 | 18 | 0 | 50 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 160 | 0 | 0 | 0 | 160 | 0 | 414 | 0 | 0 | 0 | 49 | 75 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 242 | 124 | 220 | 0 | 393 | 1020 | 11 | 6789 | 14763 | 79.1
19:30 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 277 | 36 | 17 | 106 | 105 | 286 | 55 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 55 | 302 | 0 | 0 | 0 | 134 | 19 | 14 | 0 | 496 | 0 | 0 | 46 | 0 | 0 | 50 | 7 | 0 | 0 | 0 | 0 | 40 | 50 | 5 | 935 | 32 | 0 | 19 | 16 | 49 | 144 | 0 | 0 | 0 | 1161 | 0 | 150 | 102 | 393 | 356 | 0 | 51 | 20 | 201 | 40 | 89 | 147 | 100 | 18 | 19 | 0 | 144 | 8 | 0 | 23 | 315 | 0 | 334 | 42 | 30 | 147 | 0 | 16 | 0 | 84 | 20 | 100 | 0 | 100 | 17 | 9 | 87 | 0 | 0 | 0 | 12 | 8193 | 880 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1204 | 0 | 0 | 0 | 1452 | 0 | 0 | 0 | 70 | 110 | 0 | 51 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 160 | 0 | 0 | 0 | 160 | 0 | 414 | 0 | 0 | 0 | 49 | 110 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 227 | 124 | 220 | 0 | 403 | 1100 | 35 | 7095 | 15288
20:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 289 | 36 | 17 | 106 | 105 | 292 | 55 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 55 | 304 | 0 | 0 | 0 | 131 | 0 | 14 | 0 | 512 | 0 | 0 | 46 | 0 | 0 | 50 | 7 | 0 | 0 | 0 | 0 | 40 | 33 | 12 | 860 | 33 | 0 | 19 | 17 | 34 | 144 | 0 | 0 | 0 | 1161 | 0 | 150 | 83 | 391 | 356 | 0 | 51 | 20 | 196 | 40 | 88 | 147 | 100 | 18 | 19 | 0 | 148 | 12 | 0 | 23 | 315 | 0 | 334 | 42 | 30 | 138 | 0 | 16 | 0 | 84 | 20 | 101 | 0 | 101 | 17 | 9 | 87 | 0 | 0 | 0 | 12 | 8086 | 879 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1208 | 0 | 0 | 0 | 1447 | 0 | 0 | 0 | 70 | 101 | 0 | 51 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 160 | 0 | 0 | 0 | 160 | 0 | 414 | 0 | 0 | 0 | 48 | 109 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 213 | 124 | 220 | 0 | 407 | 1080 | 35 | 7055 | 15141 | 79.09
21:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 287 | 36 | 17 | 106 | 105 | 292 | 55 | 24 | 90 | 0 | 0 | 0 | 0 | 0 | 35 | 306 | 0 | 0 | 0 | 123 | 19.5 | 14 | 0 | 505 | 0 | 0 | 54 | 0 | 0 | 50 | 7 | 0 | 0 | 0 | 0 | 40 | 32 | 18 | 910 | 35 | 0 | 19 | 17 | 17 | 145 | 0 | 0 | 0 | 1160 | 0 | 148 | 55 | 360 | 355 | 0 | 51 | 10 | 197 | 40 | 74 | 147 | 100 | 18 | 19 | 0 | 146 | 25 | 0 | 23 | 315 | 0 | 334 | 42 | 30 | 151 | 0 | 16 | 0 | 84 | 20 | 100 | 0 | 101 | 17 | 9 | 87 | 0 | 0 | 0 | 12 | 8092.5 | 879 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1211 | 0 | 0 | 0 | 1460 | 0 | 0 | 0 | 70 | 111 | 0 | 51 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 0 | 0 | 160 | 0 | 414 | 0 | 0 | 0 | 49 | 112 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 242 | 124 | 220 | 0 | 464 | 1078 | 35 | 7162 | 15254.5 | 79.09
22:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 289 | 36 | 17 | 106 | 105 | 293 | 55 | 24 | 90 | 0 | 0 | 0 | 0 | 0 | 17 | 302 | 0 | 0 | 0 | 105 | 19.5 | 14 | 0 | 500 | 0 | 0 | 58 | 0 | 0 | 50 | 7 | 0 | 0 | 0 | 0 | 41 | 32 | 24 | 855 | 35 | 0 | 19 | 17 | 14 | 146 | 0 | 0 | 0 | 1160 | 0 | 145 | 26 | 390 | 356 | 0 | 51 | 10 | 197 | 40 | 69 | 147 | 100 | 19 | 19 | 0 | 150 | 25 | 0 | 23 | 310 | 0 | 334 | 42 | 30 | 146 | 0 | 16 | 0 | 84 | 20 | 100 | 0 | 101 | 17 | 9 | 77 | 0 | 0 | 0 | 12 | 7976.5 | 880 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1218 | 0 | 0 | 0 | 1444 | 0 | 0 | 0 | 70 | 113 | 0 | 51 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 0 | 0 | 160 | 0 | 414 | 0 | 0 | 0 | 48 | 110 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 231 | 126 | 220 | 0 | 501 | 1081 | 35 | 7182 | 15158.5 | 79.09
23:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 315 | 36 | 17 | 106 | 75 | 293 | 55 | 24 | 72 | 0 | 0 | 0 | 0 | 0 | 17 | 313 | 0 | 0 | 0 | 86 | 19 | 14 | 0 | 540 | 0 | 0 | 56 | 0 | 0 | 49 | 7 | 0 | 0 | 0 | 0 | 42 | 0 | 24 | 860 | 0 | 0 | 19 | 8 | 15 | 145 | 0 | 0 | 0 | 1162 | 0 | 140 | 26 | 393 | 355 | 0 | 51 | 10 | 202 | 40 | 56 | 147 | 95 | 18 | 19 | 0 | 158 | 25 | 0 | 30 | 315 | 0 | 334 | 42 | 30 | 143 | 0 | 16 | 0 | 84 | 20 | 100 | 0 | 101 | 17 | 9 | 77 | 0 | 0 | 0 | 12 | 7907 | 879 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1215 | 0 | 0 | 0 | 1456 | 0 | 0 | 0 | 70 | 113 | 0 | 51 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 160 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 48 | 114 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 227 | 126 | 220 | 0 | 450 | 1040 | 35 | 7077 | 14984 | 79.08
Total KWH | 0 | 993600 | 517440 | 0 | 0 | 0 | 0 | 0 | 6516000 | 0 | 7115550 | 261360 | 143640 | 2061216 | 795840 | 2351269 | 540736 | 88140 | 804960 | 0 | 0 | 0 | 0 | 0 | 270476 | 7212176 | 0 | 0 | 231687 | 1401600 | 433200 | 347040 | 0 | 12169545.45 | 13800 | 17564 | 561600 | 0 | 62737 | 314817 | 34368 | 0 | 0 | 0 | 29879 | 979200 | 584600 | 385440 | 16094545.46 | 130473 | 0 | 187200 | 66681 | 646509 | 4302850 | 0 | 0 | 0 | 26143634 | 0 | 1239490 | 1722909 | 8841500 | 8807600 | 0 | 1249360 | 228000 | 4951000 | 954360 | 564480 | 3528037 | 554880 | 101640 | 453790 | 0 | 3321040 | 121070 | 511018 | 184080 | 7457000 | 0 | 8354000 | 998000 | 723600 | 3505827.27 | 78986 | 396480 | 0 | 1918080 | 544896 | 2139700 | 0 | 2445490 | 95400 | 192000 | 1800000 | 129600 | 15950 | 365810 | 70800 | 163377246.18 | 21261818 | 4877280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 663840 | 25912730 | 0 | 0 | 0 | 27709091 | 0 | 0 | 0 | 388032 | 575808 | 0 | 274601 | 0 | 0 | 386784 | 806650 | 143839 | 0 | 444000 | 3629818 | 0 | 0 | 0 | 3990372 | 0 | 9139781 | 0 | 39000 | 0 | 1174254 | 646043 | 244471 | 629328 | 0 | 0 | 0 | 54158.16 | 1500480 | 4080 | 194976 | 5106000 | 2905000 | 5343970 | 0 | 9323636 | 21675636.36 | 193200 | 149238676.52 | 312615922.7

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 09-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12601.97 | MW | 12:00 Hr. | Energy Generated |  |  | 312.6159 |  | MKWHr.
| Day Peak Demand |  |  | 12642.97 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.707 |  | MKWHr.
| Evening Peak Generation |  |  | 15288 | MW | 19:30 Hr. | Energy Demand |  |  | 313.3229 |  | MKWHr.
| Evening Peak Demand |  |  | 15414 | MW | 19:30 Hr. | Maximum Temperature |  |  | 35 |  | °C
| Minimum Generation of the Day |  |  | 11022.18 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 939.58 |  | MMCFD
| Maximum Generation of the Day |  |  | 15288 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.0319 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.7935 | 0 | 10.2303 | 0 | 0 | 0.23169 | 0 | 0 | 44.2555 | Gas | 127.7173 | Gas | 448843742.7849
| Chattogram Zone |  |  | 4.6883 | 42.2382 | 2.5576 | 0 | 0.9792 | 0.029879 | 0 | 0.062737 | 50.5559 | Coal | 105.4304 | Coal | 704306907.761
| Cumilla Zone |  |  | 30.7366 | 0 | 2.7656 | 0 | 0 | 0.51102 | 3.321 | 0 | 37.3343 | HFO | 20.7576 | HFO | 343092900.26
| Mymensingh Zone |  |  | 0.1296 | 0 | 2.1582 | 0 | 0 | 0.38176 | 0 | 0 | 2.6696 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.4831 | 0 | 0 | 0 | 0 | 0.078986 | 0 | 0 | 28.5621 | Hydro | 0.9792 | Hydro | 97920
| Khulna Zone |  |  | 4.8773 | 25.9127 | 0 | 0 | 0 | 0.66384 | 21.2618 | 0 | 52.7157 | Solar | 5.3768 | Solar | 86804250.56
| Barishal Zone |  |  | 8.249 | 36.1053 | 0.38818 | 0 | 0 | 0.00408 | 0 | 0 | 44.7465 | Import | 52.2919 | Import | 301591755.01
| Rajshahi Zone |  |  | 16.76 | 0 | 1.3823 | 0 | 0 | 1.6764 | 27.7091 | 0 | 47.5278 | Wind | 0.062737 | Wind | 922861.27
| Rangpur Zone |  |  | 0 | 1.1743 | 1.2754 | 0 | 0 | 1.7991 | 0 | 0 | 4.2487
| Total |  |  | 127.7173 | 105.4304 | 20.7576 | 0 | 0.9792 | 5.3768 | 52.2919 | 0.062737 | 312.6159
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 448843742.7849 |  | Hydro | 97920
|  |  |  | Coal | 704306907.761 |  | Solar | 86804250.56
|  |  |  | HFO | 343092900.26 |  | Import | 301591755.01
|  |  |  | HSD | 0 |  | Wind | 922861.27
[5 empty] | Total: | 188,56,60,337 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.2618 | Peak Hr Flow | 880.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 53045618.18 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.7091 | Peak Hr Flow | 1452.00 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2375 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.321 | Peak Hr Flow | 144.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2909 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.2919 | Peak Hr Flow | 2476.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5672
|  |  |  | Chattogram |  | 0 |  | 1496
|  |  |  | Cumilla |  | 0 |  | 1471
|  |  |  | Mymensingh |  | 121 |  | 1132
|  |  |  | Sylhet |  | 0 |  | 619
|  |  |  | Khulna |  | 0 |  | 1584
|  |  |  | Barishal |  | 0 |  | 474
|  |  |  | Rajshahi |  | 0 |  | 1490
|  |  |  | Rangpur |  | 0 |  | 944
|  |  |  | Total |  | 121 |  | 14882
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:28 | 12:30 | Kulaura 132/33kV S/S TR-2 LT Scheduled S/D Due to PDB bus DS maintenance.shudown taken by | [7 empty] | 10.0MW load
|  |  | PDB authority. | [7 empty] | interrup.
| 08:28 | 12:30 | Kulaura 132/33kV S/S TR-2 HT Scheduled S/D Due to PDB bus DS maintenance.shudown taken by | [7 empty] | 10.0MW load
|  |  | PDB authority. | [7 empty] | interrup.
| 08:35 | 15:03 | Khulna (S)-Satkhira 132kV Ckt-1 Scheduled S/D from Satkhira 132/33kV end Due to 110v DC | [7 empty] | 43.0MW load
|  |  | system installation work and from Khulna(S) 230/132kVend. | [7 empty] | interrup. Satkhira
132/33kV end
| 08:35 | 15:06 | Khulna (S)-Satkhira 132kV Ckt-2 Scheduled S/D from Satkhira 132/33kV end Due to 110v DC | [7 empty] | 42.5MW load
|  |  | system installation work and from Khulna(S) 230/132kVend. | [7 empty] | interrup. Satkhira
132/33kV end
| 08:39 | 13:48 | Benapole-Jashore 132 kV Ckt-1 Forced S/D from Benapole 132/33kV end Due to VT MCB fail
Maintenance and from Jashore 132/33kVend.
| 09:10 | 18:13 | Tongi 230/132/33kV S/S T-04 LT Scheduled S/D
| 09:10 | 18:13 | Tongi 230/132/33kV S/S T-04 HT Scheduled S/D
|  | 09:17 | Feni 132/33kV S/S T-1(405T) LT is restored.
|  | 09:17 | Feni 132/33kV S/S T-1(405T) HT is restored.
| 09:19 | 12:06 | Daudkandi 132/33kV S/S Transformer-2 LT Scheduled S/D Due to 33 kV bay extension works by | [7 empty] | 60.0MW load
|  |  | Comilla PBS-3 | [7 empty] | interrup.
| 09:20 | 12:53 | Savar 132/33kV S/S T-1 LT Scheduled S/D
| 09:20 | 12:04 | Daudkandi 132/33kV S/S Transformer-2 HT Scheduled S/D Due to 33 kV bay extension works by | [7 empty] | 60.0MW load
|  |  | Comilla PBS-3 | [7 empty] | interrup.
| 09:21 | 12:51 | Savar 132/33kV S/S T-1 HT Scheduled S/D
| 09:22 | 16:03 | Savar 132/33kV S/S T-2 LT Scheduled S/D
| 09:23 | 16:02 | Savar 132/33kV S/S T-2 HT Scheduled S/D
| 09:26 | 16:10 | Savar 132/33kV S/S T-3 LT Scheduled S/D
| 09:27 | 16:08 | Savar 132/33kV S/S T-3 HT Scheduled S/D
| 09:28 | 16:06 | Savar 132/33kV S/S T-4 LT Scheduled S/D
| 09:31 | 16:04 | Savar 132/33kV S/S T-4 HT Scheduled S/D
| 09:35 | 21:14 | Baghabari-Sirajganj 230 kV Ckt-1 Scheduled S/D from Baghabari 230/132kV end Due to DFDR
Commissioning work and from Sirajgonj 230 end Due to DFDR commitioning and testing
Baghabari end
| 09:40 | 16:00 | Savar 132/33kV S/S Main Bus-I Scheduled S/D
| 09:42 | 10:58 | Bogura-Bogura (New)) 132 kV Ckt-1 Scheduled S/D from Bogura 132/33kV end Due to New
Bogura-1 Sf6 gas pressar meetar repear and from Bogura 230/132kV end Due to Old Bogura132
Kv Substation issue.
| 09:44 | 13:54 | Savar 132/33kV S/S Bus-A Scheduled S/D
| 09:45 | 16:01 | Savar 132/33kV S/S Bus-B Scheduled S/D
| 10:02 |  | Mymensingh 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D Due to For oil Centrfuse
|  | 10:03 | Chandpur 132/33kV S/S 402T (T-01) HT is restored.
|  | 10:03 | Chandpur 132/33kV S/S 402T (T-01) LT is restored.
|  | 10:03 | Chandpur 132/33kV S/S 402T (T-01) LT is restored.
| 11:05 | 11:25 | Lalmonirhat 132/33kV S/S T-2 (415T) HT Forced S/D Due to Transformer breaker Commission
|  | 11:30 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) HT is restored.
|  | 11:31 | Chuadanga 132/33kV S/S 132kV Tr. T3 HT is restored.
|  | 11:31 | Chuadanga 132/33kV S/S 132kV Tr. T3 LT is restored.
|  | 11:36 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) LT is restored.
| 11:41 | 13:56 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) HT Scheduled S/D Due to 33kV Busbar | [7 empty] | 45.0MW load
|  |  | Maintenance. | [7 empty] | interrup.
| 11:42 | 13:58 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) LT Scheduled S/D Due to 33kV Busbar | [7 empty] | 45.0MW load
|  |  | Maintenance. | [7 empty] | interrup.
| 12:00 |  | Day Peak Generation is 12599 MW.
| 12:20 | 19:17 | Kabirpur -Tongi 132kV Ckt-2 Project Work S/D from Tongi 230/132/33kV end Due to Project
work
| 12:27 | 16:05 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Project Work S/D Due to R phase CT Oil Leakage
Maintenance
| 12:27 | 16:06 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Project Work S/D Due to R phase CT Oil Leakage | [7 empty] | 10.0MW load
|  |  | Maintenance | [7 empty] | interrup.
| 13:24 | 18:04 | Gopalganj-Madhumati 132kV Ckt-1 Project Work S/D from Gopalganj 132/33kV end Due to
Main bus connection of T3
| 13:26 | 17:48 | Gopalganj 132/33kV S/S Gopalganj 100 MW PS Project Work S/D Due to Main bus connection of
T3
| 13:26 | 17:52 | Gopalganj 132/33kV S/S Gallamari-1 Project Work S/D Due to Bus connection of T3 | [7 empty] | 1.0MW load
interrup.
| 13:27 | 17:55 | Gopalganj 132/33kV S/S Gallamari-2 Project Work S/D Due to Bus connection of T 3 | [7 empty] | 1.0MW load
interrup.
| 13:29 | 17:24 | Gopalganj (O) - Gopalgan (N) Ckt-1 Scheduled S/D from Gopalganj 400/132kV end. and from | [7 empty] | and 40.0MW load
|  |  | Gopalganj 132/33kV end Due to Bus connection of T3 | [7 empty] | interrup. Gopalganj
132/33kV end
| 13:38 | 17:24 | Gopalganj 132/33kV S/S Main Bus Project Work S/D Due to Bus connection of T3 | [7 empty] | 82.0MW load
interrup.
| 13:38 | 17:39 | Gopalganj- Gopalganj(N) 132kV Ckt-2 Scheduled S/D from Gopalganj 400/132kV end. and from | [7 empty] | and 40.0MW load
|  |  | Gopalganj 132/33kV end Due to Bus connection of T3 | [7 empty] | interrup. Gopalganj
132/33kV end
| 14:51 |  | Shahjibazar 330 MW CCPP GT was sync.
| 16:27 | 16:40 | Cumilla(S) 132/33kV S/S TR-4 LT Tripped showing REF615 relays Due to FEEDER FAULT | [7 empty] | 30.0MW load
interrup.
| 16:27 | 16:40 | Cumilla(S) 132/33kV S/S TR-3 HT Tripped showing REF 615 relays Due to Feeder fault | [7 empty] | 30.0MW load
interrup.
|  | 16:36 | Coxsbazar 132/33kV S/S T3 HT is restored.
| 17:02 |  | Haripur EGCB 412 MW CCPP ST was sync.
| 17:02 |  | Haripur 412 MW CCPP Synchronized with remarks:- ST
| 18:06 |  | Dhaka University - Rampura 132kV ckt-1 Tripped from Rampura 230/132kV end showing 87L
trip 21 trip Z com trip relays Due to N/A
|  | 18:22 | Barishal-Barishal(N) 132 kV Ckt-1 is restored.
|  | 19:42 | Baroaulia-Hathazari 132 kV Ckt-1 is restored.
| 20:31 | 21:42 | Kabirpur -Tongi 132kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to SCADA
integration
| 22:21 | 23:46 | Srinagar 132/33kV S/S Tr-02 LT Scheduled S/D Due to Red Hot Maintenance by PBS at Feeder | [7 empty] | 12.0MW load
|  |  | No -05 | [7 empty] | interrup.
| 22:23 | 23:44 | Srinagar 132/33kV S/S Tr-02 HT Scheduled S/D Due to Red Hot Maintenance by PBS at Feeder | [7 empty] | 12.0MW load
|  |  | No -05 | [7 empty] | interrup.
| 02:02 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 04:52 | 05:10 | Brahmanbaria 132/33kV S/S 402T LT Tripped showing EF & OC relays. | [7 empty] | 70.0MW load
interrup.
| 06:00 |  | Minimum generation 12244 MW
| 07:00 | 08:00 | Bogura-Rahanpur 400kV Ckt-2 Project Work S/D from Bogura 400/230kV end Due to Energy
Meter Change at Rahanpur and from Rahanpur 400/132kV end Due to Due to check energy meter
change.
| 07:37 |  | Barishal-Barishal(N) 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to Ofcn
work and from Barishal 230/132kVend.
| 07:53 |  | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D | [7 empty] | 25.0MW load
interrup.
| 07:53 |  | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D | [7 empty] | 25.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 09-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 320 | 6516000 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 540736 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 302 | 7212176 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 36 | 261360 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 105 | 795840 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 88140 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 270476 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 433200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 347040 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 48 | 517440 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 286 | 2351269 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 106 | 2061216 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 993600 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 804960 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 231687 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 143640 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 496 | 12169545.45 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 277 | 7115550 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 134 | 1401600 | Engine Problem
Dhaka Area Total |  |  |  |  | 6668.974 | 2465 | 44255475.45
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 16 | 66681 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 0 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 187200 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 979200 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 144 | 4302850 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 49 | 646509 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 7 | 34368 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 314817 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 5 | 385440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 46 | 561600 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 29879 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 17564 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 50 | 584600 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 13800 | -
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 32 | 130473 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1161 | 26143634 | AGC
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 62737 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 935 | 16094545.46 | AGC
Chattogram Area Total |  |  |  |  | 4898.863 | 2554 | 50555897.46
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 201 | 4951000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 356 | 8807600 | FGMO not available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 0 | 0 | Under maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 8841500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 40 | 954360 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 20 | 228000 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 102 | 1722909 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1249360 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 1239490 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 184080 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 147 | 3528037 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 554880 | -
| Import (Tripura) |  | Import | 0 | 160 | 144 | 3321040 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 121070 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 453790 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 18 | 101640 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 564480 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 511018 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1861 | 37334254
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 129600 | Under Maintenance
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 1800000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 192000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 365810 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 70800 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 95400 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 125 | 2669560
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 78986 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 998000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 723600 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 147 | 3505827.27 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 100 | 2139700 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 544896 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1918080 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2445490 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 396480 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7457000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 334 | 8354000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1188 | 28562059.27
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 880 | 21261818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 173 | 4877280 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 663840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1204 | 25912730 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2257 | 52715668
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 403 | 9323636 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 194976 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 124 | 2905000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1100 | 21675636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5343970 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 193200 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 227 | 5106000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4080 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2141 | 44746498.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 386784 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 160 | 3629818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Fuel shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 160 | 3990372 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9139781 | Gas shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 143839 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 274601 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 110 | 575808 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 70 | 388032 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 39000 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1452 | 27709091 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 444000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 806650 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2441 | 47527776
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1174254 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 97 | 629328 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 54158.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 110 | 646043 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 244471 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1500480 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 256 | 4248734.16
Eastern Grid Total |  |  |  |  | 17418.042 | 8193 | 163377246.18
Western Grid Total |  |  |  |  | 11852.195 | 7095 | 149238676.52
National Grid Total |  |  |  |  | 29270.237 | 15288 | 312615922.7
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 09-05-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10269.1 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4491.4 | MW
i) Dhaka area |  |  | 5671.7 |  | MW | i) Khulna area |  |  |  | 1584 | MW
ii) Chattogram area |  |  | 1496.4 |  | MW | ii) Barishal area |  |  |  | 473.6 | MW
iii) Cumilla area |  |  | 1471 |  | MW | iii) Rajshahi area |  |  |  | 1489.8 | MW
iv) Mymensingh area |  |  | 1011 |  | MW | iv) Rangpur area |  |  |  | 944 | MW
v) Sylhet area |  |  | 619 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14760.5 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 13 | 01:00 | 67 | Hasnabad | 96 | 19:30 | 133 | Natore | 149 | 20:00
2 | AKSML | 96 | 04:00 | 68 | Hathazari | 97 | 19:00 | 134 | Nawabganj | 61.4 | 19:30
3 | Aftabnagar | 40 | 13:00 | 69 | Hatirjheel | 37 | 16:00 | 135 | Netrakona | 118 | 20:00
4 | Agargaon | 119 | 13:00 | 70 | Ishurdi | 83 | 19:30 | 136 | New | 83.6 | 12:00
5 | Agrabad | 58 | 00:00 | 71 | Jaldhaka | 72 | 19:30 | 137 | Niamatpur | 62 | 19:00
6 | Amnura | 26 | 21:00 | 72 | Jamalpur | 88 | 00:00 | 138 | Noapara | 46 | 19:30
7 | Ashuganj | 88 | 00:00 | 73 | Jashore | 125 | 13:00 | 139 | PHP | 10 | 12:00
8 | BSRM | 207 | 07:00 | 74 | Jhenaidah | 97 | 00:00 | 140 | Pabna | 101 | 19:00
9 | Bagerhat | 83 | 19:30 | 75 | Joydebpur | 168 | 19:00 | 141 | Palashbari | 110 | 23:00
10 | Bajitpur | 91 | 20:00 | 76 | Joypurhat | 59 | 21:00 | 142 | Panchagarh | 58 | 19:30
11 | Bakerganj | 11.1 | 19:30 | 77 | Juldah | 17 | 12:00 | 143 | Patiya | 11.7 | 19:00
12 | Bakulia | 96 | 22:00 | 78 | KSRM | 11 | 12:00 | 144 | Patuakhali | 71 | 22:00
13 | Banani | 41.6 | 13:00 | 79 | Kabirpur | 291 | 18:30 | 145 | Payra | 34 | 01:00
14 | Bangabhaban | 6 | 10:00 | 80 | Kachua | 96 | 21:00 | 146 | Postogola | 55 | 13:00
15 | Barapukuria | 59 | 20:00 | 81 | Kaliganj | 17 | 00:00 | 147 | Pubail | 24 | 18:30
16 | Barguna | 20 | 00:00 | 82 | Kallyanpur | 114 | 19:00 | 148 | Purbachal | 34 | 12:00
17 | Barishal | 114 | 13:00 | 83 | Kalurghat | 43 | 19:00 | 149 | Purbasadipur | 127 | 20:00
18 | Barishal-230 | 102 | 19:30 | 84 | Kamrangirchar | 79 | 12:00 | 150 | Rahanpur | 33 | 22:00
19 | Baroaulia | 62 | 21:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 35 | 08:00
20 | Baroirhat | 54 | 19:30 | 86 | Kasba | 39 | 19:30 | 152 | Rajbari | 83 | 18:30
21 | Bashundhara | 185 | 13:00 | 87 | Kazla | 120 | 13:00 | 153 | Rajendrapur | 130 | 19:00
22 | BashundharaCement | 12 | 17:00 | 88 | Keranigonj | 89 | 20:00 | 154 | Rajshahi | 123 | 22:00
23 | Beanibazar | 76 | 19:30 | 89 | Khagrachori | 34 | 19:00 | 155 | Rajshahi-230 | 76 | 22:00
24 | Benapole | 74 | 14:00 | 90 | Khulna | 63 | 13:00 | 156 | Ramganj | 118 | 19:00
25 | Bhaluka | 179 | 19:00 | 91 | Khulshi | 178 | 22:00 | 157 | Rampur | 46 | 23:00
26 | Bhandaria | 54 | 19:00 | 92 | Kishoreganj | 136 | 19:00 | 158 | Rangamati | 17 | 19:00
27 | Bhangura | 39 | 19:30 | 93 | Kodda | 338 | 21:00 | 159 | Rangpur | 142 | 19:00
28 | Bheramara(GK) | 68 | 19:00 | 94 | Kulaura | 58 | 19:00 | 160 | Ruppur | 2.4 | 14:00
29 | Bhulta | 197 | 20:00 | 95 | Kurigram | 67 | 19:30 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 70 | 22:00 | 96 | Kushtia | 156 | 19:30 | 162 | Saidpur | 103 | 19:00
31 | Bogura | 160 | 19:00 | 97 | Laksam | 35 | 19:00 | 163 | Santhia | 36 | 19:00
32 | Borhanuddin | 94 | 19:00 | 98 | Lakshmipur | 40 | 19:30 | 164 | Satkhira | 124 | 19:00
33 | Brahmanbaria | 134 | 20:00 | 99 | Lalbag | 68 | 13:00 | 165 | Satmasjid | 100 | 14:00
34 | Cantonment | 112 | 13:00 | 100 | Lalmonirhat | 60 | 20:00 | 166 | Savar | 218 | 21:00
35 | Chandina | 42 | 19:00 | 101 | MI_Cement | 17.2 | 11:00 | 167 | SevenRings | 15.28 | 15:00
36 | Chandpur | 87 | 22:00 | 102 | Madanganj | 42 | 15:00 | 168 | ShahCement | 40 | 00:00
37 | Chandraghona | 39 | 20:00 | 103 | Madaripur | 114 | 19:30 | 169 | Shahjadpur | 84 | 19:30
38 | Chapai | 69 | 21:00 | 104 | Madartek | 78 | 22:00 | 170 | Shahjibazar | 120 | 22:00
39 | Charsaidpur | 43 | 16:00 | 105 | Madunaghat | 59 | 23:00 | 171 | Shahmirpur | 65 | 18:00
40 | Chauddagram | 85 | 19:00 | 106 | Magura | 55 | 00:00 | 172 | Shariatpur | 93 | 20:00
41 | Chhatak | 40 | 19:30 | 107 | Mahasthangarh | 78 | 19:30 | 173 | Sherpur | 108 | 13:00
42 | Chowmuhani | 154 | 18:30 | 108 | Maijdee | 48 | 21:00 | 174 | Shikalbaha | 38 | 00:00
43 | Chuadanga | 116 | 19:30 | 109 | Manikganj | 130 | 15:00 | 175 | Shitalakhya | 87.2 | 16:00
44 | Coxsbazar | 152 | 22:00 | 110 | Maniknagar | 70 | 13:00 | 176 | Sholosohor | 47 | 12:00
45 | Cumilla(N) | 124 | 22:00 | 111 | Matarbari | 53 | 19:30 | 177 | Shyampur | 200 | 13:00
46 | Cumilla(S) | 157 | 00:00 | 112 | Matuail | 76 | 15:00 | 178 | Siddhirganj | 132 | 12:00
47 | Daganbhuiyan | 42 | 22:00 | 113 | Metrorail_Motijheel | 16 | 14:00 | 179 | Sirajganj | 120 | 19:30
48 | Daudkandi | 152 | 20:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sonargaon | 145 | 19:30
49 | DhakaUniversity | 78 | 13:00 | 115 | Millgate | 100 | 15:00 | 181 | Sreemongol | 85 | 20:00
50 | Dhamrai | 130 | 20:00 | 116 | Mirpur | 140 | 15:00 | 182 | Sreepur | 113 | 19:00
51 | Dhanmondi | 113 | 13:00 | 117 | Mirsorai | 57 | 14:00 | 183 | Srinagar | 51.6 | 22:00
52 | Dohazari | 100 | 22:00 | 118 | Mirzapur | 39 | 13:00 | 184 | Sunamganj | 60 | 19:00
53 | Faridpur | 168 | 20:00 | 119 | Mithapukur | 58 | 19:30 | 185 | Sylhet | 66 | 19:00
54 | Fatullah | 91 | 15:00 | 120 | Modern | N/A | N/A | 186 | Sylhet-132 | 115 | 14:00
55 | Fenchuganj | 43 | 19:00 | 121 | Mogbazar | 79.9 | 13:00 | 187 | TK | 25 | 19:30
56 | Feni | 116 | 18:30 | 122 | Mongla | 36 | 15:00 | 188 | Tangail | 148 | 00:00
57 | GPH | 77 | 12:00 | 123 | Motijheel | 44 | 13:00 | 189 | Taraganj | 25 | 19:00
58 | Ghatail | 70 | 00:00 | 124 | Muktagacha | 32 | 19:00 | 190 | Tasnim | 24 | 23:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 114 | 20:00 | 191 | Thakurgaon | 100 | 19:30
60 | Ghorashal-230 | 113 | 20:00 | 126 | Muradnagar | 52 | 20:00 | 192 | Tongi | 159 | 15:00
61 | Goalpara | 39 | 20:00 | 127 | Mymensingh | 150 | 19:30 | 193 | Ullahpara | 43 | 19:30
62 | Gollamari | 102 | 13:00 | 128 | Nabinagar | 93 | 12:00 | 194 | Ullon | 54 | 19:00
63 | Gopalganj | 117 | 18:30 | 129 | Naogaon | 128 | 19:30 | 195 | Uttara | 84 | 14:00
64 | Gulshan | 104 | 14:00 | 130 | Narail | 49.5 | 13:00 | 196 | UttaraNew | 54 | 22:00
65 | Halishahar | 100 | 14:00 | 131 | Narinda | 74 | 13:00 | 197 | Zigatola | 92 | 14:00
66 | HaripurSBU | 134 | 00:00 | 132 | Narshingdi | 198 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 09-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13442.06 | 0 |  | 13442.06
1:00 | 12795.3 | 0 |  | 12795.3
2:00 | 12051.42 | 0 |  | 12051.42
3:00 | 11588.34 | 0 |  | 11588.34
4:00 | 11356.59 | 0 |  | 11356.59
5:00 | 11162.9 | 0 |  | 11162.9
6:00 | 11068.08 | 0 |  | 11068.08
7:00 | 11320.39 | 0 |  | 11320.39
8:00 | 11184.07 | 0 |  | 11184.07
9:00 | 11022.18 | 0 |  | 11022.18
10:00 | 11251.04 | 0 |  | 11251.04
11:00 | 11995.37 | 0 |  | 11995.37
12:00 | 12601.97 | 39 |  | 12642.97
13:00 | 13108.23 | 33 |  | 13142.23
14:00 | 13161.45 | 0 |  | 13161.45
15:00 | 13400.5 | 0 |  | 13400.5
16:00 | 13385.55 | 0 |  | 13385.55
17:00 | 13210.79 | 0 |  | 13210.79
18:00 | 13162.92 | 53 |  | 13217.92
19:00 | 14763 | 121 |  | 14889
19:30 | 15288 | 121 |  | 15414
20:00 | 15141 | 123 |  | 15270
21:00 | 15254.5 | 120 |  | 15379.5
22:00 | 15158.5 | 107 |  | 15270.5
23:00 | 14984 | 111 |  | 15100
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 09-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 129 | -11 | 556 | 130 | 1694 | 352 | Ishurdi-Ghorashal Ckt-1 | Export | 4034618.18
1:00 | 168 | 0 | 656 | 140 | 1824 | 378
2:00 | 204 | 12 | 656 | 142 | 1772 | 402 |  | Import | 0
3:00 | 183 | 6 | 630 | 140 | 1582 | 380
4:00 | 159 | -3 | 550 | 100 | 1468 | 348 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 176 | 3 | 580 | 118 | 1622 | 410
6:00 | 161 | -2 | 560 | 112 | 1478 | 394 |  | Import | 0
7:00 | 145 | -4 | 510 | 116 | 1396 | 386
8:00 | 172 | -3 | 550 | 130 | 1482 | 408 | Sirajganj-Sreepur Ckt-1 | Export | 3701000
9:00 | 190 | 0 | 590 | 134 | 1532 | 444
10:00 | 199 | 6 | 610 | 164 | 1624 | 506 |  | Import | 0
11:00 | 205 | 8 | 680 | 190 | 1730 | 528
12:00 | 202 | 6 | 700 | 186 | 1830 | 552 | Sirajganj-Sreepur Ckt-2 | Export | 3710000
13:00 | 203 | 6 | 700 | 178 | 2006 | 534
14:00 | 188 | -2 | 670 | 148 | 1972 | 494 |  | Import | 0
15:00 | 187 | 1 | 690 | 188 | 2020 | 514
16:00 | 167 | 3 | 640 | 150 | 1930 | 496 | Gopalganj-Aminbazar Ckt-1 | Export | 20770000
17:00 | 158 | 7 | 630 | 154 | 1900 | 510
18:00 | 150 | 9 | 570 | 138 | 1668 | 446 |  | Import | 0
18:30 | 150 | 9 | 590 | 156 | 1728 | 474
19:00 | 113 | -6 | 550 | 168 | 1594 | 360 | Gopalganj-Aminbazar Ckt-2 | Export | 20830000
19:30 | 123 | -6 | 570 | 144 | 1682 | 390
20:00 | 122 | -8 | 570 | 140 | 1662 | 378 |  | Import | 0
21:00 | 129 | -6 | 620 | 170 | 1804 | 392
22:00 | 135 | -7 | 630 | 164 | 1804 | 376 |  | Total Export | 53045618.18
23:00 | 142 | -2 | 640 | 186 | 1818 | 420 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 09-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6974.5 | 6467.56 | 13442.06 | DAILY GENERATION CURVE
00:30 | 6720.75 | 6397.93 | 13118.68
01:00 | 6467 | 6328.3 | 12795.3 | 09-05-2026
01:30 | 6360.5 | 6062.86 | 12423.36
02:00 | 6254 | 5797.42 | 12051.42
02:30 | 6240.5 | 5579.38 | 11819.88
03:00 | 6227 | 5361.34 | 11588.34
03:30 | 6146 | 5326.465 | 11472.465
04:00 | 6065 | 5291.59 | 11356.59
04:30 | 5955.5 | 5304.245 | 11259.745
05:00 | 5846 | 5316.9 | 11162.9
05:30 | 5812.97 | 5302.52 | 11115.49
06:00 | 5779.94 | 5288.14 | 11068.08
06:30 | 5890.675 | 5303.56 | 11194.235
07:00 | 6001.41 | 5318.98 | 11320.39
07:30 | 5962.67 | 5289.56 | 11252.23
08:00 | 5923.93 | 5260.14 | 11184.07
08:30 | 5894.1 | 5209.025 | 11103.125
09:00 | 5864.27 | 5157.91 | 11022.18
09:30 | 5920.07 | 5216.54 | 11136.61
10:00 | 5975.87 | 5275.17 | 11251.04
10:30 | 6077.39 | 5545.815 | 11623.205
11:00 | 6178.91 | 5816.46 | 11995.37
11:30 | 6273.12 | 6025.55 | 12298.67
12:00 | 6367.33 | 6234.64 | 12601.97
12:30 | 6441.605 | 6413.495 | 12855.1
13:00 | 6515.88 | 6592.35 | 13108.23
13:30 | 6551.46 | 6583.38 | 13134.84
14:00 | 6587.04 | 6574.41 | 13161.45
14:30 | 6696.575 | 6584.4 | 13280.975
15:00 | 6806.11 | 6594.39 | 13400.5
15:30 | 6845.195 | 6547.83 | 13393.025
16:00 | 6884.28 | 6501.27 | 13385.55
16:30 | 6891.21 | 6406.96 | 13298.17
17:00 | 6898.14 | 6312.65 | 13210.79
17:30 | 7003.525 | 6183.33 | 13186.855
18:00 | 7108.91 | 6054.01 | 13162.92
18:30 | 7541.455 | 6421.505 | 13962.96
19:00 | 7974 | 6789 | 14763
19:30 | 8193 | 7095 | 15288
20:00 | 8086 | 7055 | 15141
20:30 | 8089.25 | 7108.5 | 15197.75 |  | Executive Engineer
21:00 | 8092.5 | 7162 | 15254.5 |  | Network Operation Division
21:30 | 8034.5 | 7172 | 15206.5
22:00 | 7976.5 | 7182 | 15158.5
22:30 | 7941.75 | 7129.5 | 15071.25
23:00 | 7907 | 7077 | 14984

## En-Curve
QF-LDC-12
Date | 09-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3558 | 1750.5 | 879 | 0 | 158 | 1360.56 | 43 | 4869 | 0 | 143 | 681 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3596 | 1721.25 | 879 | 0 | 152 | 1344.43 | 43 | 4762 | 0 | 105.5 | 515.5 | 0 | 0 | 0 | 0 | 09-05-2026
01:00 | 3634 | 1692 | 879 | 0 | 146 | 1328.3 | 43 | 4655 | 0 | 68 | 350 | 0 | 0 | 0 | 0
01:30 | 3630 | 1694 | 879 | 0 | 145 | 1217.86 | 43 | 4424 | 0 | 59.5 | 330.5 | 0 | 0 | 0.5 | 0 | Energy Generated | 312.6159 |  | MKWHr
02:00 | 3626 | 1696 | 879 | 0 | 144 | 1107.42 | 43 | 4193 | 0 | 51 | 311 | 0 | 0 | 1 | 0 | Energy not Served | 0.707 |  | MKWHr
02:30 | 3607 | 1726 | 879.5 | 0 | 144 | 1009.88 | 43 | 4087.5 | 0 | 51 | 271.5 | 0 | 0 | 0.5 | 0 | Total Energy Requirement | 313.3229 |  | MKWHr
03:00 | 3588 | 1756 | 880 | 0 | 144 | 912.34 | 43 | 3982 | 0 | 51 | 232 | 0 | 0 | 0 | 0
03:30 | 3597 | 1754.5 | 879.5 | 0 | 144 | 911.465 | 43 | 3926 | 0 | 42.5 | 172.5 | 0 | 0 | 2 | 0
04:00 | 3606 | 1753 | 879 | 0 | 144 | 910.59 | 43 | 3870 | 0 | 34 | 113 | 0 | 0 | 4 | 0
04:30 | 3515.5 | 1788.5 | 879 | 0 | 137 | 907.245 | 43 | 3902.5 | 0 | 17 | 64.5 | 0 | 0 | 5.5 | 0
05:00 | 3425 | 1824 | 879 | 0 | 130 | 903.9 | 43 | 3935 | 0 | 0 | 16 | 0 | 0 | 7 | 0
05:30 | 3466.5 | 1782 | 879 | 0 | 132 | 913.32 | 43 | 3867.5 | 10.67 | 0 | 17 | 0 | 0 | 4.5 | 0
06:00 | 3508 | 1740 | 879 | 0 | 134 | 922.74 | 43 | 3800 | 21.34 | 0 | 18 | 0 | 0 | 2 | 0
06:30 | 3534.5 | 1747 | 879 | 0 | 131 | 922.64 | 42.5 | 3790 | 85.095 | 0 | 60 | 0 | 0 | 2.5 | 0
07:00 | 3561 | 1754 | 879 | 0 | 128 | 922.54 | 42 | 3780 | 148.85 | 0 | 102 | 0 | 0 | 3 | 0
07:30 | 3497 | 1695.5 | 879 | 0 | 128 | 917.06 | 41.5 | 3711 | 233.67 | 16.5 | 131 | 0 | 0 | 2 | 0
08:00 | 3433 | 1637 | 879 | 0 | 128 | 911.58 | 41 | 3642 | 318.49 | 33 | 160 | 0 | 0 | 1 | 0
08:30 | 3354.5 | 1639.5 | 879.5 | 0 | 131 | 909.79 | 41.5 | 3532.5 | 418.335 | 33.5 | 161.5 | 0 | 0 | 1.5 | 0
09:00 | 3276 | 1642 | 880 | 0 | 134 | 908 | 42 | 3423 | 518.18 | 34 | 163 | 0 | 0 | 2 | 0
09:30 | 3258.5 | 1694 | 879.5 | 0 | 136 | 920.5 | 42 | 3430.5 | 569.61 | 34 | 167.5 | 0 | 0 | 4.5 | 0
10:00 | 3241 | 1746 | 879 | 0 | 138 | 933 | 42 | 3438 | 621.04 | 34 | 172 | 0 | 0 | 7 | 0
10:30 | 3355 | 1759 | 879.5 | 0 | 144 | 947 | 42.5 | 3602.5 | 669.705 | 34.5 | 186 | 0 | 0 | 3.5 | 0
11:00 | 3469 | 1772 | 880 | 0 | 150 | 961 | 43 | 3767 | 718.37 | 35 | 200 | 0 | 0 | 0 | 0
11:30 | 3479.5 | 1761.5 | 879.5 | 0 | 151 | 1004.5 | 43 | 3950 | 737.17 | 79 | 213.5 | 0 | 0 | 0 | 19.5
12:00 | 3490 | 1751 | 879 | 0 | 152 | 1048 | 43 | 4133 | 755.97 | 123 | 227 | 0 | 0 | 0 | 39
12:30 | 3478.5 | 1763 | 879.5 | 0 | 153 | 1085.5 | 43 | 4285 | 738.6 | 148.5 | 280.5 | 0 | 0 | 0 | 36
13:00 | 3467 | 1775 | 880 | 0 | 154 | 1123 | 43 | 4437 | 721.23 | 174 | 334 | 0 | 0 | 0 | 33
13:30 | 3401.5 | 1748.5 | 879.5 | 0 | 153 | 1119 | 43 | 4447 | 681.54 | 171.5 | 488.3 | 0 | 0 | 2 | 16.5
14:00 | 3336 | 1722 | 879 | 0 | 152 | 1115 | 43 | 4457 | 641.85 | 169 | 642.6 | 0 | 0 | 4 | 0
14:30 | 3364.5 | 1762.5 | 879 | 0 | 146 | 1170 | 43 | 4518 | 569.675 | 160 | 659.3 | 0 | 0 | 9 | 0
15:00 | 3393 | 1803 | 879 | 0 | 140 | 1225 | 43 | 4579 | 497.5 | 151 | 676 | 0 | 0 | 14 | 0
15:30 | 3359.5 | 1786 | 879 | 0 | 130 | 1242 | 43 | 4669.5 | 398.525 | 157.5 | 716 | 0 | 0 | 12 | 0
16:00 | 3326 | 1769 | 879 | 0 | 120 | 1259 | 43 | 4760 | 299.55 | 164 | 756 | 0 | 0 | 10 | 0
16:30 | 3327 | 1767.5 | 879 | 0 | 106 | 1260.5 | 43 | 4736 | 211.67 | 185 | 773.5 | 0 | 0 | 9 | 0
17:00 | 3328 | 1766 | 879 | 0 | 92 | 1262 | 43 | 4712 | 123.79 | 206 | 791 | 0 | 0 | 8 | 0
17:30 | 3367 | 1759 | 879 | 0 | 93 | 1268.5 | 42.5 | 4654 | 75.855 | 238.5 | 805.5 | 0 | 0 | 4 | 26.5
18:00 | 3406 | 1752 | 879 | 0 | 94 | 1275 | 42 | 4596 | 27.92 | 271 | 820 | 0 | 0 | 0 | 53
18:30 | 3483.5 | 1777.5 | 879 | 0 | 123 | 1355 | 41 | 4829.5 | 13.96 | 387.5 | 1073 | 0 | 0 | 0 | 87
19:00 | 3561 | 1803 | 879 | 0 | 152 | 1435 | 40 | 5063 | 0 | 504 | 1326 | 0 | 0 | 0 | 121
19:30 | 3560 | 1785 | 880 | 0 | 144 | 1452 | 40 | 5079 | 0 | 547 | 1801 | 0 | 0 | 0 | 121
20:00 | 3559 | 1773 | 879 | 0 | 148 | 1447 | 40 | 4977 | 0 | 548 | 1770 | 0 | 0 | 0 | 123
20:30 | 3547.5 | 1768.75 | 879 | 0 | 147 | 1453.5 | 40 | 5045.5 | 0 | 542.5 | 1774 | 0 | 0 | 0 | 121.5
21:00 | 3536 | 1764.5 | 879 | 0 | 146 | 1460 | 40 | 5114 | 0 | 537 | 1778 | 0 | 0 | 0 | 120
21:30 | 3546.5 | 1746.5 | 879.5 | 0 | 148 | 1452 | 40.5 | 5104 | 0 | 528 | 1761.5 | 0 | 0 | 0 | 113.5
22:00 | 3557 | 1728.5 | 880 | 0 | 150 | 1444 | 41 | 5094 | 0 | 519 | 1745 | 0 | 0 | 0 | 107
22:30 | 3554 | 1762.25 | 879.5 | 0 | 154 | 1450 | 41.5 | 5048 | 0 | 494.5 | 1687.5 | 0 | 0 | 0 | 109
23:00 | 3551 | 1796 | 879 | 0 | 158 | 1456 | 42 | 5002 | 0 | 470 | 1630 | 0 | 0 | 0 | 111
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 09-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 379 | 00:00 | 375 | 12:00 | Madunaghat | 401 | 07:00 | 391 | 22:00
Amtali | 414 | 09:00 | 404 | 21:00 | Meghnaghat | 393 | 04:00 | 377 | 13:00
Ashuganj | 402 | 08:00 | 386 | 21:00 | Payra | 414 | 06:00 | 406 | 19:00
Bhulta | 403 | 04:00 | 384 | 13:00 | Rahanpur | 414 | 04:00 | 396 | 19:00
Bibiana | 405 | 08:00 | 394 | 15:00 | Rampal | 406 | 08:00 | 390 | 16:00
BIPTC | 401 | 04:00 | 394 | 20:00
Bogura | 406 | 03:00 | 383 | 19:00
Gopalganj | 402 | 08:00 | 386 | 21:00
Kaliakoir | 385 | 03:00 | 368 | 15:00
Korerhat | 402 | 09:00 | 387 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 250 | 14:00 | 216 | 13:00 | Jhenaidah | 232 | 08:00 | 216 | 00:00
AKSML | 234 | 09:00 | 222 | 23:00 | Kachua | 229 | 09:00 | 218 | 23:00
Aminbazar | 224 | 00:00 | 219 | 12:00 | Kaliakoir | 232 | 03:00 | 220 | 12:00
Ashuganj | 229 | 04:00 | 219 | 13:00 | Keranigonj | 230 | 04:00 | 214 | 13:00
Ashuganj-400 | 229 | 04:00 | 219 | 13:00 | Khulna(S) | 235 | 08:00 | 219 | 00:00
Baghabari | 236 | 06:00 | 224 | 19:00 | Korerhat | 229 | 07:00 | 219 | 13:00
Barapukuria | 227 | 04:00 | 210 | 19:00 | Madunaghat | 233 | 07:00 | 226 | 21:00
Barapukuria-230 | 227 | 04:00 | 210 | 19:00 | Madunaghat-400 | 234 | 07:00 | 227 | 21:00
Barishal | 229 | 09:00 | 220 | 19:00 | Maniknagar | 228 | 05:00 | 214 | 12:00
Bheramara | 234 | 03:00 | 221 | 13:00 | Meghnaghat | 236 | 05:00 | 222 | 13:00
Bhulta | 229 | 04:00 | 216 | 13:00 | Meghnaghat-400 | 231 | 04:00 | 218 | 13:00
Bibiana | 234 | 05:00 | 225 | 23:00 | Mirsorai | 233 | 07:00 | 225 | 13:00
BIPTC | 236 | 02:00 | 222 | 13:00 | Naogaon | 226 | 02:00 | 207 | 19:00
Bogura | 238 | 03:00 | 224 | 19:00 | Purbasadipur | 226 | 04:00 | 208 | 19:00
Bogura-400 | 236 | 02:00 | 223 | 19:00 | Rajshahi | 235 | 03:00 | 220 | 00:00
Borhanuddin | 232 | 06:00 | 227 | 00:00 | Rampal | 233 | 08:00 | 220 | 00:00
BSRM | 229 | 08:00 | 220 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 227 | 07:00 | 218 | 15:00 | Rampura | 229 | 04:00 | 214 | 13:00
Cumilla(N) | 228 | 06:00 | 218 | 13:00 | Shikalbaha | 231 | 09:00 | 222 | 23:00
Faridpur | 226 | 09:00 | 213 | 18:30 | Shyampur | 229 | 04:00 | 215 | 13:00
Fenchuganj | 236 | 07:00 | 226 | 23:00 | Siddhirganj | 230 | 06:00 | 216 | 15:00
Feni | 228 | 08:00 | 218 | 23:00 | Sirajgonj | 241 | 04:00 | 232 | 19:00
Ghorashal | 230 | 07:00 | 220 | 11:00 | Sreepur | 226 | 04:00 | 214 | 15:00
Ghorashal-230 | 228 | 04:00 | 214 | 13:00 | Tongi | 227 | 07:00 | 215 | 12:00
Gopalganj | 225 | 08:00 | 215 | 19:00
GPH | 229 | 04:00 | 223 | 10:00
Haripur | 229 | 04:00 | 216 | 13:00
Hasnabad | 229 | 05:00 | 214 | 12:00
Hathazari | 231 | 07:00 | 222 | 23:00
Ishurdi | 237 | 02:00 | 224 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 04:00 | 126 | 13:00 | Madunaghat | 135 | 07:00 | 128 | 22:00
Agargaon | 133 | 04:00 | 122 | 13:00 | Magura | 137 | 08:00 | 125 | 00:00
Agrabad | 134 | 07:00 | 128 | 00:00 | Mahasthangarh | 136 | 05:00 | 126 | 19:00
AKS | 131 | 06:00 | 126 | 23:00 | Maijdee | 127 | 09:00 | 121 | 13:00
Aminbazar | 127 | 00:00 | 123 | 18:30 | Manikganj | 133 | 12:00 | 112 | 15:00
Amnura | 136 | 09:00 | 126 | 13:00 | Maniknagar | 135 | 04:00 | 124 | 13:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 128 | 07:00 | 109 | 01:00
Ashuganj-230 | 137 | 05:00 | 132 | 13:00 | Matuail | 133 | 06:00 | 124.4 | 16:00
Bagerhat | 138 | 09:00 | 120 | 19:00 | Metrorail_Motijheel | 135 | 04:00 | 124 | 13:00
Bajitpur | 132 | 05:00 | 123 | 19:00 | Metrorail_Uttara | 132 | 03:00 | 121 | 13:00
Bakerganj | 133 | 04:00 | 127 | 19:00 | Millgate | 133 | 03:00 | 122 | 11:00
Bakulia | 134 | 07:00 | 129 | 00:00 | Mirpur | 132 | 09:00 | 121 | 13:00
Banani | 135 | 03:00 | 124 | 13:00 | Mirzapur | 134 | 04:00 | 123 | 17:00
Bangabhaban | 134 | 04:00 | 123 | 13:00 | Mithapukur | 133 | 06:00 | 122 | 19:00
Barapukuria | 132 | 04:00 | 121 | 19:00 | MI_Cement | 131 | 04:00 | 117.2 | 13:00
Barguna | 133 | 09:00 | 127 | 00:00 | Modern | 0 | 0:00 | 0 | 0
Barishal | 133 | 06:00 | 126 | 13:00 | Mogbazar | 133 | 01:00 | 127 | 13:00
Barishal-230 | 133 | 08:00 | 127 | 00:00 | Mongla | 137 | 09:00 | 121 | 21:00
Baroaulia | 133 | 08:00 | 129 | 00:00 | Motijheel | 134 | 04:00 | 123 | 13:00
Baroirhat | 132 | 07:00 | 127 | 13:00 | Muktagacha | 129 | 09:00 | 114 | 21:00
Bashundhara | 136 | 06:00 | 122 | 11:00 | Munshiganj | 131 | 05:00 | 122 | 16:00
BashundharaCement | 133 | 08:00 | 125 | 15:00 | Muradnagar | 128 | 08:00 | 120 | 16:00
Beanibazar | 126 | 08:00 | 117 | 19:00 | Mymensingh | 130 | 09:00 | 113 | 19:00
Benapole | 134 | 08:00 | 120 | 13:00 | Nabinagar | 133 | 04:00 | 119 | 11:00
Bhaluka | 129 | 03:00 | 120 | 19:00 | Naogaon | 137 | 02:00 | 125 | 19:00
Bhandaria | 131 | 06:00 | 8 | 09:00 | Narail | 137 | 08:00 | 125 | 00:00
Bhangura | 138 | 03:00 | 127 | 13:00 | Narinda | 135 | 04:00 | 124 | 13:00
Bheramara | 137 | 08:00 | 131 | 19:00 | Narshingdi | 128 | 04:00 | 118 | 21:00
Bheramara(GK) | 137 | 08:00 | 130 | 00:00 | Natore | 136 | 02:00 | 126 | 19:00
Bhulta | 128 | 09:00 | 123 | 18:30 | Nawabganj | 135 | 04:00 | 125 | 13:00
Bog-Sherpur | 138 | 05:00 | 128 | 19:00 | Netrakona | 127 | 05:00 | 110 | 19:00
Bogura | 138 | 02:00 | 128 | 19:00 | New | 133 | 05:00 | 123 | 11:00
Bogura-230 | 138 | 03:00 | 130 | 13:00 | Niamatpur | 136 | 04:00 | 127 | 19:00
Brahmanbaria | 128 | 06:00 | 121 | 21:00 | Noapara | 137 | 08:00 | 124 | 00:00
Cantonment | 133 | 05:00 | 122 | 13:00 | Pabna | 136 | 02:00 | 128 | 13:00
Chandina | 131 | 06:00 | 124 | 16:00 | Palashbari | 131 | 04:00 | 121 | 19:00
Chandpur | 128 | 08:00 | 124 | 12:00 | Panchagarh | 136 | 00:00 | 126 | 16:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 135 | 07:00 | 129 | 23:00 | Patiya | 134 | 07:00 | 127 | 00:00
Chapai | 135 | 03:00 | 127 | 21:00 | Patuakhali | 133 | 04:00 | 127 | 22:00
Charsaidpur | 131 | 03:00 | 124 | 13:00 | Payra | 136 | 07:00 | 132 | 00:00
Chauddagram | 129 | 06:00 | 123 | 16:00 | PHP | 131 | 07:00 | 125 | 21:00
Chhatak | 125 | 07:00 | 115 | 19:00 | Postogola | 133 | 02:00 | 122 | 12:00
Chowmuhani | 127 | 08:00 | 121 | 16:00 | Pubail | 135 | 06:00 | 126 | 12:00
Chuadanga | 139 | 08:00 | 122 | 00:00 | Purbachal | 136 | 03:00 | 122 | 11:00
Coxsbazar | 128 | 08:00 | 111 | 00:00 | Purbasadipur | 133 | 04:00 | 123 | 19:00
Cumilla(N) | 131 | 05:00 | 124 | 16:00 | Rahanpur | 137 | 05:00 | 130 | 18:00
Cumilla(S) | 131 | 06:00 | 119 | 13:00 | Rahanpur-400 | 137 | 03:00 | 130 | 19:00
Daganbhuiyan | 129 | 06:00 | 123 | 23:00 | Rahim | 133 | 06:00 | 125 | 16:00
Daudkandi | 127 | 10:00 | 118 | 16:00 | Rajbari | 129 | 06:00 | 120 | 18:30
DhakaUniversity | 136 | 04:00 | 45 | 13:00 | Rajendrapur | 130 | 03:00 | 119 | 19:00
Dhamrai | 132 | 23:00 | 120 | 11:00 | Rajshahi | 135 | 02:00 | 125 | 00:00
Dhanmondi | 136 | 05:00 | 126 | 13:00 | Rajshahi-230 | 135 | 02:00 | 126 | 13:00
Dohazari | 133 | 06:00 | 122 | 01:00 | Ramganj | 125 | 07:00 | 120 | 13:00
Faridpur | 130 | 03:00 | 124 | 18:30 | Rampur | 133 | 07:00 | 128 | 00:00
Fatullah | 132 | 04:00 | 119 | 13:00 | Rampura | 136 | 06:00 | 125 | 13:00
Fenchuganj | 132 | 06:00 | 126 | 19:00 | Rangamati | 134 | 07:00 | 129 | 23:00
Feni | 129 | 08:00 | 125 | 00:00 | Rangpur | 130 | 02:00 | 121 | 19:00
Feni-230 | 130 | 08:00 | 122 | 00:00 | Ruppur | 137 | 03:00 | 130 | 18:30
Ghatail | 132 | 04:00 | 116 | 17:00 | Saidpur | 131 | 03:00 | 121 | 19:00
Ghorashal | 137 | 04:00 | 130 | 11:00 | Santhia | 138 | 02:00 | 128 | 19:30
Goalpara | 140 | 09:00 | 127 | 00:00 | Satkhira | 133 | 08:00 | 121 | 00:00
Gollamari | 138 | 09:00 | 127 | 00:00 | Satmasjid | 132 | 04:00 | 121 | 13:00
Gopalganj | 134 | 08:00 | 124 | 18:00 | Savar | 131 | 09:00 | 120 | 19:00
Gopalganj-400 | 134 | 08:00 | 127 | 21:00 | SevenRings | 137 | 04:00 | 128 | 13:00
Gulshan | 135 | 05:00 | 26 | 17:00 | ShahCement | 131 | 03:00 | 124 | 13:00
Halishahar | 134 | 07:00 | 128 | 00:00 | Shahjadpur | 140 | 03:00 | 131 | 13:00
Haripur | 133 | 04:00 | 125 | 16:00 | Shahjibazar | 129 | 09:00 | 119 | 18:30
HaripurSBU | 133 | 04:00 | 125 | 16:00 | Shahmirpur | 134 | 07:00 | 129 | 00:00
Hasnabad | 132 | 03:00 | 121 | 13:00 | Shariatpur | 132 | 07:00 | 123 | 19:00
Hathazari | 135 | 05:00 | 129 | 23:00 | Sherpur | 126 | 10:00 | 111 | 23:00
Hatirjheel | 136 | 04:00 | 125 | 13:00 | Shikalbaha | 124 | 09:00 | 120 | 00:00
Ishurdi | 139 | 02:00 | 131 | 19:00 | Shikalbaha-230 | 135 | 07:00 | 129 | 00:00
Jaldhaka | 129 | 02:00 | 117 | 19:00 | Shitalakhya | 131 | 04:00 | 117.2 | 13:00
Jamalpur | 130 | 03:00 | 114 | 22:00 | Sholosohor | 133 | 06:00 | 130 | 22:00
Jashore | 136 | 08:00 | 122 | 00:00 | Shyampur | 130 | 01:00 | 121 | 13:00
Jhenaidah | 139 | 08:00 | 127 | 00:00 | Shyampur-230 | 132 | 04:00 | 123 | 13:00
Jhenaidah-230 | 139 | 09:00 | 127 | 00:00 | Siddhirganj | 133 | 04:00 | 125 | 16:00
Joydebpur | 133 | 04:00 | 123 | 13:00 | Sirajganj | 137 | 03:00 | 125 | 19:00
Joypurhat | 134 | 03:00 | 124 | 19:00 | Sonargaon | 130 | 03:00 | 123 | 16:00
Juldah | 133 | 09:00 | 5 | 03:00 | Sreemongol | 129 | 08:00 | 119 | 21:00
Kabirpur | 135 | 22:00 | 118 | 11:00 | Sreepur | 132 | 04:00 | 123 | 15:00
Kachua | 129 | 07:00 | 124 | 13:00 | Srinagar | 135 | 03:00 | 125 | 13:00
Kaliakoir | 136 | 03:00 | 126 | 11:00 | SSM | 136 | 14:00 | 132 | 16:00
Kaliganj | 138 | 07:00 | 125 | 00:00 | Sunamganj | 124 | 08:00 | 112 | 18:30
Kallyanpur | 132 | 09:00 | 121 | 19:00 | Sylhet | 128 | 08:00 | 120 | 19:00
Kalurghat | 135 | 07:00 | 131 | 00:00 | Sylhet-132 | 127 | 09:00 | 121 | 19:00
Kamrangirchar | 135 | 04:00 | 120 | 19:00 | Tangail | 130 | 03:00 | 121 | 15:00
Kaptai | N/A | N/A | N/A | N/A | Taraganj | 130 | 05:00 | 120 | 19:00
Kasba | 128 | 08:00 | 119 | 16:00 | Tasnim | 131 | 05:00 | 123 | 16:00
Kazla | 134 | 04:00 | 123 | 13:00 | Thakurgaon | 135 | 00:00 | 125 | 16:00
Keranigonj | 136 | 04:00 | 125 | 13:00 | TK | 135 | 07:00 | 130 | 23:00
Khagrachori | 134 | 07:00 | 127 | 21:00 | Tongi | 133 | 04:00 | 125 | 15:00
Khulna | 138 | 09:00 | 126 | 19:00 | Ullahpara | 137 | 05:00 | 126 | 19:00
Khulna(S) | 140 | 09:00 | 127 | 00:00 | Ullon | 135 | 05:00 | 125 | 13:00
Khulshi | 133 | 07:00 | 127 | 00:00 | Uttara | 133 | 04:00 | 121 | 13:00
Kishoreganj | 131 | 05:00 | 120 | 19:00 | UttaraNew | 132 | 03:00 | 121 | 13:00
Kodda | 134 | 19:00 | 126 | 17:00 | Zigatola | 136 | 04:00 | 126 | 13:00
Korerhat | 132 | 06:00 | 128 | 15:00
KSRM | 134 | 08:00 | 130 | 13:00
Kulaura | 132 | 08:00 | 124 | 19:00
Kurigram | 130 | 03:00 | 116 | 19:00
Kushtia | 137 | 08:00 | 128 | 00:00
Laksam | 128 | 07:00 | 124 | 00:00
Lakshmipur | 127 | 09:00 | 120 | 16:00
Lalbag | 135 | 07:00 | 125 | 13:00
Lalmonirhat | 129 | 05:00 | 118 | 19:00
Madanganj | 133 | 08:00 | 125 | 15:00
Madaripur | 133 | 09:00 | 126 | 19:00
Madartek | 135 | 04:00 | 125 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division