## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 12-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-05-2026 | during | 12-05-2026 | during | 12-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | -
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 352 | 332 | 412 | 412 | 412 | 412 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 30 | 55 | 55 | 55 | 15 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 306 | 300 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 10 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 17 | 17 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 30 | 149.36 | 149.36 | 46 | 46 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 16 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 50 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19 | 18 | 33 | 33 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 14 | 14 | 14 | 14 | One unit Schedule maintenance is going on.
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 40 | 51 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 195 | 195 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 109 | 133 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 86 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 460 | 420 | 584 | 584 | 526 | 526 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 281 | 288 | 718 | 718 | 335 | 335 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 60 | 86 | 160 | 160 | 17 | 70 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2018 | 2225 | 5946.22 | 5914.22 | 2417.19 | 2638.19
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 0 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 12 | 0 | 12 | 0 | 12 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 80 | 82 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 147 | 149 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 37 | 45 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 51 | 51 | 0 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 9 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 38 | 108 | 108 | 18 | 68 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.69 | 0 | 1.56 | 0 | 1.56 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 14 | 33 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 5 | 30 | 116 | 116 | 105 | 105 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 6 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1080 | 1224 | 1224 | 1150 | 1150 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 7 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 900 | 990 | 1150 | 1150 | 950 | 950 | plant availability zero
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2416.69 | 2580 | 3913.42 | 3930.86 | 2886.56 | 3030
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 197 | 198 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 320 | 355 | 350.01 | 350.01 | 350.01 | 350.01 | FGMO not available
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 300 | 342 | 342.01 | 342.01 | 342.01 | 342.01 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 220 | 300 | 393 | 393 | 215 | 215 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 40 | 40 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 86 | 135 | 150 | 150 | 25 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 31 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 149 | 154 | 163 | 163 | 150 | 150 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 38 | 66 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 132 | 152 | 84 | 80 | 148 | 148 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 8 | 52 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 17 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 5 | 18 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 12 | 90 | 115 | 115 | 17 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 62 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1583 | 1911 | 2754.44 | 2690.44 | 1869.27 | 2135.27
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-05-2026 | during | 12-05-2026 | during | 12-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.25 | 0 | 2.3 | 0 | 2.3 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 10 | 10 | 10 | 10 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 87 | 88 | 90 | 90 | 86 | 86 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 45.69 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 143.94 | 109 | 381.3 | 334 | 197.8 | 125
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 42 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 150 | 148 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 100 | 100 | 100 | 100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 28 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 86 | 86 | 86 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 104 | 102 | 100 | 100 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 290 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 357 | 364 | 380 | 380 | 380 | 380 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | plant will be shutdown due to 3rd Minor Inspection
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1104 | 1109 | 1305 | 1305 | 1225 | 1225
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 912 | 908 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 36 | 36 | 36 | 36 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 195 | 220 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 99 | 0 | 95 | 0 | 95 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1052 | 1145 | 1234.2 | 1234.2 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2258 | 2273 | 3265.2 | 3170.2 | 2557.1 | 2462.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 393 | 472 | 400 | 500 | 380 | 480 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 32 | 110 | 110 | 16 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 127 | 127 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 930 | 1060 | 1244 | 1244 | 1100 | 1100 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 251 | 230 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.7 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1921.7 | 2141 | 2562 | 2661 | 2151 | 2381
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 58.5 | 0 | 61.55 | 0 | 61.55 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 160 | 150 | 214 | 214 | 180 | 180 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Liquid fuel shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 150 | 220 | 220 | 160 | 160 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 362 | 413.79 | 413.79 | 372.41 | 372.41 | AGC
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0.03 | 0.03 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 92 | 92 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.97 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1225 | 1286 | 1435.88 | 1435.88 | 1356 | 1356 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 41.12 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 81 | 0 | 80 | 0 | 80 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2114.59 | 2018 | 3209.27 | 3000.87 | 2599.84 | 2476.44
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 49 | 50 | 50 | 50 | 50 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 88 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.7 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 108 | 115 | 115 | 0 | 70 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 199 | 0 | 200 | 0 | 200 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 288.7 | 245 | 534 | 298 | 399 | 233
System Total |  |  |  |  | 28823.2 | 29270.237 | 13848.62 | 14611 | 23870.85 | 23304.59 | 16302.76 | 16706
Forecast Scenario (12-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13800 |  | 0 |  | 13800
|  |  |  | 1:00 | 13290 |  | 0 |  | 13290
|  |  |  | 2:00 | 12770 |  | 0 |  | 12770
|  |  |  | 3:00 | 12370 |  | 0 |  | 12370
|  |  |  | 4:00 | 11990 |  | 0 |  | 11990
|  |  |  | 5:00 | 11780 |  | 0 |  | 11780
|  |  |  | 6:00 | 11890 |  | 0 |  | 11890
|  |  |  | 7:00 | 12200 |  | 0 |  | 12200
|  |  |  | 8:00 | 12290 |  | 0 |  | 12290
|  |  |  | 9:00 | 12460 |  | 0 |  | 12460
|  |  |  | 10:00 | 12900 |  | 0 |  | 12900
|  |  |  | 11:00 | 13230 |  | 0 |  | 13230
|  |  |  | 12:00 | 14000 |  | 0 |  | 14000
|  |  |  | 13:00 | 14100 |  | 0 |  | 14100
|  |  |  | 14:00 | 13900 |  | 0 |  | 13900
|  |  |  | 15:00 | 14030 |  | 0 |  | 14030
|  |  |  | 16:00 | 13900 |  | 0 |  | 13900
|  |  |  | 17:00 | 13370 |  | 0 |  | 13370
|  |  |  | 18:00 | 13220 |  | 0 |  | 13220
|  |  |  | 18:30 | 14000 |  | 0 |  | 14000
|  |  |  | 19:00 | 14800 |  | 0 |  | 14800
|  |  |  | 19:30 | 15100 |  | 0 |  | 15100
|  |  |  | 20:00 | 15000 |  | 0 |  | 15000
|  |  |  | 21:00 | 14770 |  | 0 |  | 14770
|  |  |  | 22:00 | 14570 |  | 0 |  | 14570
|  |  |  | 23:00 | 14370 |  | 0 |  | 14370
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 14000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15100.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15100.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 321.00 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:25 hrs on 12-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 11-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13848.62 | MW | 12:00 Hr. | Energy Generated |  |  | 313.1753 |  | MKWHr.
| Day Peak Demand |  |  | 13879.62 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.891 |  | MKWHr.
| Evening Peak Generation |  |  | 14611 | MW | 19:30 Hr. | Energy Demand |  |  | 314.0663 |  | MKWHr.
| Evening Peak Demand |  |  | 14750 | MW | 19:30 Hr. | Maximum Temperature |  |  | 32.9 |  | °C
| Minimum Generation of the Day |  |  | 11332.09 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 914.5 |  | MMCFD
| Maximum Generation of the Day |  |  | 14611 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.9254 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.3887 | 0 | 8.951 | 0 | 0 | 0.20587 | 0 | 0 | 43.5456 | Gas | 124.5282 | Gas | 434665329.3988
| Chattogram Zone |  |  | 3.7794 | 46.6545 | 3.0615 | 0 | 1.564 | 0.099659 | 0 | 0.12384 | 55.283 | Coal | 109.9689 | Coal | 732757457.7044
| Cumilla Zone |  |  | 31.4772 | 0 | 2.2669 | 0 | 0 | 0.32367 | 3.1152 | 0 | 37.1829 | HFO | 18.2637 | HFO | 295664854.22
| Mymensingh Zone |  |  | 0 | 0 | 2.3016 | 0 | 0 | 0.34426 | 0 | 0 | 2.6459 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.973 | 0 | 0 | 0 | 0 | 0.08299 | 0 | 0 | 26.056 | Hydro | 1.564 | Hydro | 156402
| Khulna Zone |  |  | 4.8986 | 24.1891 | 0 | 0 | 0 | 0.70776 | 21.8116 | 0 | 51.6071 | Solar | 4.8955 | Solar | 80597530.78
| Barishal Zone |  |  | 8.2051 | 37.9611 | 0.054336 | 0 | 0 | 0.004051 | 0 | 0 | 46.2245 | Import | 53.8311 | Import | 310011926.609
| Rajshahi Zone |  |  | 15.8062 | 0 | 0.28947 | 0 | 0 | 1.3783 | 28.9042 | 0 | 46.3782 | Wind | 0.12384 | Wind | 1821686.4
| Rangpur Zone |  |  | 0 | 1.1642 | 1.3389 | 0 | 0 | 1.7489 | 0 | 0 | 4.2521
| Total |  |  | 124.5282 | 109.9689 | 18.2637 | 0 | 1.564 | 4.8955 | 53.8311 | 0.12384 | 313.1753
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 434665329.3988 |  | Hydro | 156402
|  |  |  | Coal | 732757457.7044 |  | Solar | 80597530.78
|  |  |  | HFO | 295664854.22 |  | Import | 310011926.609
|  |  |  | HSD | 0 |  | Wind | 1821686.4
[5 empty] | Total: | 185,56,75,187 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.8116 | Peak Hr Flow | 908.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47820909.09 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.9042 | Peak Hr Flow | 1286.00 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1836 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.1152 | Peak Hr Flow | 152.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2710 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.8311 | Peak Hr Flow | 2346.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 9 |  | 5233
|  |  |  | Chattogram |  | 16 |  | 1462
|  |  |  | Cumilla |  | 0 |  | 1300
|  |  |  | Mymensingh |  | 108 |  | 1002
|  |  |  | Sylhet |  | 0 |  | 537
|  |  |  | Khulna |  | 0 |  | 1729
|  |  |  | Barishal |  | 0 |  | 430
|  |  |  | Rajshahi |  | 0 |  | 1515
|  |  |  | Rangpur |  | 0 |  | 1003
|  |  |  | Total |  | 133 |  | 14211
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:12 | 11:12 | Benapole 132/33kV S/S Transformer-1(406T) LT Forced S/D Due to Red Hot Maintenance at R
phase Source side
| 09:12 | 18:09 | Barishal-Barishal(N) 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to for
OPGW Upgradation work by OFCN and from Barishal 230/132kVend.
| 09:13 | 11:11 | Benapole 132/33kV S/S Transformer-1(406T) HT Forced S/D Due to Red Hot Maintenance at R
phase Source side
| 09:15 | 19:34 | Ishurdi 230/132kV S/S 230 kV Bus 2 Project Work S/D
|  | 09:31 | Purbasadipur 230/132/33kV S/S TR-1 (H01R22) HT is restored.
|  | 09:33 | Purbasadipur 230/132/33kV S/S TR-1 (H01R22) LT is restored.
| 09:40 |  | Chandpur 132/33kV S/S 422T(T-5) HT Scheduled S/D Due to Transformer Colouring
| 09:40 |  | Chandpur 132/33kV S/S 422T(T-5) LT Scheduled S/D Due to Transformer Colouring
| 09:55 | 21:01 | Baghabari 230/132kV S/S T-2 Bank HT Project Work S/D Due to DFDR commissioning
| 10:36 |  | Jhenaidah 132/33kV S/S Jhenaidah-Kushtia 132kV Circuit-2(L2) Scheduled S/D Due to 132kV
Jhenaidah-Kushtia CKT-2 Distance Relay Changing work.
| 10:37 |  | Jhenaidah-Kushtia 132kV Ckt-2 Forced S/D from Kushtia 132/33kV end Due to For changing
Distance Relay.
| 11:16 | 17:40 | Meghnaghat 400/230kV S/S Meghnaghat-Summit PP 400KV Ckt-1 Scheduled S/D Due to For
maintenance work.
| 12:00 |  | Day Peak Generation: 13844 MW.
| 14:25 | 15:18 | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) Tripped showing Distance trip zone-1 | [7 empty] | 70.0MW load
|  |  | relays Due to Unknown | [7 empty] | interrup.
| 15:03 | 15:31 | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T LT Scheduled S/D Due to TRTUD Bogura
work
| 15:05 | 15:30 | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T HT Scheduled S/D Due to TRTUD Bogura
work
| 16:36 | 17:51 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T LT Forced S/D Due to IED Device change
work
| 16:36 | 17:49 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T HT Forced S/D Due to IED Device change
work
| 17:07 | 17:14 | Brahmanbaria-Shahjibazar 132 kV Ckt-1 Tripped from Shahjibazar 132/33kV end showing
Distance Relay relays Due to Non
| 19:02 |  | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D
|  | 19:13 | Sylhet (South) S/S Sylhet (S)-Biyanibazar 132KV Ckt-2 is restored.
| 19:30 |  | Evening Peak Generation is 14611 MW.
| 02:48 |  | Amtali 400/132kV S/S Amtali - RNPL 400 kV Ckt - 2 Forced S/D Due to Blue Phase DS Red
hot.
| 06:00 |  | Minimum Generation is 11527 MW.
| 06:51 |  | Kallyanpur-Lalbag 132kV Ckt-2 Scheduled S/D from Kallyanpur 132/33kV end Due to
Aminbazar Ckt-2 Reserve Bus Isolator Finger Maintenance Work
| 06:51 |  | Kallyanpur-Lalbag 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end Due to Reserve
Bus Isolator Finger Maintenance Work
| 07:07 |  | Kallyanpur 132/33kV S/S Main bus Scheduled S/D Due to Aminbazar Ckt-2 Reserve Bus
Isolator Finger Maintenance Work
| 07:11 |  | Aminbazar-Kallyanpur 132kV Ckt-2 Scheduled S/D from Kallyanpur 132/33kV end Due to
Reserve Bus Isolator Finger Maintenance Work
| 07:13 |  | Jamalpur-Mymensingh 132kV Ckt-2 Project Work S/D from Jamalpur 132/33kV end Due to T3 DS
Upgradation and from Mymensingh 132/33kVend.
| 07:20 |  | Jamalpur 132/33kV S/S Bus-B Project Work S/D Due to T3 DS Upgradation
| 07:31 |  | Barishal-Barishal(N) 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to OPGW
Upgradation work done by OFCN and from Barishal 230/132kV end Due to Replace of OPGW
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 11-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 332 | 8395200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 459027 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7268003 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 10 | 70848 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 259200 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 30 | 108000 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 251036 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 50 | 180383 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 426000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 347400 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 51 | 906240 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 2059964 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 2172528 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 761280 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 86 | 555840 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 205869 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 188640 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 420 | 10951363.64 | FGMO
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 288 | 7000740 | FGMO
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 86 | 978000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2225 | 43545561.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 50554.8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 78300 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1072320 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 82 | 1564020 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 149 | 3489971 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 45 | 592145 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 309956 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 9 | 289440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 38 | 356160 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21359 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 33 | 452500 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 30 | 204491 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 23418 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1080 | 25330907 | U2 on AGC
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 7 | 123840 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 990 | 21323636.36 | AGC
Chattogram Area Total |  |  |  |  | 4898.863 | 2580 | 55283018.16
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 198 | 4915000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 355 | 8180800 | FGMO not available
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 342 | 7258000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 300 | 5832000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 16727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1182328 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 135 | 1145818 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 31 | 252272 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 154 | 3614853 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 66 | 220800 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 152 | 3115200 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 22421 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 477470 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 18 | 56280 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 569280 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 323673 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1911 | 37182922
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 211200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 88 | 1971600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 330810 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 72000 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 46800 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 109 | 2645860
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 82990 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 763000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 723960 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 148 | 3458782 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 194000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 710976 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1905600 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 102 | 2447700 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 372000 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7095000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 364 | 8302000 | FGMO not available because of Cooling Tower Fan
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1109 | 26056008
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 908 | 21811636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 220 | 4898592 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 707760 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1145 | 24189090 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2273 | 51607078
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 472 | 9047272 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 54336 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 127 | 2894000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1060 | 23349818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5311070 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 230 | 5564000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4051 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2141 | 46224547.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 368400 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 150 | 3631909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 150 | 3444327 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 362 | 8729963 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 4256 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 208416 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 76800 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 31740 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1286 | 28904229.3 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 308992 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 669210 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2018 | 46378242.3
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1164218 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 88 | 756240 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 52099.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 108 | 582689 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 255389 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1441440 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 245 | 4252075.56
Eastern Grid Total |  |  |  |  | 17418.042 | 7934 | 164713369.8
Western Grid Total |  |  |  |  | 11852.195 | 6677 | 148461943.04
National Grid Total |  |  |  |  | 29270.237 | 14611 | 313175312.84
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 11-05-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9400.54 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4677 | MW
i) Dhaka area |  |  | 5223.54 |  | MW | i) Khulna area |  |  |  | 1729.3 | MW
ii) Chattogram area |  |  | 1446 |  | MW | ii) Barishal area |  |  |  | 429.5 | MW
iii) Cumilla area |  |  | 1300 |  | MW | iii) Rajshahi area |  |  |  | 1515.2 | MW
iv) Mymensingh area |  |  | 894 |  | MW | iv) Rangpur area |  |  |  | 1003 | MW
v) Sylhet area |  |  | 537 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14077.54 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 11 | 16:00 | 67 | Hasnabad | 91 | 12:00 | 133 | Natore | 149 | 20:00
2 | AKSML | 121 | 16:00 | 68 | Hathazari | 82 | 19:00 | 134 | Nawabganj | 51.4 | 22:00
3 | Aftabnagar | 38 | 13:00 | 69 | Hatirjheel | 39 | 12:00 | 135 | Netrakona | 105 | 13:00
4 | Agargaon | 121 | 13:00 | 70 | Ishurdi | 84 | 19:30 | 136 | New | 86 | 12:00
5 | Agrabad | 56 | 15:00 | 71 | Jaldhaka | 74 | 19:30 | 137 | Niamatpur | 65 | 21:00
6 | Amnura | 29 | 20:00 | 72 | Jamalpur | 102 | 14:00 | 138 | Noapara | 49 | 19:30
7 | Ashuganj | 84 | 23:00 | 73 | Jashore | 142 | 19:30 | 139 | PHP | 8 | 17:00
8 | BSRM | 196 | 03:00 | 74 | Jhenaidah | 112 | 19:00 | 140 | Pabna | 98 | 19:30
9 | Bagerhat | 83 | 21:00 | 75 | Joydebpur | 162 | 12:00 | 141 | Palashbari | 124 | 19:30
10 | Bajitpur | 81 | 14:00 | 76 | Joypurhat | 64 | 20:00 | 142 | Panchagarh | 64 | 19:30
11 | Bakerganj | 10 | 19:30 | 77 | Juldah | 15 | 11:00 | 143 | Patiya | 10 | 00:00
12 | Bakulia | 97 | 18:30 | 78 | KSRM | 13 | 09:00 | 144 | Patuakhali | 66.2 | 22:00
13 | Banani | 48 | 11:00 | 79 | Kabirpur | 265 | 19:30 | 145 | Payra | 32 | 00:00
14 | Bangabhaban | 18 | 10:00 | 80 | Kachua | 76 | 19:00 | 146 | Postogola | 47 | 12:00
15 | Barapukuria | 68 | 20:00 | 81 | Kaliganj | 20 | 19:30 | 147 | Pubail | 20 | 21:00
16 | Barguna | 20 | 00:00 | 82 | Kallyanpur | 105 | 13:00 | 148 | Purbachal | 30 | 11:00
17 | Barishal | 99 | 12:00 | 83 | Kalurghat | 42 | 15:00 | 149 | Purbasadipur | 142 | 19:30
18 | Barishal-230 | 90 | 19:30 | 84 | Kamrangirchar | 84 | 13:00 | 150 | Rahanpur | 35 | 23:00
19 | Baroaulia | 76 | 12:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 41 | 00:00
20 | Baroirhat | 52 | 19:30 | 86 | Kasba | 35 | 19:30 | 152 | Rajbari | 74.5 | 19:30
21 | Bashundhara | 180 | 12:00 | 87 | Kazla | 111 | 12:00 | 153 | Rajendrapur | 126 | 19:00
22 | BashundharaCement | 8 | 16:00 | 88 | Keranigonj | 85 | 13:00 | 154 | Rajshahi | 121 | 19:30
23 | Beanibazar | 62 | 21:00 | 89 | Khagrachori | 26 | 00:00 | 155 | Rajshahi-230 | 78 | 23:00
24 | Benapole | 60 | 19:30 | 90 | Khulna | 66 | 13:00 | 156 | Ramganj | 90 | 19:00
25 | Bhaluka | 146 | 19:30 | 91 | Khulshi | 201 | 18:00 | 157 | Rampur | 42 | 20:00
26 | Bhandaria | 54 | 22:00 | 92 | Kishoreganj | 105 | 19:00 | 158 | Rangamati | 18 | 19:00
27 | Bhangura | 37 | 20:00 | 93 | Kodda | 328 | 18:00 | 159 | Rangpur | 144 | 20:00
28 | Bheramara(GK) | 63 | 19:30 | 94 | Kulaura | 42 | 14:00 | 160 | Ruppur | 4 | 11:00
29 | Bhulta | 215 | 12:00 | 95 | Kurigram | 66 | 19:00 | 161 | SSM | 10 | 02:00
30 | Bog-Sherpur | 74 | 20:00 | 96 | Kushtia | 150 | 19:00 | 162 | Saidpur | 106 | 19:00
31 | Bogura | 162 | 20:00 | 97 | Laksam | 30 | 19:30 | 163 | Santhia | 32 | 19:00
32 | Borhanuddin | 90 | 00:00 | 98 | Lakshmipur | 33 | 19:30 | 164 | Satkhira | 138 | 22:00
33 | Brahmanbaria | 121 | 19:00 | 99 | Lalbag | 77 | 13:00 | 165 | Satmasjid | 99 | 13:00
34 | Cantonment | 110 | 12:00 | 100 | Lalmonirhat | 64 | 19:30 | 166 | Savar | 212 | 12:00
35 | Chandina | 12 | 11:00 | 101 | MI_Cement | 16.2 | 12:00 | 167 | SevenRings | 17.23 | 13:00
36 | Chandpur | 68 | 19:00 | 102 | Madanganj | 42 | 12:00 | 168 | ShahCement | 37 | 11:00
37 | Chandraghona | 36 | 19:00 | 103 | Madaripur | 89 | 21:00 | 169 | Shahjadpur | 86 | 19:30
38 | Chapai | 74 | 23:00 | 104 | Madartek | 69 | 13:00 | 170 | Shahjibazar | 112 | 19:30
39 | Charsaidpur | 45 | 00:00 | 105 | Madunaghat | 55 | 19:00 | 171 | Shahmirpur | 63.5 | 09:00
40 | Chauddagram | 70 | 19:00 | 106 | Magura | 65 | 19:30 | 172 | Shariatpur | 70 | 21:00
41 | Chhatak | 33 | 21:00 | 107 | Mahasthangarh | 79 | 19:30 | 173 | Sherpur | 106 | 07:00
42 | Chowmuhani | 124 | 19:00 | 108 | Maijdee | 42 | 21:00 | 174 | Shikalbaha | 32 | 00:00
43 | Chuadanga | 119 | 19:00 | 109 | Manikganj | 125 | 22:00 | 175 | Shitalakhya | 83.4 | 14:00
44 | Coxsbazar | 134 | 18:30 | 110 | Maniknagar | 67 | 11:00 | 176 | Sholosohor | 48 | 18:30
45 | Cumilla(N) | 112 | 19:00 | 111 | Matarbari | 51 | 21:00 | 177 | Shyampur | 156 | 04:00
46 | Cumilla(S) | 163 | 18:30 | 112 | Matuail | 78 | 12:00 | 178 | Siddhirganj | 114 | 11:00
47 | Daganbhuiyan | 34 | 00:00 | 113 | Metrorail_Motijheel | 31 | 16:00 | 179 | Sirajganj | 116 | 19:30
48 | Daudkandi | 138 | 19:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sonargaon | 132 | 19:00
49 | DhakaUniversity | 82 | 11:00 | 115 | Millgate | 104 | 12:00 | 181 | Sreemongol | 72 | 19:00
50 | Dhamrai | 114 | 12:00 | 116 | Mirpur | 138 | 12:00 | 182 | Sreepur | 114 | 19:00
51 | Dhanmondi | 104 | 13:00 | 117 | Mirsorai | 48 | 09:00 | 183 | Srinagar | 40.6 | 22:00
52 | Dohazari | 106 | 22:00 | 118 | Mirzapur | 41 | 12:00 | 184 | Sunamganj | 53 | 21:00
53 | Faridpur | 157 | 20:00 | 119 | Mithapukur | 62 | 19:30 | 185 | Sylhet | 48 | 14:00
54 | Fatullah | 92 | 12:00 | 120 | Modern | N/A | N/A | 186 | Sylhet-132 | 119 | 14:00
55 | Fenchuganj | 37 | 13:00 | 121 | Mogbazar | 81.4 | 13:00 | 187 | TK | 23 | 18:30
56 | Feni | 92 | 19:00 | 122 | Mongla | 53 | 15:00 | 188 | Tangail | 152 | 13:00
57 | GPH | 73 | 04:00 | 123 | Motijheel | 45 | 11:00 | 189 | Taraganj | 24 | 19:00
58 | Ghatail | 76 | 13:00 | 124 | Muktagacha | 31 | 14:00 | 190 | Tasnim | 31 | 03:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 99 | 12:00 | 191 | Thakurgaon | 109 | 19:30
60 | Ghorashal-230 | 110 | 21:00 | 126 | Muradnagar | 43 | 19:30 | 192 | Tongi | 144 | 15:00
61 | Goalpara | 42 | 19:30 | 127 | Mymensingh | 145 | 13:00 | 193 | Ullahpara | 41 | 19:30
62 | Gollamari | 100 | 13:00 | 128 | Nabinagar | 90 | 19:00 | 194 | Ullon | 49 | 19:00
63 | Gopalganj | 99.4 | 19:00 | 129 | Naogaon | 131 | 20:00 | 195 | Uttara | 83 | 12:00
64 | Gulshan | 116 | 11:00 | 130 | Narail | 45 | 19:00 | 196 | UttaraNew | 48 | 12:00
65 | Halishahar | 107 | 12:00 | 131 | Narinda | 70 | 13:00 | 197 | Zigatola | 88 | 13:00
66 | HaripurSBU | 140 | 11:00 | 132 | Narshingdi | 176 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 11-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13140.62 | 0 |  | 13140.62
1:00 | 12656.3 | 0 |  | 12656.3
2:00 | 12294.72 | 0 |  | 12294.72
3:00 | 11904.01 | 0 |  | 11904.01
4:00 | 11610.41 | 0 |  | 11610.41
5:00 | 11332.09 | 0 |  | 11332.09
6:00 | 11431.75 | 0 |  | 11431.75
7:00 | 11839.88 | 0 |  | 11839.88
8:00 | 11848.91 | 0 |  | 11848.91
9:00 | 12340.69 | 0 |  | 12340.69
10:00 | 12755.09 | 0 |  | 12755.09
11:00 | 13321.56 | 27 |  | 13349.56
12:00 | 13848.62 | 30 |  | 13879.62
13:00 | 13791.22 | 46 |  | 13839.22
14:00 | 12759.02 | 44 |  | 12805.02
15:00 | 12668.71 | 34 |  | 12704.71
16:00 | 12612.77 | 67 |  | 12682.77
17:00 | 12593.89 | 48 |  | 12643.89
18:00 | 12542.14 | 66 |  | 12611.14
19:00 | 14101 | 114 |  | 14220
19:30 | 14611 | 133 |  | 14750
20:00 | 14554 | 120 |  | 14679
21:00 | 14360 | 115 |  | 14480
22:00 | 14096 | 90 |  | 14190
23:00 | 13926 | 90 |  | 14020
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 11-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 126 | 2 | 504 | 124 | 1766 | 424 | Ishurdi-Ghorashal Ckt-1 | Export | 3102909.09
1:00 | 126 | 4 | 514 | 112 | 1714 | 420
2:00 | 129 | 3 | 502 | 104 | 1570 | 426 |  | Import | 0
3:00 | 122 | 1 | 476 | 102 | 1454 | 412
4:00 | 122 | -2 | 454 | 92 | 1408 | 400 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 121 | -6 | 442 | 78 | 1388 | 386
6:00 | 115 | -6 | 420 | 84 | 1352 | 416 |  | Import | 0
7:00 | 114 | -9 | 436 | 88 | 1390 | 408
8:00 | 161 | 0 | 544 | 110 | 1566 | 476 | Sirajganj-Sreepur Ckt-1 | Export | 3583000
9:00 | 179 | 6 | 604 | 132 | 1660 | 512
10:00 | 181 | 9 | 612 | 142 | 1732 | 544 |  | Import | 0
11:00 | 190 | 12 | 658 | 172 | 1862 | 590
12:00 | 171 | 3 | 618 | 152 | 1790 | 588 | Sirajganj-Sreepur Ckt-2 | Export | 3645000
13:00 | 156 | -7 | 594 | 116 | 1652 | 450
14:00 | 112 | -13 | 454 | 54 | 1458 | 328 |  | Import | 0
15:00 | 124 | -15 | 440 | 50 | 1550 | 364
16:00 | 140 | -11 | 512 | 98 | 1644 | 430 | Gopalganj-Aminbazar Ckt-1 | Export | 18730000
17:00 | 150 | -5 | 540 | 110 | 1710 | 490
18:00 | 142 | -2 | 524 | 120 | 1678 | 482 |  | Import | 0
18:30 | 127 | -7 | 476 | 88 | 1616 | 426
19:00 | 71 | -15 | 390 | 88 | 1410 | 294 | Gopalganj-Aminbazar Ckt-2 | Export | 18760000
19:30 | 62 | -17 | 354 | 74 | 1420 | 302
20:00 | 63 | -15 | 352 | 68 | 1410 | 294 |  | Import | 0
21:00 | 92 | -8 | 456 | 100 | 1476 | 324
22:00 | 98 | -8 | 90 | 464 | 1482 | 336 |  | Total Export | 47820909.09
23:00 | 99 | -8 | 462 | 74 | 1426 | 342 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 11-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6695 | 6445.62 | 13140.62 | DAILY GENERATION CURVE
00:30 | 6538.5 | 6359.96 | 12898.46
01:00 | 6382 | 6274.3 | 12656.3 | 11-05-2026
01:30 | 6356.5 | 6119.01 | 12475.51
02:00 | 6331 | 5963.72 | 12294.72
02:30 | 6307 | 5792.365 | 12099.365
03:00 | 6283 | 5621.01 | 11904.01
03:30 | 6238 | 5519.21 | 11757.21
04:00 | 6193 | 5417.41 | 11610.41
04:30 | 6103.5 | 5367.75 | 11471.25
05:00 | 6014 | 5318.09 | 11332.09
05:30 | 6079.235 | 5302.685 | 11381.92
06:00 | 6144.47 | 5287.28 | 11431.75
06:30 | 6217.845 | 5417.97 | 11635.815
07:00 | 6291.22 | 5548.66 | 11839.88
07:30 | 6229.705 | 5614.69 | 11844.395
08:00 | 6168.19 | 5680.72 | 11848.91
08:30 | 6309.325 | 5785.475 | 12094.8
09:00 | 6450.46 | 5890.23 | 12340.69
09:30 | 6577.8 | 5970.09 | 12547.89
10:00 | 6705.14 | 6049.95 | 12755.09
10:30 | 6812.905 | 6225.42 | 13038.325
11:00 | 6920.67 | 6400.89 | 13321.56
11:30 | 7093.15 | 6491.94 | 13585.09
12:00 | 7265.63 | 6582.99 | 13848.62
12:30 | 7221.34 | 6598.58 | 13819.92
13:00 | 7177.05 | 6614.17 | 13791.22
13:30 | 6961.335 | 6313.785 | 13275.12
14:00 | 6745.62 | 6013.4 | 12759.02
14:30 | 6695.755 | 6018.11 | 12713.865
15:00 | 6645.89 | 6022.82 | 12668.71
15:30 | 6572.535 | 6068.205 | 12640.74
16:00 | 6499.18 | 6113.59 | 12612.77
16:30 | 6494.75 | 6108.58 | 12603.33
17:00 | 6490.32 | 6103.57 | 12593.89
17:30 | 6510.2 | 6057.815 | 12568.015
18:00 | 6530.08 | 6012.06 | 12542.14
18:30 | 7133.54 | 6188.03 | 13321.57
19:00 | 7737 | 6364 | 14101
19:30 | 7934 | 6677 | 14611
20:00 | 7832 | 6722 | 14554
20:30 | 7689 | 6768 | 14457 |  | Executive Engineer
21:00 | 7546 | 6814 | 14360 |  | Network Operation Division
21:30 | 7464.5 | 6763.5 | 14228
22:00 | 7383 | 6713 | 14096
22:30 | 7374 | 6637 | 14011
23:00 | 7365 | 6561 | 13926

## En-Curve
QF-LDC-12
Date | 11-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3531 | 1622 | 888 | 0 | 126 | 1317.62 | 42 | 5143 | 0 | 84 | 387 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3469.5 | 1593 | 883 | 0 | 124 | 1320.96 | 42.5 | 5062.5 | 0 | 75.5 | 327.5 | 0 | 0 | 0 | 0 | 11-05-2026
01:00 | 3408 | 1564 | 878 | 0 | 122 | 1324.3 | 43 | 4982 | 0 | 67 | 268 | 0 | 0 | 0 | 0
01:30 | 3418.5 | 1574 | 878 | 0 | 121 | 1324.51 | 43 | 4836.5 | 0 | 41.5 | 238.5 | 0 | 0 | 0 | 0 | Energy Generated | 313.1753 |  | MKWHr
02:00 | 3429 | 1584 | 878 | 0 | 120 | 1324.72 | 43 | 4691 | 0 | 16 | 209 | 0 | 0 | 0 | 0 | Energy not Served | 0.891 |  | MKWHr
02:30 | 3443 | 1606.5 | 884 | 0 | 115 | 1222.865 | 43 | 4571 | 0 | 16 | 198 | 0 | 0 | 0 | 0 | Total Energy Requirement | 314.0663 |  | MKWHr
03:00 | 3457 | 1629 | 890 | 0 | 110 | 1121.01 | 43 | 4451 | 0 | 16 | 187 | 0 | 0 | 0 | 0
03:30 | 3462.5 | 1613 | 890 | 0 | 111 | 1053.71 | 43 | 4389.5 | 0 | 16 | 178.5 | 0 | 0 | 0 | 0
04:00 | 3468 | 1597 | 890 | 0 | 112 | 986.41 | 43 | 4328 | 0 | 16 | 170 | 0 | 0 | 0 | 0
04:30 | 3464.5 | 1578.5 | 890.5 | 0 | 111 | 968.25 | 43 | 4237.5 | 0 | 16 | 162 | 0 | 0 | 0 | 0
05:00 | 3461 | 1560 | 891 | 0 | 110 | 950.09 | 43 | 4147 | 0 | 16 | 154 | 0 | 0 | 0 | 0
05:30 | 3484.5 | 1592.5 | 890.5 | 0 | 108 | 962.05 | 43 | 4119 | 17.37 | 26 | 139 | 0 | 0 | 0 | 0
06:00 | 3508 | 1625 | 890 | 0 | 106 | 974.01 | 43 | 4091 | 34.74 | 36 | 124 | 0 | 0 | 0 | 0
06:30 | 3503 | 1616 | 890 | 0 | 108 | 1018.755 | 43 | 4169 | 97.06 | 51 | 140 | 0 | 0 | 0 | 0
07:00 | 3498 | 1607 | 890 | 0 | 110 | 1063.5 | 43 | 4247 | 159.38 | 66 | 156 | 0 | 0 | 0 | 0
07:30 | 3495.5 | 1548.5 | 899 | 0 | 111 | 1061.59 | 43 | 4201.5 | 245.305 | 71 | 168 | 0 | 0 | 0 | 0
08:00 | 3493 | 1490 | 908 | 0 | 112 | 1059.68 | 43 | 4156 | 331.23 | 76 | 180 | 0 | 0 | 0 | 0
08:30 | 3526 | 1556 | 908 | 0 | 114 | 1058.84 | 43 | 4199 | 400.46 | 80 | 209.5 | 0 | 0 | 0 | 0
09:00 | 3559 | 1622 | 908 | 0 | 116 | 1058 | 43 | 4242 | 469.69 | 84 | 239 | 0 | 0 | 0 | 0
09:30 | 3559 | 1623.5 | 907.5 | 0 | 124 | 1054.5 | 42 | 4325 | 539.39 | 96 | 277 | 0 | 0 | 0 | 0
10:00 | 3559 | 1625 | 907 | 0 | 132 | 1051 | 41 | 4408 | 609.09 | 108 | 315 | 0 | 0 | 0 | 0
10:30 | 3575 | 1639.5 | 907 | 0 | 141 | 1102 | 60.5 | 4495.5 | 649.325 | 114 | 354.5 | 0 | 0 | 0 | 13.5
11:00 | 3591 | 1654 | 907 | 0 | 150 | 1153 | 80 | 4583 | 689.56 | 120 | 394 | 0 | 0 | 0 | 27
11:30 | 3578.5 | 1627.5 | 909.5 | 0 | 141 | 1189 | 80 | 4659.5 | 692.09 | 127 | 581 | 0 | 0 | 0 | 28.5
12:00 | 3566 | 1601 | 912 | 0 | 132 | 1225 | 80 | 4736 | 694.62 | 134 | 768 | 0 | 0 | 0 | 30
12:30 | 3535.5 | 1513 | 912.5 | 0 | 130 | 1252.5 | 80.5 | 4695.5 | 647.42 | 139 | 913.5 | 0 | 0 | 0.5 | 38
13:00 | 3505 | 1425 | 913 | 0 | 128 | 1280 | 81 | 4655 | 600.22 | 144 | 1059 | 0 | 0 | 1 | 46
13:30 | 3318.5 | 1405 | 862.5 | 0 | 138 | 1269 | 81.5 | 4487.5 | 573.62 | 150.5 | 987.5 | 0 | 0 | 1.5 | 45
14:00 | 3132 | 1385 | 812 | 0 | 148 | 1258 | 82 | 4320 | 547.02 | 157 | 916 | 0 | 0 | 2 | 44
14:30 | 3141.5 | 1475.5 | 862.5 | 0 | 144 | 1251.5 | 82 | 4299 | 474.065 | 165.5 | 812.3 | 0 | 0 | 6 | 39
15:00 | 3151 | 1566 | 913 | 0 | 140 | 1245 | 82 | 4278 | 401.11 | 174 | 708.6 | 0 | 0 | 10 | 34
15:30 | 3232 | 1570.5 | 912.5 | 0 | 129 | 1253 | 82 | 4345.5 | 321.94 | 153.5 | 626.8 | 0 | 0 | 14 | 50.5
16:00 | 3313 | 1575 | 912 | 0 | 118 | 1261 | 82 | 4413 | 242.77 | 133 | 545 | 0 | 0 | 18 | 67
16:30 | 3340 | 1595.5 | 912.5 | 0 | 123 | 1264 | 82 | 4421.5 | 194.83 | 132.5 | 521 | 0 | 0 | 16.5 | 57.5
17:00 | 3367 | 1616 | 913 | 0 | 128 | 1267 | 82 | 4430 | 146.89 | 132 | 497 | 0 | 0 | 15 | 48
17:30 | 3402 | 1628 | 913 | 0 | 132 | 1264.5 | 82 | 4408 | 85.515 | 137 | 503 | 0 | 0 | 13 | 57
18:00 | 3437 | 1640 | 913 | 0 | 136 | 1262 | 82 | 4386 | 24.14 | 142 | 509 | 0 | 0 | 11 | 66
18:30 | 3589 | 1678.5 | 910 | 0 | 139 | 1272.5 | 82 | 4600.5 | 12.07 | 212 | 811 | 0 | 0 | 15 | 90
19:00 | 3741 | 1717 | 907 | 0 | 142 | 1283 | 82 | 4815 | 0 | 282 | 1113 | 0 | 0 | 19 | 114
19:30 | 3707 | 1580 | 908 | 0 | 152 | 1286 | 82 | 5026 | 0 | 318 | 1545 | 0 | 0 | 7 | 133
20:00 | 3778 | 1602 | 908 | 0 | 152 | 1266 | 81 | 5040 | 0 | 303 | 1405 | 0 | 0 | 19 | 120
20:30 | 3760 | 1631 | 907.5 | 0 | 150 | 1325.5 | 80 | 4995 | 0 | 276 | 1314.5 | 0 | 0 | 17.5 | 117.5
21:00 | 3742 | 1660 | 907 | 0 | 148 | 1385 | 79 | 4950 | 0 | 249 | 1224 | 0 | 0 | 16 | 115
21:30 | 3703 | 1643.5 | 906.5 | 0 | 148 | 1387 | 78 | 4928.5 | 0 | 241.5 | 1179.5 | 0 | 0 | 12.5 | 102.5
22:00 | 3664 | 1627 | 906 | 0 | 148 | 1389 | 77 | 4907 | 0 | 234 | 1135 | 0 | 0 | 9 | 90
22:30 | 3692 | 1617.5 | 906 | 0 | 147 | 1360.5 | 77 | 4847.5 | 0 | 234 | 1123 | 0 | 0 | 6.5 | 90
23:00 | 3720 | 1608 | 906 | 0 | 146 | 1332 | 77 | 4788 | 0 | 234 | 1111 | 0 | 0 | 4 | 90
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 11-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 391 | 04:00 | 370 | 12:00 | Madunaghat | 399 | 06:00 | 390 | 12:00
Amtali | 413 | 08:00 | 406 | 00:00 | Meghnaghat | 392 | 05:00 | 374 | 12:00
Ashuganj | 402 | 05:00 | 387 | 12:00 | Payra | 414 | 04:00 | 408 | 00:00
Bhulta | 407 | 05:00 | 381 | 12:00 | Rahanpur | 413 | 05:00 | 396 | 19:00
Bibiana | 402 | 04:00 | 391 | 11:00 | Rampal | 406 | 07:00 | 390 | 12:00
BIPTC | 402 | 06:00 | 391 | 23:00
Bogura | 404 | 05:00 | 384 | 19:00
Gopalganj | 402 | 05:00 | 387 | 12:00
Kaliakoir | 382 | 05:00 | 362 | 12:00
Korerhat | 400 | 05:00 | 387 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 231 | 05:00 | 214 | 12:00 | Jhenaidah | 231 | 05:00 | 215 | 19:00
AKSML | 232 | 05:00 | 223 | 12:00 | Kachua | 230 | 13:00 | 220 | 11:00
Aminbazar | 232 | 05:00 | 215 | 12:00 | Kaliakoir | 235 | 14:00 | 219 | 12:00
Ashuganj | 233 | 05:00 | 222 | 12:00 | Keranigonj | 230 | 05:00 | 213 | 12:00
Ashuganj-400 | 233 | 05:00 | 222 | 12:00 | Khulna(S) | 233 | 05:00 | 218 | 19:00
Baghabari | 233 | 05:00 | 225 | 12:00 | Korerhat | 228 | 05:00 | 220 | 11:00
Barapukuria | 224 | 05:00 | 207 | 19:00 | Madunaghat | 231 | 06:00 | 225 | 11:00
Barapukuria-230 | 224 | 05:00 | 207 | 19:00 | Madunaghat-400 | 233 | 06:00 | 227 | 11:00
Barishal | 229 | 06:00 | 222 | 12:00 | Maniknagar | 229 | 05:00 | 213 | 11:00
Bheramara | 234 | 04:00 | 221 | 12:00 | Meghnaghat | 236 | 07:00 | 220 | 12:00
Bhulta | 230 | 05:00 | 214 | 11:00 | Meghnaghat-400 | 230 | 04:00 | 217 | 12:00
Bibiana | 232 | 08:00 | 224 | 12:00 | Mirsorai | 232 | 14:00 | 225 | 11:00
BIPTC | 236 | 04:00 | 221 | 12:00 | Naogaon | 222 | 04:00 | 208 | 20:00
Bogura | 236 | 05:00 | 222 | 19:00 | Purbasadipur | 221 | 04:00 | 204 | 19:00
Bogura-400 | 235 | 05:00 | 222 | 19:00 | Rajshahi | 234 | 04:00 | 220 | 19:00
Borhanuddin | 232 | 05:00 | 227 | 12:00 | Rampal | 232 | 04:00 | 219 | 18:30
BSRM | 228 | 05:00 | 220 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 228 | 14:00 | 218 | 11:00 | Rampura | 229 | 05:00 | 212 | 12:00
Cumilla(N) | 228 | 05:00 | 217 | 12:00 | Shikalbaha | 229 | 14:00 | 221 | 11:00
Faridpur | 225 | 05:00 | 215 | 12:00 | Shyampur | 230 | 05:00 | 210 | 10:00
Fenchuganj | 234 | 06:00 | 227 | 12:00 | Siddhirganj | 230 | 04:00 | 215 | 12:00
Feni | 227 | 05:00 | 218 | 12:00 | Sirajgonj | 241 | 05:00 | 232 | 19:00
Ghorashal | 232 | 02:00 | 220 | 11:00 | Sreepur | 229 | 04:00 | 216 | 12:00
Ghorashal-230 | 228 | 05:00 | 214 | 12:00 | Tongi | 230 | 23:00 | 214 | 11:00
Gopalganj | 225 | 05:00 | 216 | 12:00
GPH | 230 | 05:00 | 223 | 12:00
Haripur | 230 | 05:00 | 214 | 12:00
Hasnabad | 230 | 04:00 | 214 | 11:00
Hathazari | 229 | 15:00 | 223 | 02:00
Ishurdi | 237 | 04:00 | 224 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 05:00 | 127 | 12:00 | Madunaghat | 134 | 04:00 | 130 | 11:00
Agargaon | 134 | 04:00 | 123 | 12:00 | Magura | 135 | 08:00 | 123 | 19:00
Agrabad | 135 | 06:00 | 130 | 11:00 | Mahasthangarh | 134 | 04:00 | 124 | 19:00
AKS | 131 | 05:00 | 128 | 11:00 | Maijdee | 128 | 14:00 | 122 | 00:00
Aminbazar | 132 | 04:00 | 121 | 11:00 | Manikganj | 128 | 14:00 | 116 | 12:00
Amnura | 135 | 03:00 | 127 | 19:00 | Maniknagar | 134 | 05:00 | 123 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 122 | 09:00 | 114 | 00:00
Ashuganj-230 | 139 | 06:00 | 133 | 11:00 | Matuail | 133 | 05:00 | 124 | 11:00
Bagerhat | 133 | 08:00 | 117 | 19:00 | Metrorail_Motijheel | 134 | 07:00 | 123 | 12:00
Bajitpur | 133 | 04:00 | 125 | 12:00 | Metrorail_Uttara | 133 | 04:00 | 121 | 12:00
Bakerganj | 132 | 06:00 | 128 | 00:00 | Millgate | 134 | 03:00 | 122 | 12:00
Bakulia | 136 | 09:00 | 131 | 00:00 | Mirpur | 132 | 14:00 | 119 | 12:00
Banani | 140 | 05:00 | 127 | 12:00 | Mirzapur | 132 | 05:00 | 122 | 12:00
Bangabhaban | 135 | 04:00 | 123 | 12:00 | Mithapukur | 132 | 04:00 | 119 | 19:00
Barapukuria | 130 | 04:00 | 119 | 19:00 | MI_Cement | 131 | 05:00 | 118 | 12:00
Barguna | 133 | 06:00 | 128 | 00:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 133 | 05:00 | 127 | 12:00 | Mogbazar | 139 | 04:00 | 130 | 11:00
Barishal-230 | 133 | 05:00 | 128 | 12:00 | Mongla | 134 | 08:00 | 118 | 19:00
Baroaulia | 133 | 03:00 | 129 | 11:00 | Motijheel | 135 | 04:00 | 123 | 12:00
Baroirhat | 132 | 05:00 | 126 | 11:00 | Muktagacha | 126 | 04:00 | 115 | 12:00
Bashundhara | 139 | 03:00 | 122 | 12:00 | Munshiganj | 131 | 05:00 | 122 | 11:00
BashundharaCement | 132 | 06:00 | 124 | 11:00 | Muradnagar | 130 | 05:00 | 121 | 12:00
Beanibazar | 127 | 06:00 | 121 | 12:00 | Mymensingh | 127 | 05:00 | 114 | 12:00
Benapole | 134 | 08:00 | 119 | 19:00 | Nabinagar | 138 | 14:00 | 122 | 12:00
Bhaluka | 132 | 15:00 | 123 | 11:00 | Naogaon | 135 | 04:00 | 124 | 19:00
Bhandaria | 128 | 07:00 | 121 | 00:00 | Narail | 136 | 06:00 | 124 | 19:00
Bhangura | 135 | 04:00 | 127 | 12:00 | Narinda | 134 | 05:00 | 123 | 12:00
Bheramara | 137 | 04:00 | 131 | 12:00 | Narshingdi | 126 | 05:00 | 115 | 12:00
Bheramara(GK) | 137 | 04:00 | 131 | 12:00 | Natore | 134 | 03:00 | 126 | 19:00
Bhulta | 127 | 07:00 | 120 | 11:00 | Nawabganj | 135 | 05:00 | 124 | 12:00
Bog-Sherpur | 135 | 04:00 | 126 | 19:00 | Netrakona | 125 | 03:00 | 117 | 12:00
Bogura | 136 | 05:00 | 129 | 19:30 | New | 134 | 14:00 | 123 | 12:00
Bogura-230 | 137 | 05:00 | 127 | 19:00 | Niamatpur | 135 | 05:00 | 127 | 20:00
Brahmanbaria | 133 | 05:00 | 126 | 11:00 | Noapara | 136 | 05:00 | 122 | 19:00
Cantonment | 134 | 03:00 | 123 | 11:00 | Pabna | 135 | 06:00 | 127 | 19:00
Chandina | 132 | 05:00 | 125 | 12:00 | Palashbari | 128 | 04:00 | 117 | 19:00
Chandpur | 131 | 18:30 | 125 | 00:00 | Panchagarh | 135 | 04:00 | 122 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 135 | 06:00 | 130 | 12:00 | Patiya | 133 | 07:00 | 129 | 12:00
Chapai | 135 | 05:00 | 129 | 00:00 | Patuakhali | 133 | 08:00 | 127 | 00:00
Charsaidpur | 132 | 05:00 | 124 | 11:00 | Payra | 136 | 08:00 | 132 | 00:00
Chauddagram | 130 | 04:00 | 19 | 07:00 | PHP | 131 | 05:00 | 126 | 12:00
Chhatak | 127 | 05:00 | 120 | 14:00 | Postogola | 133 | 04:00 | 121 | 12:00
Chowmuhani | 128 | 05:00 | 123 | 00:00 | Pubail | 136 | 05:00 | 126 | 12:00
Chuadanga | 135 | 05:00 | 119 | 19:00 | Purbachal | 140 | 05:00 | 122 | 12:00
Coxsbazar | 123 | 08:00 | 114 | 18:30 | Purbasadipur | 131 | 23:00 | 119 | 19:00
Cumilla(N) | 132 | 04:00 | 63 | 01:00 | Rahanpur | 136 | 04:00 | 131 | 18:30
Cumilla(S) | 131 | 06:00 | 122 | 11:00 | Rahanpur-400 | 137 | 05:00 | 131 | 19:00
Daganbhuiyan | 130 | 05:00 | 125 | 11:00 | Rahim | 133 | 06:00 | 124 | 11:00
Daudkandi | 127 | 05:00 | 119 | 12:00 | Rajbari | 129 | 05:00 | 123 | 12:00
DhakaUniversity | 140 | 05:00 | 128 | 11:00 | Rajendrapur | 130 | 04:00 | 122 | 12:00
Dhamrai | 140 | 14:00 | 125 | 11:00 | Rajshahi | 133 | 03:00 | 124 | 12:00
Dhanmondi | 140 | 05:00 | 127 | 12:00 | Rajshahi-230 | 134 | 04:00 | 126 | 19:00
Dohazari | 130 | 07:00 | 126 | 21:00 | Ramganj | 127 | 14:00 | 122 | 00:00
Faridpur | 131 | 05:00 | 125 | 12:00 | Rampur | 133 | 05:00 | 129 | 11:00
Fatullah | 137 | 05:00 | 119 | 12:00 | Rampura | 140 | 05:00 | 128 | 11:00
Fenchuganj | 134 | 05:00 | 130 | 12:00 | Rangamati | 133 | 05:00 | 128 | 12:00
Feni | 130 | 05:00 | 126 | 00:00 | Rangpur | 130 | 02:00 | 119 | 19:00
Feni-230 | 131 | 05:00 | 125 | 12:00 | Ruppur | 137 | 04:00 | 130 | 12:00
Ghatail | 126 | 05:00 | 115 | 12:00 | Saidpur | 129 | 23:00 | 115 | 19:00
Ghorashal | 138 | 02:00 | 130 | 11:00 | Santhia | 136 | 03:00 | 127 | 19:00
Goalpara | 138 | 08:00 | 125 | 19:00 | Satkhira | 133 | 05:00 | 119 | 19:00
Gollamari | 136 | 05:00 | 126 | 19:00 | Satmasjid | 135 | 06:00 | 123 | 12:00
Gopalganj | 134 | 05:00 | 126 | 19:00 | Savar | 133 | 14:00 | 118 | 11:00
Gopalganj-400 | 135 | 03:00 | 128 | 12:00 | SevenRings | 138 | 05:00 | 129 | 12:00
Gulshan | 139 | 05:00 | 127 | 12:00 | ShahCement | 132 | 05:00 | 123 | 13:00
Halishahar | 135 | 05:00 | 130 | 11:00 | Shahjadpur | 138 | 04:00 | 130 | 12:00
Haripur | 134 | 05:00 | 124 | 12:00 | Shahjibazar | 131 | 05:00 | 125 | 12:00
HaripurSBU | 134 | 05:00 | 126 | 12:00 | Shahmirpur | 135 | 05:00 | 131 | 11:00
Hasnabad | 134 | 03:00 | 121 | 12:00 | Shariatpur | 133 | 04:00 | 127 | 12:00
Hathazari | 135 | 15:00 | 130 | 11:00 | Sherpur | 124 | 04:00 | 112 | 07:00
Hatirjheel | 140 | 05:00 | 128 | 12:00 | Shikalbaha | 125 | 04:00 | 120 | 12:00
Ishurdi | 138 | 03:00 | 131 | 12:00 | Shikalbaha-230 | 136 | 08:00 | 131 | 11:00
Jaldhaka | 129 | 04:00 | 116 | 19:00 | Shitalakhya | 131 | 05:00 | 118 | 12:00
Jamalpur | 126 | 04:00 | 116 | 01:00 | Sholosohor | 134 | 05:00 | 129 | 12:00
Jashore | 135 | 08:00 | 120 | 19:00 | Shyampur | 136 | 05:00 | 127 | 11:00
Jhenaidah | 136 | 03:00 | 125 | 19:00 | Shyampur-230 | 138 | 05:00 | 128 | 12:00
Jhenaidah-230 | 137 | 04:00 | 125 | 19:30 | Siddhirganj | 134 | 04:00 | 125 | 11:00
Joydebpur | 134 | 02:00 | 123 | 12:00 | Sirajganj | 133 | 04:00 | 124 | 12:00
Joypurhat | 133 | 04:00 | 121 | 19:00 | Sonargaon | 131 | 07:00 | 122 | 12:00
Juldah | 134 | 01:00 | 130 | 11:00 | Sreemongol | 131 | 06:00 | 125 | 12:00
Kabirpur | 136 | 14:00 | 118 | 12:00 | Sreepur | 133 | 05:00 | 125 | 12:00
Kachua | 130 | 15:00 | 125 | 00:00 | Srinagar | 135 | 04:00 | 125 | 12:00
Kaliakoir | 142 | 14:00 | 128 | 12:00 | SSM | 138 | 00:00 | 133 | 12:00
Kaliganj | 136 | 08:00 | 125 | 19:00 | Sunamganj | 125 | 05:00 | 119 | 13:00
Kallyanpur | 134 | 14:00 | 120 | 12:00 | Sylhet | 129 | 05:00 | 125 | 12:00
Kalurghat | 135 | 08:00 | 130 | 11:00 | Sylhet-132 | 129 | 06:00 | 125 | 11:00
Kamrangirchar | 135 | 06:00 | 118 | 12:00 | Tangail | 128 | 03:00 | 117 | 12:00
Kaptai | N/A | N/A | N/A | N/A | Taraganj | 130 | 05:00 | 11 | 19:00
Kasba | 129 | 05:00 | 121 | 12:00 | Tasnim | 134 | 13:00 | 122 | 12:00
Kazla | 135 | 06:00 | 123 | 12:00 | Thakurgaon | 133 | 21:00 | 120 | 19:00
Keranigonj | 136 | 05:00 | 125 | 12:00 | TK | 134 | 05:00 | 131 | 00:00
Khagrachori | 133 | 06:00 | 127 | 00:00 | Tongi | 135 | 04:00 | 129 | 17:00
Khulna | 136 | 04:00 | 125 | 19:00 | Ullahpara | 134 | 04:00 | 125 | 19:00
Khulna(S) | 137 | 05:00 | 126 | 19:00 | Ullon | 138 | 04:00 | 127 | 12:00
Khulshi | 132 | 03:00 | 128 | 11:00 | Uttara | 133 | 06:00 | 119 | 12:00
Kishoreganj | 132 | 05:00 | 123 | 12:00 | UttaraNew | 133 | 04:00 | 121 | 12:00
Kodda | 134 | 19:30 | 124 | 11:00 | Zigatola | 136 | 05:00 | 125 | 12:00
Korerhat | 134 | 05:00 | 128 | 12:00
KSRM | 134 | 15:00 | 129 | 12:00
Kulaura | 134 | 06:00 | 129 | 12:00
Kurigram | 128 | 03:00 | 111 | 19:00
Kushtia | 136 | 05:00 | 128 | 19:00
Laksam | 129 | 05:00 | 124 | 12:00
Lakshmipur | 128 | 14:00 | 122 | 11:00
Lalbag | 135 | 14:00 | 33 | 05:00
Lalmonirhat | 128 | 06:00 | 115 | 19:00
Madanganj | 132 | 05:00 | 124 | 11:00
Madaripur | 132 | 08:00 | 129 | 00:00
Madartek | 138 | 04:00 | 127 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 11-05-2026 | [28 empty] | Date: | 11-05-2026 | [28 empty] | Date: | 11-05-2026 | [28 empty] | Date: | 11-05-2026 | [28 empty] | Date: | 11-05-2026 | [17 empty] | Date: | 11-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [17 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 275 | 36 | 17 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 18 | 14 | 0 | 465 | 0 | 0 | 38 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 17 | 935 | 0 | 0 | 50 | 0 | 0 | 151 | 0 | 0 | 0 | 1155 | 0 | 0 | 0 | 215 | 320 | 300 | 51 | 0 | 210 | 0 | 0 | 152 | 0 | 0 | 19 | 0 | 126 | 0 | 0 | 0 | 295 | 0 | 321 | 30 | 30 | 148 | 0 | 16 | 0 | 84 | 28 | 110 | 0 | 102 | 0 | 78 | 9 | 0 | 0 | 0 | 0 | 6695 | 888 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1205 | 0 | 0 | 0 | 1317.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 120 | 0 | 367 | 0 | 0 | 0 | 51 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 269 | 126 | 220 | 0 | 408 | 1120 | 0 | 6445.62 | 13140.62 | 78.98
01:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 255 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 17 | 19 | 14 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 19 | 930 | 0 | 0 | 50 | 0 | 0 | 151 | 0 | 0 | 0 | 1140 | 0 | 0 | 0 | 215 | 320 | 300 | 51 | 0 | 215 | 0 | 0 | 152 | 0 | 0 | 19 | 0 | 122 | 0 | 0 | 0 | 295 | 0 | 321 | 30 | 30 | 142 | 0 | 16 | 0 | 84 | 30 | 0 | 0 | 102 | 0 | 78 | 9 | 0 | 0 | 0 | 0 | 6382 | 878 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 0 | 0 | 1324.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 120 | 0 | 350 | 0 | 0 | 0 | 51 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 126 | 220 | 0 | 389 | 1100 | 0 | 6274.3 | 12656.3 | 78.97
02:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 259 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 19 | 14 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 930 | 0 | 0 | 50 | 0 | 0 | 151 | 0 | 0 | 0 | 1140 | 0 | 0 | 0 | 215 | 320 | 300 | 51 | 0 | 219 | 0 | 0 | 153 | 0 | 0 | 19 | 0 | 120 | 0 | 0 | 0 | 290 | 0 | 321 | 30 | 30 | 138 | 0 | 16 | 0 | 81 | 30 | 0 | 0 | 102 | 0 | 78 | 9 | 0 | 0 | 0 | 0 | 6331 | 878 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 898 | 0 | 0 | 0 | 1324.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 120 | 0 | 359 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 126 | 220 | 0 | 352 | 1050 | 0 | 5963.72 | 12294.72 | 78.97
03:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 276 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 0 | 19 | 14 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 900 | 0 | 0 | 50 | 0 | 0 | 151 | 0 | 0 | 0 | 1093 | 0 | 0 | 0 | 230 | 320 | 300 | 51 | 0 | 220 | 0 | 0 | 153 | 0 | 0 | 19 | 0 | 110 | 0 | 0 | 0 | 290 | 0 | 321 | 30 | 30 | 140 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 102 | 0 | 78 | 9 | 0 | 0 | 0 | 0 | 6283 | 890 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 812 | 0 | 0 | 0 | 1121.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 120 | 0 | 366 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 269 | 126 | 220 | 0 | 330 | 995 | 0 | 5621.01 | 11904.01 | 78.96
04:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 269 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 0 | 0 | 19 | 14 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 24 | 850 | 0 | 0 | 50 | 0 | 0 | 151 | 0 | 0 | 0 | 1090 | 0 | 0 | 0 | 235 | 330 | 300 | 51 | 0 | 220 | 0 | 0 | 153 | 0 | 0 | 19 | 0 | 112 | 0 | 0 | 0 | 290 | 0 | 321 | 30 | 30 | 143 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 102 | 0 | 77 | 9 | 0 | 0 | 0 | 0 | 6193 | 890 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802 | 0 | 0 | 0 | 986.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 120 | 0 | 362 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244 | 126 | 220 | 0 | 330 | 960 | 0 | 5417.41 | 11610.41 | 78.96
05:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 261 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 0 | 0 | 0 | 19 | 14 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 25 | 850 | 0 | 0 | 50 | 0 | 0 | 151 | 0 | 0 | 0 | 967 | 0 | 0 | 0 | 260 | 320 | 300 | 51 | 0 | 198 | 0 | 0 | 153 | 0 | 0 | 19 | 0 | 110 | 0 | 0 | 0 | 295 | 0 | 321 | 30 | 30 | 143 | 0 | 17 | 0 | 81 | 30 | 0 | 0 | 102 | 0 | 78 | 9 | 0 | 0 | 0 | 0 | 6014 | 891 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 812 | 0 | 0 | 0 | 950.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 120 | 0 | 356 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 126 | 220 | 0 | 330 | 915 | 0 | 5318.09 | 11332.09 | 78.95
06:00 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 299 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 2 | 0 | 19 | 14 | 0 | 485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 43 | 0 | 27 | 867 | 0 | 0 | 20 | 0 | 0 | 151 | 0 | 0 | 0 | 967 | 0 | 0 | 0 | 260 | 320 | 300 | 51 | 0 | 201 | 0 | 0 | 153 | 0 | 0 | 19 | 0 | 106 | 0 | 3 | 0 | 290 | 0 | 321 | 30 | 30 | 143 | 1 | 17 | 0 | 81 | 30 | 0 | 0 | 102 | 0 | 78 | 9 | 0 | 0.08 | 3.24 | 0 | 6144.47 | 890 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.83 | 806 | 0 | 0 | 0 | 974.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.79 | 1 | 0 | 0 | 1.43 | 140 | 0 | 0 | 0 | 120 | 0 | 380 | 0 | 0.18 | 0 | 50 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 12 | 0.04 | 0 | 208 | 126 | 180 | 0 | 328 | 865 | 0 | 5287.28 | 11431.75 | 78.95
07:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 286 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 7 | 7 | 19 | 14 | 0 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 43 | 0 | 31 | 867 | 0 | 0 | 19 | 0 | 0 | 151 | 0 | 0 | 0 | 1040 | 2 | 0 | 0 | 250 | 320 | 300 | 51 | 0 | 197 | 0 | 0 | 152 | 0 | 0 | 19 | 0 | 110 | 0 | 18 | 0 | 295 | 0 | 321 | 30 | 30 | 153 | 3 | 8 | 0 | 81 | 30 | 0 | 0 | 102 | 0 | 78 | 9 | 0 | 0.44 | 12.13 | 0 | 6291.22 | 890 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 859 | 0 | 0 | 0 | 1063.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.82 | 10 | 0 | 0 | 13.03 | 140 | 0 | 0 | 0 | 120 | 0 | 370 | 0 | 1.07 | 0 | 50 | 0 | 7 | 0 | 0 | 0 | 0 | 2.1 | 50 | 0.14 | 0 | 217 | 126 | 180 | 0 | 349 | 865 | 0 | 5548.66 | 11839.88 | 78.94
08:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 246 | 0 | 0 | 70 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 10 | 17 | 19 | 14 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.15 | 43 | 0 | 5 | 850 | 0 | 0 | 19 | 0 | 0 | 151 | 0 | 0 | 0 | 1010 | 4 | 0 | 0 | 240 | 320 | 300 | 51 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 19 | 0 | 112 | 0 | 22 | 0 | 295 | 0 | 321 | 30 | 30 | 142 | 5 | 8 | 0 | 81 | 30 | 0 | 0 | 102 | 0 | 78 | 9 | 0 | 0.48 | 24.56 | 0 | 6168.19 | 908 | 207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 851 | 0 | 0 | 0 | 1059.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.64 | 45 | 0 | 0 | 23.04 | 140 | 0 | 0 | 0 | 130 | 0 | 370 | 0 | 2.65 | 0 | 49 | 0 | 15 | 0 | 0 | 0 | 0 | 3.5 | 97 | 0.21 | 0 | 196 | 126 | 180 | 0 | 350 | 850 | 0 | 5680.72 | 11848.91 | 78.94
09:00 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 283 | 0 | 0 | 73 | 0 | 45 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 21 | 17 | 19 | 14 | 0 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 43 | 0 | 2 | 850 | 0 | 0 | 19 | 0 | 0 | 149 | 0 | 0 | 0 | 1077 | 4 | 0 | 0 | 230 | 320 | 300 | 51 | 0 | 196 | 0 | 0 | 150 | 0 | 0 | 19 | 0 | 116 | 0 | 23 | 0 | 295 | 0 | 356 | 30 | 30 | 151 | 8 | 17 | 0 | 81 | 30 | 0 | 0 | 102 | 0 | 78 | 9 | 0 | 0.53 | 36.23 | 0 | 6450.46 | 908 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 926 | 0 | 0 | 0 | 1058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.93 | 69 | 0 | 0 | 22.28 | 140 | 0 | 0 | 0 | 130 | 0 | 410 | 0 | 2.96 | 0 | 49 | 0 | 24 | 0 | 0 | 0 | 0 | 5.6 | 144 | 0.46 | 0 | 202 | 126 | 220 | 0 | 338 | 800 | 0 | 5890.23 | 12340.69 | 78.93
10:00 | 0 | 34 | 50 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 287 | 0 | 1 | 87 | 0 | 95 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 29 | 24 | 19 | 14 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.42 | 41 | 0 | 2 | 880 | 0 | 0 | 21 | 0 | 0 | 149 | 0 | 0 | 0 | 1132 | 5 | 0 | 0 | 230 | 320 | 300 | 43 | 0 | 195 | 0 | 0 | 149 | 0 | 0 | 19 | 0 | 132 | 0 | 58 | 0 | 295 | 0 | 357 | 30 | 30 | 148 | 8 | 17 | 0 | 81 | 30 | 0 | 0 | 102 | 0 | 87 | 9 | 0 | 1.5 | 42.22 | 0 | 6705.14 | 907 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 998 | 0 | 0 | 0 | 1051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.41 | 88 | 0 | 0 | 49.22 | 140 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 3.85 | 0 | 49 | 0 | 29 | 0 | 0 | 0 | 0 | 5.9 | 152 | 0.57 | 0 | 208 | 126 | 220 | 0 | 341 | 800 | 0 | 6049.95 | 12755.09 | 78.93
11:00 | 0 | 34 | 50 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 284 | 0 | 17 | 87 | 0 | 95 | 15 | 14 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 31 | 36 | 19 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.63 | 80 | 0 | 2 | 855 | 0 | 0 | 46 | 0 | 0 | 146 | 0 | 0 | 0 | 1170 | 10 | 1 | 0 | 230 | 320 | 300 | 43 | 0 | 192 | 0 | 0 | 149 | 0 | 0 | 19 | 0 | 150 | 0 | 52 | 0 | 300 | 0 | 357 | 30 | 30 | 155 | 11 | 17 | 0 | 81 | 30 | 0 | 0 | 103 | 0 | 87 | 9 | 0 | 2.1 | 46.94 | 0 | 6920.67 | 907 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 1035 | 0 | 0 | 0 | 1153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.48 | 102 | 0 | 0 | 37.9 | 160 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 4.72 | 0 | 49 | 0 | 33 | 0 | 0 | 0 | 0 | 7.5 | 196 | 0.29 | 0 | 257 | 126 | 220 | 0 | 377 | 840 | 0 | 6400.89 | 13321.56 | 78.91
12:00 | 0 | 34 | 40 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 281 | 0 | 17 | 109 | 0 | 195 | 30 | 16 | 35 | 0 | 0 | 0 | 0 | 0 | 17 | 306 | 0 | 0 | 33 | 60 | 19 | 14 | 0 | 460 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.69 | 80 | 14 | 2 | 900 | 6 | 0 | 50 | 0 | 37 | 147 | 0 | 0 | 0 | 1160 | 12 | 86 | 0 | 220 | 320 | 300 | 43 | 0 | 197 | 0 | 12 | 149 | 38 | 5 | 19 | 0 | 132 | 0 | 62 | 0 | 295 | 0 | 357 | 30 | 30 | 150 | 12 | 17 | 0 | 81 | 28 | 0 | 0 | 104 | 0 | 87 | 9 | 0 | 2.25 | 45.69 | 0 | 7265.63 | 912 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 1052 | 0 | 0 | 0 | 1225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.5 | 81 | 0 | 0 | 41.12 | 160 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 4.97 | 0 | 50 | 0 | 33 | 0 | 0 | 0 | 0 | 6.7 | 199 | 0.7 | 0 | 251 | 127 | 220 | 0 | 393 | 930 | 0 | 6582.99 | 13848.62 | 78.9
13:00 | 0 | 34 | 42 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 213 | 0 | 17 | 128 | 0 | 270 | 55 | 17 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 9 | 68 | 19 | 14 | 0 | 360 | 16 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2.58 | 81 | 34 | 2 | 850 | 14 | 0 | 50 | 1 | 51 | 146 | 0 | 0 | 0 | 1110 | 6 | 147 | 0 | 220 | 320 | 300 | 43 | 0 | 191 | 0 | 18 | 145 | 51 | 9 | 19 | 0 | 128 | 10 | 64 | 0 | 300 | 0 | 356 | 30 | 30 | 137 | 11 | 17 | 0 | 81 | 28 | 0 | 0 | 102 | 10 | 87 | 9 | 0 | 2.15 | 38.32 | 0 | 7177.05 | 913 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 1095 | 0 | 0 | 0 | 1280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.13 | 36 | 0 | 0 | 40.36 | 160 | 0 | 0 | 0 | 130 | 0 | 403 | 0 | 5.2 | 0 | 49 | 0 | 34 | 30 | 0 | 0 | 0 | 7.9 | 193 | 0.58 | 0 | 215 | 127 | 220 | 0 | 376 | 960 | 0 | 6614.17 | 13791.22 | 78.89
14:00 | 0 | 34 | 42 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 211 | 35 | 0 | 112 | 0 | 210 | 55 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 27 | 68 | 16 | 14 | 0 | 380 | 13 | 0 | 11 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 3.88 | 82 | 33 | 0 | 800 | 0 | 0 | 50 | 0 | 45 | 145 | 0 | 0 | 0 | 950 | 13 | 147 | 0 | 240 | 291 | 250 | 43 | 0 | 190 | 0 | 17 | 145 | 17 | 11 | 19 | 0 | 148 | 0 | 29 | 13 | 300 | 0 | 321 | 30 | 30 | 125 | 8 | 16 | 0 | 81 | 28 | 0 | 0 | 103 | 17 | 87 | 9 | 0 | 1.92 | 45.82 | 0 | 6745.62 | 812 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 1062 | 0 | 0 | 0 | 1258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.53 | 27 | 0 | 0 | 41.31 | 130 | 0 | 0 | 0 | 130 | 0 | 200 | 0 | 2.61 | 0 | 50 | 0 | 31 | 30 | 0 | 0 | 0 | 2.8 | 180 | 0.15 | 0 | 197 | 100 | 180 | 0 | 311 | 950 | 0 | 6013.4 | 12759.02 | 78.88
15:00 | 7 | 34 | 42 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 303 | 25.6 | 0 | 87 | 0 | 145 | 30 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 5 | 75 | 0 | 14 | 0 | 500 | 15 | 0 | 23 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 3.22 | 82 | 34 | 2 | 844 | 0 | 0 | 50 | 0 | 48 | 145 | 0 | 0 | 0 | 860 | 9 | 80 | 0 | 240 | 280 | 250 | 43 | 0 | 205 | 0 | 18 | 151 | 0 | 0 | 19 | 0 | 140 | 0 | 3 | 23 | 260 | 0 | 306 | 10 | 30 | 148 | 8 | 16 | 0 | 81 | 30 | 0 | 0 | 103 | 0 | 88 | 9 | 0 | 1.52 | 35.55 | 0 | 6645.89 | 913 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 1010 | 0 | 0 | 0 | 1245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.98 | 75 | 0 | 0 | 17.58 | 130 | 0 | 0 | 0 | 130 | 0 | 200 | 0 | 3.21 | 0 | 51 | 0 | 24 | 32 | 0 | 0 | 0 | 4.9 | 134 | 0.15 | 0 | 251 | 100 | 180 | 0 | 332 | 930 | 0 | 6022.82 | 12668.71 | 78.87
16:00 | 0 | 34 | 42 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 305 | 18 | 12 | 87 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 9 | 34 | 0 | 14 | 0 | 470 | 15 | 0 | 24 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 2.01 | 82 | 33 | 4 | 845 | 0 | 0 | 50 | 0 | 34 | 147 | 0 | 0 | 0 | 920 | 9 | 24 | 0 | 240 | 300 | 250 | 43 | 0 | 204 | 0 | 27 | 152 | 0 | 0 | 17 | 0 | 118 | 0 | 19 | 23 | 295 | 0 | 308 | 12 | 30 | 149 | 3 | 16 | 0 | 82 | 30 | 0 | 0 | 101 | 0 | 88 | 9 | 0 | 1.01 | 1.16 | 0 | 6499.18 | 912 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 987 | 0 | 0 | 0 | 1261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.03 | 48 | 0 | 0 | 9.86 | 130 | 0 | 0 | 0 | 130 | 0 | 320 | 0 | 0.87 | 0 | 52 | 0 | 14 | 34 | 0 | 0 | 0 | 3.8 | 93 | 0.03 | 0 | 244 | 100 | 180 | 0 | 385 | 980 | 0 | 6113.59 | 12612.77 | 78.86
17:00 | 5 | 34 | 50 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 304 | 18 | 0 | 87 | 0 | 30 | 15 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 7 | 17 | 18 | 14 | 0 | 450 | 15 | 0 | 25 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0.66 | 82 | 32 | 6 | 880 | 0 | 0 | 50 | 0 | 31 | 147 | 0 | 0 | 0 | 920 | 4 | 24 | 0 | 240 | 300 | 250 | 43 | 0 | 201 | 0 | 0 | 152 | 0 | 0 | 19 | 0 | 128 | 0 | 8 | 31 | 295 | 0 | 308 | 42 | 30 | 146 | 1 | 16 | 0 | 85 | 30 | 0 | 0 | 101 | 0 | 87 | 9 | 0 | 0.4 | 4.26 | 0 | 6490.32 | 913 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 985 | 0 | 0 | 0 | 1267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.76 | 23 | 0 | 0 | 12.02 | 130 | 0 | 0 | 0 | 130 | 0 | 353 | 0 | 0.89 | 0 | 50 | 0 | 6 | 34 | 0 | 0 | 0 | 1.8 | 44 | 0.1 | 0 | 247 | 100 | 220 | 0 | 383 | 965 | 0 | 6103.57 | 12593.89 | 78.85
18:00 | 7 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 308 | 18 | 0 | 87 | 5 | 30 | 15 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 1 | 18 | 18 | 14 | 0 | 460 | 13 | 0 | 31 | 0 | 11 | 3 | 0 | 0 | 0 | 0 | 0.05 | 82 | 33 | 12 | 890 | 0 | 0 | 50 | 1 | 30 | 148 | 0 | 0 | 0 | 915 | 0 | 24 | 0 | 240 | 300 | 250 | 51 | 0 | 198 | 0 | 0 | 154 | 0 | 0 | 19 | 0 | 136 | 0 | 0 | 31 | 305 | 0 | 308 | 42 | 30 | 141 | 0 | 16 | 0 | 76 | 30 | 0 | 0 | 101 | 0 | 88 | 9 | 0 | 0 | 2.03 | 10 | 6530.08 | 913 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 982 | 0 | 0 | 0 | 1262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.73 | 3 | 0 | 0 | 1.76 | 130 | 0 | 0 | 0 | 130 | 0 | 397 | 0 | 0.17 | 0 | 50 | 0 | 1 | 34 | 0 | 0 | 0 | 0.4 | 8 | 0 | 0 | 234 | 100 | 220 | 0 | 370 | 945 | 0 | 6012.06 | 12542.14 | 78.82
19:00 | 7 | 70 | 50 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 330 | 35 | 17 | 123 | 30 | 145 | 50 | 35 | 65 | 0 | 0 | 0 | 0 | 0 | 30 | 306 | 0 | 0 | 0 | 51 | 18 | 14 | 0 | 500 | 22 | 0 | 37 | 0 | 19 | 50 | 0 | 0 | 0 | 0 | 0 | 82 | 34 | 17 | 985 | 0 | 0 | 50 | 17 | 44 | 148 | 0 | 0 | 0 | 1080 | 0 | 73 | 0 | 300 | 300 | 345 | 51 | 0 | 205 | 0 | 39 | 152 | 36 | 1 | 19 | 0 | 142 | 0 | 0 | 31 | 300 | 0 | 354 | 42 | 30 | 145 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 102 | 0 | 88 | 9 | 0 | 0 | 0 | 12 | 7737 | 907 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1049 | 0 | 0 | 0 | 1283 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 150 | 0 | 414 | 0 | 0 | 0 | 49 | 50 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238 | 127 | 220 | 0 | 434 | 980 | 0 | 6364 | 14101 | 78.8
19:30 | 10 | 70 | 51 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 288 | 35 | 17 | 133 | 30 | 195 | 55 | 35 | 86 | 0 | 0 | 0 | 0 | 0 | 50 | 300 | 0 | 0 | 0 | 86 | 18 | 14 | 0 | 420 | 30 | 0 | 38 | 0 | 7 | 50 | 0 | 0 | 0 | 0 | 0 | 82 | 33 | 9 | 990 | 0 | 0 | 50 | 17 | 45 | 149 | 0 | 0 | 0 | 1080 | 0 | 135 | 0 | 300 | 355 | 342 | 51 | 0 | 198 | 0 | 90 | 154 | 66 | 18 | 19 | 0 | 152 | 0 | 0 | 31 | 290 | 0 | 364 | 42 | 30 | 148 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 102 | 0 | 88 | 9 | 0 | 0 | 0 | 12 | 7934 | 908 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1145 | 0 | 0 | 0 | 1286 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 150 | 0 | 362 | 0 | 0 | 0 | 49 | 108 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 230 | 127 | 220 | 0 | 472 | 1060 | 0 | 6677 | 14611 | 78.8
20:00 | 16 | 70 | 51 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 288 | 36 | 17 | 133 | 15 | 195 | 30 | 17 | 83 | 0 | 0 | 0 | 0 | 0 | 40 | 300 | 0 | 0 | 0 | 86 | 18 | 14 | 0 | 450 | 17 | 0 | 36 | 0 | 19 | 50 | 0 | 0 | 0 | 0 | 0 | 81 | 33 | 8 | 960 | 0 | 0 | 50 | 17 | 48 | 149 | 0 | 0 | 0 | 1080 | 0 | 147 | 0 | 330 | 355 | 342 | 51 | 0 | 200 | 0 | 85 | 154 | 0 | 0 | 19 | 0 | 152 | 0 | 0 | 31 | 290 | 0 | 370 | 42 | 30 | 141 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 102 | 0 | 88 | 9 | 0 | 0 | 0 | 12 | 7832 | 908 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1201 | 0 | 0 | 0 | 1266 | 0 | 0 | 0 | 35 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 150 | 0 | 375 | 0 | 0 | 0 | 49 | 110 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 222 | 127 | 220 | 0 | 468 | 1060 | 0 | 6722 | 14554 | 78.78
21:00 | 7 | 34 | 51 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 316 | 36 | 17 | 133 | 15 | 125 | 15 | 17 | 84 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 68 | 18 | 14 | 0 | 475 | 15 | 0 | 38 | 0 | 16 | 50 | 0 | 0 | 0 | 0 | 0 | 79 | 34 | 10 | 945 | 0 | 0 | 50 | 0 | 47 | 149 | 0 | 0 | 0 | 1085 | 0 | 80 | 0 | 235 | 355 | 345 | 51 | 0 | 190 | 0 | 88 | 152 | 0 | 0 | 19 | 0 | 148 | 0 | 0 | 31 | 290 | 0 | 394 | 42 | 30 | 144 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 102 | 0 | 88 | 9 | 0 | 0 | 0 | 12 | 7546 | 907 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1217 | 0 | 0 | 0 | 1385 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 150 | 0 | 407 | 0 | 0 | 0 | 49 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 210 | 127 | 220 | 0 | 444 | 1000 | 0 | 6814 | 14360 | 78.76
22:00 | 7 | 34 | 51 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 304 | 36 | 17 | 113 | 15 | 125 | 15 | 17 | 87 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 68 | 18 | 14 | 0 | 450 | 16 | 0 | 38 | 0 | 9 | 50 | 0 | 0 | 0 | 0 | 0 | 77 | 33 | 14 | 920 | 0 | 0 | 50 | 0 | 48 | 150 | 0 | 0 | 0 | 1090 | 0 | 80 | 0 | 215 | 355 | 320 | 51 | 0 | 172 | 0 | 88 | 154 | 0 | 0 | 19 | 0 | 148 | 0 | 0 | 16 | 285 | 0 | 394 | 42 | 30 | 149 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 102 | 0 | 78 | 9 | 0 | 0 | 0 | 12 | 7383 | 906 | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 1389 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 150 | 0 | 394 | 0 | 0 | 0 | 49 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 127 | 220 | 0 | 459 | 977 | 0 | 6713 | 14096 | 78.74
23:00 | 7 | 34 | 51 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 296 | 18 | 17 | 113 | 15 | 125 | 15 | 17 | 83 | 0 | 0 | 0 | 0 | 0 | 17 | 296 | 0 | 0 | 0 | 68 | 18 | 14 | 0 | 455 | 15 | 0 | 37 | 0 | 4 | 50 | 0 | 0 | 0 | 0 | 0 | 77 | 33 | 12 | 900 | 0 | 0 | 50 | 0 | 47 | 150 | 0 | 0 | 0 | 1056 | 0 | 80 | 0 | 215 | 356 | 320 | 51 | 0 | 172 | 0 | 89 | 151 | 0 | 0 | 19 | 0 | 146 | 0 | 0 | 16 | 285 | 0 | 394 | 42 | 30 | 135 | 0 | 17 | 0 | 86 | 30 | 100 | 0 | 102 | 0 | 78 | 9 | 0 | 0 | 0 | 12 | 7365 | 906 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1211 | 0 | 0 | 0 | 1332 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 150 | 0 | 370 | 0 | 0 | 0 | 48 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 127 | 220 | 0 | 425 | 940 | 0 | 6561 | 13926 | 78.72
Total KWH | 70848 | 761280 | 906240 | 0 | 0 | 0 | 0 | 0 | 8395200 | 0 | 7000740 | 259200 | 188640 | 2172528 | 108000 | 2059964 | 459027 | 251036 | 555840 | 0 | 0 | 0 | 0 | 0 | 180383 | 7268003 | 0 | 0 | 205869 | 978000 | 426000 | 347400 | 0 | 10951363.64 | 204491 | 0 | 356160 | 0 | 123840 | 309956 | 0 | 0 | 0 | 0 | 21359 | 1564020 | 452500 | 289440 | 21323636.36 | 23418 | 0 | 1072320 | 50554.8 | 592145 | 3489971 | 0 | 0 | 0 | 25330907 | 78300 | 1145818 | 16727 | 5832000 | 8180800 | 7258000 | 1182328 | 0 | 4915000 | 0 | 569280 | 3614853 | 220800 | 56280 | 477470 | 0 | 3115200 | 22421 | 323673 | 252272 | 7095000 | 0 | 8302000 | 763000 | 723960 | 3458782 | 82990 | 372000 | 0 | 1905600 | 710976 | 194000 | 0 | 2447700 | 46800 | 1971600 | 211200 | 0 | 13450 | 330810 | 72000 | 164713369.8 | 21811636 | 4898592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 707760 | 24189090 | 0 | 0 | 0 | 28904229.3 | 0 | 0 | 0 | 76800 | 208416 | 0 | 4256 | 0 | 0 | 368400 | 669210 | 0 | 0 | 308992 | 3631909 | 0 | 0 | 0 | 3444327 | 0 | 8729963 | 0 | 31740 | 0 | 1164218 | 582689 | 255389 | 756240 | 0 | 0 | 0 | 52099.56 | 1441440 | 4051 | 54336 | 5564000 | 2894000 | 5311070 | 0 | 9047272 | 23349818.18 | 0 | 148461943.04 | 313175312.84