## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 16-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-05-2026 | during | 16-05-2026 | during | 16-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 404 | 412 | 412 | 412 | 392 | 392 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 39 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 331 | 335 | 335 | 315 | 315 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17.5 | 53.97 | 53.97 | 0 | 0 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 0 | 149.36 | 149.36 | 46 | 46 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 4 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 20 | 33 | 33 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 14 | 22 | 22 | 14 | 14 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 33 | 16 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 125 | 195 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 99 | 116 | 149 | 149 | 133 | 133 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 82 | 50 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 35 | 162 | 162 | 18 | 36 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 0 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 405 | 495 | 584 | 584 | 500 | 500 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 240 | 262 | 718 | 718 | 335 | 335 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 107 | 51 | 160 | 160 | 17 | 70 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1891 | 2138.5 | 5954.22 | 5922.22 | 2341.19 | 2467.19
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 0 | 17 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 15 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 10 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 78 | 80 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 214 | 215 | 215 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 8 | 49 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 51 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 42 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 17 | 63 | 108 | 108 | 18 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.26 | 0 | 4.47 | 0 | 4.47 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 49 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 38 | 0 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1162 | 1224 | 1224 | 1204 | 1204 | U2 on AGC
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 8 | 0 | 5 | 1 | 5 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 625 | 1110 | 720 | 1150 | 1010 | 1010 | AGC
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2187.26 | 2837 | 3603.33 | 4036.86 | 3096.83 | 3188.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 196 | 195 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 0 | 0 | 0 | 0 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 342 | 345 | 342.01 | 342.01 | 342.01 | 342.01 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 327 | 340 | 393 | 393 | 270 | 270 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 31 | 43 | 41.65 | 41.65 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 17 | 40 | 52.82 | 52.82 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 16 | 167 | 195 | 195 | 100 | 100 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 15 | 150 | 150 | 150 | 25 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 31 | 40 | 40 | 40 | 40 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 95 | 98 | 163 | 163 | 140 | 140 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 89 | 0 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 146 | 150 | 84 | 80 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 8 | 52 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 11 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 17 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 7 | 18 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 51 | 115 | 115 | 0 | 50 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 50 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1393 | 1690 | 2417.43 | 2348.43 | 2012.27 | 2272.27
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-05-2026 | during | 16-05-2026 | during | 16-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.5 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 87 | 87 | 90 | 90 | 10 | 10 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 10 | 10 | 10 | 10 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 45.63 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 143.13 | 108 | 381.1 | 334 | 121.6 | 49
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 148 | 153 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 153 | 154 | 150 | 150 | 100 | 100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 85 | 85 | 85 | 86 | 86 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 101 | 102 | 102 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 320 | 366 | 380 | 380 | 340 | 340 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1215 | 1253 | 1368 | 1368 | 1199 | 1199
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 906 | 906 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 36 | 36 | 36 | 36 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 226 | 190 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 98 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 545 | 574 | 617.1 | 617.1 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1775 | 1670 | 2973.1 | 2883.1 | 2657.1 | 2567.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 330 | 450 | 330 | 450 | 602 | 602 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 8 | 104 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 124 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 990 | 1210 | 1244 | 1244 | 1184 | 1184 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 258 | 276 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.67 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1926.67 | 2384 | 2492 | 2611 | 2551 | 2587
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 51.06 | 0 | 48 | 0 | 48 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 189 | 197 | 214 | 214 | 180 | 180 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 40 | 207 | 220 | 220 | 0 | 0 | Liquid fuel shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 180 | 180 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 352 | 406 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0.03 | 0.03 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 85 | 85 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 4 | 35 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1298 | 1455 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 34 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2068.06 | 2300 | 3210.72 | 2995.87 | 2706.17 | 2576.32
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 45 | 48 | 48 | 50 | 50 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 20 | 69 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.7 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 50 | 115 | 115 | 0 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 179 | 0 | 140.71 | 0 | 140.71 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 322.7 | 164 | 472.71 | 296 | 339.71 | 278
System Total |  |  |  |  | 28823.2 | 29270.237 | 12921.82 | 14544.5 | 22872.61 | 22795.48 | 17024.87 | 17184.24
Forecast Scenario (16-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14300 |  | 0 |  | 14300
|  |  |  | 1:00 | 13990 |  | 0 |  | 13990
|  |  |  | 2:00 | 13810 |  | 0 |  | 13810
|  |  |  | 3:00 | 13330 |  | 0 |  | 13330
|  |  |  | 4:00 | 13160 |  | 0 |  | 13160
|  |  |  | 5:00 | 12730 |  | 0 |  | 12730
|  |  |  | 6:00 | 12680 |  | 0 |  | 12680
|  |  |  | 7:00 | 12930 |  | 0 |  | 12930
|  |  |  | 8:00 | 12920 |  | 0 |  | 12920
|  |  |  | 9:00 | 13020 |  | 0 |  | 13020
|  |  |  | 10:00 | 13100 |  | 0 |  | 13100
|  |  |  | 11:00 | 13180 |  | 0 |  | 13180
|  |  |  | 12:00 | 13800 |  | 0 |  | 13800
|  |  |  | 13:00 | 14300 |  | 0 |  | 14300
|  |  |  | 14:00 | 14300 |  | 0 |  | 14300
|  |  |  | 15:00 | 14400 |  | 0 |  | 14400
|  |  |  | 16:00 | 14380 |  | 0 |  | 14380
|  |  |  | 17:00 | 14200 |  | 0 |  | 14200
|  |  |  | 18:00 | 14200 |  | 0 |  | 14200
|  |  |  | 18:30 | 14900 |  | 0 |  | 14900
|  |  |  | 19:00 | 15610 |  | 0 |  | 15610
|  |  |  | 19:30 | 15900 |  | 0 |  | 15900
|  |  |  | 20:00 | 15800 |  | 0 |  | 15800
|  |  |  | 21:00 | 15750 |  | 0 |  | 15750
|  |  |  | 22:00 | 15700 |  | 0 |  | 15700
|  |  |  | 23:00 | 15600 |  | 0 |  | 15600
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 13800.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15900.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15900.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 337.19 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:19 hrs on 16-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 15-05-2026 | [28 empty] | Date: | 15-05-2026 | [28 empty] | Date: | 15-05-2026 | [28 empty] | Date: | 15-05-2026 | [28 empty] | Date: | 15-05-2026 | [17 empty] | Date: | 15-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [17 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 283 | 0 | 0 | 133 | 39 | 277 | 55 | 30 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 18 | 14 | 0 | 450 | 0 | 0 | 51 | 0 | 21 | 0 | 24 | 0 | 0 | 0 | 0 | 74 | 0 | 32 | 935 | 6 | 0 | 7 | 0 | 35 | 219 | 0 | 0 | 0 | 1160 | 0 | 26 | 0 | 240 | 204 | 270 | 51 | 0 | 216 | 0 | 68 | 98 | 52 | 0 | 19 | 17 | 152 | 0 | 0 | 32 | 295 | 0 | 368 | 42 | 30 | 147 | 0 | 17 | 0 | 86 | 0 | 153 | 0 | 101 | 35 | 9 | 78 | 0 | 0 | 0 | 0 | 7621 | 912 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 991 | 0 | 0 | 0 | 1450.71 | 0 | 0 | 0 | 95 | 85 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 387 | 0 | 0 | 0 | 46 | 70 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 281 | 124 | 220 | 0 | 551 | 1120 | 90 | 7176.71 | 14797.71 | 77.21
01:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 288 | 0 | 0 | 133 | 105 | 272 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 470 | 0 | 0 | 22 | 0 | 14 | 0 | 16 | 0 | 0 | 0 | 0 | 72 | 0 | 32 | 785 | 61 | 0 | 6 | 0 | 56 | 221 | 0 | 0 | 0 | 1181 | 0 | 26 | 0 | 255 | 204 | 270 | 51 | 0 | 216 | 0 | 44 | 98 | 120 | 0 | 19 | 17 | 144 | 0 | 0 | 32 | 295 | 0 | 368 | 42 | 30 | 154 | 0 | 17 | 0 | 86 | 0 | 151 | 0 | 100 | 35 | 9 | 78 | 0 | 0 | 0 | 0 | 7683 | 913 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 573 | 0 | 0 | 0 | 1449.2 | 0 | 0 | 0 | 113 | 110 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 394 | 0 | 0 | 0 | 46 | 91 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 272 | 124 | 220 | 0 | 450 | 1150 | 35 | 6648.2 | 14331.2 | 77.19
02:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 254 | 0 | 0 | 133 | 105 | 260 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 420 | 0 | 0 | 18 | 0 | 4 | 0 | 8 | 0 | 0 | 0 | 0 | 72 | 0 | 32 | 730 | 118 | 0 | 6 | 0 | 68 | 221 | 0 | 0 | 0 | 1168 | 0 | 26 | 0 | 250 | 205 | 270 | 51 | 0 | 210 | 0 | 0 | 98 | 161 | 0 | 19 | 72 | 138 | 0 | 0 | 32 | 295 | 0 | 368 | 42 | 30 | 143 | 0 | 17 | 0 | 86 | 0 | 153 | 0 | 100 | 35 | 9 | 78 | 0 | 0 | 0 | 0 | 7565 | 890 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 581 | 0 | 0 | 0 | 1454.05 | 0 | 0 | 0 | 113 | 109 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 359 | 0 | 0 | 0 | 47 | 94 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 266 | 124 | 220 | 0 | 330 | 1140 | 35 | 6473.05 | 14038.05 | 77.17
03:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 220 | 0 | 0 | 133 | 105 | 260 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 380 | 0 | 0 | 19 | 0 | 9 | 0 | 8 | 0 | 0 | 0 | 0 | 74 | 0 | 32 | 700 | 127 | 0 | 6 | 0 | 65 | 222 | 0 | 0 | 0 | 1172 | 0 | 26 | 0 | 250 | 205 | 270 | 51 | 0 | 204 | 0 | 0 | 98 | 193 | 0 | 19 | 91 | 140 | 0 | 0 | 32 | 290 | 0 | 308 | 42 | 30 | 126 | 0 | 17 | 0 | 86 | 0 | 152 | 0 | 101 | 35 | 9 | 78 | 0 | 0 | 0 | 0 | 7410 | 890 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 584 | 0 | 0 | 0 | 1451.91 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 95 | 0 | 355 | 0 | 0 | 0 | 47 | 90 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 260 | 103 | 180 | 0 | 330 | 1040 | 35 | 6260.91 | 13670.91 | 77.15
04:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 221 | 0 | 0 | 132 | 75 | 260 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 370 | 0 | 0 | 19 | 0 | 13 | 0 | 8 | 0 | 0 | 0 | 0 | 76 | 0 | 33 | 700 | 122 | 0 | 6 | 0 | 17 | 222 | 0 | 0 | 0 | 1165 | 0 | 26 | 0 | 260 | 204 | 270 | 51 | 0 | 197 | 0 | 0 | 99 | 193 | 0 | 19 | 108 | 132 | 0 | 0 | 32 | 290 | 0 | 308 | 42 | 30 | 126 | 0 | 17 | 0 | 86 | 0 | 152 | 0 | 101 | 22 | 9 | 78 | 0 | 0 | 0 | 0 | 7312 | 890 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 587 | 0 | 0 | 0 | 1455.75 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 47 | 92 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 260 | 100 | 180 | 0 | 330 | 900 | 35 | 6006.75 | 13318.75 | 77.13
05:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 217 | 0 | 0 | 133 | 30 | 195 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 286 | 0 | 0 | 0 | 86 | 18 | 21 | 0 | 370 | 0 | 0 | 19 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 34 | 700 | 52 | 0 | 6 | 0 | 17 | 222 | 0 | 0 | 0 | 1160 | 0 | 26 | 0 | 280 | 204 | 270 | 51 | 0 | 189 | 0 | 0 | 99 | 100 | 0 | 19 | 17 | 128 | 0 | 0 | 0 | 290 | 0 | 320 | 42 | 30 | 139 | 0 | 17 | 0 | 86 | 0 | 153 | 0 | 101 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 6895 | 890 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 588 | 0 | 0 | 0 | 1456.54 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 47 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 258 | 127 | 220 | 0 | 330 | 894 | 35 | 5796.54 | 12691.54 | 77.11
06:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 216 | 0 | 0 | 133 | 15 | 95 | 30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 2 | 51 | 20 | 21 | 0 | 370 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0.27 | 79 | 0 | 25 | 700 | 0 | 0 | 2 | 0 | 16 | 222 | 0 | 0 | 0 | 1158 | 0 | 26 | 0 | 280 | 205 | 270 | 51 | 0 | 193 | 0 | 0 | 99 | 34 | 0 | 19 | 0 | 122 | 0 | 3 | 0 | 295 | 0 | 332 | 42 | 30 | 125 | 1 | 17 | 0 | 86 | 0 | 152 | 0 | 101 | 0 | 9 | 78 | 0 | 0.15 | 3.14 | 0 | 6484.56 | 890 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | 590 | 0 | 0 | 0 | 1454.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 3.13 | 4 | 0 | 0 | 3.33 | 140 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0.3 | 0 | 47 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 6 | 0.04 | 0 | 262 | 127 | 220 | 0 | 330 | 1090 | 0 | 5689.61 | 12174.17 | 77.09
07:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 211 | 0 | 0 | 133 | 15 | 45 | 30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 7 | 51 | 20 | 21 | 0 | 370 | 0 | 0 | 19 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 1.52 | 80 | 0 | 0 | 700 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1145 | 0 | 26 | 0 | 270 | 204 | 270 | 51 | 0 | 186 | 0 | 0 | 99 | 34 | 0 | 11 | 0 | 124 | 0 | 19 | 0 | 295 | 0 | 332 | 42 | 30 | 128 | 2 | 17 | 0 | 86 | 0 | 151 | 0 | 101 | 0 | 9 | 78 | 0 | 0.28 | 6.8 | 0 | 6431.6 | 890 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.67 | 589 | 0 | 0 | 0 | 1448.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.58 | 23 | 0 | 0 | 10.61 | 140 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 1 | 0 | 47 | 0 | 4 | 0 | 0 | 0 | 0 | 1.1 | 4 | 0.05 | 0 | 255 | 125 | 220 | 0 | 330 | 1086 | 0 | 5736.86 | 12168.46 | 77.07
08:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 210 | 0 | 0 | 104 | 15 | 0 | 42 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 14 | 51 | 21 | 20 | 0 | 370 | 0 | 0 | 11 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2.64 | 80 | 0 | 0 | 700 | 0 | 0 | 12 | 0 | 0 | 221 | 0 | 0 | 0 | 1110 | 0 | 0 | 0 | 270 | 203 | 270 | 51 | 0 | 181 | 0 | 0 | 98 | 0 | 0 | 11 | 0 | 118 | 0 | 39 | 0 | 290 | 0 | 332 | 42 | 30 | 127 | 4 | 17 | 0 | 86 | 0 | 152 | 0 | 101 | 0 | 9 | 78 | 0 | 1.2 | 13.36 | 0 | 6359.2 | 898 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.8 | 583 | 0 | 0 | 0 | 1326.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.64 | 44 | 0 | 0 | 17.96 | 140 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 1.21 | 0 | 48 | 0 | 14 | 0 | 0 | 0 | 0 | 3.4 | 2 | 0.34 | 0 | 253 | 125 | 220 | 0 | 330 | 1040 | 0 | 5656.2 | 12015.4 | 77.05
09:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 247 | 0 | 0 | 96 | 0 | 0 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 56 | 21 | 0 | 0 | 430 | 0 | 0 | 5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3.75 | 80 | 0 | 0 | 700 | 0 | 0 | 19 | 0 | 0 | 218 | 0 | 0 | 0 | 1100 | 15 | 0 | 0 | 320 | 0 | 270 | 51 | 0 | 200 | 0 | 0 | 98 | 0 | 0 | 11 | 0 | 116 | 0 | 59 | 0 | 305 | 0 | 300 | 42 | 30 | 130 | 10 | 17 | 0 | 84 | 0 | 151 | 0 | 101 | 0 | 9 | 78 | 0 | 1.78 | 35.27 | 0 | 6297.8 | 897 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.97 | 583 | 0 | 0 | 0 | 1295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.97 | 71 | 0 | 0 | 33 | 140 | 0 | 7 | 0 | 0 | 0 | 360 | 0 | 3.07 | 0 | 47 | 0 | 9 | 0 | 0 | 0 | 0 | 1.4 | 25 | 0.59 | 0 | 250 | 100 | 180 | 0 | 331 | 915 | 0 | 5563 | 11860.8 | 77.03
10:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 273 | 0 | 0 | 96 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 68 | 21 | 0 | 0 | 435 | 0 | 0 | 6 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 3.29 | 80 | 0 | 0 | 650 | 0 | 0 | 19 | 0 | 0 | 216 | 0 | 0 | 0 | 1075 | 19 | 0 | 0 | 342 | 0 | 300 | 51 | 0 | 204 | 0 | 0 | 97 | 0 | 0 | 11 | 0 | 128 | 0 | 70 | 0 | 300 | 0 | 320 | 42 | 30 | 138 | 11 | 17 | 0 | 83 | 0 | 151 | 0 | 101 | 0 | 9 | 86 | 0 | 2.22 | 39.71 | 0 | 6333.22 | 898 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 560 | 0 | 0 | 0 | 1259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.94 | 92 | 0 | 0 | 35.17 | 140 | 0 | 0 | 8 | 0 | 0 | 392 | 0 | 2.14 | 0 | 50 | 0 | 10 | 0 | 0 | 0 | 0 | 3.4 | 198 | 0.38 | 0 | 235 | 122 | 220 | 0 | 330 | 853 | 0 | 5768.03 | 12101.25 | 77.01
11:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 293 | 0 | 0 | 96 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 68 | 21 | 0 | 0 | 485 | 0 | 0 | 5 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 5.26 | 78 | 0 | 0 | 670 | 0 | 0 | 19 | 0 | 0 | 215 | 0 | 0 | 0 | 1140 | 12 | 0 | 16 | 362 | 0 | 338 | 51 | 3 | 205 | 18 | 0 | 95 | 0 | 0 | 11 | 0 | 138 | 0 | 73 | 0 | 315 | 0 | 320 | 42 | 30 | 152 | 12 | 17 | 0 | 83 | 0 | 152 | 0 | 101 | 0 | 9 | 86 | 0 | 1 | 28.9 | 0 | 6599.16 | 897 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 464 | 0 | 0 | 0 | 1282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.37 | 100 | 0 | 0 | 58.17 | 172 | 0 | 7 | 0 | 0 | 0 | 399 | 0 | 0 | 0 | 49 | 0 | 13 | 0 | 0 | 0 | 0 | 7.1 | 93 | 0.66 | 0 | 280 | 122 | 220 | 0 | 330 | 864 | 0 | 5696.3 | 12295.46 | 76.98
12:00 | 0 | 82 | 33 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 240 | 0 | 0 | 99 | 15 | 125 | 39 | 4 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 107 | 21 | 0 | 0 | 405 | 0 | 0 | 17 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 4.26 | 78 | 0 | 0 | 625 | 38 | 0 | 19 | 0 | 8 | 215 | 0 | 0 | 0 | 1160 | 15 | 15 | 16 | 327 | 0 | 342 | 51 | 17 | 196 | 31 | 0 | 95 | 89 | 7 | 11 | 0 | 146 | 0 | 50 | 0 | 315 | 0 | 320 | 42 | 30 | 148 | 7 | 17 | 0 | 82 | 0 | 153 | 0 | 101 | 0 | 9 | 87 | 0 | 1.5 | 45.63 | 0 | 6829.39 | 906 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 545 | 0 | 0 | 0 | 1298 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 51.06 | 100 | 0 | 0 | 34 | 189 | 0 | 40 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 48 | 35 | 33 | 20 | 0 | 0 | 0 | 7.7 | 179 | 0.67 | 8 | 258 | 120 | 220 | 0 | 330 | 990 | 0 | 6092.43 | 12921.82 | 76.95
13:00 | 0 | 105 | 47 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 254 | 17 | 0 | 114 | 60 | 261 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 298 | 0 | 0 | 0 | 125 | 21 | 0 | 0 | 465 | 0 | 0 | 24 | 0 | 9 | 0 | 2 | 0 | 0 | 0 | 4.32 | 70 | 0 | 0 | 635 | 103 | 0 | 19 | 0 | 15 | 213 | 0 | 0 | 0 | 1160 | 16 | 25 | 53 | 324 | 0 | 338 | 51 | 24 | 195 | 42 | 0 | 94 | 185 | 8 | 18 | 34 | 156 | 0 | 55 | 0 | 310 | 0 | 320 | 42 | 30 | 148 | 9 | 17 | 0 | 82 | 0 | 154 | 0 | 101 | 14 | 9 | 86 | 0 | 0.45 | 43.01 | 0 | 7496.78 | 906 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 585 | 0 | 0 | 0 | 1341 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 52.7 | 84 | 0 | 0 | 53 | 188 | 0 | 110 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 48 | 50 | 33 | 42 | 0 | 0 | 0 | 5.9 | 114 | 0.81 | 27 | 268 | 120 | 220 | 0 | 330 | 1094 | 34 | 6417.41 | 13914.19 | 76.92
14:00 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 253 | 17 | 2 | 87 | 15 | 225 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 125 | 23 | 7 | 0 | 465 | 0 | 0 | 24 | 0 | 10 | 0 | 14 | 0 | 0 | 0 | 3.09 | 70 | 0 | 0 | 620 | 0 | 0 | 3 | 0 | 15 | 213 | 0 | 0 | 0 | 1160 | 16 | 25 | 55 | 336 | 0 | 338 | 51 | 32 | 201 | 41 | 0 | 94 | 17 | 9 | 19 | 0 | 152 | 0 | 52 | 12 | 310 | 0 | 329 | 42 | 30 | 133 | 4 | 17 | 0 | 82 | 0 | 153 | 0 | 101 | 0 | 9 | 87 | 0 | 0 | 3.49 | 0 | 6982.58 | 906 | 218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 586 | 0 | 0 | 0 | 1267 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 47.59 | 65 | 0 | 0 | 36 | 189 | 0 | 134 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 43 | 35 | 26 | 34 | 0 | 0 | 0 | 6.7 | 86 | 0.43 | 32 | 217 | 120 | 220 | 0 | 330 | 1110 | 16 | 6227.72 | 13210.3 | 76.89
15:00 | 0 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 240 | 17.5 | 17 | 65 | 0 | 225 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 86 | 23 | 7 | 0 | 460 | 0 | 0 | 24 | 0 | 14 | 0 | 14 | 0 | 0 | 0 | 2.43 | 70 | 0 | 0 | 670 | 0 | 0 | 0 | 0 | 15 | 214 | 0 | 0 | 0 | 1160 | 13 | 26 | 71 | 335 | 0 | 335 | 51 | 40 | 203 | 41 | 0 | 94 | 16 | 9 | 19 | 0 | 144 | 0 | 49 | 30 | 305 | 0 | 332 | 42 | 30 | 144 | 0 | 17 | 0 | 82 | 0 | 154 | 0 | 101 | 0 | 9 | 86 | 0 | 0 | 0.79 | 0 | 6927.72 | 905 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 582 | 0 | 0 | 0 | 1277 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 33.09 | 57 | 0 | 0 | 28 | 188 | 0 | 141 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 46 | 35 | 13 | 34 | 0 | 0 | 0 | 2.3 | 108 | 0.54 | 14 | 236 | 120 | 220 | 0 | 332 | 1095 | 16 | 6166.93 | 13094.65 | 76.86
16:00 | 0 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 231 | 0 | 17 | 60 | 0 | 80 | 30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 17 | 23 | 14 | 0 | 415 | 0 | 0 | 24 | 0 | 6 | 0 | 14 | 0 | 0 | 0 | 1.07 | 72 | 0 | 0 | 820 | 0 | 0 | 18 | 0 | 0 | 215 | 0 | 0 | 0 | 1160 | 8 | 26 | 73 | 345 | 0 | 335 | 51 | 40 | 200 | 41 | 0 | 94 | 15 | 9 | 19 | 0 | 144 | 0 | 32 | 29 | 305 | 0 | 332 | 42 | 30 | 140 | 0 | 17 | 0 | 83 | 0 | 155 | 0 | 101 | 0 | 9 | 45 | 0 | 0 | 15.02 | 0 | 6740.09 | 905 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 584 | 0 | 0 | 0 | 1204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.34 | 17 | 0 | 0 | 18 | 188 | 0 | 156 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 46 | 0 | 13 | 0 | 0 | 0 | 0 | 3.5 | 76 | 0.34 | 14 | 194 | 120 | 220 | 0 | 332 | 1040 | 16 | 5771.18 | 12511.27 | 76.83
17:00 | 0 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 250 | 0 | 17 | 60 | 0 | 30 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 17 | 23 | 0 | 0 | 420 | 0 | 0 | 24 | 0 | 2 | 0 | 14 | 0 | 0 | 0 | 1.02 | 75 | 0 | 0 | 820 | 0 | 0 | 19 | 0 | 0 | 215 | 0 | 0 | 0 | 1055 | 3 | 16 | 0 | 330 | 0 | 345 | 0 | 0 | 194 | 0 | 0 | 94 | 16 | 9 | 19 | 0 | 142 | 0 | 13 | 29 | 305 | 0 | 332 | 42 | 30 | 142 | 0 | 17 | 0 | 85 | 0 | 152 | 0 | 101 | 0 | 9 | 45 | 0 | 0 | 6.87 | 5 | 6309.89 | 905 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 570 | 0 | 0 | 0 | 1150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.94 | 9 | 0 | 0 | 2 | 187 | 0 | 156 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 47 | 0 | 6 | 0 | 0 | 0 | 0 | 1.7 | 31 | 0.17 | 14 | 160 | 120 | 220 | 0 | 450 | 950 | 16 | 5599.81 | 11909.7 | 76.81
18:00 | 0 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 223 | 17 | 17 | 60 | 0 | 30 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 326 | 0 | 0 | 0 | 17 | 23 | 21 | 0 | 405 | 0 | 0 | 24 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0.1 | 75 | 0 | 0 | 820 | 0 | 0 | 19 | 1 | 0 | 214 | 0 | 0 | 0 | 1055 | 0 | 18 | 71 | 340 | 0 | 345 | 32 | 25 | 195 | 30 | 0 | 94 | 15 | 17 | 0 | 0 | 116 | 0 | 2 | 25 | 300 | 0 | 332 | 42 | 30 | 140 | 0 | 17 | 0 | 85 | 0 | 152 | 0 | 101 | 0 | 9 | 45 | 0 | 0.08 | 3.63 | 12 | 6447.81 | 906 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 502 | 0 | 0 | 0 | 1053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81 | 2 | 0 | 0 | 0 | 189 | 0 | 172 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 46 | 0 | 2 | 0 | 0 | 0 | 0 | 0.4 | 2 | 0.03 | 14 | 156 | 120 | 220 | 0 | 451 | 860 | 16 | 5277.24 | 11725.05 | 76.79
19:00 | 0 | 40 | 42 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 248 | 17.5 | 17 | 79 | 60 | 160 | 26 | 17 | 35 | 0 | 0 | 0 | 0 | 0 | 17 | 330 | 0 | 0 | 0 | 53 | 18 | 21 | 0 | 430 | 0 | 0 | 64 | 0 | 1 | 50 | 23 | 0 | 0 | 0 | 0 | 79 | 6 | 2 | 1050 | 11 | 0 | 0 | 8 | 13 | 214 | 0 | 0 | 0 | 1156 | 0 | 73 | 127 | 330 | 0 | 345 | 51 | 25 | 193 | 39 | 19 | 94 | 54 | 12 | 0 | 30 | 92 | 0 | 0 | 31 | 310 | 0 | 332 | 42 | 30 | 145 | 0 | 17 | 0 | 85 | 0 | 152 | 0 | 101 | 2 | 9 | 85 | 0 | 0 | 0 | 12 | 7536.5 | 906 | 195 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 525 | 0 | 0 | 0 | 1358 | 0 | 0 | 0 | 50 | 27 | 0 | 70 | 9 | 8 | 0 | 0 | 24 | 0 | 0 | 198 | 0 | 197 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 47 | 67 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 241 | 124 | 220 | 0 | 450 | 850 | 16 | 6096 | 13632.5 | 76.77
19:30 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 213 | 17.5 | 17 | 115 | 40 | 195 | 55 | 17 | 35 | 0 | 0 | 0 | 0 | 0 | 17 | 331 | 0 | 0 | 0 | 51 | 18 | 21 | 0 | 370 | 0 | 0 | 64 | 0 | 0 | 50 | 31 | 0 | 0 | 0 | 0 | 80 | 41 | 40 | 1075 | 0 | 0 | 0 | 8 | 48 | 214 | 0 | 0 | 0 | 1160 | 0 | 150 | 127 | 335 | 0 | 345 | 51 | 40 | 193 | 40 | 52 | 94 | 51 | 18 | 0 | 24 | 120 | 0 | 0 | 31 | 305 | 0 | 332 | 42 | 30 | 130 | 0 | 17 | 0 | 85 | 0 | 154 | 0 | 101 | 17 | 9 | 85 | 0 | 0 | 0 | 12 | 7872.5 | 906 | 195 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 562 | 0 | 0 | 0 | 1442 | 0 | 0 | 0 | 30 | 35 | 0 | 55 | 14 | 8 | 0 | 0 | 26 | 0 | 0 | 197 | 0 | 200 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 46 | 70 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 195 | 124 | 220 | 0 | 450 | 1040 | 16 | 6365 | 14237.5
20:00 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 227 | 17.5 | 17 | 114 | 0 | 195 | 55 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 17 | 331 | 0 | 0 | 0 | 51 | 18 | 21 | 0 | 415 | 0 | 0 | 64 | 0 | 0 | 50 | 31 | 0 | 0 | 0 | 0 | 80 | 41 | 42 | 1110 | 0 | 0 | 0 | 8 | 50 | 214 | 0 | 0 | 0 | 1162 | 0 | 147 | 160 | 330 | 0 | 345 | 51 | 40 | 195 | 40 | 50 | 97 | 17 | 17 | 11 | 0 | 138 | 0 | 0 | 31 | 305 | 0 | 332 | 42 | 30 | 130 | 0 | 17 | 0 | 85 | 0 | 150 | 0 | 101 | 0 | 9 | 86 | 0 | 0 | 0 | 12 | 7882.5 | 906 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 572 | 0 | 0 | 0 | 1456 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 201 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 46 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 161 | 124 | 220 | 0 | 450 | 1110 | 16 | 6260 | 14142.5 | 76.75
21:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 262 | 17.5 | 17 | 116 | 0 | 195 | 55 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 17 | 331 | 0 | 0 | 0 | 51 | 20 | 14 | 0 | 495 | 0 | 0 | 63 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 80 | 49 | 42 | 1110 | 0 | 0 | 10 | 8 | 49 | 214 | 0 | 0 | 0 | 1162 | 0 | 150 | 167 | 340 | 0 | 345 | 51 | 40 | 195 | 43 | 51 | 98 | 0 | 18 | 11 | 0 | 150 | 0 | 0 | 31 | 305 | 0 | 366 | 42 | 30 | 153 | 0 | 17 | 0 | 85 | 0 | 154 | 0 | 101 | 0 | 9 | 87 | 0 | 0 | 0 | 12 | 8026.5 | 906 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 0 | 0 | 0 | 1455 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 207 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 45 | 50 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 276 | 124 | 220 | 0 | 450 | 1210 | 0 | 6518 | 14544.5 | 76.73
22:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 277 | 17.5 | 17 | 133 | 0 | 195 | 55 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 311 | 0 | 0 | 0 | 51 | 20 | 14 | 0 | 520 | 0 | 0 | 63 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 80 | 51 | 42 | 1110 | 0 | 0 | 25 | 0 | 50 | 217 | 0 | 0 | 0 | 1170 | 0 | 145 | 65 | 393 | 0 | 345 | 51 | 40 | 201 | 40 | 47 | 98 | 0 | 18 | 15 | 0 | 152 | 0 | 0 | 32 | 310 | 0 | 368 | 42 | 30 | 158 | 0 | 17 | 0 | 85 | 0 | 153 | 0 | 101 | 0 | 9 | 77 | 0 | 0 | 0 | 12 | 8019.5 | 905 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 570 | 0 | 0 | 0 | 1458 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 198 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 46 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 278 | 124 | 220 | 0 | 450 | 1185 | 0 | 6485 | 14504.5 | 76.71
23:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 265 | 0 | 0 | 133 | 15 | 225 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 51 | 20 | 14 | 0 | 500 | 0 | 0 | 61 | 0 | 12 | 50 | 0 | 0 | 0 | 0 | 0 | 80 | 51 | 42 | 1110 | 0 | 0 | 26 | 0 | 51 | 217 | 0 | 0 | 0 | 1162 | 0 | 41 | 45 | 393 | 0 | 345 | 51 | 12 | 192 | 43 | 31 | 30 | 0 | 18 | 17 | 0 | 148 | 0 | 0 | 32 | 305 | 0 | 373 | 42 | 30 | 158 | 0 | 17 | 0 | 85 | 0 | 152 | 0 | 101 | 0 | 9 | 77 | 0 | 0 | 0 | 8 | 7710 | 905 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 0 | 0 | 0 | 1453 | 0 | 0 | 0 | 20 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 198 | 0 | 0 | 0 | 399 | 0 | 0 | 0 | 46 | 67 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 278 | 124 | 220 | 0 | 450 | 1175 | 6 | 6521 | 14231 | 76.69
Total KWH | 0 | 1729920 | 831840 | 0 | 0 | 0 | 0 | 0 | 9381600 | 0 | 6190000 | 130320 | 149040 | 2608272 | 671040 | 3623880 | 1122010 | 136101 | 403200 | 0 | 0 | 0 | 0 | 0 | 138183 | 7485876 | 0 | 0 | 16723 | 2004000 | 501000 | 311400 | 0 | 10610454.55 | 0 | 0 | 689280 | 0 | 170880 | 268782 | 157776 | 0 | 0 | 0 | 28590 | 1825500 | 253418 | 413760 | 19192727.27 | 734327 | 0 | 329280 | 25561.8 | 629781 | 5092912 | 0 | 0 | 0 | 27534543 | 109620 | 941745 | 920000 | 7628500 | 1776400 | 6588000 | 1179540 | 346080 | 4930000 | 456408 | 285120 | 2199427 | 1450080 | 157080 | 357230 | 332880 | 3213120 | 0 | 496800 | 433632 | 7299000 | 0 | 8176000 | 995000 | 729240 | 3394800 | 50771 | 404016 | 0 | 1992000 | 0 | 3533500 | 0 | 2420880 | 181440 | 222000 | 1864800 | 0 | 8750 | 251160 | 86880 | 170803876.62 | 21786182 | 4701600 | 0 | 3360 | 0 | 0 | 0 | 0 | 0 | 0 | 393840 | 699840 | 14094550 | 0 | 0 | 0 | 31870182 | 0 | 0 | 0 | 653376 | 1015296 | 0 | 73056 | 10182 | 56093 | 347424 | 666030 | 28152 | 0 | 330368 | 4152545 | 0 | 2188200 | 0 | 484682 | 0 | 8942400 | 0 | 9800 | 0 | 1103999 | 946424 | 160814 | 1014624 | 0 | 0 | 0 | 45029.88 | 838800 | 4830 | 1258272 | 5913000 | 2877000 | 5319210 | 0 | 9076364 | 25450181.82 | 444000 | 146959706.7 | 317763583.32

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 15-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12921.82 | MW | 12:00 Hr. | Energy Generated |  |  | 317.7636 |  | MKWHr.
| Day Peak Demand |  |  | 12982.82 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.233 |  | MKWHr.
| Evening Peak Generation |  |  | 14544.5 | MW | 21:00 Hr. | Energy Demand |  |  | 318.9966 |  | MKWHr.
| Evening Peak Demand |  |  | 14599.89 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.2 |  | °C
| Minimum Generation of the Day |  |  | 11860.8 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 937.4 |  | MMCFD
| Maximum Generation of the Day |  |  | 14797.71 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.1907 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.4803 | 0 | 13.5478 | 0 | 0 | 0.016723 | 0 | 0 | 48.0449 | Gas | 123.9787 | Gas | 435271994.7635
| Chattogram Zone |  |  | 5.5067 | 46.7273 | 3.0882 | 0 | 1.8255 | 0.13821 | 0 | 0.17088 | 57.4567 | Coal | 102.3654 | Coal | 661365570.8401
| Cumilla Zone |  |  | 26.3816 | 0 | 3.6005 | 0 | 0 | 0.4968 | 3.2131 | 0 | 33.692 | HFO | 28.4883 | HFO | 475914320.526
| Mymensingh Zone |  |  | 0 | 0 | 2.3551 | 0 | 0 | 0.25991 | 0 | 0 | 2.615 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.9444 | 0 | 0 | 0 | 0 | 0.050771 | 0 | 0 | 28.9952 | Hydro | 1.8255 | Hydro | 182550
| Khulna Zone |  |  | 4.7016 | 14.0945 | 0.3972 | 0 | 0 | 0.69984 | 21.7862 | 0 | 41.6794 | Solar | 4.0653 | Solar | 64079745.3376
| Barishal Zone |  |  | 8.1962 | 40.4395 | 1.7023 | 0 | 0 | 0.00483 | 0 | 0 | 50.3429 | Import | 56.8695 | Import | 327854423.44
| Rajshahi Zone |  |  | 15.7678 | 0 | 1.8362 | 0 | 0 | 1.3536 | 31.8702 | 0 | 50.8278 | Wind | 0.17088 | Wind | 2513644.8
| Rangpur Zone |  |  | 0 | 1.104 | 1.961 | 0 | 0 | 1.0446 | 0 | 0 | 4.1097
| Total |  |  | 123.9787 | 102.3654 | 28.4883 | 0 | 1.8255 | 4.0653 | 56.8695 | 0.17088 | 317.7636
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 435271994.7635 |  | Hydro | 182550
|  |  |  | Coal | 661365570.8401 |  | Solar | 64079745.3376
|  |  |  | HFO | 475914320.526 |  | Import | 327854423.44
|  |  |  | HSD | 0 |  | Wind | 2513644.8
[5 empty] | Total: | 196,71,82,249 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7862 | Peak Hr Flow | 906.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 39853600 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.8702 | Peak Hr Flow | 1455.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1612 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.2131 | Peak Hr Flow | 150.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2314 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 56.8695 | Peak Hr Flow | 2511.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5123
|  |  |  | Chattogram |  | 0 |  | 1472
|  |  |  | Cumilla |  | 0 |  | 1382
|  |  |  | Mymensingh |  | 53 |  | 1002
|  |  |  | Sylhet |  | 0 |  | 488
|  |  |  | Khulna |  | 0 |  | 1882
|  |  |  | Barishal |  | 0 |  | 494
|  |  |  | Rajshahi |  | 0 |  | 1451
|  |  |  | Rangpur |  | 0 |  | 893
|  |  |  | Total |  | 53 |  | 14187
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:28 |  | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Project Work S/D Due to PTR-1 transformer
dismantle by project-2
| 08:29 |  | Sreepur 230/132/33kV S/S 132/33 kV T-1 HT Project Work S/D Due to PTR-1 Transformer
dismantle by project-2.
| 08:31 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
| 08:32 |  | Sirajgonj 225MW CCPP Unit-2 GT Synchronized with remarks:- GTG has been synchronized with
grid as per NLDC demand.
| 08:32 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized with remarks:- GT
| 08:32 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized with remarks:- GT
| 08:32 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized
| 08:32 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized with remarks:- GT
| 08:41 | 11:55 | Ghorasal-Joydeb-B 132kV Ckt-1 Project Work S/D from Pubail 132/33kV end Due to line
maintenance
|  | 08:50 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 HT is restored.
|  | 08:53 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 LT is restored.
|  | 08:58 | Aminbazar 400/230/132kV S/S 132 kv Bus 02 is restored.
| 09:35 | 20:32 | Hasnabad-Shyampur 230kV Ckt-1 Scheduled S/D from Shyampur 230/132kV end Due to To
control the load flow of Meghnaghat Ckt-01
| 09:37 | 16:38 | GPH 230/33kV S/S Transformer -2 (D07) HT Scheduled S/D Due to for general maintenance
| 09:37 | 09:38 | GPH 230/33kV S/S Transformer-01(D05) HT Scheduled S/D Due to for general maintenance
|  | 09:40 | Daudkandi 132/33kV S/S Transformer-3 HT is restored.
|  | 09:42 | Daudkandi 132/33kV S/S Transformer-3 LT is restored.
| 09:42 |  | Sirajgonj 225MW CCPP Unit-2, fuel is changed from HSD to Gas with remarks:-
| 09:46 | 18:36 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Scheduled S/D Due to Due to
Conductor Shifting from Exiting line tower to ERS tower.
| 09:46 | 18:36 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-1 Scheduled S/D Due to Due to
Conductor Shifting from Exiting line tower to ERS tower.
| 09:48 | 12:58 | Maijdee 132/33kV S/S Tr-02 HT Scheduled S/D Due to Mohabbotpur Feeder 33KV Bus Red Hot
Maintenance.
| 09:57 | 12:55 | Maijdee 132/33kV S/S TR-01 HT Scheduled S/D Due to Subarnochor Feeder 33KV Bus Red Hot
Maintenance.
| 10:24 | 12:12 | Sreepur 230/132/33kV S/S 230 kV Bus-1 Project Work S/D Due to PSDC Project Work.
|  | 10:29 | Daudkandi 132/33kV S/S Transformer-2 HT is restored.
|  | 10:32 | Daudkandi 132/33kV S/S Transformer-2 LT is restored.
| 11:35 |  | Sirajgonj 225MW CCPP Unit-2 ST Synchronized with remarks:- STG has been synchronized with
grid as per NLDC demand.
| 11:35 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized with remarks:- ST
| 12:00 |  | Day peak generation 12919 MW
|  | 12:14 | Ghorasal-Joydeb-B 132kV Ckt-2 is restored.
| 12:35 |  | Khagrachari-Rangamati 132kV Ckt-2 Tripped from Khagrachori 132/33kV end showing REL 670
relays Due to Rangamati Ckt-2 Y ph Loop Broken
|  | 14:06 | Halishahar 132/33kV S/S 405T(TR-1) HT is restored.
|  | 14:09 | Halishahar 132/33kV S/S 415T(TR-2) HT is restored.
| 14:56 | 17:18 | Ghorasal-Joydeb-B 132kV Ckt-2 Project Work S/D from Joydebpur 132/33kV end. | [7 empty] | 60.0MW load
interrup. Joydebpur
132/33kV end
| 15:38 | 15:43 | Bhaluka 132/33kV S/S 03. Transformer-03 LT Tripped showing O/C,E/F Relay relays. | [7 empty] | 7.0MW load
interrup.
|  | 20:32 | Meghnaghat-Shyampur 230kV Ckt-2 is restored.
|  | 20:34 | Haripur-Meghnaghat 230kV Ckt-1 is restored.
| 21:00 |  | Evening Peak Generation is 14544 MW.
| 22:26 | 23:28 | Bashundhara-Tongi 132 kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Hotspot
maintenance
| 01:32 | 02:16 | Dohazari 132/33kV S/S Power Transformer -T-1 LT Scheduled S/D Due to Banshkhali 33 kv | [7 empty] | 25.0MW load
|  |  | feeder redhot maintenance | [7 empty] | interrup.
| 01:33 | 02:15 | Dohazari 132/33kV S/S Power Transformer -T-1 HT Scheduled S/D Due to Banshkhali 33kv | [7 empty] | 25.0MW load
|  |  | feeder redhot maintenance | [7 empty] | interrup.
| 03:40 |  | Sonargaon 132/33kV S/S Bashundhara Line Tripped showing Line distance & differential | [7 empty] | 4.0MW load
|  |  | relays Due to Due To line distance and diffential fault | [7 empty] | interrup.
| 05:38 |  | Meghnaghat-Shyampur 230kV Ckt-2 Scheduled S/D from Shyampur 230/132kV end Due to OPGW
Conductor repairing at tower no-22-26 and from Meghnaghat 400/230kV end Due to for
maintenance work
| 07:02 |  | Mongla 132/33kV S/S T-1 LT Scheduled S/D Due to WZPDCL 33KV BUS SIDE RED HOT | [7 empty] | 7.0MW load
interrup.
| 07:02 |  | Mongla 132/33kV S/S T-1 HT Scheduled S/D Due to WZPDCL 33KV BUS SIDE RED HOT | [7 empty] | 7.0MW load
interrup.
| 07:03 |  | Shariatpur 132/33kV S/S T1-406T LT Scheduled S/D Due to Maintenance Work by PBS. | [7 empty] | 30.0MW load
interrup.
| 07:04 |  | Shariatpur 132/33kV S/S T1-406T HT Scheduled S/D Due to Maintenance Work by PBS. | [7 empty] | 30.0MW load
interrup.
| 07:10 |  | Borhanuddin 230/33kV S/S Bus Forced S/D Due to 33 kv incomer Breacar Red Hot maintains | [7 empty] | 90.0MW load
interrup.
| 07:16 |  | Mymensingh 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D
| 07:16 |  | Mymensingh 132/33kV S/S Transformer-1 (404T) HT Scheduled S/D
| 07:45 |  | Faridpur 132/33kV S/S Transformer-2 LT Scheduled S/D | [7 empty] | 39.0MW load
interrup.
| 07:45 |  | Faridpur 132/33kV S/S Transformer-2 HT Scheduled S/D | [7 empty] | 39.0MW load interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 15-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 412 | 9381600 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1122010 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 331 | 7485876 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17.5 | 130320 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 671040 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 136101 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 138183 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 501000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 311400 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 831840 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 3623880 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 116 | 2608272 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 1729920 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 403200 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 16723 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 149040 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 495 | 10610454.55 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 262 | 6190000 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 51 | 2004000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2138.5 | 48044859.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 25561.8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 109620 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 10 | 329280 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 1825500 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 214 | 5092912 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 49 | 629781 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 157776 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 268782 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 42 | 413760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 63 | 689280 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 28590 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 49 | 253418 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 734327 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1162 | 27534543 | U2 on AGC
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 170880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1110 | 19192727.27 | AGC
Chattogram Area Total |  |  |  |  | 4898.863 | 2837 | 57456738.07
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 195 | 4930000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 0 | 1776400 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 345 | 6588000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 340 | 7628500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 43 | 456408 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 40 | 346080 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 167 | 920000 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1179540 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 941745 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 31 | 433632 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 98 | 2199427 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 1450080 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 150 | 3213120 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 11 | 357230 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 332880 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 18 | 157080 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 51 | 285120 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 496800 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1690 | 33692042
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8750 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 1864800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 222000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 251160 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 86880 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 181440 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 108 | 2615030
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 50771 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 995000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 729240 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 153 | 3394800 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 154 | 3533500 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1992000 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2420880 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 404016 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7299000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 366 | 8176000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1253 | 28995207
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 906 | 21786182 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 3360 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 190 | 4701600 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 393840 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 699840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 574 | 14094550 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1670 | 41679372
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 450 | 9076364 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 104 | 1258272 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 124 | 2877000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1210 | 25450181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5319210 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 444000 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 276 | 5913000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4830 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2384 | 50342857.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 347424 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 10182 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 197 | 4152545 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 207 | 2188200 | Liquid fuel shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 484682 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 406 | 8942400 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 28152 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 56093 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 73056 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 1015296 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 653376 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 9800 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1455 | 31870182 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 330368 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 666030 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2300 | 50827786
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 45 | 1103999 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 69 | 1014624 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 45029.88 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 946424 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 160814 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 838800 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 164 | 4109690.88
Eastern Grid Total |  |  |  |  | 17418.042 | 8026.5 | 170803876.62
Western Grid Total |  |  |  |  | 11852.195 | 6518 | 146959706.7
National Grid Total |  |  |  |  | 29270.237 | 14544.5 | 317763583.32
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 15-05-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9413.7 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4720.5 | MW
i) Dhaka area |  |  | 5123.1 |  | MW | i) Khulna area |  |  |  | 1882.5 | MW
ii) Chattogram area |  |  | 1471.6 |  | MW | ii) Barishal area |  |  |  | 493.8 | MW
iii) Cumilla area |  |  | 1382 |  | MW | iii) Rajshahi area |  |  |  | 1451.2 | MW
iv) Mymensingh area |  |  | 949 |  | MW | iv) Rangpur area |  |  |  | 893 | MW
v) Sylhet area |  |  | 488 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14134.2 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 7 | 00:00 | 67 | Hasnabad | 89 | 13:00 | 133 | Natore | 158 | 21:00
2 | AKSML | 137.7 | 13:00 | 68 | Hathazari | 93 | 23:00 | 134 | Nawabganj | 65.4 | 22:00
3 | Aftabnagar | 42 | 13:00 | 69 | Hatirjheel | 34 | 15:00 | 135 | Netrakona | 131 | 19:00
4 | Agargaon | 113 | 13:00 | 70 | Ishurdi | 85 | 19:00 | 136 | New | 72 | 00:00
5 | Agrabad | 62 | 20:00 | 71 | Jaldhaka | 73 | 19:30 | 137 | Niamatpur | 71 | 21:00
6 | Amnura | 27 | 23:00 | 72 | Jamalpur | 94 | 11:00 | 138 | Noapara | 46 | 00:00
7 | Ashuganj | 92 | 00:00 | 73 | Jashore | 153 | 19:00 | 139 | PHP | 9 | 03:00
8 | BSRM | 196 | 04:00 | 74 | Jhenaidah | 119 | 19:00 | 140 | Pabna | 100 | 19:00
9 | Bagerhat | 85 | 23:00 | 75 | Joydebpur | 143 | 01:00 | 141 | Palashbari | 108 | 20:00
10 | Bajitpur | 83 | 00:00 | 76 | Joypurhat | 60 | 19:30 | 142 | Panchagarh | 65 | 19:30
11 | Bakerganj | 11.5 | 22:00 | 77 | Juldah | 13 | 00:00 | 143 | Patiya | 13 | 22:00
12 | Bakulia | 90 | 20:00 | 78 | KSRM | 11.5 | 17:00 | 144 | Patuakhali | 74.5 | 22:00
13 | Banani | 37 | 15:00 | 79 | Kabirpur | 215 | 00:00 | 145 | Payra | 36 | 23:00
14 | Bangabhaban | 4 | 00:00 | 80 | Kachua | 90 | 19:30 | 146 | Postogola | 51 | 00:00
15 | Barapukuria | 61 | 19:30 | 81 | Kaliganj | 19 | 00:00 | 147 | Pubail | 27 | 21:00
16 | Barguna | 24 | 22:00 | 82 | Kallyanpur | 120 | 12:00 | 148 | Purbachal | 34 | 15:00
17 | Barishal | 107 | 13:00 | 83 | Kalurghat | 35 | 00:00 | 149 | Purbasadipur | 132 | 19:30
18 | Barishal-230 | 110 | 23:00 | 84 | Kamrangirchar | 75 | 00:00 | 150 | Rahanpur | 35 | 21:00
19 | Baroaulia | 67 | 12:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 29 | 02:00
20 | Baroirhat | 60 | 00:00 | 86 | Kasba | 34 | 21:00 | 152 | Rajbari | 88 | 19:00
21 | Bashundhara | 188 | 12:00 | 87 | Kazla | 105 | 01:00 | 153 | Rajendrapur | 120 | 00:00
22 | BashundharaCement | 7 | 01:00 | 88 | Keranigonj | 80 | 13:00 | 154 | Rajshahi | 118 | 21:00
23 | Beanibazar | 58 | 00:00 | 89 | Khagrachori | 36 | 19:00 | 155 | Rajshahi-230 | 84 | 13:00
24 | Benapole | 65 | 19:00 | 90 | Khulna | 66 | 23:00 | 156 | Ramganj | 116 | 19:00
25 | Bhaluka | 151 | 00:00 | 91 | Khulshi | 187 | 20:00 | 157 | Rampur | 46 | 12:00
26 | Bhandaria | 59 | 23:00 | 92 | Kishoreganj | 114 | 00:00 | 158 | Rangamati | 18 | 20:00
27 | Bhangura | 40 | 19:30 | 93 | Kodda | 295 | 00:00 | 159 | Rangpur | 130 | 19:00
28 | Bheramara(GK) | 68 | 19:00 | 94 | Kulaura | 40 | 19:30 | 160 | Ruppur | 4.2 | 11:00
29 | Bhulta | 215 | 03:00 | 95 | Kurigram | 66 | 19:00 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 74 | 00:00 | 96 | Kushtia | 156 | 20:00 | 162 | Saidpur | 91 | 20:00
31 | Bogura | 147 | 00:00 | 97 | Laksam | 33 | 19:00 | 163 | Santhia | 38 | 19:30
32 | Borhanuddin | 96 | 02:00 | 98 | Lakshmipur | 41 | 19:00 | 164 | Satkhira | 145 | 19:30
33 | Brahmanbaria | 121 | 13:00 | 99 | Lalbag | 72 | 00:00 | 165 | Satmasjid | 95 | 13:00
34 | Cantonment | 112 | 13:00 | 100 | Lalmonirhat | 64 | 19:00 | 166 | Savar | 184 | 00:00
35 | Chandina | 24 | 19:30 | 101 | MI_Cement | 12 | 02:00 | 167 | SevenRings | 17.77 | 01:00
36 | Chandpur | 84 | 19:30 | 102 | Madanganj | 42 | 12:00 | 168 | ShahCement | 42 | 10:00
37 | Chandraghona | 39 | 19:30 | 103 | Madaripur | 121 | 22:00 | 169 | Shahjadpur | 78 | 21:00
38 | Chapai | 67 | 21:00 | 104 | Madartek | 80 | 12:00 | 170 | Shahjibazar | 114 | 00:00
39 | Charsaidpur | 41 | 03:00 | 105 | Madunaghat | 53 | 00:00 | 171 | Shahmirpur | 52 | 00:00
40 | Chauddagram | 65 | 02:00 | 106 | Magura | 72 | 19:00 | 172 | Shariatpur | 96 | 23:00
41 | Chhatak | 30 | 20:00 | 107 | Mahasthangarh | 80 | 20:00 | 173 | Sherpur | 118 | 18:30
42 | Chowmuhani | 155 | 19:00 | 108 | Maijdee | 49 | 20:00 | 174 | Shikalbaha | 29 | 00:00
43 | Chuadanga | 116 | 21:00 | 109 | Manikganj | 139 | 20:00 | 175 | Shitalakhya | 68.6 | 13:00
44 | Coxsbazar | 148 | 20:00 | 110 | Maniknagar | 74 | 13:00 | 176 | Sholosohor | 44 | 11:00
45 | Cumilla(N) | 121 | 16:00 | 111 | Matarbari | 54 | 22:00 | 177 | Shomvuganj | N/A | N/A
46 | Cumilla(S) | 155 | 13:00 | 112 | Matuail | 64 | 00:00 | 178 | Shyampur | 184 | 12:00
47 | Daganbhuiyan | 42 | 19:00 | 113 | Metrorail_Motijheel | 32 | 17:00 | 179 | Siddhirganj | 108 | 12:00
48 | Daudkandi | 130 | 00:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 94 | 00:00
49 | DhakaUniversity | 54 | 12:00 | 115 | Millgate | 81 | 12:00 | 181 | Sonargaon | 140 | 00:00
50 | Dhamrai | 112 | 00:00 | 116 | Mirpur | 148 | 12:00 | 182 | Sreemongol | 60 | 00:00
51 | Dhanmondi | 91 | 17:00 | 117 | Mirsorai | 46 | 13:00 | 183 | Sreepur | 88 | 00:00
52 | Dohazari | 110 | 21:00 | 118 | Mirzapur | 42 | 19:00 | 184 | Srinagar | 51.76 | 13:00
53 | Faridpur | 181 | 22:00 | 119 | Mithapukur | 60 | 19:00 | 185 | Sunamganj | 52 | 00:00
54 | Fatullah | 89 | 00:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 62 | 13:00
55 | Fenchuganj | 39 | 19:00 | 121 | Mogbazar | 90.6 | 15:00 | 187 | Sylhet-132 | 91 | 21:00
56 | Feni | 107 | 13:00 | 122 | Mongla | 32 | 00:00 | 188 | TK | 25 | 20:00
57 | GPH | 2 | 00:00 | 123 | Motijheel | 39 | 13:00 | 189 | Tangail | 172 | 19:30
58 | Ghatail | 84 | 06:00 | 124 | Muktagacha | 31 | 19:00 | 190 | Taraganj | 20 | 19:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 109 | 13:00 | 191 | Tasnim | 30 | 04:00
60 | Ghorashal-230 | 110 | 00:00 | 126 | Muradnagar | 46 | 21:00 | 192 | Thakurgaon | 107 | 19:30
61 | Goalpara | 45 | 23:00 | 127 | Mymensingh | 159 | 13:00 | 193 | Tongi | 152 | 11:00
62 | Gollamari | 108 | 00:00 | 128 | Nabinagar | 79 | 13:00 | 194 | Ullahpara | 38 | 19:30
63 | Gopalganj | 114.2 | 19:30 | 129 | Naogaon | 131 | 19:30 | 195 | Ullon | 46 | 19:00
64 | Gulshan | 94 | 15:00 | 130 | Narail | 63 | 19:00 | 196 | Uttara | 89 | 15:00
65 | Halishahar | 79 | 21:00 | 131 | Narinda | 51 | 13:00 | 197 | UttaraNew | 55 | 13:00
66 | HaripurSBU | 135 | 00:00 | 132 | Narshingdi | 174 | 00:00 | 198 | Zigatola | 82 | 11:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 15-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14797.71 | 117 |  | 14919.71
1:00 | 14331.2 | 104 |  | 14440.2
2:00 | 14038.05 | 107 |  | 14149.87
3:00 | 13670.91 | 96 |  | 13771.23
4:00 | 13318.75 | 69 |  | 13390.86
5:00 | 12691.54 | 42 |  | 12735.43
6:00 | 12174.17 | 41 |  | 12217.02
7:00 | 12168.46 | 68 |  | 12239.46
8:00 | 12015.4 | 81 |  | 12100.4
9:00 | 11860.8 | 85 |  | 11949.8
10:00 | 12101.25 | 69 |  | 12173.25
11:00 | 12295.46 | 54 |  | 12351.46
12:00 | 12921.82 | 58 |  | 12982.82
13:00 | 13914.19 | 26 |  | 13941.19
14:00 | 13210.3 | 0 |  | 13210.3
15:00 | 13094.65 | 0 |  | 13094.65
16:00 | 12511.27 | 0 |  | 12511.27
17:00 | 11909.7 | 0 |  | 11909.7
18:00 | 11725.05 | 0 |  | 11725.05
19:00 | 13632.5 | 17 |  | 13650.5
19:30 | 14237.5 | 46 |  | 14285.5
20:00 | 14142.5 | 51 |  | 14195.5
21:00 | 14544.5 | 53 |  | 14599.89
22:00 | 14504.5 | 53 |  | 14559.5
23:00 | 14231 | 42 |  | 14274.89
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 15-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7621 | 7176.71 | 14797.71 | DAILY GENERATION CURVE
00:30 | 7652 | 6912.455 | 14564.455
01:00 | 7683 | 6648.2 | 14331.2 | 15-05-2026
01:30 | 7624 | 6560.625 | 14184.625
02:00 | 7565 | 6473.05 | 14038.05
02:30 | 7487.5 | 6366.98 | 13854.48
03:00 | 7410 | 6260.91 | 13670.91
03:30 | 7361 | 6133.83 | 13494.83
04:00 | 7312 | 6006.75 | 13318.75
04:30 | 7103.5 | 5901.645 | 13005.145
05:00 | 6895 | 5796.54 | 12691.54
05:30 | 6689.78 | 5743.075 | 12432.855
06:00 | 6484.56 | 5689.61 | 12174.17
06:30 | 6458.08 | 5713.235 | 12171.315
07:00 | 6431.6 | 5736.86 | 12168.46
07:30 | 6395.4 | 5696.53 | 12091.93
08:00 | 6359.2 | 5656.2 | 12015.4
08:30 | 6328.5 | 5609.6 | 11938.1
09:00 | 6297.8 | 5563 | 11860.8
09:30 | 6315.51 | 5665.515 | 11981.025
10:00 | 6333.22 | 5768.03 | 12101.25
10:30 | 6466.19 | 5732.165 | 12198.355
11:00 | 6599.16 | 5696.3 | 12295.46
11:30 | 6714.275 | 5894.365 | 12608.64
12:00 | 6829.39 | 6092.43 | 12921.82
12:30 | 7163.085 | 6254.92 | 13418.005
13:00 | 7496.78 | 6417.41 | 13914.19
13:30 | 7239.68 | 6322.565 | 13562.245
14:00 | 6982.58 | 6227.72 | 13210.3
14:30 | 6955.15 | 6197.325 | 13152.475
15:00 | 6927.72 | 6166.93 | 13094.65
15:30 | 6833.905 | 5969.055 | 12802.96
16:00 | 6740.09 | 5771.18 | 12511.27
16:30 | 6524.99 | 5685.495 | 12210.485
17:00 | 6309.89 | 5599.81 | 11909.7
17:30 | 6378.85 | 5438.525 | 11817.375
18:00 | 6447.81 | 5277.24 | 11725.05
18:30 | 6992.155 | 5686.62 | 12678.775
19:00 | 7536.5 | 6096 | 13632.5
19:30 | 7872.5 | 6365 | 14237.5
20:00 | 7882.5 | 6260 | 14142.5
20:30 | 7954.5 | 6389 | 14343.5 |  | Executive Engineer
21:00 | 8026.5 | 6518 | 14544.5 |  | Network Operation Division
21:30 | 8023 | 6501.5 | 14524.5
22:00 | 8019.5 | 6485 | 14504.5
22:30 | 7864.75 | 6503 | 14367.75
23:00 | 7710 | 6521 | 14231

## En-Curve
QF-LDC-12
Date | 15-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3536 | 1632 | 912 | 0 | 152 | 1450.71 | 74 | 5084 | 0 | 491 | 1445 | 0 | 0 | 21 | 117 | DAILY ENERGY CURVE
00:30 | 3558 | 1651.5 | 912.5 | 0 | 148 | 1449.955 | 73 | 4770.5 | 0 | 504 | 1479.5 | 0 | 0 | 17.5 | 110.5 | 15-05-2026
01:00 | 3580 | 1671 | 913 | 0 | 144 | 1449.2 | 72 | 4457 | 0 | 517 | 1514 | 0 | 0 | 14 | 104
01:30 | 3544.5 | 1623.5 | 901.5 | 0 | 141 | 1451.625 | 72 | 4359.5 | 0 | 513 | 1569 | 0 | 0 | 9 | 105.5 | Energy Generated | 317.7636 |  | MKWHr
02:00 | 3509 | 1576 | 890 | 0 | 138 | 1454.05 | 72 | 4262 | 0 | 509 | 1624 | 0 | 0 | 4 | 107 | Energy not Served | 1.233 |  | MKWHr
02:30 | 3425.5 | 1508 | 890 | 0 | 139 | 1452.98 | 73 | 4197.5 | 0 | 509 | 1653 | 0 | 0 | 6.5 | 101.5 | Total Energy Requirement | 318.9966 |  | MKWHr
03:00 | 3342 | 1440 | 890 | 0 | 140 | 1451.91 | 74 | 4133 | 0 | 509 | 1682 | 0 | 0 | 9 | 96
03:30 | 3288.5 | 1436 | 890 | 0 | 136 | 1453.83 | 75 | 4061 | 0 | 485.5 | 1658 | 0 | 0 | 11 | 82.5
04:00 | 3235 | 1432 | 890 | 0 | 132 | 1455.75 | 76 | 3989 | 0 | 462 | 1634 | 0 | 0 | 13 | 69
04:30 | 3265.5 | 1457 | 890 | 0 | 130 | 1456.145 | 77 | 3983 | 0 | 391.5 | 1341 | 0 | 0 | 14 | 55.5
05:00 | 3296 | 1482 | 890 | 0 | 128 | 1456.54 | 78 | 3977 | 0 | 321 | 1048 | 0 | 0 | 15 | 42
05:30 | 3301 | 1473.5 | 890 | 0 | 125 | 1455.475 | 78.5 | 4077 | 16.88 | 245 | 757.5 | 0 | 0 | 13 | 41.5
06:00 | 3306 | 1465 | 890 | 0 | 122 | 1454.41 | 79 | 4177 | 33.76 | 169 | 467 | 0 | 0 | 11 | 41
06:30 | 3332 | 1447.5 | 890 | 0 | 123 | 1451.63 | 79.5 | 4164.5 | 77.185 | 169 | 429 | 0 | 0 | 8 | 54.5
07:00 | 3358 | 1430 | 890 | 0 | 124 | 1448.85 | 80 | 4152 | 120.61 | 169 | 391 | 0 | 0 | 5 | 68
07:30 | 3394.5 | 1426.5 | 894 | 0 | 121 | 1387.85 | 80 | 4108 | 175.58 | 169 | 332 | 0 | 0 | 3.5 | 74.5
08:00 | 3431 | 1423 | 898 | 0 | 118 | 1326.85 | 80 | 4064 | 230.55 | 169 | 273 | 0 | 0 | 2 | 81
08:30 | 3352 | 1449.5 | 897.5 | 0 | 117 | 1310.925 | 80 | 3995 | 294.675 | 164 | 276 | 0 | 0 | 1.5 | 83
09:00 | 3273 | 1476 | 897 | 0 | 116 | 1295 | 80 | 3926 | 358.8 | 159 | 279 | 0 | 0 | 1 | 85
09:30 | 3336.5 | 1512.5 | 897.5 | 0 | 122 | 1277 | 80 | 3839.5 | 487.525 | 160.5 | 262.5 | 4 | 0 | 1.5 | 77
10:00 | 3400 | 1549 | 898 | 0 | 128 | 1259 | 80 | 3753 | 616.25 | 162 | 246 | 8 | 0 | 2 | 69
10:30 | 3463.5 | 1608 | 897.5 | 0 | 133 | 1270.5 | 79 | 3775 | 565.355 | 153 | 245.5 | 4 | 0 | 4 | 61.5
11:00 | 3527 | 1667 | 897 | 0 | 138 | 1282 | 78 | 3797 | 514.46 | 144 | 245 | 0 | 0 | 6 | 54
11:30 | 3505 | 1605 | 901.5 | 0 | 142 | 1290 | 78 | 3876.5 | 570.64 | 190.5 | 442.5 | 0 | 0 | 7 | 56
12:00 | 3483 | 1543 | 906 | 0 | 146 | 1298 | 78 | 3956 | 626.82 | 237 | 640 | 0 | 0 | 8 | 58
12:30 | 3520 | 1603 | 906 | 0 | 151 | 1319.5 | 74 | 4038 | 587.505 | 288 | 922.5 | 0 | 0 | 8.5 | 42
13:00 | 3557 | 1663 | 906 | 0 | 156 | 1341 | 70 | 4120 | 548.19 | 339 | 1205 | 0 | 0 | 9 | 26
13:30 | 3595 | 1665 | 906 | 0 | 154 | 1304 | 70 | 4093 | 487.745 | 303.5 | 974.5 | 0 | 0 | 9.5 | 13
14:00 | 3633 | 1667 | 906 | 0 | 152 | 1267 | 70 | 4066 | 427.3 | 268 | 744 | 0 | 0 | 10 | 0
14:30 | 3620 | 1673 | 905.5 | 0 | 148 | 1272 | 70 | 4093.5 | 405.225 | 223.5 | 729.75 | 0 | 0 | 12 | 0
15:00 | 3607 | 1679 | 905 | 0 | 144 | 1277 | 70 | 4121 | 383.15 | 179 | 715.5 | 0 | 0 | 14 | 0
15:30 | 3628.5 | 1655 | 905 | 0 | 144 | 1240.5 | 71 | 4148.5 | 308.71 | 144 | 547.75 | 0 | 0 | 10 | 0
16:00 | 3650 | 1631 | 905 | 0 | 144 | 1204 | 72 | 4176 | 234.27 | 109 | 380 | 0 | 0 | 6 | 0
16:30 | 3624 | 1556 | 905 | 0 | 143 | 1177 | 73.5 | 4114 | 167.485 | 109 | 337.5 | 0 | 0 | 4 | 0
17:00 | 3598 | 1481 | 905 | 0 | 142 | 1150 | 75 | 4052 | 100.7 | 109 | 295 | 0 | 0 | 2 | 0
17:30 | 3625.5 | 1521.5 | 905.5 | 0 | 129 | 1101.5 | 75 | 3971 | 59.875 | 107 | 320.5 | 0 | 0 | 1 | 0
18:00 | 3653 | 1562 | 906 | 0 | 116 | 1053 | 75 | 3890 | 19.05 | 105 | 346 | 0 | 0 | 0 | 0
18:30 | 3673 | 1630.5 | 906 | 0 | 104 | 1205.5 | 77 | 4104.5 | 9.525 | 271.5 | 696.75 | 0 | 0 | 0.5 | 8.5
19:00 | 3693 | 1699 | 906 | 0 | 92 | 1358 | 79 | 4319 | 0 | 438 | 1047.5 | 0 | 0 | 1 | 17
19:30 | 3679 | 1637 | 906 | 0 | 120 | 1442 | 80 | 4528 | 0 | 481 | 1364.5 | 0 | 0 | 0 | 46
20:00 | 3691 | 1742 | 906 | 0 | 138 | 1456 | 80 | 4611 | 0 | 280 | 1238.5 | 0 | 0 | 0 | 51
20:30 | 3743 | 1812 | 906 | 0 | 144 | 1455.5 | 80 | 4719 | 0 | 239 | 1245 | 0 | 0 | 0 | 52
21:00 | 3795 | 1882 | 906 | 0 | 150 | 1455 | 80 | 4827 | 0 | 198 | 1251.5 | 0 | 0 | 0 | 53
21:30 | 3810.5 | 1858 | 905.5 | 0 | 151 | 1456.5 | 80 | 4818 | 0 | 198.5 | 1246.5 | 0 | 0 | 0 | 53
22:00 | 3826 | 1834 | 905 | 0 | 152 | 1458 | 80 | 4809 | 0 | 199 | 1241.5 | 0 | 0 | 0 | 53
22:30 | 3776.5 | 1792.5 | 905 | 0 | 150 | 1455.5 | 80 | 4802 | 0 | 216.5 | 1183.75 | 0 | 0 | 6 | 47.5
23:00 | 3727 | 1751 | 905 | 0 | 148 | 1453 | 80 | 4795 | 0 | 234 | 1126 | 0 | 0 | 12 | 42
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 15-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 132 | 3 | 588 | 164 | 1594 | 426 | Ishurdi-Ghorashal Ckt-1 | Export | 3109600
1:00 | 113 | -3 | 548 | 140 | 1428 | 370
2:00 | 115 | 0 | 536 | 124 | 1342 | 202 |  | Import | 0
3:00 | 120 | 2 | 532 | 114 | 1254 | 410
4:00 | 122 | 4 | 516 | 100 | 1228 | 412 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 121 | 5 | 500 | 98 | 1406 | 402
6:00 | 121 | 4 | 474 | 100 | 1392 | 392 |  | Import | 0
7:00 | 128 | -5 | 494 | 100 | 1300 | 368
8:00 | 139 | 0 | 490 | 108 | 1230 | 422 | Sirajganj-Sreepur Ckt-1 | Export | 3026000
9:00 | 177 | 19 | 564 | 140 | 1272 | 468
10:00 | 194 | 22 | 612 | 144 | 1330 | 506 |  | Import | 0
11:00 | 189 | 25 | 604 | 148 | 1386 | 522
12:00 | 182 | 21 | 580 | 144 | 1358 | 450 | Sirajganj-Sreepur Ckt-2 | Export | 3048000
13:00 | 157 | 10 | 584 | 148 | 1370 | 396
14:00 | 158 | 6 | 550 | 116 | 1314 | 400 |  | Import | 0
15:00 | 159 | 8 | 520 | 94 | 1392 | 440
16:00 | 139 | 7 | 420 | 72 | 1290 | 474 | Gopalganj-Aminbazar Ckt-1 | Export | 15320000
17:00 | 136 | 5 | 470 | 110 | 1230 | 460
18:00 | 111 | -2 | 400 | 82 | 976 | 428 |  | Import | 0
18:30 | 113 | -2 | 432 | 70 | 978 | 374
19:00 | 92 | -15 | 430 | 68 | 1042 | 310 | Gopalganj-Aminbazar Ckt-2 | Export | 15350000
19:30 | 88 | -18 | 412 | 76 | 1036 | 300
20:00 | 68 | -26 | 378 | 56 | 1008 | 286 |  | Import | 0
21:00 | 76 | -27 | 424 | 72 | 1112 | 272
22:00 | 82 | -24 | 458 | 90 | 1120 | 304 |  | Total Export | 39853600
23:00 | 97 | -10 | 536 | 140 | 1300 | 340 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 15-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 386 | 04:00 | 373 | 00:00 | Madunaghat | 397 | 04:00 | 389 | 00:00
Amtali | 411 | 04:00 | 404 | 00:00 | Meghnaghat | 390 | 18:00 | 377 | 00:00
Ashuganj | 407 | 8:00 | 388 | 13:00 | Payra | 413 | 04:00 | 406 | 21:00
Bhulta | 400 | 07:00 | 383 | 11:00 | Rahanpur | 405 | 04:00 | 390 | 21:00
Bibiana | 396 | 04:00 | 389 | 00:00 | Rampal | 400 | 18:00 | 384 | 22:00
BIPTC | 398 | 08:00 | 388 | 16:00
Bogura | 394 | 04:00 | 376 | 21:00
Gopalganj | 398 | 04:00 | 383 | 22:00
Kaliakoir | 380 | 04:00 | 368 | 00:00
Korerhat | 398 | 04:00 | 387 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 04:00 | 221 | 00:00 | Jhenaidah | 228 | 09:00 | 211 | 21:00
AKSML | 231.3 | 04:00 | 223 | 00:00 | Kachua | 227 | 18:00 | 217 | 23:00
Aminbazar | 228 | 04:00 | 221 | 00:00 | Kaliakoir | 233 | 04:00 | 225 | 00:00
Ashuganj | 232 | 18:00 | 222 | 00:00 | Keranigonj | 227 | 04:00 | 219 | 00:00
Ashuganj-400 | 232 | 18:00 | 222 | 0:00 | Khulna(S) | 228 | 09:00 | 213 | 22:00
Baghabari | 234 | 17:00 | 225 | 22:00 | Korerhat | 227 | 18:00 | 219 | 23:00
Barapukuria | 224 | 17:00 | 210 | 20:00 | Madunaghat | 230 | 04:00 | 225 | 00:00
Barapukuria-230 | 224 | 17:00 | 210 | 20:00 | Madunaghat-400 | 231 | 03:00 | 226 | 00:00
Barishal | 227 | 04:00 | 220 | 22:00 | Maniknagar | 224 | 04:00 | 217 | 00:00
Bheramara | 234 | 04:00 | 221 | 21:00 | Meghnaghat | 235 | 19:00 | 224 | 00:00
Bhulta | 228 | 08:00 | 218 | 00:00 | Meghnaghat-400 | 229 | 18:30 | 219 | 00:00
Bibiana | 236 | 18:30 | 229 | 00:00 | Mirsorai | 234 | 04:00 | 223 | 22:00
BIPTC | 236 | 04:00 | 220 | 22:00 | Naogaon | 218 | 04:00 | 204 | 21:00
Bogura | 239 | 04:00 | 226 | 21:00 | Purbasadipur | 229 | 04:00 | 207 | 20:00
Bogura-400 | 239 | 04:00 | 226 | 21:00 | Rajshahi | 233 | 04:00 | 218 | 22:00
Borhanuddin | 231 | 05:00 | 226 | 23:00 | Rampal | 228 | 09:00 | 214 | 22:00
BSRM | 226 | 04:00 | 219 | 23:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 230 | 22:00 | 220 | 00:00 | Rampura | 227 | 07:00 | 214 | 13:00
Cumilla(N) | 228 | 18:00 | 218 | 00:00 | Shikalbaha | 227 | 02:00 | 224 | 00:00
Faridpur | 222 | 04:00 | 211 | 22:00 | Shyampur | 227 | 18:00 | 219 | 00:00
Fenchuganj | 237 | 17:00 | 231 | 00:00 | Siddhirganj | 226 | 05:00 | 218 | 00:00
Feni | 227 | 18:00 | 218 | 23:00 | Sirajgonj | 240 | 18:00 | 234 | 22:00
Ghorashal | 230 | 18:30 | 220 | 00:00 | Sreepur | 227 | 15:00 | 218 | 00:00
Ghorashal-230 | 226 | 18:00 | 216 | 11:00 | Tongi | 227 | 19:30 | 217 | 00:00
Gopalganj | 222 | 04:00 | 213 | 22:00
GPH | 228 | 03:00 | 220 | 19:00
Haripur | 225 | 04:00 | 218 | 00:00
Hasnabad | 226 | 18:00 | 219 | 00:00
Hathazari | 229 | 18:00 | 224 | 00:00
Ishurdi | 239 | 09:00 | 223 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 07:00 | 131 | 11:00 | Madunaghat | 134 | 04:00 | 130 | 00:00
Agargaon | 134 | 04:00 | 128 | 00:00 | Magura | 133 | 09:00 | 121 | 22:00
Agrabad | 132 | 02:00 | 129 | 00:00 | Mahasthangarh | 136 | 03:00 | 126 | 20:00
AKS | 130 | 03:00 | 128 | 00:00 | Maijdee | 126 | 04:00 | 121 | 23:00
Aminbazar | 130 | 05:00 | 125 | 00:00 | Manikganj | 132 | 05:00 | 125 | 21:00
Amnura | 134 | 05:00 | 126 | 21:00 | Maniknagar | 132 | 04:00 | 126 | 00:00
Ashuganj | 141 | 17:00 | 126 | 21:00 | Matarbari | 119 | 05:00 | 109 | 22:00
Ashuganj-230 | 141 | 17:00 | 132 | 00:00 | Matuail | 131.5 | 18:00 | 126 | 00:00
Bagerhat | 129 | 09:00 | 113 | 22:00 | Metrorail_Motijheel | 132 | 04:00 | 126 | 00:00
Bajitpur | 133 | 16:00 | 125 | 00:00 | Metrorail_Uttara | 132 | 03:00 | 124 | 11:00
Bakerganj | 133 | 04:00 | 126 | 22:00 | Millgate | 133 | 03:00 | 125 | 11:00
Bakulia | 134 | 08:00 | 130 | 23:00 | Mirpur | 130 | 05:00 | 123 | 11:00
Banani | 139 | 07:00 | 130 | 12:00 | Mirzapur | 130 | 03:00 | 124 | 22:00
Bangabhaban | 132 | 06:00 | 126 | 00:00 | Mithapukur | 135 | 04:00 | 125 | 20:00
Barapukuria | 132 | 14:00 | 123 | 20:00 | MI_Cement | 130 | 18:00 | 122.4 | 13:00
Barguna | 133 | 18:00 | 126 | 22:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 04:00 | 127 | 22:00 | Mogbazar | 139 | 08:00 | 131 | 12:00
Barishal-230 | 134 | 04:00 | 127 | 22:00 | Mongla | 129 | 09:00 | 115 | 22:00
Baroaulia | 133 | 18:00 | 129 | 00:00 | Motijheel | 132 | 06:00 | 126 | 00:00
Baroirhat | 130 | 03:00 | 125 | 23:00 | Muktagacha | 128 | 14:00 | 115 | 00:00
Bashundhara | 138 | 07:00 | 126 | 11:00 | Munshiganj | 130 | 18:00 | 123 | 00:00
BashundharaCement | 131 | 14:00 | 124 | 00:00 | Muradnagar | 133 | 18:00 | 120 | 13:00
Beanibazar | 131 | 06:00 | 125 | 00:00 | Mymensingh | 129 | 15:00 | 113 | 23:00
Benapole | 129 | 09:00 | 115 | 21:00 | Nabinagar | 133 | 03:00 | 126 | 00:00
Bhaluka | 131 | 15:00 | 124 | 00:00 | Naogaon | 137 | 04:00 | 123 | 21:00
Bhandaria | 129 | 18:00 | 120 | 22:00 | Narail | 134 | 09:00 | 120 | 22:00
Bhangura | 135 | 16:00 | 129 | 21:00 | Narinda | 132 | 4:00 | 126 | 0:00
Bheramara | 136 | 04:00 | 130 | 21:00 | Narshingdi | 137 | 17:00 | 116 | 13:00
Bheramara(GK) | 137 | 09:00 | 130 | 21:00 | Natore | 135 | 04:00 | 125 | 21:00
Bhulta | 130 | 17:00 | 122 | 00:00 | Nawabganj | 133 | 04:00 | 128 | 00:00
Bog-Sherpur | 138 | 04:00 | 128 | 21:00 | Netrakona | 123 | 14:00 | 115 | 00:00
Bogura | 136 | 02:00 | 130 | 20:00 | New | 133 | 18:00 | 127 | 11:00
Bogura-230 | 140 | 04:00 | 130 | 21:00 | Niamatpur | 132 | 17:00 | 125 | 21:00
Brahmanbaria | 137 | 17:00 | 121 | 13:00 | Noapara | 132 | 09:00 | 119 | 22:00
Cantonment | 133 | 06:00 | 127 | 11:00 | Pabna | 134 | 04:00 | 127 | 22:00
Chandina | 133 | 18:00 | 126 | 00:00 | Palashbari | 130 | 04:00 | 122 | 20:00
Chandpur | 130 | 03:00 | 121 | 23:00 | Panchagarh | 141 | 04:00 | 128 | 20:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 134 | 05:00 | 130 | 00:00 | Patiya | 133 | 18:00 | 128 | 03:00
Chapai | 133 | 03:00 | 127 | 23:00 | Patuakhali | 132 | 18:00 | 126 | 22:00
Charsaidpur | 130 | 08:00 | 125 | 00:00 | Payra | 135 | 04:00 | 132 | 21:00
Chauddagram | 131 | 18:00 | 124 | 23:00 | PHP | 131 | 04:00 | 125 | 00:00
Chhatak | 129 | 05:00 | 122 | 00:00 | Postogola | 131 | 04:00 | 126 | 00:00
Chowmuhani | 126 | 06:00 | 122 | 00:00 | Pubail | 135 | 18:30 | 127 | 00:00
Chuadanga | 131 | 11:00 | 117 | 21:00 | Purbachal | 138 | 07:00 | 125 | 11:00
Coxsbazar | 122 | 04:00 | 112 | 19:30 | Purbasadipur | 136 | 04:00 | 122 | 20:00
Cumilla(N) | 133 | 18:00 | 126 | 00:00 | Rahanpur | 134 | 17:00 | 128 | 21:00
Cumilla(S) | 133 | 18:00 | 123 | 13:00 | Rahanpur-400 | 134 | 04:00 | 129 | 22:00
Daganbhuiyan | 129 | 18:00 | 123 | 23:00 | Rahim | 131 | 18:00 | 126 | 00:00
Daudkandi | 131 | 18:00 | 118 | 11:00 | Rajbari | 126 | 04:00 | 119 | 00:00
DhakaUniversity | 139 | 06:00 | 130 | 12:00 | Rajendrapur | 133 | 16:00 | 123 | 00:00
Dhamrai | 134 | 04:00 | 128 | 00:00 | Rajshahi | 132 | 01:00 | 123 | 21:00
Dhanmondi | 138 | 07:00 | 129.6 | 12:00 | Rajshahi-230 | 134 | 04:00 | 125 | 21:00
Dohazari | 129 | 08:00 | 124 | 13:00 | Ramganj | 125 | 12:00 | 118 | 23:00
Faridpur | 129 | 04:00 | 123 | 22:00 | Rampur | 132 | 01:00 | 129 | 00:00
Fatullah | 136 | 18:00 | 124 | 00:00 | Rampura | 138 | 07:00 | 129 | 13:00
Fenchuganj | 136 | 17:00 | 132 | 00:00 | Rangamati | 133 | 18:00 | 129 | 00:00
Feni | 128 | 03:00 | 124 | 15:00 | Rangpur | 133 | 03:00 | 125 | 20:00
Feni-230 | 130 | 04:00 | 125 | 00:00 | Ruppur | 136 | 04:00 | 130 | 21:00
Ghatail | 128 | 15:00 | 116 | 00:00 | Saidpur | 131 | 14:00 | 122 | 20:00
Ghorashal | 136 | 08:00 | 130 | 00:00 | Santhia | 135 | 17:00 | 129 | 21:00
Goalpara | 133 | 09:00 | 121 | 21:00 | Satkhira | 128 | 09:00 | 113 | 21:00
Gollamari | 133 | 06:00 | 121 | 22:00 | Satmasjid | 133 | 04:00 | 126 | 13:00
Gopalganj | 132 | 04:00 | 121 | 22:00 | Savar | 127 | 17:00 | 121 | 11:00
Gopalganj-400 | 132 | 04:00 | 126 | 22:00 | SevenRings | 136 | 08:00 | 130 | 13:00
Gulshan | 138 | 06:00 | 130 | 12:00 | ShahCement | 130 | 08:00 | 125 | 00:00
Halishahar | 134 | 18:00 | 130 | 00:00 | Shahjadpur | 136 | 17:00 | 133 | 00:00
Haripur | 132 | 18:00 | 126 | 00:00 | Shahjibazar | 137 | 17:00 | 122 | 00:00
HaripurSBU | 132 | 18:00 | 126 | 00:00 | Shahmirpur | 134 | 03:00 | 131 | 00:00
Hasnabad | 130 | 18:30 | 126 | 00:00 | Shariatpur | 131 | 05:00 | 123 | 21:00
Hathazari | 135 | 18:00 | 130 | 01:00 | Sherpur | 125 | 15:00 | 112 | 00:00
Hatirjheel | 138 | 07:00 | 129 | 13:00 | Shikalbaha | 124 | 05:00 | 120 | 00:00
Ishurdi | 138 | 09:00 | 130 | 22:00 | Shikalbaha-230 | 135 | 17:00 | 132 | 00:00
Jaldhaka | 131 | 23:00 | 120 | 20:00 | Shitalakhya | 130 | 18:00 | 122.4 | 13:00
Jamalpur | 129 | 15:00 | 115 | 23:00 | Sholosohor | 133 | 03:00 | 130 | 00:00
Jashore | 130 | 09:00 | 117 | 21:00 | Shomvuganj | 130 | 15:00 | 124 | 13:00
Jhenaidah | 134 | 08:00 | 123 | 21:00 | Shyampur | 136 | 18:00 | 128 | 11:00
Jhenaidah-230 | 135 | 09:00 | 123 | 21:00 | Shyampur-230 | 136 | 18:00 | 130 | 11:00
Joydebpur | 133 | 12:00 | 126 | 13:00 | Siddhirganj | 131 | 05:00 | 126 | 00:00
Joypurhat | 133 | 02:00 | 124 | 20:00 | Sirajganj | 133 | 17:00 | 128 | 21:00
Juldah | 134 | 18:00 | 130 | 00:00 | Sonargaon | 130 | 18:00 | 124 | 00:00
Kabirpur | 135 | 13:00 | 123 | 11:00 | Sreemongol | 135 | 17:00 | 124 | 00:00
Kachua | 129 | 03:00 | 123 | 23:00 | Sreepur | 133 | 15:00 | 126 | 00:00
Kaliakoir | 138 | 04:00 | 131 | 20:00 | Srinagar | 133 | 18:00 | 128 | 00:00
Kaliganj | 133 | 05:00 | 122 | 21:00 | SSM | 138 | 01:00 | 133 | 10:00
Kallyanpur | 129 | 18:00 | 124 | 11:00 | Sunamganj | 128 | 17:00 | 119 | 00:00
Kalurghat | 134 | 18:00 | 131 | 00:00 | Sylhet | 132 | 06:00 | 127 | 00:00
Kamrangirchar | 133 | 05:00 | 122 | 00:00 | Sylhet-132 | 131 | 17:00 | 126 | 00:00
Kaptai | 136 | 6:00 | 133 | 1:00 | Tangail | 127 | 18:30 | 119 | 21:00
Kasba | 133 | 18:00 | 120 | 13:00 | Taraganj | 132 | 03:00 | 121 | 20:00
Kazla | 132 | 05:00 | 127 | 00:00 | Tasnim | 130 | 18:00 | 124 | 00:00
Keranigonj | 134 | 05:00 | 129 | 00:00 | Thakurgaon | 140 | 04:00 | 125 | 20:00
Khagrachori | 132 | 05:00 | 127 | 19:00 | TK | 135 | 18:00 | 130 | 00:00
Khulna | 132 | 09:00 | 119 | 22:00 | Tongi | 134 | 18:30 | 128 | 00:00
Khulna(S) | 133 | 09:00 | 122 | 21:00 | Ullahpara | 134 | 17:00 | 128 | 21:00
Khulshi | 132 | 18:00 | 129 | 00:00 | Ullon | 137 | 05:00 | 130 | 12:00
Kishoreganj | 132 | 18:30 | 122 | 00:00 | Uttara | 132 | 03:00 | 124 | 11:00
Kodda | 136 | 03:00 | 125 | 15:00 | UttaraNew | 132 | 03:00 | 124 | 11:00
Korerhat | 133 | 04:00 | 128 | 23:00 | Zigatola | 134 | 04:00 | 128 | 11:00
KSRM | 132 | 01:00 | 129 | 02:00
Kulaura | 135 | 06:00 | 130 | 01:00
Kurigram | 130 | 17:00 | 120 | 21:00
Kushtia | 136 | 04:00 | 126 | 21:00
Laksam | 129 | 18:00 | 122 | 23:00
Lakshmipur | 126 | 18:00 | 120 | 23:00
Lalbag | 132 | 08:00 | 128 | 00:00
Lalmonirhat | 130 | 00:00 | 119 | 18:30
Madanganj | 131 | 14:00 | 124 | 00:00
Madaripur | 131 | 06:00 | 126 | 21:00
Madartek | 137 | 08:00 | 129 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division