## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 17-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-05-2026 | during | 17-05-2026 | during | 17-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 402 | 365 | 412 | 412 | 392 | 392 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 42 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 304 | 304 | 335 | 335 | 315 | 315 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 0 | 0 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 45 | 129 | 149.36 | 149.36 | 46 | 46 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19 | 19 | 33 | 33 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 14 | 14 | 14 | 14 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 48 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 245 | 295 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 118 | 133 | 149 | 149 | 133 | 133 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 56 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 54 | 162 | 162 | 18 | 36 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 15 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 525 | 490 | 584 | 584 | 500 | 500 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 277 | 326 | 718 | 718 | 335 | 335 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 38 | 142 | 160 | 160 | 17 | 70 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2247 | 2601 | 5946.22 | 5914.22 | 2341.19 | 2467.19
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 0 | 17 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 45 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 76 | 60 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 213 | 217 | 215 | 215 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 50 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 30 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 49 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 2 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 18 | 57 | 108 | 108 | 18 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.97 | 0 | 4.87 | 0 | 4.87 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 16 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 144 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1224 | 1224 | 1224 | 1204 | 1204 | U2 on AGC
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 10 | 3 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 720 | 1125 | 1150 | 1150 | 1010 | 1010 | AGC
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2228.97 | 3030 | 3977.73 | 4035.86 | 3092.23 | 3187.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 191 | 192 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 0 | 0 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 342 | 345 | 342.01 | 342.01 | 342.01 | 342.01 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 370 | 393 | 393 | 393 | 270 | 270 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 38 | 35 | 41.65 | 41.65 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 5 | 5 | 52.82 | 52.82 | 30 | 30 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 63 | 73 | 195 | 195 | 100 | 100 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 33 | 150 | 150 | 150 | 25 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 23 | 32 | 32 | 40 | 40 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 143 | 147 | 163 | 163 | 140 | 140 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 29 | 193 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 168 | 180 | 84 | 80 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 8 | 52 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 110 | 114 | 114 | 17 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 17 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 43 | 108 | 115 | 115 | 0 | 50 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 56 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1560 | 2041 | 2759.44 | 2690.44 | 2012.27 | 2272.27
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-05-2026 | during | 17-05-2026 | during | 17-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.95 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 76 | 87 | 90 | 90 | 10 | 10 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 17 | 20 | 10 | 10 | 10 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 36.88 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 133.83 | 121 | 391.1 | 334 | 121.6 | 49
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 148 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 154 | 153 | 150 | 150 | 100 | 100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 83 | 85 | 85 | 86 | 86 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 102 | 102 | 102 | 102 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 357 | 232 | 380 | 380 | 340 | 340 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1246 | 1142 | 1368 | 1368 | 1199 | 1199
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 923 | 895 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 30 | 36 | 36 | 36 | 36 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 180 | 149 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 105 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 72 | 0 | 100 | 0 | 100 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 553 | 588 | 617.1 | 617.1 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1728 | 1767 | 2983.1 | 2883.1 | 2667.1 | 2567.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 330 | 590 | 630 | 630 | 602 | 602 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 102 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 100 | 118 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 880 | 1200 | 1244 | 1244 | 1184 | 1184 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 72 | 150 | 150 | 17 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 150 | 307 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.73 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1680.73 | 2609 | 2792 | 2791 | 2551 | 2587
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 26.09 | 0 | 48 | 0 | 48 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 160 | 183 | 214 | 214 | 180 | 180 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 160 | 183 | 220 | 220 | 0 | 0 | Liquid fuel shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 180 | 180 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 396 | 390 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 26 | 26 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 0.03 | 0.03 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 85 | 85 | 85 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 1 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1324 | 1470 | 1435.88 | 1435.88 | 1356 | 1356 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 52.29 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 94 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2213.38 | 2677.2 | 3211.72 | 2996.87 | 2626.29 | 2496.44
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 46 | 48 | 48 | 50 | 50 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 98 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 0 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 0 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 145 | 0 | 90.26 | 0 | 90.26 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 296 | 424 | 422.26 | 296 | 289.26 | 278
System Total |  |  |  |  | 28823.2 | 29270.237 | 13333.91 | 16412.2 | 23851.57 | 23309.49 | 16899.94 | 17103.36
Forecast Scenario (17-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15400 |  | 0 |  | 15400
|  |  |  | 1:00 | 14550 |  | 0 |  | 14550
|  |  |  | 2:00 | 13970 |  | 0 |  | 13970
|  |  |  | 3:00 | 13520 |  | 0 |  | 13520
|  |  |  | 4:00 | 12980 |  | 0 |  | 12980
|  |  |  | 5:00 | 12800 |  | 0 |  | 12800
|  |  |  | 6:00 | 12820 |  | 0 |  | 12820
|  |  |  | 7:00 | 13210 |  | 0 |  | 13210
|  |  |  | 8:00 | 13380 |  | 0 |  | 13380
|  |  |  | 9:00 | 13690 |  | 0 |  | 13690
|  |  |  | 10:00 | 14040 |  | 0 |  | 14040
|  |  |  | 11:00 | 14160 |  | 0 |  | 14160
|  |  |  | 12:00 | 14500 |  | 0 |  | 14500
|  |  |  | 13:00 | 14990 |  | 0 |  | 14990
|  |  |  | 14:00 | 15230 |  | 0 |  | 15230
|  |  |  | 15:00 | 15550 |  | 0 |  | 15550
|  |  |  | 16:00 | 15320 |  | 0 |  | 15320
|  |  |  | 17:00 | 15290 |  | 0 |  | 15290
|  |  |  | 18:00 | 15520 |  | 0 |  | 15520
|  |  |  | 18:30 | 15700 |  | 286.5 |  | 16000
|  |  |  | 19:00 | 16200 |  | 362.9 |  | 16580
|  |  |  | 19:30 | 16700 |  | 191 |  | 16900
|  |  |  | 20:00 | 16600 |  | 248.3 |  | 16860
|  |  |  | 21:00 | 16500 |  | 372.45 |  | 16890
|  |  |  | 22:00 | 16400 |  | 296.05 |  | 16710
|  |  |  | 23:00 | 16100 |  | 392.505 |  | 16511
Probable Maximum Temperature: |  |  | 35.5°C
Probable Maximum Demand at Day Peak: |  |  | 14500.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 191
Probable Maximum Demand at Evening Peak: |  |  | 16900.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16700.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 352.72 MKWHr. |  | 40 | 30 | 30 | 25 | 0 | 30 | 0 | 21 | 15 | 191
*** This report is generated digitally from Operation Information System (OIS) at 10:40 hrs on 17-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 16-05-2026 | [28 empty] | Date: | 16-05-2026 | [28 empty] | Date: | 16-05-2026 | [28 empty] | Date: | 16-05-2026 | [28 empty] | Date: | 16-05-2026 | [17 empty] | Date: | 16-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 267 | 0 | 0 | 133 | 15 | 225 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 51 | 18 | 7 | 0 | 520 | 0 | 0 | 39 | 0 | 21 | 50 | 0 | 0 | 0 | 0 | 0 | 76 | 50 | 42 | 935 | 0 | 0 | 26 | 0 | 50 | 220 | 0 | 0 | 0 | 1168 | 0 | 25 | 65 | 393 | 0 | 345 | 51 | 6 | 200 | 43 | 35 | 30 | 32 | 0 | 17 | 0 | 140 | 0 | 0 | 32 | 305 | 0 | 372 | 42 | 30 | 157 | 0 | 17 | 0 | 85 | 0 | 152 | 0 | 101 | 0 | 9 | 77 | 0 | 0 | 0 | 12 | 7565 | 905 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 569 | 0 | 0 | 0 | 1456 | 0 | 0 | 0 | 70 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 198 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 45 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 275 | 124 | 220 | 0 | 330 | 1170 | 35 | 6533 | 14098 | 76.67
01:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 266 | 0 | 0 | 133 | 15 | 225 | 55 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 34 | 20 | 14 | 0 | 490 | 0 | 0 | 20 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 0 | 74 | 34 | 42 | 785 | 0 | 0 | 26 | 0 | 34 | 220 | 0 | 0 | 0 | 1160 | 0 | 26 | 65 | 393 | 0 | 345 | 51 | 18 | 195 | 43 | 0 | 30 | 51 | 0 | 17 | 0 | 142 | 0 | 0 | 32 | 300 | 0 | 374 | 42 | 30 | 151 | 0 | 17 | 0 | 85 | 0 | 152 | 0 | 101 | 0 | 9 | 77 | 0 | 0 | 0 | 0 | 7254 | 923 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 582 | 0 | 0 | 0 | 1451 | 0 | 0 | 0 | 35 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 198 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 47 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 276 | 124 | 220 | 0 | 330 | 1150 | 35 | 6396 | 13650 | 76.65
02:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 247 | 0 | 0 | 133 | 0 | 225 | 30 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 34 | 20 | 14 | 0 | 470 | 0 | 0 | 20 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 32 | 42 | 720 | 0 | 0 | 26 | 0 | 31 | 220 | 0 | 0 | 0 | 1163 | 0 | 26 | 65 | 393 | 0 | 345 | 51 | 20 | 197 | 43 | 0 | 30 | 0 | 0 | 17 | 0 | 140 | 0 | 0 | 32 | 295 | 0 | 374 | 42 | 30 | 140 | 9 | 17 | 0 | 85 | 0 | 152 | 0 | 101 | 0 | 9 | 77 | 0 | 0 | 0 | 0 | 6991 | 923 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 581 | 0 | 0 | 0 | 1458 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 200 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 48 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 250 | 124 | 220 | 0 | 330 | 1150 | 35 | 6230 | 13221 | 76.63
03:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 255 | 0 | 0 | 133 | 0 | 225 | 15 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 34 | 20 | 14 | 0 | 470 | 0 | 0 | 19 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 33 | 42 | 720 | 0 | 0 | 26 | 0 | 32 | 220 | 0 | 0 | 0 | 1160 | 0 | 28 | 65 | 393 | 0 | 345 | 51 | 20 | 196 | 43 | 0 | 30 | 0 | 0 | 17 | 0 | 136 | 0 | 0 | 0 | 295 | 0 | 374 | 42 | 30 | 142 | 0 | 17 | 0 | 85 | 0 | 152 | 0 | 103 | 0 | 9 | 77 | 0 | 0 | 0 | 0 | 6918 | 923 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584 | 0 | 0 | 0 | 1455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 201 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 268 | 124 | 220 | 0 | 330 | 1140 | 0 | 6105 | 13023 | 76.61
04:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 244 | 0 | 0 | 133 | 0 | 145 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 17 | 20 | 14 | 0 | 450 | 0 | 0 | 19 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 32 | 42 | 720 | 0 | 0 | 26 | 0 | 31 | 220 | 0 | 0 | 0 | 1160 | 0 | 0 | 65 | 393 | 0 | 345 | 51 | 20 | 198 | 43 | 0 | 30 | 0 | 0 | 17 | 0 | 124 | 0 | 0 | 0 | 300 | 0 | 374 | 42 | 30 | 137 | 0 | 17 | 0 | 85 | 0 | 153 | 0 | 102 | 0 | 9 | 77 | 0 | 0 | 0 | 0 | 6710 | 923 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584 | 0 | 0 | 0 | 1450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 201 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 124 | 220 | 0 | 330 | 1130 | 0 | 6008 | 12718 | 76.59
05:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 237 | 0 | 0 | 124 | 0 | 60 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 20 | 14 | 0 | 440 | 0 | 0 | 18 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 42 | 720 | 0 | 0 | 26 | 0 | 31 | 220 | 0 | 0 | 0 | 1163 | 0 | 0 | 65 | 393 | 0 | 345 | 51 | 20 | 198 | 43 | 0 | 30 | 0 | 0 | 17 | 0 | 136 | 0 | 0 | 0 | 295 | 0 | 374 | 42 | 30 | 136 | 0 | 17 | 0 | 85 | 0 | 151 | 0 | 102 | 0 | 9 | 77 | 18 | 0 | 0 | 0 | 6585 | 922 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 571 | 0 | 0 | 0 | 1441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 201 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 124 | 180 | 0 | 330 | 1090 | 0 | 5861 | 12446 | 76.57
06:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 253 | 0 | 0 | 124 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 1 | 17 | 20 | 14 | 0 | 490 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 77 | 0 | 27 | 720 | 0 | 0 | 26 | 0 | 0 | 221 | 0 | 0 | 0 | 1100 | 2 | 0 | 65 | 393 | 0 | 345 | 51 | 20 | 198 | 43 | 0 | 30 | 0 | 0 | 17 | 0 | 126 | 0 | 3 | 0 | 300 | 0 | 380 | 42 | 30 | 133 | 0 | 0 | 0 | 85 | 0 | 152 | 0 | 102 | 0 | 9 | 77 | 18 | 0.08 | 0.43 | 0 | 6508.68 | 923 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.65 | 556 | 0 | 0 | 0 | 1351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 2 | 0 | 0 | 2.13 | 200 | 0 | 201 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.04 | 0 | 187 | 124 | 180 | 0 | 330 | 1015 | 0 | 5702.72 | 12211.4 | 76.55
07:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 246 | 0 | 0 | 124 | 30 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 4 | 19 | 19 | 14 | 0 | 455 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.41 | 78 | 0 | 22 | 720 | 0 | 0 | 26 | 0 | 0 | 220 | 0 | 0 | 0 | 1160 | 6 | 0 | 100 | 393 | 0 | 345 | 51 | 27 | 198 | 43 | 0 | 30 | 5 | 0 | 17 | 0 | 122 | 0 | 14 | 0 | 295 | 0 | 380 | 42 | 30 | 141 | 0 | 8 | 0 | 85 | 0 | 152 | 0 | 102 | 0 | 9 | 77 | 10 | 0.25 | 5.42 | 0 | 6638.08 | 923 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.93 | 573 | 0 | 0 | 0 | 1362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6 | 12 | 0 | 0 | 10.38 | 201 | 0 | 201 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 50 | 0 | 3 | 0 | 0 | 0 | 0 | 0.7 | 30 | 0.16 | 7 | 192 | 124 | 220 | 0 | 330 | 1005 | 0 | 5818.77 | 12456.85 | 76.53
08:00 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 239 | 0 | 0 | 113 | 15 | 15 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 5 | 17 | 0 | 14 | 0 | 440 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.35 | 79 | 0 | 10 | 720 | 0 | 0 | 26 | 0 | 0 | 216 | 0 | 0 | 0 | 1100 | 0 | 12 | 102 | 393 | 0 | 345 | 51 | 30 | 190 | 43 | 0 | 50 | 17 | 0 | 17 | 0 | 130 | 0 | 43 | 0 | 300 | 0 | 380 | 42 | 30 | 133 | 3 | 8 | 0 | 82 | 0 | 152 | 0 | 102 | 0 | 9 | 77 | 10 | 0.28 | 11.31 | 0 | 6606.94 | 923 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.46 | 565 | 0 | 0 | 0 | 1317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.52 | 23 | 0 | 0 | 8.85 | 160 | 0 | 160 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 51 | 0 | 14 | 0 | 0 | 0 | 0 | 1.3 | 59 | 0.21 | 14 | 225 | 100 | 220 | 0 | 330 | 950 | 0 | 5733.34 | 12340.28 | 76.51
09:00 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 229 | 0 | 0 | 105 | 15 | 15 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 14 | 17 | 20 | 14 | 0 | 415 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.38 | 80 | 0 | 3 | 720 | 0 | 0 | 26 | 0 | 0 | 216 | 0 | 0 | 0 | 1100 | 15 | 12 | 63 | 393 | 0 | 345 | 51 | 24 | 190 | 43 | 1 | 85 | 15 | 0 | 17 | 0 | 144 | 0 | 37 | 0 | 300 | 0 | 382 | 42 | 30 | 135 | 2 | 17 | 0 | 82 | 0 | 154 | 0 | 102 | 0 | 9 | 76 | 10 | 0.85 | 19.34 | 0 | 6617.57 | 923 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 550 | 0 | 0 | 0 | 1270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.82 | 29 | 0 | 0 | 6.26 | 160 | 0 | 160 | 0 | 0 | 0 | 354 | 0 | 0.46 | 0 | 50 | 0 | 14 | 0 | 0 | 0 | 0 | 3.2 | 129 | 0.54 | 14 | 199 | 100 | 220 | 0 | 330 | 920 | 0 | 5699.28 | 12316.85 | 76.48
10:00 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 215 | 0 | 0 | 105 | 15 | 105 | 30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 30 | 17 | 19.5 | 14 | 0 | 390 | 0 | 0 | 18 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 4.08 | 40 | 0 | 2 | 720 | 0 | 0 | 26 | 0 | 0 | 216 | 0 | 0 | 0 | 1160 | 17 | 12 | 63 | 393 | 0 | 345 | 51 | 5 | 185 | 42 | 16 | 145 | 16 | 0 | 17 | 0 | 156 | 0 | 47 | 0 | 300 | 0 | 368 | 42 | 30 | 130 | 2 | 17 | 0 | 82 | 0 | 155 | 0 | 104 | 0 | 19 | 75 | 8 | 0.23 | 11.22 | 0 | 6779.03 | 923 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 550 | 0 | 0 | 0 | 1215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.35 | 83 | 0 | 0 | 23.55 | 160 | 0 | 160 | 0 | 0 | 0 | 334 | 0 | 1.58 | 0 | 49 | 0 | 7 | 0 | 0 | 0 | 0 | 1.3 | 146 | 0.64 | 14 | 185 | 100 | 220 | 0 | 330 | 860 | 0 | 5638.42 | 12417.45 | 76.45
11:00 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 265 | 0 | 0 | 105 | 15 | 195 | 30 | 4 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 13 | 17 | 19.5 | 14 | 0 | 515 | 0 | 0 | 19 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 4.51 | 40 | 0 | 2 | 720 | 0 | 0 | 6 | 0 | 0 | 214 | 0 | 0 | 0 | 1160 | 11 | 13 | 63 | 350 | 0 | 342 | 44 | 5 | 193 | 42 | 17 | 144 | 16 | 1 | 15 | 0 | 152 | 0 | 48 | 0 | 305 | 0 | 369 | 42 | 30 | 139 | 10 | 17 | 0 | 82 | 0 | 154 | 0 | 102 | 0 | 19 | 76 | 5 | 0.45 | 35.78 | 0 | 7006.24 | 923 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 553 | 0 | 0 | 0 | 1241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.28 | 90 | 0 | 0 | 25.94 | 160 | 0 | 160 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 49 | 10 | 9 | 10 | 0 | 0 | 0 | 5.3 | 32 | 0.75 | 15 | 198 | 100 | 220 | 0 | 330 | 920 | 0 | 5760.27 | 12766.51 | 76.42
12:00 | 0 | 56 | 24 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 277 | 17 | 0 | 118 | 45 | 245 | 42 | 17 | 72 | 0 | 0 | 0 | 0 | 0 | 17 | 304 | 0 | 0 | 15 | 38 | 19 | 14 | 0 | 525 | 0 | 0 | 18 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 3.97 | 76 | 0 | 4 | 720 | 0 | 0 | 6 | 0 | 0 | 213 | 0 | 0 | 0 | 1160 | 18 | 33 | 63 | 370 | 0 | 342 | 51 | 5 | 191 | 38 | 43 | 143 | 29 | 9 | 19 | 0 | 168 | 0 | 56 | 0 | 300 | 0 | 357 | 42 | 30 | 153 | 9 | 17 | 0 | 82 | 0 | 154 | 0 | 102 | 0 | 19 | 76 | 0 | 1.95 | 36.88 | 0 | 7415.8 | 923 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 553 | 0 | 0 | 0 | 1324 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 26.09 | 94 | 0 | 0 | 52.29 | 160 | 0 | 160 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 50 | 35 | 32 | 34 | 0 | 0 | 0 | 0 | 145 | 0.73 | 0 | 150 | 100 | 220 | 0 | 330 | 880 | 0 | 5918.11 | 13333.91 | 76.39
13:00 | 0 | 105 | 32 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 262 | 17 | 0 | 132 | 65 | 287 | 55 | 17 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 297 | 0 | 0 | 30 | 80 | 19 | 14 | 0 | 500 | 0 | 0 | 19 | 0 | 14 | 32 | 0 | 0 | 0 | 0 | 2.89 | 70 | 8 | 7 | 720 | 41 | 0 | 6 | 0 | 10 | 212 | 0 | 0 | 0 | 1224 | 16 | 80 | 63 | 385 | 0 | 342 | 51 | 5 | 186 | 38 | 87 | 142 | 105 | 9 | 19 | 0 | 158 | 0 | 69 | 0 | 300 | 0 | 230 | 42 | 20 | 152 | 12 | 17 | 0 | 81 | 0 | 153 | 0 | 102 | 17 | 19 | 76 | 0 | 2.3 | 40.9 | 0 | 7804.09 | 923 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 580 | 0 | 0 | 0 | 1402 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 32.36 | 94 | 0 | 0 | 28.63 | 160 | 0 | 160 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 48 | 35 | 32 | 45 | 0 | 0 | 0 | 4.3 | 136 | 0.23 | 0 | 170 | 120 | 220 | 0 | 330 | 820 | 0 | 5997.52 | 13801.61 | 76.36
14:00 | 0 | 105 | 32 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 244 | 17 | 7 | 132 | 90 | 295 | 55 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 303 | 0 | 0 | 15 | 118 | 19 | 14 | 0 | 470 | 0 | 0 | 18 | 0 | 16 | 34 | 0 | 0 | 0 | 0 | 3.97 | 67 | 16 | 5 | 720 | 107 | 0 | 6 | 0 | 17 | 212 | 0 | 0 | 0 | 1224 | 16 | 80 | 63 | 385 | 0 | 335 | 51 | 5 | 190 | 37 | 90 | 142 | 132 | 8 | 19 | 11 | 168 | 0 | 46 | 0 | 315 | 0 | 232 | 42 | 20 | 146 | 9 | 17 | 0 | 79 | 0 | 153 | 0 | 102 | 35 | 9 | 86 | 0 | 1.05 | 24.26 | 0 | 7918.28 | 923 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 590 | 0 | 0 | 0 | 1376 | 0 | 0 | 0 | 15 | 70 | 0 | 0 | 0 | 0 | 45.19 | 92 | 0 | 0 | 38.95 | 160 | 0 | 160 | 0 | 0 | 0 | 370 | 0 | 2.47 | 0 | 45 | 50 | 27 | 47 | 0 | 0 | 0 | 2.7 | 96 | 0.62 | 0 | 206 | 122 | 220 | 0 | 330 | 845 | 0 | 6048.93 | 13967.21 | 76.33
15:00 | 0 | 105 | 40 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 267 | 17 | 17 | 132 | 100 | 280 | 55 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 310 | 0 | 0 | 23 | 136 | 19 | 14 | 0 | 545 | 0 | 0 | 18 | 0 | 18 | 34 | 0 | 0 | 0 | 0 | 3.29 | 60 | 16 | 2 | 785 | 125 | 0 | 6 | 0 | 33 | 212 | 0 | 0 | 0 | 1224 | 12 | 80 | 80 | 389 | 0 | 338 | 51 | 6 | 202 | 38 | 90 | 141 | 135 | 9 | 19 | 38 | 158 | 0 | 49 | 0 | 310 | 0 | 232 | 42 | 30 | 151 | 5 | 17 | 0 | 79 | 0 | 152 | 0 | 102 | 0 | 9 | 86 | 0 | 1.56 | 29 | 0 | 8183.85 | 923 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 590 | 0 | 0 | 0 | 1405 | 0 | 0 | 0 | 35 | 70 | 0 | 0 | 0 | 0 | 22.88 | 52 | 0 | 0 | 39.27 | 164 | 0 | 160 | 0 | 0 | 0 | 396 | 0 | 2.55 | 0 | 46 | 50 | 21 | 49 | 0 | 0 | 0 | 3.7 | 69 | 0.49 | 0 | 248 | 120 | 220 | 0 | 330 | 890 | 0 | 6092.89 | 14276.74 | 76.3
16:00 | 0 | 105 | 40 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 271 | 0 | 17 | 132 | 110 | 280 | 55 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 11 | 142 | 19 | 14 | 0 | 485 | 0 | 0 | 18 | 0 | 21 | 32 | 0 | 0 | 0 | 0 | 2 | 60 | 15 | 2 | 920 | 135 | 0 | 6 | 0 | 32 | 213 | 0 | 0 | 0 | 1224 | 8 | 30 | 120 | 390 | 0 | 287 | 51 | 4 | 196 | 24 | 89 | 141 | 168 | 8 | 19 | 85 | 150 | 0 | 31 | 28 | 310 | 0 | 232 | 42 | 30 | 151 | 3 | 17 | 0 | 79 | 0 | 155 | 0 | 102 | 0 | 13 | 85 | 0 | 0.98 | 12.53 | 0 | 8200.51 | 896 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 578 | 0 | 0 | 0 | 1437 | 0 | 0 | 0 | 35 | 80 | 0 | 0 | 0 | 0 | 24.78 | 45 | 0 | 0 | 20.72 | 170 | 0 | 170 | 0 | 0 | 0 | 393 | 0 | 0 | 0 | 46 | 70 | 11 | 69 | 0 | 0 | 0 | 2.1 | 89 | 0.34 | 0 | 272 | 120 | 220 | 0 | 330 | 915 | 0 | 6174.94 | 14375.45 | 76.27
17:00 | 0 | 105 | 40 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 260 | 0 | 17 | 132 | 125 | 280 | 55 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 7 | 142 | 19 | 14 | 0 | 430 | 0 | 0 | 18 | 0 | 15 | 34 | 2 | 0 | 0 | 0 | 0.94 | 60 | 15 | 2 | 1100 | 140 | 0 | 6 | 0 | 31 | 214 | 0 | 0 | 0 | 1190 | 0 | 20 | 147 | 384 | 0 | 345 | 51 | 20 | 194 | 29 | 100 | 142 | 192 | 9 | 19 | 114 | 160 | 0 | 13 | 23 | 315 | 0 | 232 | 42 | 30 | 146 | 3 | 17 | 0 | 83 | 30 | 154 | 0 | 102 | 0 | 12 | 85 | 0 | 0.4 | 5.92 | 0 | 8452.26 | 895 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 580 | 0 | 0 | 0 | 1411 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 0 | 0 | 9.93 | 21 | 0 | 0 | 10.21 | 170 | 0 | 170 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 46 | 110 | 3 | 92 | 0 | 0 | 0 | 1.8 | 16 | 0.17 | 0 | 255 | 100 | 180 | 0 | 330 | 900 | 0 | 5983.11 | 14435.37 | 76.25
18:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 237 | 17 | 17 | 132 | 125 | 280 | 55 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 2 | 142 | 19 | 14 | 0 | 430 | 0 | 0 | 20 | 0 | 9 | 34 | 23 | 0 | 0 | 0 | 0.1 | 60 | 16 | 2 | 1125 | 141 | 0 | 8 | 1 | 32 | 215 | 0 | 0 | 0 | 1160 | 0 | 20 | 130 | 390 | 0 | 345 | 51 | 40 | 192 | 30 | 105 | 142 | 192 | 17 | 19 | 108 | 166 | 0 | 2 | 23 | 315 | 0 | 232 | 42 | 30 | 134 | 0 | 17 | 0 | 82 | 30 | 155 | 0 | 102 | 1 | 15 | 86 | 0 | 0.08 | 2.04 | 0 | 8464.22 | 895 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 4.97 | 578 | 0 | 0 | 0 | 1357 | 0 | 0 | 0 | 35 | 113 | 0 | 30 | 7 | 8 | 2.03 | 5 | 0 | 0 | 2.2 | 170 | 0 | 170 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 47 | 115 | 1 | 99 | 0 | 0 | 0 | 0.4 | 6 | 0.03 | 8 | 210 | 100 | 180 | 0 | 330 | 873 | 4 | 5883.63 | 14347.85 | 76.23
19:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 332 | 29.5 | 17 | 132 | 126 | 280 | 55 | 17 | 72 | 0 | 0 | 0 | 0 | 0 | 25 | 303 | 0 | 0 | 0 | 142 | 19 | 14 | 0 | 505 | 0 | 0 | 39 | 0 | 6 | 49 | 23 | 0 | 0 | 0 | 0 | 60 | 16 | 5 | 1125 | 142 | 0 | 24 | 8 | 33 | 216 | 0 | 0 | 0 | 1224 | 0 | 51 | 73 | 393 | 0 | 345 | 51 | 15 | 195 | 32 | 109 | 146 | 192 | 12 | 19 | 110 | 186 | 0 | 0 | 23 | 325 | 0 | 232 | 42 | 30 | 147 | 0 | 17 | 0 | 83 | 30 | 155 | 0 | 102 | 17 | 15 | 86 | 0 | 0 | 0 | 0 | 8807.5 | 895 | 155 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 566 | 0 | 0 | 0 | 1461 | 0 | 40 | 0 | 90 | 113 | 0 | 76 | 21 | 16 | 0 | 0 | 26 | 0 | 0 | 177 | 0 | 183 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 47 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 244 | 118 | 220 | 0 | 455 | 1025 | 54 | 6681 | 15488.5 | 76.21
19:30 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 340 | 35 | 17 | 132 | 126 | 280 | 55 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 317 | 0 | 0 | 0 | 142 | 19 | 14 | 0 | 530 | 0 | 0 | 39 | 0 | 3 | 49 | 30 | 0 | 0 | 0 | 0 | 60 | 15 | 7 | 1125 | 142 | 0 | 24 | 8 | 45 | 216 | 0 | 0 | 0 | 1224 | 0 | 150 | 73 | 393 | 0 | 345 | 51 | 5 | 206 | 33 | 115 | 146 | 195 | 18 | 19 | 114 | 182 | 0 | 0 | 23 | 325 | 0 | 232 | 42 | 30 | 152 | 0 | 17 | 0 | 83 | 30 | 152 | 0 | 102 | 17 | 17 | 86 | 0 | 0 | 0 | 0 | 9027 | 895 | 154 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 582 | 0 | 0 | 0 | 1471 | 0 | 40 | 0 | 113 | 113 | 0 | 76 | 21 | 25 | 0 | 0 | 26 | 0 | 0 | 183 | 0 | 183 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 45 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 279 | 118 | 220 | 0 | 455 | 1110 | 72 | 6935 | 15962
20:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 213 | 35 | 17 | 132 | 128 | 280 | 55 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 288 | 0 | 0 | 0 | 142 | 5 | 14 | 0 | 380 | 0 | 0 | 41 | 0 | 3 | 49 | 30 | 0 | 0 | 0 | 0 | 60 | 15 | 9 | 1125 | 143 | 0 | 26 | 8 | 44 | 217 | 0 | 0 | 0 | 1224 | 0 | 148 | 73 | 393 | 0 | 345 | 51 | 5 | 181 | 35 | 110 | 146 | 193 | 17 | 19 | 108 | 184 | 0 | 0 | 23 | 320 | 0 | 232 | 42 | 30 | 147 | 0 | 17 | 0 | 83 | 30 | 153 | 0 | 102 | 17 | 11 | 86 | 0 | 0 | 0 | 0 | 8652 | 895 | 149 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 588 | 0 | 0 | 0 | 1462 | 0 | 40 | 0 | 113 | 113 | 0 | 76 | 22 | 43 | 0 | 0 | 26 | 0 | 0 | 183 | 0 | 183 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 46 | 115 | 0 | 98 | 0 | 120 | 0 | 0 | 0 | 0 | 105 | 307 | 118 | 220 | 0 | 455 | 1158 | 72 | 7158 | 15810 | 76.19
21:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 326 | 35 | 17 | 133 | 129 | 295 | 55 | 35 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 304 | 0 | 0 | 0 | 142 | 19 | 14 | 0 | 490 | 0 | 0 | 57 | 0 | 3 | 49 | 30 | 0 | 0 | 0 | 0 | 60 | 16 | 2 | 1125 | 144 | 0 | 45 | 8 | 50 | 217 | 0 | 0 | 0 | 1224 | 0 | 150 | 73 | 393 | 0 | 345 | 51 | 5 | 192 | 35 | 108 | 147 | 193 | 17 | 19 | 110 | 180 | 0 | 0 | 23 | 305 | 0 | 232 | 42 | 30 | 148 | 0 | 17 | 0 | 83 | 30 | 153 | 0 | 102 | 17 | 17 | 87 | 0 | 0 | 0 | 0 | 8935 | 895 | 149 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 588 | 0 | 0 | 0 | 1470 | 0 | 40 | 0 | 113 | 113 | 0 | 85 | 22 | 52.2 | 0 | 0 | 26 | 0 | 0 | 183 | 0 | 183 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 46 | 115 | 0 | 98 | 0 | 165 | 0 | 0 | 0 | 0 | 102 | 307 | 118 | 220 | 0 | 590 | 1200 | 72 | 7477.2 | 16412.2 | 76.17
22:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 234 | 35 | 17 | 132 | 129 | 295 | 55 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 35 | 298 | 0 | 0 | 0 | 142 | 19 | 14 | 0 | 365 | 0 | 0 | 58 | 0 | 0 | 49 | 30 | 0 | 0 | 0 | 0 | 60 | 16 | 13 | 1120 | 138 | 0 | 45 | 0 | 50 | 217 | 0 | 0 | 0 | 1224 | 0 | 75 | 73 | 380 | 0 | 345 | 51 | 5 | 180 | 37 | 110 | 100 | 192 | 17 | 19 | 106 | 174 | 0 | 0 | 24 | 310 | 0 | 232 | 42 | 30 | 148 | 0 | 17 | 0 | 83 | 30 | 153 | 0 | 102 | 17 | 18 | 78 | 0 | 0 | 0 | 0 | 8532 | 895 | 147 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 588 | 0 | 0 | 0 | 1447 | 0 | 31 | 0 | 113 | 113 | 0 | 85 | 21 | 52.2 | 0 | 0 | 26 | 0 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 48 | 115 | 0 | 99 | 0 | 165 | 0 | 0 | 0 | 0 | 104 | 307 | 118 | 220 | 0 | 590 | 1200 | 72 | 7276.2 | 15808.2 | 76.15
23:00 | 0 | 105 | 41 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 274 | 36 | 0 | 132 | 129 | 295 | 55 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 142 | 18 | 14 | 0 | 480 | 0 | 0 | 55 | 0 | 0 | 49 | 30 | 0 | 0 | 0 | 0 | 60 | 15 | 20 | 1120 | 144 | 0 | 45 | 0 | 46 | 213 | 0 | 0 | 0 | 1160 | 0 | 26 | 73 | 393 | 0 | 250 | 51 | 5 | 195 | 34 | 69 | 70 | 181 | 17 | 19 | 34 | 170 | 0 | 0 | 24 | 310 | 0 | 232 | 42 | 30 | 127 | 0 | 17 | 0 | 83 | 30 | 153 | 0 | 101 | 0 | 9 | 77 | 0 | 0 | 0 | 0 | 8191 | 895 | 146 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 592 | 0 | 0 | 0 | 1457 | 0 | 31 | 0 | 50 | 50 | 0 | 85 | 21 | 52.2 | 0 | 0 | 26 | 0 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 48 | 115 | 0 | 98 | 0 | 72 | 0 | 0 | 0 | 0 | 97 | 307 | 100 | 180 | 0 | 590 | 1225 | 54 | 7038.2 | 15229.2 | 76.13
Total KWH | 0 | 1790400 | 668160 | 0 | 0 | 0 | 0 | 0 | 9550800 | 0 | 6536760 | 259200 | 154440 | 3061008 | 1492320 | 4864124 | 1025853 | 334306 | 803520 | 0 | 0 | 0 | 0 | 0 | 270414 | 7295812 | 0 | 0 | 171543 | 1968000 | 451200 | 339480 | 0 | 11273181.82 | 0 | 0 | 623040 | 0 | 187200 | 495009 | 211632 | 1927 | 0 | 0 | 30484 | 1588680 | 358800 | 419040 | 20487272.73 | 1569018 | 0 | 537120 | 27147.6 | 658218 | 5245560 | 0 | 0 | 0 | 28281815 | 115560 | 971854 | 1906909 | 9315000 | 0 | 9170000 | 1230524 | 348960 | 4827000 | 903384 | 1206720 | 2289107 | 2233920 | 159600 | 438860 | 971280 | 3706560 | 0 | 467527 | 280720 | 7384000 | 0 | 7523000 | 997000 | 695520 | 3434318.18 | 58565 | 355248 | 0 | 1967040 | 217638 | 3530500 | 0 | 2448300 | 164160 | 289200 | 1910400 | 64320 | 10100 | 216060 | 1440 | 184842779.33 | 22048000 | 4118688 | 0 | 111360 | 0 | 0 | 0 | 0 | 0 | 0 | 351792 | 624240 | 14138180 | 0 | 0 | 0 | 33832909 | 0 | 250000 | 0 | 801024 | 1327968 | 0 | 472496 | 109809 | 241709 | 290000 | 604558 | 127096 | 0 | 260704 | 4502318 | 0 | 4408191 | 0 | 0 | 0 | 9149818 | 0 | 10750 | 0 | 1093964 | 1190656 | 167358 | 1133683 | 0 | 510614 | 0 | 33838.8 | 916560 | 4384 | 877536 | 5717000 | 2747000 | 5254800 | 0 | 9149091 | 24948363.64 | 428400 | 151954858.44 | 336797637.77

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 16-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13333.91 | MW | 12:00 Hr. | Energy Generated |  |  | 336.7976 |  | MKWHr.
| Day Peak Demand |  |  | 13373.91 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.393 |  | MKWHr.
| Evening Peak Generation |  |  | 16412.2 | MW | 21:00 Hr. | Energy Demand |  |  | 339.1906 |  | MKWHr.
| Evening Peak Demand |  |  | 16620.2 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.5 |  | °C
| Minimum Generation of the Day |  |  | 12211.4 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 921.48 |  | MMCFD
| Maximum Generation of the Day |  |  | 16412.2 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.4603 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 35.4472 | 0 | 16.6917 | 0 | 0 | 0.17154 | 0 | 0 | 52.3105 | Gas | 130.3393 | Gas | 459935586.195
| Chattogram Zone |  |  | 5.6646 | 48.7691 | 4.4819 | 0 | 1.5887 | 0.14604 | 0 | 0.1872 | 60.8375 | Coal | 103.8157 | Coal | 670343199.5109
| Cumilla Zone |  |  | 30.4297 | 0 | 5.8241 | 0 | 0 | 0.46753 | 3.7066 | 0 | 40.4279 | HFO | 36.7865 | HFO | 616523944.362
| Mymensingh Zone |  |  | 0.06432 | 0 | 2.3652 | 0 | 0 | 0.22616 | 0 | 0 | 2.6557 | HSD | 0.51061 | HSD | 15767760.32
| Sylhet Zone |  |  | 28.5526 | 0 | 0 | 0 | 0 | 0.058565 | 0 | 0 | 28.6111 | Hydro | 1.5887 | Hydro | 158868
| Khulna Zone |  |  | 4.1187 | 14.1382 | 0.46315 | 0 | 0 | 0.62424 | 22.048 | 0 | 41.3923 | Solar | 3.9822 | Solar | 63523963.836
| Barishal Zone |  |  | 8.0018 | 39.8145 | 1.3059 | 0 | 0 | 0.004384 | 0 | 0 | 49.1266 | Import | 59.5875 | Import | 346802351.96
| Rajshahi Zone |  |  | 18.0603 | 0 | 3.3301 | 0 | 0 | 1.166 | 33.8329 | 0 | 56.3894 | Wind | 0.1872 | Wind | 2753712
| Rangpur Zone |  |  | 0 | 1.094 | 2.3243 | 0.51061 | 0 | 1.1178 | 0 | 0 | 5.0467
| Total |  |  | 130.3393 | 103.8157 | 36.7865 | 0.51061 | 1.5887 | 3.9822 | 59.5875 | 0.1872 | 336.7976
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 459935586.195 |  | Hydro | 158868
|  |  |  | Coal | 670343199.5109 |  | Solar | 63523963.836
|  |  |  | HFO | 616523944.362 |  | Import | 346802351.96
|  |  |  | HSD | 15767760.32 |  | Wind | 2753712
[5 empty] | Total: | 217,58,09,386 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.048 | Peak Hr Flow | 895.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 42526272.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 33.8329 | Peak Hr Flow | 1470.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2003 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.7066 | Peak Hr Flow | 180.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2418 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 59.5875 | Peak Hr Flow | 2545.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 6070
|  |  |  | Chattogram |  | 29 |  | 1566
|  |  |  | Cumilla |  | 0 |  | 1542
|  |  |  | Mymensingh |  | 140 |  | 1124
|  |  |  | Sylhet |  | 0 |  | 581
|  |  |  | Khulna |  | 30 |  | 2030
|  |  |  | Barishal |  | 0 |  | 520
|  |  |  | Rajshahi |  | 0 |  | 1705
|  |  |  | Rangpur |  | 0 |  | 974
|  |  |  | Total |  | 199 |  | 16112
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:01 |  | Chandpur CCPP ST was sync.
| 08:34 | 17:26 | Ishurdi 132/33kV S/S 132/33 kV T-3 LT Scheduled S/D | [7 empty] | 20.0MW load
interrup.
| 08:34 | 17:26 | Ishurdi 132/33kV S/S 132/33 kV T-3 HT Scheduled S/D | [7 empty] | 20.0MW load
interrup.
|  | 08:42 | Mymensingh 132/33kV S/S Transformer-1 (404T) HT is restored.
|  | 08:43 | Mymensingh 132/33kV S/S Transformer-2 (414T) HT is restored.
| 08:52 | 11:30 | Pabna- Shahjadpur 132kV Ckt-1 Forced S/D from Shahjadpur 132/33kV end Due to পাবনা
গ্রিডে জরুরি সংরক্ষণ কাজের জন্য। and from Pabna 132/33kV end Due to Redhot Maintenance
|  | 09:33 | Mongla 132/33kV S/S T-1 HT is restored.
|  | 09:33 | Mongla 132/33kV S/S T-1 LT is restored.
| 09:33 | 11:08 | Chandraghona-Kaptai 132 kV Ckt-1 Scheduled S/D from Chandraghona 132/33kV end Due to
Relay functional test performed by SPMD
| 09:41 | 15:46 | Barapukuria-Bogura 230 kV Ckt-2 Project Work S/D from Bogura 400/230kV end Due to Project
work shutdown and from Barapukuria 230/132/33kV end Due to ERS
| 09:53 |  | At Bhola P/S,Tr-(230/33)Kv S/D is Restored.
| 09:56 | 12:32 | Chattak-Sylhet 132 kV Ckt-1 Tripped from Sylhet 132/33kV end showing Distance A & B | [7 empty] | 20.0MW load
|  |  | Phase, Zone-2 relays. | [7 empty] | interrup. Sylhet
132/33kV end
| 10:48 | 15:56 | Tangail 132/33kV S/S Tr-3 LT Scheduled S/D Due to 33 kv ghatail feeder redhot maintenance
| 10:48 | 15:56 | Tangail 132/33kV S/S Tr-3 HT Scheduled S/D Due to 33 kv ghatail feeder redhot maintenance
| 10:50 |  | Aminbazar-Kaliakor 400 ckt shutdown
| 11:07 | 13:20 | Khulna (C) S/S Tr-2 415 T LT Scheduled S/D Due to Wz red hot maintenance
| 11:08 | 13:19 | Khulna (C) S/S Tr-2 415 T HT Scheduled S/D Due to Wz red hot maintenance.
| 11:10 | 13:30 | Chandraghona-Kaptai 132 kV Ckt-2 Scheduled S/D from Chandraghona 132/33kV end Due to
Relay functional test performed by SPMD
| 11:13 | 15:44 | GPH 230/33kV S/S Transformer-01(D05) HT Scheduled S/D Due to for general maintenance
|  | 11:29 | Shariatpur 132/33kV S/S T1-406T HT is restored.
|  | 11:30 | Shariatpur 132/33kV S/S T1-406T LT is restored.
| 11:38 | 13:21 | Narshingdi 132/33kV S/S T-4 LT Scheduled S/D Due to টি-৪ ,৩৩ কেভি বাসের আওতাধীন শিবপুর ৩৩ | [7 empty] | 17.0MW load
|  |  | কেভি ফিডারের সোর্স সাইডর রাইজার রেড হট হওয়ায় জরুরী রক্ষনাবেক্ষন কাজ | [7 empty] | interrup.
| 11:38 | 13:20 | Narshingdi 132/33kV S/S T-4 HT Scheduled S/D Due to টি-৪ ,৩৩ কেভি বাসের আওতাধীন শিবপুর ৩৩ | [7 empty] | 17.0MW load
|  |  | কেভি ফিডারের সোর্স সাইডর রাইজার রেড হট হওয়ায় জরুরী রক্ষনাবেক্ষন কাজ | [7 empty] | interrup.
| 11:42 | 15:49 | Shariatpur 132/33kV S/S T2-416T LT Scheduled S/D Due to Maintenance Work by PBS. | [7 empty] | 32.0MW load
interrup.
| 11:45 | 15:39 | Shariatpur 132/33kV S/S T2-416T HT Scheduled S/D Due to Maintenance Work by PBS. | [7 empty] | 32.0MW load
interrup.
| 11:51 | 12:57 | Chandraghona-Rangamati 132 kV Ckt-1 Scheduled S/D from Chandraghona 132/33kV end Due to
Relay functional test performed by SPMD
| 12:00 |  | Day Peak Generation is 13330 MW.
| 12:08 | 12:18 | Nabinagar 132/33kV S/S T-1 LT Tripped showing 7SJ81 relays Due to Over load | [7 empty] | 105.0MW load
interrup.
| 12:08 | 12:18 | Nabinagar 132/33kV S/S T-1 HT Tripped showing SIPROTEC 7UT85 relays Due to Over Load | [7 empty] | 105.0MW load
interrup.
| 12:33 | 13:30 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Scheduled S/D Due to
33kV GT-4 Redhot.
|  | 12:38 | Faridpur 132/33kV S/S Transformer-2 HT is restored.
|  | 12:39 | Faridpur 132/33kV S/S Transformer-2 LT is restored.
|  | 12:39 | Faridpur 132/33kV S/S Transformer-2 HT is restored.
| 13:04 | 13:46 | Chandraghona-Rangamati 132 kV Ckt-2 Scheduled S/D from Chandraghona 132/33kV end Due to
Relay functional test performed by SPMD
| 13:18 | 19:52 | Ishurdi-Pabna 132kV ckt Forced S/D from Pabna 132/33kV end. and from Ishurdi 132/33kVend.
| 14:19 | 14:57 | Chandraghona-Madunaghat 132 kV Ckt-1 Scheduled S/D from Chandraghona 132/33kV end Due to
Relay functional test performed by SPMD and from Madunaghat 132/33kV end Due to Annual
Relay functional test by SPMD Chattogram at Chandraghona grid .
|  | 14:37 | Khagrachari-Rangamati 132kV Ckt-2 is restored.
| 15:00 | 15:38 | Chandraghona-Madunaghat 132 kV Ckt-2 Scheduled S/D from Chandraghona 132/33kV end Due to
Relay functional test performed by SPMD and from Madunaghat 132/33kV end Due to Annual
Relay functional test by SPMD at Chandraghona Grid
| 15:02 | 18:10 | Bog-Sherpur 132/33kV S/S Transformer-3 (424T) LT Forced S/D Due to Oil sample collection
| 15:02 | 18:10 | Bog-Sherpur 132/33kV S/S Transformer-3 (424T) HT Forced S/D Due to Oil sample collection
|  | 17:21 | Meghnaghat-Shyampur 230kV Ckt-2 is restored.
|  | 17:21 | Meghnaghat-Shyampur 230kV Ckt-2 is restored.
| 18:47 | 19:10 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing Instant o/c,definite o/c relays Due | [7 empty] | 50.0MW load
|  |  | to Due to auxiliary transformer fuse fault | [7 empty] | interrup.
| 18:57 | 19:15 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Tripped showing Over current Relay relays Due
to Over Load
| 18:57 | 19:15 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Tripped showing Over Current Relay relays Due | [7 empty] | 106.0MW load
|  |  | to Over Load | [7 empty] | interrup.
| 21:00 |  | Evening Peak Generation is 16412 MW.
| 21:02 | 23:08 | Nawabganj 132/33kV S/S TR-2 LT Forced S/D Due to Emergency red hot maintenance at 33kV | [7 empty] | 15.0MW load
|  |  | incomer-02, BUS section-02 side. | [7 empty] | interrup.
| 21:03 | 23:06 | Nawabganj 132/33kV S/S TR-2 HT Forced S/D Due to Emergency red hot maintenance at 33kV | [7 empty] | 15.0MW load
|  |  | incomer-02, BUS section-02 side. | [7 empty] | interrup.
| 02:20 |  | Sirajgonj 225MW CCPP Unit-1 Tripped with remarks:- ST
| 03:05 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- gt
| 04:05 | 04:48 | Bogura(New)-Naogaon 132 kV Ckt-1 Tripped from Naogaon 132/33kV end showing Z-1 (siemens,
Siprotec 7SA87), Distance 5.7 km, 1ms relays Due to Thunderstorms
| 04:25 | 04:58 | Rampura-Ullon-2 132kV Ckt-2 Tripped from Rampura 230/132kV end showing distance relays.
| 04:25 | 05:11 | Maniknagar-Siddhirganj 230kV Ckt-1 Tripped from Maniknagar 230/132kV end showing General
Trip, Distance Trip, 21 start L1 and Zone-1 Trip. relays Due to Thunderstrom and from
Siddhirganj 230/132kV end showing General Trip,21Trip,zone-2 phase R relays Due to Trip
| 04:34 | 06:41 | Maniknagar-Siddhirganj 230kV Ckt-2 Tripped from Maniknagar 230/132kV end showing General | [7 empty] | 194.0MW load
|  |  | Trip, Distance Trip, 21 start L3, 21 start Block and Zone-1 Trip. relays Due to | [7 empty] | interrup.
|  |  | Thunderstrom and from Siddhirganj 230/132kV end showing General Trip, Distance | [7 empty] | Maniknagar
|  |  | Trip,zone-1,phase B,Fault distance 4.3km relays Due to Trip | [7 empty] | 230/132kV end and
194.0MW load
interrup.
Siddhirganj
230/132kV end
| 04:35 | 05:01 | Siddhirganj-Ullon (T at Maniknagar) 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end
showing DiSTANCE RELAY 9.4 KM relays Due to DiSTANCE RELAY 9.4 KM , heavy Rainy & stromy
wind.
| 04:48 | 05:05 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing MiCOM 1) Ph-B, 2) Zone-1,
3) Inst. Send relays Due to Heavy Rain
| 05:27 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- GT
| 05:27 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- ST
| 06:00 |  | Minimum Generation: 10322 MW.
| 07:10 | 07:40 | Rangpur 132/33kV S/S T-2 (404T) LT Tripped showing MICOM 127 relays Due to "Heavy rain
and thunderstorms."
| 07:10 | 07:40 | Rangpur 132/33kV S/S T-1(414T) LT Tripped showing MICOM 127 relays Due to "Heavy rain and
thunderstorms."
| 07:55 |  | Srinagar 132/33kV S/S Tr-01 LT Tripped showing Lockout Relay 1, 2 Over current relay | [7 empty] | 10.0MW load
|  |  | relays Due to 33 KV Feeder 2 Tripped due to bad weather | [7 empty] | interrup.
| 07:55 |  | Srinagar 132/33kV S/S Tr-02 LT Tripped showing Over Current Relay Lockout Relay 1, 2 | [7 empty] | 10.0MW load
|  |  | relays Due to 33 KV Feeder 2 Tripped due to bad weather | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 16-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 365 | 9550800 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1025853 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 304 | 7295812 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 259200 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 129 | 1492320 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 334306 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 270414 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 451200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 339480 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 48 | 668160 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 295 | 4864124 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 3061008 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1790400 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 803520 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 171543 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 154440 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 490 | 11273181.82 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 326 | 6536760 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1968000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2601 | 52310521.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 27147.6 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 115560 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 45 | 537120 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 60 | 1588680 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5245560 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 50 | 658218 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 30 | 211632 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 49 | 495009 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 2 | 419040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 57 | 623040 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 30484 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 1927 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 16 | 358800 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 144 | 1569018 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28281815 | U2 on AGC
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 3 | 187200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1125 | 20487272.73 | AGC
Chattogram Area Total |  |  |  |  | 4898.863 | 3030 | 60837523.33
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 192 | 4827000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 0 | 0 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 345 | 9170000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 9315000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 35 | 903384 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 5 | 348960 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 73 | 1906909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1230524 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 971854 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 280720 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 147 | 2289107 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 193 | 2233920 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 180 | 3706560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 438860 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 110 | 971280 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 17 | 159600 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 108 | 1206720 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 467527 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 2041 | 40427925
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 64320 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 1910400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 17 | 289200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 216060 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 1440 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 164160 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 121 | 2655680
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 58565 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 997000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 695520 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 148 | 3434318.18 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 153 | 3530500 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 217638 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1967040 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 102 | 2448300 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 355248 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7384000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 232 | 7523000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1142 | 28611129.18
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 895 | 22048000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 30 | 111360 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 149 | 4118688 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 351792 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 624240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 588 | 14138180 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1767 | 41392260
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 590 | 9149091 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 102 | 877536 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 118 | 2747000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 24948363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5254800 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 72 | 428400 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5717000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4384 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2609 | 49126574.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 290000 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 250000 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 109809 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 183 | 4502318 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 183 | 4408191 | Liquid fuel shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 390 | 9149818 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 127096 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 241709 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 85 | 472496 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1327968 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 801024 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 10750 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1470 | 33832909 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 260704 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 604558 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2677.2 | 56389350
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 165 | 510614 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 46 | 1093964 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1133683 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 33838.8 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1190656 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 167358 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 916560 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 424 | 5046673.8
Eastern Grid Total |  |  |  |  | 17418.042 | 8935 | 184842779.33
Western Grid Total |  |  |  |  | 11852.195 | 7477.2 | 151954858.44
National Grid Total |  |  |  |  | 29270.237 | 16412.2 | 336797637.77
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 16-05-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10713.37 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5199 | MW
i) Dhaka area |  |  | 6069.67 |  | MW | i) Khulna area |  |  |  | 2000 | MW
ii) Chattogram area |  |  | 1536.7 |  | MW | ii) Barishal area |  |  |  | 519.8 | MW
iii) Cumilla area |  |  | 1542 |  | MW | iii) Rajshahi area |  |  |  | 1705.2 | MW
iv) Mymensingh area |  |  | 984 |  | MW | iv) Rangpur area |  |  |  | 974 | MW
v) Sylhet area |  |  | 581 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15912.37 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 6 | 18:00 | 67 | Hasnabad | 102 | 13:00 | 133 | Natore | 181 | 21:00
2 | AKSML | 139.8 | 11:00 | 68 | Hathazari | 100 | 21:00 | 134 | Nawabganj | 65.6 | 19:30
3 | Aftabnagar | 48 | 12:00 | 69 | Hatirjheel | 41 | 13:00 | 135 | Netrakona | 134 | 19:30
4 | Agargaon | 124 | 13:00 | 70 | Ishurdi | 97 | 21:00 | 136 | New | 84.8 | 15:00
5 | Agrabad | 72 | 14:00 | 71 | Jaldhaka | 58 | 22:00 | 137 | Niamatpur | 77 | 20:00
6 | Amnura | 33 | 22:00 | 72 | Jamalpur | 94 | 13:00 | 138 | Noapara | 46 | 16:00
7 | Ashuganj | 81 | 00:00 | 73 | Jashore | 165 | 13:00 | 139 | PHP | 10 | 20:00
8 | BSRM | 202 | 01:00 | 74 | Jhenaidah | 130 | 19:00 | 140 | Pabna | 113 | 22:00
9 | Bagerhat | 84 | 19:00 | 75 | Joydebpur | 172 | 21:00 | 141 | Palashbari | 128 | 21:00
10 | Bajitpur | 89 | 20:00 | 76 | Joypurhat | 70 | 23:00 | 142 | Panchagarh | 56 | 21:00
11 | Bakerganj | 12.2 | 22:00 | 77 | Juldah | 19 | 17:00 | 143 | Patiya | 12 | 19:00
12 | Bakulia | 104 | 11:00 | 78 | KSRM | 21 | 11:00 | 144 | Patuakhali | 75.5 | 21:00
13 | Banani | 47.8 | 15:00 | 79 | Kabirpur | 272 | 18:30 | 145 | Payra | 36 | 00:00
14 | Bangabhaban | 7 | 10:00 | 80 | Kachua | 103 | 22:00 | 146 | Postogola | 59 | 13:00
15 | Barapukuria | 66 | 21:00 | 81 | Kaliganj | 23 | 20:00 | 147 | Pubail | 31 | 19:00
16 | Barguna | 24 | 22:00 | 82 | Kallyanpur | 126 | 19:00 | 148 | Purbachal | 38 | 19:00
17 | Barishal | 121 | 12:00 | 83 | Kalurghat | 44 | 15:00 | 149 | Purbasadipur | 135 | 21:00
18 | Barishal-230 | 118 | 22:00 | 84 | Kamrangirchar | 93 | 13:00 | 150 | Rahanpur | 43 | 22:00
19 | Baroaulia | 74 | 12:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 35 | 18:00
20 | Baroirhat | 64 | 19:00 | 86 | Kasba | 37 | 20:00 | 152 | Rajbari | 93.5 | 22:00
21 | Bashundhara | 210 | 19:00 | 87 | Kazla | 130 | 13:00 | 153 | Rajendrapur | 131 | 12:00
22 | BashundharaCement | 8 | 19:00 | 88 | Keranigonj | 93 | 19:00 | 154 | Rajshahi | 140 | 23:00
23 | Beanibazar | 72 | 19:00 | 89 | Khagrachori | 34 | 19:00 | 155 | Rajshahi-230 | 96 | 22:00
24 | Benapole | 66 | 19:30 | 90 | Khulna | 73 | 15:00 | 156 | Ramganj | 124 | 19:00
25 | Bhaluka | 180 | 19:00 | 91 | Khulshi | 182 | 23:00 | 157 | Rampur | 46 | 21:00
26 | Bhandaria | 58 | 00:00 | 92 | Kishoreganj | 94 | 23:00 | 158 | Rangamati | 20 | 18:30
27 | Bhangura | 44 | 19:00 | 93 | Kodda | 334 | 17:00 | 159 | Rangpur | 142 | 21:00
28 | Bheramara(GK) | 77 | 19:30 | 94 | Kulaura | 46 | 23:00 | 160 | Ruppur | 2.6 | 10:00
29 | Bhulta | 224 | 22:00 | 95 | Kurigram | 62 | 21:00 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 88 | 20:00 | 96 | Kushtia | 181 | 19:30 | 162 | Saidpur | 98 | 22:00
31 | Bogura | 187 | 21:00 | 97 | Laksam | 38 | 19:00 | 163 | Santhia | 38 | 21:00
32 | Borhanuddin | 97 | 21:00 | 98 | Lakshmipur | 44 | 22:00 | 164 | Satkhira | 144 | 21:00
33 | Brahmanbaria | 128 | 22:00 | 99 | Lalbag | 84 | 19:00 | 165 | Satmasjid | 107 | 19:30
34 | Cantonment | 123 | 13:00 | 100 | Lalmonirhat | 54 | 23:00 | 166 | Savar | 226 | 19:00
35 | Chandina | 20 | 22:00 | 101 | MI_Cement | 16 | 02:00 | 167 | SevenRings | 17.34 | 09:00
36 | Chandpur | 92 | 23:00 | 102 | Madanganj | 43 | 16:00 | 168 | ShahCement | 42 | 10:00
37 | Chandraghona | 39 | 23:00 | 103 | Madaripur | 134 | 22:00 | 169 | Shahjadpur | 97 | 21:00
38 | Chapai | 81 | 22:00 | 104 | Madartek | 88 | 21:00 | 170 | Shahjibazar | 116 | 19:00
39 | Charsaidpur | 42 | 00:00 | 105 | Madunaghat | 57 | 15:00 | 171 | Shahmirpur | 54 | 00:00
40 | Chauddagram | 78 | 19:30 | 106 | Magura | 76 | 19:30 | 172 | Shariatpur | 101 | 19:00
41 | Chhatak | 35 | 23:00 | 107 | Mahasthangarh | 84 | 19:00 | 173 | Sherpur | 104 | 00:00
42 | Chowmuhani | 163 | 22:00 | 108 | Maijdee | 50 | 22:00 | 174 | Shikalbaha | 33.5 | 12:00
43 | Chuadanga | 131 | 19:00 | 109 | Manikganj | 141 | 21:00 | 175 | Shitalakhya | 87.9 | 11:00
44 | Coxsbazar | 157 | 21:00 | 110 | Maniknagar | 78 | 13:00 | 176 | Sholosohor | 48 | 16:00
45 | Cumilla(N) | 137 | 18:30 | 111 | Matarbari | 58 | 21:00 | 177 | Shomvuganj | 21 | 18:30
46 | Cumilla(S) | 184 | 19:00 | 112 | Matuail | 84 | 12:00 | 178 | Shyampur | 192 | 13:00
47 | Daganbhuiyan | 45 | 23:00 | 113 | Metrorail_Motijheel | 33 | 21:00 | 179 | Siddhirganj | 137 | 14:00
48 | Daudkandi | 162 | 20:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 132 | 20:00
49 | DhakaUniversity | 84 | 13:00 | 115 | Millgate | 110 | 15:00 | 181 | Sonargaon | 145 | 23:00
50 | Dhamrai | 130 | 19:00 | 116 | Mirpur | 165 | 19:30 | 182 | Sreemongol | 68 | 19:30
51 | Dhanmondi | 114 | 13:00 | 117 | Mirsorai | 52 | 10:00 | 183 | Sreepur | 96 | 16:00
52 | Dohazari | 107 | 12:00 | 118 | Mirzapur | 37 | 09:00 | 184 | Srinagar | 56 | 23:00
53 | Faridpur | 195 | 19:30 | 119 | Mithapukur | 60 | 21:00 | 185 | Sunamganj | 60 | 21:00
54 | Fatullah | 96 | 15:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 70 | 19:00
55 | Fenchuganj | 43 | 19:00 | 121 | Mogbazar | 113.3 | 14:00 | 187 | Sylhet-132 | 115 | 21:00
56 | Feni | 116 | 22:00 | 122 | Mongla | 50 | 15:00 | 188 | TK | 28 | 19:00
57 | GPH | 1 | 00:00 | 123 | Motijheel | 50 | 19:00 | 189 | Tangail | 194 | 18:00
58 | Ghatail | 84 | 13:00 | 124 | Muktagacha | 30 | 07:00 | 190 | Taraganj | 25 | 19:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 125 | 21:00 | 191 | Tasnim | 34 | 19:30
60 | Ghorashal-230 | 112 | 19:30 | 126 | Muradnagar | 52 | 21:00 | 192 | Thakurgaon | 106 | 21:00
61 | Goalpara | 45 | 13:00 | 127 | Mymensingh | 181 | 22:00 | 193 | Tongi | 175 | 23:00
62 | Gollamari | 114 | 20:00 | 128 | Nabinagar | 101 | 12:00 | 194 | Ullahpara | 47 | 19:00
63 | Gopalganj | 123 | 20:00 | 129 | Naogaon | 151 | 21:00 | 195 | Ullon | 48 | 19:30
64 | Gulshan | 118 | 13:00 | 130 | Narail | 66 | 19:30 | 196 | Uttara | 102 | 19:00
65 | Halishahar | 107 | 16:00 | 131 | Narinda | 75 | 13:00 | 197 | UttaraNew | 60 | 22:00
66 | HaripurSBU | 135 | 00:00 | 132 | Narshingdi | 170 | 21:00 | 198 | Zigatola | 102 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 16-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14098 | 35 |  | 14134.58
1:00 | 13650 | 24 |  | 13675
2:00 | 13221 | 0 |  | 13221
3:00 | 13023 | 0 |  | 13023
4:00 | 12718 | 0 |  | 12718
5:00 | 12446 | 0 |  | 12446
6:00 | 12211.4 | 0 |  | 12211.4
7:00 | 12456.85 | 0 |  | 12456.85
8:00 | 12340.28 | 0 |  | 12340.28
9:00 | 12316.85 | 0 |  | 12316.85
10:00 | 12417.45 | 0 |  | 12417.45
11:00 | 12766.51 | 36 |  | 12804.51
12:00 | 13333.91 | 38 |  | 13373.91
13:00 | 13801.61 | 97 |  | 13902.61
14:00 | 13967.21 | 102 |  | 14074.21
15:00 | 14276.74 | 117 |  | 14398.74
16:00 | 14375.45 | 132 |  | 14513.39
17:00 | 14435.37 | 114 |  | 14554.5
18:00 | 14347.85 | 128 |  | 14481.85
19:00 | 15488.5 | 241 |  | 15740.5
19:30 | 15962 | 418 |  | 16399
20:00 | 15810 | 516 |  | 16349
21:00 | 16412.2 | 199 |  | 16620.2
22:00 | 15808.2 | 470 |  | 16299.2
23:00 | 15229.2 | 144 |  | 15379.2
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 16-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 121 | -8 | 604 | 140 | 1366 | 362 | Ishurdi-Ghorashal Ckt-1 | Export | 3387272.73
1:00 | 126 | -10 | 612 | 134 | 1422 | 342
2:00 | 120 | -11 | 582 | 116 | 1366 | 336 |  | Import | 0
3:00 | 121 | -11 | 560 | 104 | 1356 | 306
4:00 | 131 | -6 | 574 | 108 | 1354 | 332 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 134 | -3 | 572 | 104 | 1290 | 356
6:00 | 136 | 2 | 568 | 114 | 1262 | 402 |  | Import | 0
7:00 | 127 | 0 | 528 | 118 | 1278 | 408
8:00 | 148 | 8 | 548 | 128 | 1512 | 522 | Sirajganj-Sreepur Ckt-1 | Export | 3612000
9:00 | 185 | 32 | 595 | 152 | 1624 | 636
10:00 | 186 | 35 | 600 | 176 | 1632 | 658 |  | Import | 0
11:00 | 185 | 31 | 604 | 168 | 1466 | 600
12:00 | 179 | 29 | 616 | 166 | 1334 | 540 | Sirajganj-Sreepur Ckt-2 | Export | 3617000
13:00 | 165 | 17 | 580 | 140 | 1262 | 496
14:00 | 161 | 17 | 546 | 120 | 1210 | 476 |  | Import | 0
15:00 | 157 | 17 | 556 | 124 | 1268 | 498
16:00 | 155 | 21 | 570 | 138 | 1354 | 528 | Gopalganj-Aminbazar Ckt-1 | Export | 16440000
17:00 | 135 | 20 | 524 | 136 | 1224 | 534
18:00 | 118 | 17 | 484 | 140 | 1110 | 520 |  | Import | 0
18:30 | 121 | 17 | 530 | 172 | 1190 | 508
19:00 | 105 | 5 | 494 | 134 | 1298 | 436 | Gopalganj-Aminbazar Ckt-2 | Export | 15470000
19:30 | 101 | 11 | 504 | 174 | 1248 | 426
20:00 | 134 | 23 | 566 | 154 | 1474 | 470 |  | Import | 0
21:00 | 101 | 12 | 488 | 146 | 1414 | 416
22:00 | 104 | 5 | 506 | 140 | 1438 | 358 |  | Total Export | 42526272.73
23:00 | 136 | 15 | 576 | 138 | 1472 | 406 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 16-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7565 | 6533 | 14098 | DAILY GENERATION CURVE
00:30 | 7409.5 | 6464.5 | 13874
01:00 | 7254 | 6396 | 13650 | 16-05-2026
01:30 | 7122.5 | 6313 | 13435.5
02:00 | 6991 | 6230 | 13221
02:30 | 6954.5 | 6167.5 | 13122
03:00 | 6918 | 6105 | 13023
03:30 | 6814 | 6056.5 | 12870.5
04:00 | 6710 | 6008 | 12718
04:30 | 6647.5 | 5934.5 | 12582
05:00 | 6585 | 5861 | 12446
05:30 | 6546.84 | 5781.86 | 12328.7
06:00 | 6508.68 | 5702.72 | 12211.4
06:30 | 6573.38 | 5760.745 | 12334.125
07:00 | 6638.08 | 5818.77 | 12456.85
07:30 | 6622.51 | 5776.055 | 12398.565
08:00 | 6606.94 | 5733.34 | 12340.28
08:30 | 6612.255 | 5716.31 | 12328.565
09:00 | 6617.57 | 5699.28 | 12316.85
09:30 | 6698.3 | 5668.85 | 12367.15
10:00 | 6779.03 | 5638.42 | 12417.45
10:30 | 6892.635 | 5699.345 | 12591.98
11:00 | 7006.24 | 5760.27 | 12766.51
11:30 | 7211.02 | 5839.19 | 13050.21
12:00 | 7415.8 | 5918.11 | 13333.91
12:30 | 7609.945 | 5957.815 | 13567.76
13:00 | 7804.09 | 5997.52 | 13801.61
13:30 | 7861.185 | 6023.225 | 13884.41
14:00 | 7918.28 | 6048.93 | 13967.21
14:30 | 8051.065 | 6070.91 | 14121.975
15:00 | 8183.85 | 6092.89 | 14276.74
15:30 | 8192.18 | 6133.915 | 14326.095
16:00 | 8200.51 | 6174.94 | 14375.45
16:30 | 8326.385 | 6079.025 | 14405.41
17:00 | 8452.26 | 5983.11 | 14435.37
17:30 | 8458.24 | 5933.37 | 14391.61
18:00 | 8464.22 | 5883.63 | 14347.85
18:30 | 8635.86 | 6282.315 | 14918.175
19:00 | 8807.5 | 6681 | 15488.5
19:30 | 9027 | 6935 | 15962
20:00 | 8652 | 7158 | 15810
20:30 | 8793.5 | 7317.6 | 16111.1 |  | Executive Engineer
21:00 | 8935 | 7477.2 | 16412.2 |  | Network Operation Division
21:30 | 8733.5 | 7376.7 | 16110.2
22:00 | 8532 | 7276.2 | 15808.2
22:30 | 8361.5 | 7157.2 | 15518.7
23:00 | 8191 | 7038.2 | 15229.2

## En-Curve
QF-LDC-12
Date | 16-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3752 | 1777 | 905 | 0 | 140 | 1456 | 76 | 4492 | 0 | 249 | 1230 | 0 | 0 | 21 | 35 | DAILY ENERGY CURVE
00:30 | 3741.5 | 1766.5 | 914 | 0 | 141 | 1453.5 | 75 | 4411 | 0 | 224 | 1133 | 0 | 0 | 14.5 | 29.5 | 16-05-2026
01:00 | 3731 | 1756 | 923 | 0 | 142 | 1451 | 74 | 4330 | 0 | 199 | 1036 | 0 | 0 | 8 | 24
01:30 | 3728.5 | 1729.5 | 923 | 0 | 141 | 1454.5 | 72 | 4286 | 4.5 | 153.5 | 933 | 0 | 0 | 10 | 12 | Energy Generated | 336.7976 |  | MKWHr
02:00 | 3726 | 1703 | 923 | 0 | 140 | 1458 | 70 | 4242 | 9 | 108 | 830 | 0 | 0 | 12 | 0 | Energy not Served | 2.393 |  | MKWHr
02:30 | 3722.5 | 1708 | 923 | 0 | 138 | 1456.5 | 70.5 | 4246.5 | 4.5 | 79.5 | 761 | 0 | 0 | 12 | 0 | Total Energy Requirement | 339.1906 |  | MKWHr
03:00 | 3719 | 1713 | 923 | 0 | 136 | 1455 | 71 | 4251 | 0 | 51 | 692 | 0 | 0 | 12 | 0
03:30 | 3719 | 1697.5 | 923 | 0 | 130 | 1452.5 | 72 | 4235 | 0 | 42.5 | 589.5 | 0 | 0 | 9.5 | 0
04:00 | 3719 | 1682 | 923 | 0 | 124 | 1450 | 73 | 4219 | 0 | 34 | 487 | 0 | 0 | 7 | 0
04:30 | 3717.5 | 1650.5 | 922.5 | 0 | 130 | 1445.5 | 74.5 | 4180 | 0 | 34 | 423.5 | 0 | 0 | 4 | 0
05:00 | 3716 | 1619 | 922 | 0 | 136 | 1441 | 76 | 4141 | 0 | 34 | 360 | 0 | 0 | 1 | 0
05:30 | 3733.5 | 1637 | 922.5 | 0 | 131 | 1396 | 76.5 | 4049.5 | 9.2 | 42.5 | 330.5 | 0 | 0 | 0.5 | 0
06:00 | 3751 | 1655 | 923 | 0 | 126 | 1351 | 77 | 3958 | 18.4 | 51 | 301 | 0 | 0 | 0 | 0
06:30 | 3723 | 1677.5 | 923 | 0 | 124 | 1356.5 | 77.5 | 3994 | 68.625 | 83 | 307 | 0 | 0 | 0 | 0
07:00 | 3695 | 1700 | 923 | 0 | 122 | 1362 | 78 | 4030 | 118.85 | 115 | 313 | 0 | 0 | 0 | 0
07:30 | 3663 | 1673 | 923 | 0 | 126 | 1339.5 | 78.5 | 3985.5 | 177.065 | 110.5 | 322.5 | 0 | 0 | 0 | 0
08:00 | 3631 | 1646 | 923 | 0 | 130 | 1317 | 79 | 3941 | 235.28 | 106 | 332 | 0 | 0 | 0 | 0
08:30 | 3641.5 | 1618 | 923 | 0 | 137 | 1293.5 | 79.5 | 3905 | 298.065 | 106 | 327 | 0 | 0 | 0 | 0
09:00 | 3652 | 1590 | 923 | 0 | 144 | 1270 | 80 | 3869 | 360.85 | 106 | 322 | 0 | 0 | 0 | 0
09:30 | 3663 | 1557.75 | 923 | 0 | 150 | 1242.5 | 60 | 3861.5 | 415.4 | 106 | 387.5 | 0 | 0 | 0.5 | 0
10:00 | 3674 | 1525.5 | 923 | 0 | 156 | 1215 | 40 | 3854 | 469.95 | 106 | 453 | 0 | 0 | 1 | 0
10:30 | 3683.5 | 1615.5 | 923 | 0 | 154 | 1228 | 40 | 3892 | 443.98 | 106 | 503 | 0 | 0 | 3 | 18
11:00 | 3693 | 1705.5 | 923 | 0 | 152 | 1241 | 40 | 3930 | 418.01 | 106 | 553 | 0 | 0 | 5 | 36
11:30 | 3688.5 | 1727.25 | 923 | 0 | 160 | 1282.5 | 58 | 3886.5 | 490.46 | 134.5 | 692 | 0 | 0 | 7.5 | 37
12:00 | 3684 | 1749 | 923 | 0 | 168 | 1324 | 76 | 3843 | 562.91 | 163 | 831 | 0 | 0 | 10 | 38
12:30 | 3614 | 1729.5 | 923 | 0 | 163 | 1363 | 73 | 3867.5 | 559.26 | 238.5 | 1025 | 0 | 0 | 12 | 67.5
13:00 | 3544 | 1710 | 923 | 0 | 158 | 1402 | 70 | 3892 | 555.61 | 314 | 1219 | 0 | 0 | 14 | 97
13:30 | 3540.5 | 1688.5 | 923 | 0 | 163 | 1389 | 68.5 | 3926 | 509.91 | 346.5 | 1314.5 | 0 | 0 | 15 | 99.5
14:00 | 3537 | 1667 | 923 | 0 | 168 | 1376 | 67 | 3960 | 464.21 | 379 | 1410 | 0 | 0 | 16 | 102
14:30 | 3563.5 | 1723.5 | 923 | 0 | 163 | 1390.5 | 63.5 | 4036.5 | 410.975 | 397 | 1433.5 | 0 | 0 | 17 | 109.5
15:00 | 3590 | 1780 | 923 | 0 | 158 | 1405 | 60 | 4113 | 357.74 | 415 | 1457 | 0 | 0 | 18 | 117
15:30 | 3562 | 1771 | 909.5 | 0 | 154 | 1421 | 60 | 4199 | 318.595 | 436 | 1475.5 | 0 | 0 | 19.5 | 124.5
16:00 | 3534 | 1762 | 896 | 0 | 150 | 1437 | 60 | 4285 | 279.45 | 457 | 1494 | 0 | 0 | 21 | 132
16:30 | 3544.5 | 1732.5 | 895.5 | 0 | 155 | 1424 | 60 | 4343 | 197.91 | 464 | 1571 | 0 | 0 | 18 | 123
17:00 | 3555 | 1703 | 895 | 0 | 160 | 1411 | 60 | 4401 | 116.37 | 471 | 1648 | 0 | 0 | 15 | 114
17:30 | 3563 | 1686.5 | 895 | 0 | 163 | 1384 | 60 | 4362 | 72.11 | 511.5 | 1682.5 | 0 | 0 | 12 | 121
18:00 | 3571 | 1670 | 895 | 0 | 166 | 1357 | 60 | 4323 | 27.85 | 552 | 1717 | 0 | 0 | 9 | 128
18:30 | 3604 | 1747.5 | 895 | 0 | 176 | 1409 | 60 | 4504.5 | 13.925 | 637 | 1863.75 | 0 | 0 | 7.5 | 184.5
19:00 | 3637 | 1825 | 895 | 0 | 186 | 1461 | 60 | 4686 | 0 | 722 | 2010.5 | 0 | 0 | 6 | 241
19:30 | 3667 | 1855 | 895 | 0 | 182 | 1471 | 60 | 4820 | 0 | 762 | 2247 | 0 | 0 | 3 | 418
20:00 | 3521 | 1556 | 895 | 0 | 184 | 1462 | 60 | 4903 | 0 | 819 | 2287 | 120 | 0 | 3 | 516
20:30 | 3565.5 | 1664 | 895 | 0 | 182 | 1466 | 60 | 4991.5 | 0 | 826.5 | 2315.1 | 142.5 | 0 | 3 | 357.5
21:00 | 3610 | 1772 | 895 | 0 | 180 | 1470 | 60 | 5080 | 0 | 834 | 2343.2 | 165 | 0 | 3 | 199
21:30 | 3514.5 | 1671.5 | 895 | 0 | 177 | 1458.5 | 60 | 5078.5 | 0 | 803.5 | 2285.2 | 165 | 0 | 1.5 | 334.5
22:00 | 3419 | 1571 | 895 | 0 | 174 | 1447 | 60 | 5077 | 0 | 773 | 2227.2 | 165 | 0 | 0 | 470
22:30 | 3373.5 | 1621 | 895 | 0 | 172 | 1452 | 60 | 5059.5 | 0 | 751.5 | 2015.7 | 118.5 | 0 | 0 | 307
23:00 | 3328 | 1671 | 895 | 0 | 170 | 1457 | 60 | 5042 | 0 | 730 | 1804.2 | 72 | 0 | 0 | 144
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 16-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 381 | 07:00 | 369 | 19:00 | Madunaghat | 395 | 06:00 | 389 | 23:00
Amtali | 410 | 09:00 | 402 | 23:00 | Meghnaghat | 385 | 06:00 | 373 | 19:00
Ashuganj | 393 | 05:00 | 381 | 19:00 | Payra | 411 | 08:00 | 405 | 22:00
Bhulta | 393 | 05:00 | 377 | 12:00 | Rahanpur | 402 | 06:00 | 394 | 19:30
Bibiana | 394 | 04:00 | 380 | 23:00 | Rampal | 399 | 09:00 | 292 | 16:00
BIPTC | 398 | 07:00 | 387 | 15:00
Bogura | 388 | 06:00 | 379 | 19:30
Gopalganj | 393 | 05:00 | 381 | 19:00
Kaliakoir | 388 | 12:00 | 357 | 11:00
Korerhat | 393 | 05:00 | 386 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 03:00 | 216 | 12:00 | Jhenaidah | 228 | 09:00 | 208 | 19:00
AKSML | 230 | 06:00 | 223 | 00:00 | Kachua | 225 | 18:00 | 218 | 00:00
Aminbazar | 255 | 05:00 | 217 | 11:00 | Kaliakoir | 231 | 03:00 | 218 | 11:00
Ashuganj | 228 | 04:00 | 219 | 12:00 | Keranigonj | 225 | 03:00 | 214 | 12:00
Ashuganj-400 | 228 | 04:00 | 219 | 12:00 | Khulna(S) | 228 | 09:00 | 211 | 19:00
Baghabari | 232 | 05:00 | 225 | 19:30 | Korerhat | 225 | 04:00 | 219 | 23:00
Barapukuria | 226 | 00:00 | 209 | 11:00 | Madunaghat | 230 | 06:00 | 225 | 11:00
Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat-400 | 230 | 06:00 | 227 | 00:00
Barishal | 227 | 09:00 | 219 | 19:30 | Maniknagar | 223 | 04:00 | 212 | 19:30
Bheramara | 233 | 09:00 | 222 | 19:00 | Meghnaghat | 230 | 04:00 | 221 | 23:00
Bhulta | 225 | 05:00 | 213 | 12:00 | Meghnaghat-400 | 226 | 05:00 | 217 | 19:00
Bibiana | 233 | 05:00 | 228 | 12:00 | Mirsorai | 231 | 17:00 | 224 | 14:00
BIPTC | 236 | 10:00 | 221 | 19:00 | Naogaon | 219 | 22:00 | 201 | 21:00
Bogura | 235 | 20:00 | 230 | 19:30 | Purbasadipur | 225 | 22:00 | 207 | 11:00
Bogura-400 | 235 | 23:00 | 228 | 19:30 | Rajshahi | 233 | 09:00 | 222 | 00:00
Borhanuddin | 232 | 09:00 | 225 | 23:00 | Rampal | 228 | 10:00 | 214 | 23:00
BSRM | 224 | 18:00 | 218 | 23:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 230 | 00:00 | 217 | 23:00 | Rampura | 223 | 03:00 | 211 | 12:00
Cumilla(N) | 224 | 05:00 | 217 | 12:00 | Shikalbaha | 227 | 06:00 | 223 | 11:00
Faridpur | 222 | 09:00 | 210 | 19:00 | Shyampur | 225 | 04:00 | 213 | 12:00
Fenchuganj | 235 | 04:00 | 230 | 19:00 | Siddhirganj | 224 | 05:00 | 214 | 12:00
Feni | 222 | 05:00 | 218 | 00:00 | Sirajgonj | 239 | 23:00 | 233 | 19:30
Ghorashal | 230 | 06:00 | 220 | 08:00 | Sreepur | 223 | 02:00 | 216 | 19:30
Ghorashal-230 | 224 | 03:00 | 212 | 12:00 | Tongi | 225 | 04:00 | 212 | 11:00
Gopalganj | 221 | 08:00 | 212 | 23:00
GPH | 227 | 03:00 | 222 | 23:00
Haripur | 225 | 05:00 | 214 | 12:00
Hasnabad | 224 | 02:00 | 213 | 11:00
Hathazari | 226 | 02:00 | 223 | 15:00
Ishurdi | 235 | 09:00 | 223 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 04:00 | 126 | 19:00 | Madunaghat | 133 | 06:00 | 119 | 19:00
Agargaon | 132 | 03:00 | 124 | 17:00 | Magura | 132 | 09:00 | 119 | 19:00
Agrabad | 133 | 07:00 | 13 | 07:00 | Mahasthangarh | 135 | 23:00 | 130 | 11:00
AKS | 130 | 01:00 | 127 | 12:00 | Maijdee | 125 | 17:00 | 120 | 23:00
Aminbazar | 129 | 07:00 | 122 | 18:30 | Manikganj | 132 | 13:00 | 124 | 11:00
Amnura | 136 | 20:00 | 126 | 21:00 | Maniknagar | 132 | 05:00 | 122 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 126 | 19:00 | 106 | 21:00
Ashuganj-230 | 136 | 16:00 | 132 | 12:00 | Matuail | 130 | 03:00 | 123.5 | 12:00
Bagerhat | 130 | 09:00 | 113 | 21:00 | Metrorail_Motijheel | 132 | 05:00 | 122 | 12:00
Bajitpur | 130 | 04:00 | 125 | 19:00 | Metrorail_Uttara | 131 | 01:00 | 120 | 12:00
Bakerganj | 132 | 09:00 | 127 | 23:00 | Millgate | 132 | 02:00 | 121 | 12:00
Bakulia | 134 | 07:00 | 130 | 11:00 | Mirpur | 129 | 04:00 | 121 | 12:00
Banani | 136 | 02:00 | 126 | 12:00 | Mirzapur | 130 | 13:00 | 124 | 11:00
Bangabhaban | 131 | 02:00 | 122 | 11:00 | Mithapukur | 135 | 23:00 | 125 | 11:00
Barapukuria | 134 | 00:00 | 123 | 11:00 | MI_Cement | 128.4 | 04:00 | 117 | 11:00
Barguna | 132 | 09:00 | 127 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 08:00 | 127 | 18:30 | Mogbazar | 137 | 00:00 | 124 | 16:00
Barishal-230 | 132 | 09:00 | 127 | 23:00 | Mongla | 130 | 09:00 | 113 | 19:30
Baroaulia | 132 | 05:00 | 129 | 15:00 | Motijheel | 131 | 02:00 | 122 | 12:00
Baroirhat | 129 | 14:00 | 126 | 23:00 | Muktagacha | 126 | 10:00 | 116 | 17:00
Bashundhara | 136 | 03:00 | 120 | 12:00 | Munshiganj | 127 | 01:00 | 122 | 11:00
BashundharaCement | 129 | 01:00 | 124 | 11:00 | Muradnagar | 126 | 05:00 | 120 | 19:30
Beanibazar | 131 | 06:00 | 124 | 19:00 | Mymensingh | 125 | 09:00 | 113 | 19:30
Benapole | 130 | 08:00 | 113 | 19:00 | Nabinagar | 133 | 04:00 | 118 | 12:00
Bhaluka | 130 | 23:00 | 121 | 19:30 | Naogaon | 135 | 20:00 | 32 | 06:00
Bhandaria | 132 | 09:00 | 120 | 00:00 | Narail | 133 | 09:00 | 119 | 19:00
Bhangura | 133 | 06:00 | 127 | 19:00 | Narinda | 132 | 05:00 | 122 | 12:00
Bheramara | 136 | 09:00 | 131 | 00:00 | Narshingdi | 130 | 15:00 | 117 | 19:30
Bheramara(GK) | 137 | 10:00 | 130 | 19:00 | Natore | 134 | 09:00 | 128 | 00:00
Bhulta | 125 | 02:00 | 120 | 12:00 | Nawabganj | 135 | 05:00 | 123 | 19:00
Bog-Sherpur | 134 | 05:00 | 130 | 15:00 | Netrakona | 123 | 09:00 | 109 | 19:30
Bogura | 137 | 23:00 | 132 | 13:00 | New | 133 | 04:00 | 121 | 12:00
Bogura-230 | 137 | 20:00 | 134 | 02:00 | Niamatpur | 131 | 09:00 | 124 | 21:00
Brahmanbaria | 132 | 16:00 | 124 | 00:00 | Noapara | 133 | 09:00 | 117 | 19:00
Cantonment | 132 | 03:00 | 124 | 12:00 | Pabna | 134 | 09:00 | 117 | 19:00
Chandina | 129 | 04:00 | 125 | 12:00 | Palashbari | 132 | 02:00 | 125 | 13:00
Chandpur | 132 | 17:00 | 121 | 02:00 | Panchagarh | 137 | 00:00 | 125 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 133 | 05:00 | 130 | 12:00 | Patiya | 133 | 19:00 | 128 | 21:00
Chapai | 131 | 04:00 | 126 | 16:00 | Patuakhali | 131 | 09:00 | 128 | 00:00
Charsaidpur | 129 | 04:00 | 124 | 10:00 | Payra | 135 | 09:00 | 132 | 16:00
Chauddagram | 127 | 04:00 | 124 | 23:00 | PHP | 129 | 18:00 | 126 | 00:00
Chhatak | 132 | 04:00 | 119 | 19:30 | Postogola | 130 | 02:00 | 120 | 11:00
Chowmuhani | 126 | 18:00 | 122 | 23:00 | Pubail | 135 | 03:00 | 125 | 14:00
Chuadanga | 134 | 09:00 | 115 | 23:00 | Purbachal | 137 | 04:00 | 121 | 12:00
Coxsbazar | 121 | 08:00 | 109 | 21:00 | Purbasadipur | 133 | 20:00 | 122 | 11:00
Cumilla(N) | 128 | 04:00 | 124 | 23:00 | Rahanpur | 133 | 09:00 | 129 | 21:00
Cumilla(S) | 128 | 00:00 | 121 | 14:00 | Rahanpur-400 | 133 | 06:00 | 129 | 21:00
Daganbhuiyan | 127 | 17:00 | 123 | 23:00 | Rahim | 130 | 04:00 | 124 | 12:00
Daudkandi | 124 | 02:00 | 117 | 20:00 | Rajbari | 127 | 08:00 | 117 | 19:00
DhakaUniversity | 137 | 04:00 | 126 | 12:00 | Rajendrapur | 128 | 05:00 | 120 | 19:30
Dhamrai | 134 | 03:00 | 121 | 12:00 | Rajshahi | 133 | 10:00 | 126 | 00:00
Dhanmondi | 137 | 05:00 | 126 | 19:00 | Rajshahi-230 | 134 | 09:00 | 128 | 00:00
Dohazari | 131 | 19:00 | 123 | 21:00 | Ramganj | 127 | 18:00 | 118 | 02:00
Faridpur | 129 | 09:00 | 121 | 19:00 | Rampur | 133 | 05:00 | 129 | 12:00
Fatullah | 134 | 04:00 | 118 | 11:00 | Rampura | 136 | 03:00 | 127 | 12:00
Fenchuganj | 136 | 04:00 | 131 | 19:00 | Rangamati | 138 | 10:00 | 127 | 12:00
Feni | 128 | 08:00 | 124 | 11:00 | Rangpur | 133 | 00:00 | 125 | 12:00
Feni-230 | 128 | 18:00 | 125 | 00:00 | Ruppur | 136 | 09:00 | 130 | 00:00
Ghatail | 125 | 09:00 | 117 | 23:00 | Saidpur | 133 | 00:00 | 124 | 10:00
Ghorashal | 135 | 04:00 | 129 | 10:00 | Santhia | 134 | 18:00 | 103 | 21:00
Goalpara | 134 | 09:00 | 120 | 19:00 | Satkhira | 133 | 23:00 | 113 | 21:00
Gollamari | 134 | 09:00 | 121 | 19:00 | Satmasjid | 132 | 03:00 | 123 | 19:00
Gopalganj | 131 | 09:00 | 121 | 23:00 | Savar | 130 | 03:00 | 119 | 16:00
Gopalganj-400 | 131 | 08:00 | 125 | 23:00 | SevenRings | 135 | 05:00 | 127 | 19:00
Gulshan | 135 | 05:00 | 126 | 12:00 | ShahCement | 129 | 03:00 | 124 | 10:00
Halishahar | 134 | 06:00 | 13 | 09:00 | Shahjadpur | 137 | 04:00 | 130 | 15:00
Haripur | 131 | 05:00 | 124 | 16:00 | Shahjibazar | 131 | 16:00 | 125 | 00:00
HaripurSBU | 131 | 05:00 | 123 | 20:00 | Shahmirpur | 134 | 07:00 | 131 | 11:00
Hasnabad | 129 | 03:00 | 120 | 12:00 | Shariatpur | 131 | 09:00 | 122 | 23:00
Hathazari | 134 | 07:00 | 130 | 15:00 | Sherpur | 123 | 05:00 | 110 | 23:00
Hatirjheel | 136 | 03:00 | 127 | 12:00 | Shikalbaha | 124 | 07:00 | 120 | 02:00
Ishurdi | 138 | 10:00 | 132 | 00:00 | Shikalbaha-230 | 135 | 05:00 | 132 | 12:00
Jaldhaka | 133 | 00:00 | 123 | 11:00 | Shitalakhya | 128.4 | 04:00 | 117 | 11:00
Jamalpur | 125 | 05:00 | 116 | 01:00 | Sholosohor | 132 | 02:00 | 129 | 23:00
Jashore | 130 | 09:00 | 114 | 19:00 | Shomvuganj | 128 | 10:00 | 115 | 19:30
Jhenaidah | 134 | 09:00 | 121 | 19:00 | Shyampur | 134 | 03:00 | 125 | 12:00
Jhenaidah-230 | 135 | 09:00 | 121 | 19:00 | Shyampur-230 | 135 | 05:00 | 126 | 11:00
Joydebpur | 131 | 03:00 | 122 | 11:00 | Siddhirganj | 130 | 04:00 | 124 | 12:00
Joypurhat | 132 | 20:00 | 127 | 19:30 | Sirajganj | 133 | 05:00 | 126 | 15:00
Juldah | 133 | 01:00 | 130 | 12:00 | Sonargaon | 128 | 04:00 | 122 | 10:00
Kabirpur | 134 | 13:00 | 116 | 12:00 | Sreemongol | 132 | 07:00 | 126 | 00:00
Kachua | 128 | 18:00 | 123 | 02:00 | Sreepur | 130 | 05:00 | 122 | 19:00
Kaliakoir | 137 | 03:00 | 128 | 11:00 | Srinagar | 132 | 03:00 | 124 | 17:00
Kaliganj | 134 | 09:00 | 120 | 19:00 | SSM | 138 | 08:00 | 132 | 11:00
Kallyanpur | 129 | 05:00 | 121 | 23:00 | Sunamganj | 131 | 06:00 | 118 | 19:00
Kalurghat | 133 | 03:00 | 130 | 11:00 | Sylhet | 133 | 07:00 | 125 | 19:00
Kamrangirchar | 132 | 03:00 | 120 | 10:00 | Sylhet-132 | 131 | 06:00 | 125 | 21:00
Kaptai | N/A | N/A | N/A | N/A | Tangail | 127 | 10:00 | 118 | 18:30
Kasba | 125 | 02:00 | 119 | 23:00 | Taraganj | 133 | 00:00 | 123 | 11:00
Kazla | 131 | 03:00 | 121 | 13:00 | Tasnim | 128 | 05:00 | 122 | 11:00
Keranigonj | 133 | 03:00 | 125 | 17:00 | Thakurgaon | 137 | 00:00 | 124 | 10:00
Khagrachori | 130 | 06:00 | 25 | 13:00 | TK | 133 | 04:00 | 130 | 11:00
Khulna | 133 | 10:00 | 118 | 19:00 | Tongi | 134 | 04:00 | 124 | 15:00
Khulna(S) | 134 | 09:00 | 121 | 19:00 | Ullahpara | 132 | 04:00 | 127 | 15:00
Khulshi | 132 | 06:00 | 128 | 12:00 | Ullon | 136 | 05:00 | 126 | 12:00
Kishoreganj | 128 | 04:00 | 122 | 18:30 | Uttara | 131 | 02:00 | 30 | 06:00
Kodda | 134 | 16:00 | 124 | 11:00 | UttaraNew | 131 | 01:00 | 120 | 12:00
Korerhat | 134 | 04:00 | 129 | 00:00 | Zigatola | 133 | 05:00 | 125 | 12:00
KSRM | 133 | 07:00 | 129 | 11:00
Kulaura | 135 | 06:00 | 130 | 19:00
Kurigram | 132 | 01:00 | 119 | 11:00
Kushtia | 135 | 10:00 | 125 | 19:00
Laksam | 127 | 13:00 | 123 | 00:00
Lakshmipur | 125 | 18:00 | 120 | 00:00
Lalbag | 132 | 04:00 | 124 | 12:00
Lalmonirhat | 132 | 01:00 | 119 | 11:00
Madanganj | 129 | 01:00 | 124 | 11:00
Madaripur | 132 | 09:00 | 125 | 19:00
Madartek | 136 | 03:00 | 126 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division