## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 18-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-05-2026 | during | 18-05-2026 | during | 18-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 378 | 367 | 412 | 412 | 392 | 392 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 52 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 304 | 296 | 335 | 335 | 315 | 315 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 7 | 7 | 7 | 7 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 17 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 147 | 149.36 | 149.36 | 90 | 128 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 18 | 18 | 33 | 33 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 22 | 22 | 14 | 14 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 42 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 210 | 277 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 93 | 115 | 149 | 149 | 133 | 133 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 162 | 162 | 18 | 36 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 23 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 16 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 455 | 415 | 584 | 584 | 500 | 500 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 304 | 253 | 718 | 718 | 335 | 335 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 40 | 142 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2050 | 2475 | 5954.22 | 5922.22 | 2525.19 | 2654.19
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 0 | 17 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 60 | 55 | 60 | 60 | 60 | 60 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 216 | 215 | 215 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 67 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 39 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 32 | 0 | 0 | 0 | 51 | plant availability zero
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 16 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 18 | 48 | 108 | 108 | 18 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0.83 | 0 | 4.87 | 0 | 4.87 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 50 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 15 | 116 | 116 | 92 | 92 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 33 | 145 | 163 | 163 | 147 | 147 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1166 | 1224 | 1224 | 1224 | 1204 | 1204 | U2 on AGC
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 8 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 950 | 1000 | 930 | 1000 | 1010 | 1010 | AGC
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2490.83 | 2965 | 3737.73 | 3814.86 | 3072.23 | 3167.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 192 | 0 | 221 | 221 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 100 | 356 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 345 | 345 | 342.01 | 342.01 | 342.01 | 342.01 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 385 | 300 | 393 | 393 | 270 | 270 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 33 | 30 | 41.65 | 41.65 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 5 | 46 | 52.82 | 52.82 | 30 | 30 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 16 | 0 | 195 | 195 | 100 | 100 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 33 | 147 | 150 | 150 | 25 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 23 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 144 | 146 | 163 | 163 | 140 | 140 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 99 | 188 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 156 | 172 | 84 | 80 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 18 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 108 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 16 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 69 | 115 | 115 | 17 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 73 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1670 | 2015 | 2749.19 | 2690.19 | 2100.27 | 2230.27
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-05-2026 | during | 18-05-2026 | during | 18-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.4 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 77 | 87 | 90 | 90 | 90 | 90 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 9 | 10 | 10 | 10 | 10 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 53.8 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 151.2 | 125 | 381 | 334 | 201.5 | 129
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 143 | 163 | 163 | 147 | 147 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 152 | 153 | 150 | 150 | 100 | 100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 85 | 83 | 83 | 86 | 86 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 102 | 101 | 102 | 102 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 245 | 327 | 250 | 250 | 340 | 340 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1164 | 1238 | 1216 | 1216 | 1199 | 1199
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 908 | 907 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 28 | 30 | 30 | 30 | 30 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 27 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 166 | 144 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 81.86 | 0 | 92 | 0 | 92 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 587 | 585 | 617.1 | 617.1 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1742.86 | 1706 | 2969.1 | 2877.1 | 2653.1 | 2561.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 502 | 664 | 660 | 900 | 602 | 602 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 32 | 110 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1015 | 1220 | 1244 | 1244 | 1184 | 1184 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 17 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 277 | 276 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.34 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2166.34 | 2664 | 2822 | 3061 | 2551 | 2587
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 42.78 | 0 | 48 | 0 | 48 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 33 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 165 | 150 | 214 | 214 | 180 | 180 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 160 | 170 | 220 | 220 | 0 | 0 | Liquid fuel shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 180 | 180 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 400 | 362 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 26 | 26 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 7.5 | 83 | 85 | 85 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1325.29 | 1457.93 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 58.94 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2259.51 | 2585.93 | 3211.72 | 2996.87 | 2706.17 | 2576.32
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 48 | 50 | 50 | 50 | 50 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 99 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.6 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 35 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 21 | 0 | 0 | 0 | 0 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 83 | 0 | 181.23 | 0 | 181.23 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 157.6 | 427 | 485.23 | 298 | 385.23 | 278
System Total |  |  |  |  | 28823.2 | 29270.237 | 13852.34 | 16200.93 | 23526.19 | 23210.24 | 17393.69 | 17382.24
Forecast Scenario (18-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15500 |  | 0 |  | 15500
|  |  |  | 1:00 | 14860 |  | 0 |  | 14860
|  |  |  | 2:00 | 14470 |  | 0 |  | 14470
|  |  |  | 3:00 | 14080 |  | 0 |  | 14080
|  |  |  | 4:00 | 13570 |  | 0 |  | 13570
|  |  |  | 5:00 | 13240 |  | 0 |  | 13240
|  |  |  | 6:00 | 13200 |  | 0 |  | 13200
|  |  |  | 7:00 | 13380 |  | 0 |  | 13380
|  |  |  | 8:00 | 13370 |  | 0 |  | 13370
|  |  |  | 9:00 | 13730 |  | 0 |  | 13730
|  |  |  | 10:00 | 13790 |  | 0 |  | 13790
|  |  |  | 11:00 | 14140 |  | 0 |  | 14140
|  |  |  | 12:00 | 14200 |  | 0 |  | 14200
|  |  |  | 13:00 | 14560 |  | 0 |  | 14560
|  |  |  | 14:00 | 14770 |  | 0 |  | 14770
|  |  |  | 15:00 | 15120 |  | 0 |  | 15120
|  |  |  | 16:00 | 15180 |  | 0 |  | 15180
|  |  |  | 17:00 | 15100 |  | 0 |  | 15100
|  |  |  | 18:00 | 15440 |  | 0 |  | 15440
|  |  |  | 18:30 | 15900 |  | 0 |  | 15900
|  |  |  | 19:00 | 16450 |  | 0 |  | 16450
|  |  |  | 19:30 | 16700 |  | 0 |  | 16700
|  |  |  | 20:00 | 16660 |  | 0 |  | 16660
|  |  |  | 21:00 | 16650 |  | 0 |  | 16650
|  |  |  | 22:00 | 16500 |  | 0 |  | 16500
|  |  |  | 23:00 | 16050 |  | 0 |  | 16050
Probable Maximum Temperature: |  |  | 35.00°C
Probable Maximum Demand at Day Peak: |  |  | 14200.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16700.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16400.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 347.2382 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:12 hrs on 18-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 17-05-2026 | [28 empty] | Date: | 17-05-2026 | [28 empty] | Date: | 17-05-2026 | [28 empty] | Date: | 17-05-2026 | [28 empty] | Date: | 17-05-2026 | [17 empty] | Date: | 17-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [17 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 278 | 0 | 0 | 132 | 129 | 293 | 55 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 142 | 18 | 14 | 0 | 430 | 0 | 0 | 32 | 0 | 0 | 49 | 29 | 2 | 0 | 0 | 0 | 60 | 16 | 20 | 1120 | 141 | 0 | 19 | 0 | 56 | 217 | 0 | 0 | 0 | 1160 | 0 | 26 | 73 | 393 | 0 | 300 | 51 | 6 | 192 | 36 | 34 | 30 | 185 | 0 | 19 | 107 | 168 | 0 | 0 | 24 | 315 | 0 | 332 | 42 | 30 | 154 | 0 | 17 | 0 | 83 | 30 | 153 | 0 | 103 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 8281 | 896 | 146 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 591 | 0 | 0 | 0 | 1456 | 0 | 32 | 0 | 100 | 113 | 0 | 85 | 21 | 52.2 | 0 | 0 | 26 | 0 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 49 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 307 | 118 | 220 | 0 | 450 | 1195 | 35 | 6914.2 | 15195.2 | 76.11
01:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 217 | 0 | 0 | 132 | 90 | 293 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 105 | 18 | 14 | 0 | 365 | 12 | 15 | 19 | 0 | 0 | 28 | 29 | 17 | 0 | 0 | 0 | 60 | 14 | 20 | 1041 | 95 | 0 | 19 | 0 | 66 | 217 | 0 | 0 | 0 | 1160 | 0 | 26 | 73 | 393 | 0 | 300 | 51 | 5 | 188 | 33 | 0 | 30 | 173 | 0 | 19 | 70 | 162 | 0 | 0 | 24 | 310 | 0 | 232 | 42 | 30 | 131 | 0 | 17 | 0 | 83 | 28 | 152 | 0 | 103 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 7644 | 895 | 147 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 584 | 0 | 0 | 0 | 1436 | 0 | 32 | 0 | 113 | 113 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 49 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 284 | 118 | 220 | 0 | 400 | 1100 | 17 | 6467 | 14111 | 76.09
02:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 280 | 0 | 0 | 132 | 0 | 293 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 34 | 18 | 14 | 0 | 450 | 15 | 15 | 18 | 0 | 2 | 0 | 0 | 17 | 0 | 0 | 0 | 60 | 16 | 27 | 956 | 0 | 0 | 19 | 0 | 65 | 218 | 0 | 0 | 0 | 1160 | 0 | 26 | 73 | 393 | 0 | 300 | 51 | 5 | 191 | 33 | 0 | 20 | 68 | 0 | 14 | 0 | 158 | 0 | 0 | 0 | 310 | 0 | 232 | 42 | 30 | 139 | 0 | 17 | 0 | 83 | 28 | 153 | 0 | 103 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 7136 | 895 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588 | 0 | 0 | 0 | 1426 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 52 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 258 | 118 | 220 | 0 | 400 | 1010 | 17 | 6054 | 13190 | 76.07
03:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 302 | 0 | 0 | 130 | 0 | 160 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 0 | 18 | 14 | 0 | 460 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 16 | 27 | 916 | 0 | 0 | 19 | 0 | 64 | 219 | 0 | 0 | 0 | 1165 | 0 | 26 | 73 | 393 | 0 | 300 | 51 | 5 | 193 | 33 | 0 | 25 | 0 | 0 | 14 | 0 | 156 | 0 | 0 | 0 | 315 | 0 | 232 | 42 | 30 | 147 | 0 | 17 | 0 | 83 | 28 | 153 | 0 | 104 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 6805 | 765 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 0 | 0 | 0 | 1445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 140 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 259 | 118 | 220 | 0 | 400 | 990 | 0 | 5725 | 12530 | 76.05
04:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 221 | 0 | 0 | 50 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 0 | 18 | 14 | 0 | 360 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 15 | 28 | 838 | 0 | 0 | 19 | 0 | 40 | 219 | 0 | 0 | 0 | 1078 | 0 | 0 | 73 | 393 | 178 | 300 | 51 | 5 | 190 | 33 | 0 | 25 | 0 | 0 | 14 | 0 | 154 | 0 | 0 | 0 | 315 | 0 | 232 | 42 | 30 | 143 | 0 | 17 | 0 | 83 | 28 | 151 | 0 | 102 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 6310 | 765 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576 | 0 | 0 | 0 | 1408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 140 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 118 | 220 | 0 | 446 | 1000 | 0 | 5522 | 11832 | 76.03
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 244 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 385 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 30 | 847 | 0 | 0 | 19 | 0 | 0 | 219 | 0 | 0 | 0 | 840 | 0 | 0 | 16 | 260 | 200 | 240 | 51 | 5 | 181 | 33 | 0 | 25 | 0 | 0 | 14 | 0 | 150 | 0 | 0 | 0 | 310 | 0 | 232 | 42 | 30 | 127 | 0 | 17 | 0 | 83 | 30 | 152 | 0 | 103 | 0 | 9 | 16 | 0 | 0 | 0 | 0 | 5646 | 765 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 0 | 1254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 140 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 100 | 180 | 0 | 372 | 890 | 0 | 4982 | 10628 | 76.01
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 242 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 2 | 0 | 3 | 14 | 0 | 405 | 0 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0.33 | 60 | 0 | 31 | 840 | 0 | 0 | 19 | 0 | 0 | 219 | 0 | 0 | 0 | 722 | 1 | 0 | 16 | 260 | 200 | 240 | 51 | 5 | 178 | 33 | 0 | 25 | 0 | 0 | 0 | 0 | 124 | 0 | 5 | 0 | 305 | 0 | 232 | 42 | 30 | 130 | 0 | 17 | 0 | 83 | 30 | 153 | 0 | 102 | 0 | 9 | 8 | 0 | 0 | 0.74 | 0 | 5460.07 | 907 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 388 | 0 | 0 | 0 | 1181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.49 | 0 | 0 | 0 | 0 | 165 | 0 | 140 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.04 | 0 | 140 | 100 | 180 | 0 | 288 | 780 | 0 | 4863.53 | 10323.6 | 75.99
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 301 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 331 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 450 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.23 | 60 | 0 | 28 | 865 | 0 | 0 | 19 | 0 | 0 | 219 | 0 | 0 | 0 | 623 | 5 | 0 | 16 | 260 | 130 | 240 | 51 | 5 | 180 | 33 | 0 | 150 | 0 | 0 | 5 | 0 | 130 | 0 | 16 | 0 | 305 | 0 | 284 | 42 | 30 | 150 | 2 | 0 | 0 | 83 | 30 | 153 | 0 | 102 | 0 | 9 | 8 | 0 | 0.25 | 1.69 | 0 | 5749.17 | 907 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 387 | 0 | 0 | 0 | 1221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8 | 29 | 0 | 0 | 5.58 | 165 | 0 | 140 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 5 | 0.19 | 0 | 164 | 120 | 220 | 0 | 330 | 760 | 0 | 5087.87 | 10837.04 | 75.97
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 460 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.37 | 60 | 0 | 9 | 856 | 0 | 0 | 19 | 0 | 0 | 217 | 0 | 0 | 0 | 625 | 10 | 0 | 16 | 260 | 20 | 240 | 51 | 5 | 191 | 33 | 0 | 150 | 0 | 0 | 5 | 0 | 136 | 0 | 33 | 0 | 310 | 0 | 284 | 42 | 30 | 149 | 3 | 0 | 0 | 83 | 30 | 151 | 0 | 102 | 0 | 9 | 15 | 0 | 0.15 | 9.31 | 0 | 5642.83 | 908 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 425 | 0 | 0 | 0 | 1231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.43 | 50 | 0 | 0 | 24.45 | 165 | 0 | 140 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0.31 | 0 | 201 | 120 | 220 | 0 | 382 | 810 | 0 | 5358.09 | 11000.92 | 75.95
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 286 | 0 | 0 | 0 | 0 | 0 | 15 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 22 | 0 | 18.5 | 14 | 0 | 475 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.36 | 60 | 0 | 2 | 870 | 0 | 0 | 19 | 0 | 0 | 216 | 0 | 0 | 0 | 660 | 13 | 0 | 16 | 260 | 18 | 240 | 51 | 5 | 186 | 33 | 0 | 148 | 0 | 0 | 0 | 0 | 140 | 0 | 54 | 0 | 315 | 0 | 257 | 42 | 30 | 151 | 7 | 0 | 0 | 80 | 30 | 155 | 0 | 102 | 0 | 46 | 35 | 0 | 0.46 | 22.6 | 0 | 5810.92 | 908 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.76 | 450 | 0 | 0 | 0 | 1235.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.82 | 67 | 0 | 0 | 37.25 | 165 | 0 | 140 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 158 | 0.27 | 0 | 199 | 120 | 220 | 0 | 438 | 820 | 0 | 5671.56 | 11482.48 | 75.95
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 305 | 0 | 0 | 10 | 0 | 0 | 15 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 25 | 0 | 18.5 | 14 | 0 | 455 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.94 | 60 | 0 | 3 | 935 | 0 | 0 | 19 | 0 | 0 | 216 | 0 | 0 | 0 | 967 | 17 | 0 | 16 | 300 | 18 | 345 | 51 | 5 | 191 | 34 | 0 | 149 | 0 | 0 | 5 | 0 | 140 | 0 | 21 | 0 | 315 | 0 | 245 | 42 | 30 | 154 | 4 | 17 | 0 | 83 | 30 | 154 | 0 | 102 | 0 | 57 | 35 | 0 | 0.91 | 21.72 | 0 | 6359.07 | 907 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.49 | 513 | 0 | 0 | 0 | 1221.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.93 | 93 | 0 | 0 | 19.88 | 165 | 0 | 140 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 48 | 0 | 24 | 0 | 0 | 0 | 0 | 6.3 | 201 | 0.29 | 0 | 199 | 120 | 220 | 0 | 471 | 890 | 0 | 5922.94 | 12282.01 | 75.93
11:00 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 295 | 17 | 0 | 30 | 15 | 45 | 15 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 32 | 12 | 18.5 | 14 | 0 | 435 | 0 | 0 | 19 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 3 | 965 | 3 | 0 | 19 | 0 | 0 | 212 | 0 | 0 | 0 | 1165 | 11 | 11 | 16 | 320 | 68 | 345 | 51 | 5 | 185 | 33 | 5 | 146 | 22 | 7 | 6 | 0 | 142 | 0 | 76 | 0 | 310 | 0 | 245 | 42 | 30 | 154 | 8 | 17 | 0 | 80 | 30 | 154 | 0 | 102 | 0 | 19 | 75 | 0 | 2.2 | 54.13 | 0 | 6884.83 | 908 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.71 | 582 | 0 | 0 | 0 | 1215.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.96 | 87 | 0 | 0 | 56.51 | 165 | 0 | 140 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 47 | 0 | 20 | 0 | 0 | 0 | 0 | 7.3 | 36 | 0.34 | 0 | 247 | 120 | 220 | 0 | 486 | 980 | 0 | 6013.86 | 12898.69 | 75.92
12:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 304 | 17 | 0 | 93 | 15 | 210 | 52 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 23 | 40 | 18 | 14 | 0 | 455 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0.83 | 60 | 0 | 4 | 950 | 33 | 0 | 19 | 0 | 0 | 214 | 0 | 0 | 0 | 1166 | 18 | 33 | 16 | 385 | 100 | 345 | 51 | 5 | 192 | 33 | 17 | 144 | 99 | 9 | 12 | 0 | 156 | 0 | 73 | 0 | 305 | 0 | 245 | 42 | 30 | 155 | 4 | 17 | 0 | 82 | 30 | 152 | 0 | 102 | 0 | 19 | 77 | 0 | 1.4 | 53.8 | 0 | 7526.03 | 908 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.86 | 587 | 0 | 0 | 0 | 1325.29 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 42.78 | 100 | 0 | 0 | 58.94 | 165 | 0 | 160 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 48 | 0 | 21 | 0 | 0 | 0 | 0 | 5.6 | 83 | 0.34 | 32 | 277 | 120 | 220 | 0 | 502 | 1015 | 0 | 6326.31 | 13852.34 | 75.92
13:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 262 | 17 | 0 | 97 | 60 | 210 | 55 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 11 | 295 | 0 | 0 | 32 | 76 | 10 | 14 | 0 | 418 | 0 | 0 | 17 | 0 | 13 | 0 | 15 | 0 | 0 | 0 | 0 | 60 | 0 | 8 | 930 | 65 | 0 | 19 | 0 | 25 | 213 | 0 | 0 | 0 | 1160 | 17 | 33 | 16 | 393 | 120 | 345 | 51 | 5 | 192 | 33 | 17 | 142 | 160 | 9 | 17 | 65 | 164 | 0 | 73 | 23 | 305 | 0 | 232 | 42 | 30 | 146 | 12 | 17 | 0 | 83 | 30 | 154 | 0 | 102 | 0 | 19 | 77 | 0 | 1.29 | 21.26 | 0 | 7721.55 | 907 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.58 | 588 | 0 | 0 | 0 | 1445.56 | 0 | 0 | 0 | 0 | 4 | 0 | 7.5 | 0 | 0 | 14.32 | 69 | 0 | 0 | 55.89 | 165 | 0 | 167 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 48 | 0 | 16 | 49 | 0 | 0 | 0 | 5 | 130 | 0.67 | 100 | 277 | 120 | 220 | 0 | 534 | 1090 | 9 | 6605.52 | 14327.07 | 75.9
14:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 251 | 0 | 6 | 105 | 60 | 260 | 55 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 35 | 301 | 0 | 0 | 14 | 86 | 15 | 14 | 0 | 455 | 0 | 0 | 17 | 0 | 6 | 0 | 29 | 0 | 0 | 0 | 2.67 | 60 | 0 | 5 | 895 | 65 | 0 | 19 | 0 | 51 | 212 | 0 | 0 | 0 | 1160 | 16 | 33 | 16 | 393 | 135 | 345 | 51 | 5 | 189 | 27 | 16 | 142 | 171 | 9 | 18 | 64 | 170 | 0 | 34 | 26 | 310 | 0 | 232 | 42 | 30 | 136 | 10 | 17 | 0 | 81 | 30 | 155 | 0 | 102 | 0 | 19 | 77 | 0 | 2.12 | 28.6 | 0 | 7789.39 | 907 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 50.22 | 588 | 0 | 0 | 0 | 1447.6 | 0 | 0 | 0 | 0 | 28 | 0 | 15 | 0 | 0 | 41.06 | 92 | 0 | 0 | 43.51 | 165 | 0 | 163 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 48 | 0 | 29 | 67 | 0 | 0 | 0 | 4.2 | 168 | 0.32 | 110 | 277 | 120 | 220 | 0 | 555 | 1040 | 17 | 6714.91 | 14504.3 | 75.89
15:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 322 | 0 | 17 | 105 | 60 | 276 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 35 | 313 | 0 | 0 | 19 | 86 | 18 | 14 | 0 | 485 | 0 | 0 | 18 | 0 | 9 | 0 | 28 | 0 | 0 | 0 | 3.08 | 60 | 0 | 2 | 940 | 65 | 0 | 19 | 0 | 51 | 211 | 0 | 0 | 0 | 1175 | 11 | 35 | 16 | 388 | 148 | 340 | 51 | 7 | 110 | 33 | 17 | 142 | 180 | 8 | 18 | 66 | 170 | 0 | 22 | 23 | 310 | 0 | 232 | 42 | 30 | 150 | 6 | 8 | 0 | 81 | 30 | 152 | 0 | 101 | 3 | 19 | 77 | 0 | 0.89 | 34.55 | 0 | 7956.52 | 908 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 45.05 | 584 | 0 | 0 | 0 | 1461.33 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 26.7 | 57 | 0 | 0 | 29.9 | 165 | 0 | 173 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 48 | 0 | 15 | 69 | 0 | 0 | 0 | 0.8 | 135 | 0.35 | 110 | 282 | 120 | 220 | 0 | 613 | 1032 | 17 | 6708.13 | 14664.65 | 75.88
16:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 303 | 0 | 17 | 99 | 60 | 276 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 13 | 86 | 18 | 14 | 0 | 450 | 0 | 0 | 18 | 0 | 9 | 0 | 31 | 0 | 0 | 0 | 1.79 | 60 | 0 | 5 | 970 | 64 | 0 | 19 | 0 | 50 | 212 | 0 | 0 | 0 | 1165 | 8 | 33 | 16 | 392 | 221 | 342 | 51 | 40 | 0 | 30 | 17 | 142 | 192 | 8 | 18 | 66 | 170 | 0 | 30 | 23 | 310 | 0 | 232 | 42 | 30 | 152 | 5 | 17 | 0 | 81 | 30 | 151 | 0 | 102 | 17 | 19 | 87 | 0 | 1 | 17.55 | 0 | 7906.34 | 907 | 139 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 15 | 26.27 | 585 | 0 | 0 | 0 | 1455.54 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 12.85 | 41 | 0 | 0 | 23.26 | 130 | 0 | 174 | 0 | 0 | 0 | 394 | 0 | 2.19 | 0 | 48 | 0 | 7 | 69 | 0 | 0 | 0 | 1.5 | 85 | 0.29 | 110 | 277 | 120 | 220 | 0 | 630 | 1038 | 17 | 6565.9 | 14472.24 | 75.87
17:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 259 | 0 | 17 | 114 | 60 | 276 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 7 | 124 | 18 | 14 | 0 | 450 | 0 | 0 | 20 | 0 | 4 | 0 | 35 | 0 | 0 | 0 | 0.83 | 55 | 0 | 4 | 905 | 63 | 0 | 19 | 0 | 51 | 215 | 0 | 0 | 0 | 1165 | 3 | 33 | 16 | 380 | 352 | 342 | 51 | 45 | 0 | 30 | 26 | 143 | 193 | 8 | 18 | 65 | 172 | 0 | 10 | 23 | 310 | 0 | 232 | 42 | 30 | 142 | 1 | 17 | 0 | 85 | 30 | 153 | 0 | 102 | 17 | 9 | 86 | 0 | 0.12 | 10.75 | 8 | 7929.7 | 908 | 137 | 0 | 6 | 10 | 0 | 0 | 0 | 0 | 0 | 15 | 21.01 | 588 | 0 | 0 | 0 | 1450.3 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 5.86 | 10 | 0 | 0 | 4.82 | 130 | 0 | 170 | 0 | 0 | 0 | 378 | 0 | 0.42 | 0 | 48 | 0 | 5 | 69 | 0 | 0 | 0 | 0 | 44 | 0.16 | 110 | 280 | 120 | 220 | 0 | 627 | 1148 | 17 | 6557.57 | 14487.27 | 75.86
18:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 269 | 0 | 17 | 115 | 60 | 276 | 55 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 142 | 18 | 14 | 0 | 425 | 0 | 0 | 28 | 0 | 7 | 0 | 35 | 0 | 0 | 0 | 0.09 | 55 | 0 | 9 | 890 | 64 | 0 | 36 | 1 | 50 | 214 | 0 | 0 | 0 | 1166 | 0 | 33 | 0 | 305 | 350 | 345 | 51 | 45 | 0 | 33 | 34 | 144 | 195 | 15 | 18 | 66 | 162 | 0 | 2 | 23 | 315 | 0 | 233 | 42 | 30 | 140 | 0 | 17 | 0 | 85 | 30 | 154 | 0 | 102 | 17 | 9 | 87 | 0 | 0.08 | 0.44 | 9 | 7912.61 | 908 | 139 | 0 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 15 | 2.65 | 587 | 0 | 0 | 0 | 1455.99 | 0 | 0 | 0 | 15 | 35 | 0 | 48 | 16 | 16 | 1.76 | 2 | 26 | 0 | 1.25 | 130 | 0 | 170 | 0 | 0 | 0 | 350 | 0 | 0.11 | 0 | 47 | 40 | 1 | 70 | 0 | 0 | 0 | 0.2 | 9 | 0.02 | 110 | 277 | 120 | 220 | 0 | 591 | 1080 | 17 | 6526.98 | 14439.59 | 75.85
19:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 277 | 35 | 17 | 115 | 129 | 260 | 55 | 17 | 107 | 0 | 0 | 0 | 0 | 0 | 35 | 296 | 0 | 0 | 0 | 142 | 18 | 14 | 0 | 410 | 1 | 0 | 35 | 0 | 5 | 49 | 39 | 0 | 0 | 0 | 0 | 55 | 12 | 3 | 1000 | 90 | 0 | 46 | 8 | 51 | 214 | 0 | 0 | 0 | 1224 | 0 | 102 | 0 | 290 | 356 | 345 | 51 | 45 | 0 | 33 | 46 | 146 | 184 | 11 | 18 | 114 | 168 | 0 | 0 | 23 | 315 | 0 | 290 | 42 | 30 | 136 | 0 | 17 | 0 | 85 | 30 | 153 | 0 | 101 | 17 | 9 | 87 | 0 | 0 | 0 | 12 | 8528 | 908 | 142 | 0 | 11 | 23 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 587 | 0 | 0 | 0 | 1452.52 | 0 | 0 | 0 | 90 | 54 | 0 | 92 | 25 | 52 | 0 | 0 | 26 | 0 | 0 | 130 | 0 | 170 | 0 | 0 | 0 | 388 | 0 | 0 | 0 | 47 | 110 | 0 | 82 | 0 | 120 | 0 | 0 | 0 | 0 | 109 | 277 | 120 | 220 | 0 | 598 | 1015 | 54 | 6917.52 | 15445.52 | 75.84
19:30 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 245 | 35 | 17 | 115 | 129 | 275 | 55 | 17 | 108 | 0 | 0 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 142 | 18 | 14 | 0 | 405 | 15 | 0 | 38 | 0 | 6 | 49 | 39 | 0 | 0 | 0 | 0 | 55 | 34 | 3 | 1000 | 152 | 0 | 50 | 8 | 68 | 216 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 300 | 350 | 280 | 51 | 45 | 0 | 33 | 69 | 146 | 190 | 18 | 18 | 114 | 178 | 0 | 0 | 23 | 320 | 0 | 344 | 42 | 30 | 136 | 0 | 17 | 0 | 85 | 30 | 154 | 0 | 101 | 17 | 9 | 87 | 0 | 0 | 0 | 12 | 8710 | 907 | 142 | 0 | 11 | 23 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 587 | 0 | 0 | 0 | 1453.27 | 0 | 0 | 0 | 113 | 80 | 0 | 83 | 25 | 52 | 0 | 0 | 26 | 0 | 0 | 130 | 0 | 170 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 47 | 115 | 0 | 97 | 0 | 70 | 0 | 0 | 0 | 0 | 110 | 277 | 120 | 180 | 0 | 617 | 1140 | 54 | 6995.27 | 15705.27 | 75.83
20:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 289 | 35 | 0 | 115 | 129 | 277 | 55 | 35 | 108 | 0 | 0 | 0 | 0 | 0 | 35 | 302 | 0 | 0 | 0 | 142 | 18 | 14 | 0 | 435 | 15 | 0 | 38 | 0 | 3 | 32 | 39 | 0 | 0 | 0 | 0 | 55 | 45 | 5 | 1000 | 146 | 0 | 50 | 8 | 65 | 216 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 320 | 358 | 345 | 51 | 45 | 0 | 33 | 69 | 146 | 187 | 16 | 18 | 110 | 184 | 0 | 0 | 23 | 310 | 0 | 345 | 42 | 30 | 139 | 0 | 17 | 0 | 85 | 28 | 152 | 0 | 101 | 17 | 9 | 86 | 0 | 0 | 0 | 12 | 8862 | 907 | 144 | 0 | 18 | 25 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 588 | 0 | 0 | 0 | 1452.68 | 0 | 32 | 0 | 113 | 110 | 0 | 83 | 25 | 52 | 0 | 0 | 26 | 0 | 0 | 150 | 0 | 170 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 48 | 115 | 0 | 96 | 0 | 165 | 0 | 0 | 0 | 0 | 110 | 276 | 120 | 220 | 0 | 623 | 1170 | 54 | 7289.68 | 16151.68 | 75.82
21:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 253 | 35 | 16 | 115 | 147 | 277 | 55 | 35 | 108 | 0 | 0 | 0 | 0 | 0 | 35 | 296 | 0 | 0 | 0 | 142 | 18 | 14 | 0 | 415 | 15 | 0 | 48 | 0 | 0 | 32 | 39 | 0 | 0 | 0 | 0 | 55 | 50 | 16 | 1000 | 145 | 0 | 50 | 8 | 67 | 216 | 0 | 0 | 0 | 1224 | 0 | 147 | 0 | 300 | 356 | 345 | 51 | 46 | 0 | 30 | 69 | 146 | 188 | 16 | 18 | 108 | 172 | 0 | 0 | 23 | 310 | 0 | 327 | 42 | 30 | 143 | 0 | 17 | 0 | 85 | 30 | 153 | 0 | 101 | 17 | 9 | 87 | 0 | 0 | 0 | 12 | 8818 | 907 | 144 | 0 | 28 | 27 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 585 | 0 | 0 | 0 | 1457.93 | 0 | 33 | 0 | 113 | 113 | 0 | 83 | 26 | 52 | 0 | 0 | 26 | 0 | 0 | 150 | 0 | 170 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 48 | 115 | 0 | 99 | 0 | 165 | 0 | 0 | 0 | 0 | 110 | 276 | 120 | 220 | 0 | 664 | 1220 | 54 | 7382.93 | 16200.93 | 75.81
22:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 278 | 35 | 17 | 115 | 110 | 277 | 55 | 35 | 108 | 0 | 0 | 0 | 0 | 0 | 35 | 301 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 425 | 0 | 0 | 50 | 0 | 0 | 48 | 39 | 0 | 0 | 0 | 0 | 55 | 17 | 18 | 1000 | 147 | 0 | 50 | 0 | 66 | 217 | 0 | 0 | 0 | 1162 | 0 | 148 | 0 | 275 | 356 | 345 | 51 | 46 | 0 | 33 | 69 | 146 | 187 | 12 | 18 | 108 | 176 | 7 | 0 | 23 | 305 | 0 | 326 | 42 | 30 | 143 | 0 | 17 | 0 | 86 | 30 | 153 | 0 | 101 | 17 | 9 | 78 | 0 | 0 | 0 | 12 | 8701 | 908 | 142 | 0 | 23 | 31 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 587 | 0 | 0 | 0 | 1444.29 | 0 | 33 | 0 | 113 | 113 | 0 | 83 | 26 | 52 | 0 | 0 | 26 | 0 | 0 | 150 | 0 | 170 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 47 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 277 | 120 | 220 | 0 | 636 | 1220 | 35 | 7170.29 | 15871.29 | 75.81
23:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 254 | 35 | 0 | 115 | 110 | 293 | 55 | 35 | 108 | 0 | 0 | 0 | 0 | 0 | 35 | 302 | 0 | 0 | 0 | 142 | 20 | 21 | 0 | 415 | 0 | 0 | 43 | 0 | 0 | 48 | 38 | 0 | 0 | 0 | 0 | 55 | 15 | 26 | 930 | 147 | 0 | 50 | 0 | 65 | 217 | 0 | 0 | 0 | 1160 | 0 | 36 | 0 | 275 | 357 | 345 | 51 | 47 | 0 | 33 | 69 | 146 | 184 | 17 | 18 | 108 | 178 | 19 | 0 | 23 | 305 | 0 | 344 | 42 | 30 | 138 | 0 | 17 | 0 | 86 | 30 | 154 | 0 | 101 | 17 | 9 | 77 | 0 | 0 | 0 | 12 | 8510 | 907 | 142 | 0 | 23 | 35 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 588 | 0 | 0 | 0 | 1449.59 | 0 | 33 | 0 | 113 | 113 | 0 | 83 | 26 | 25 | 0 | 0 | 26 | 0 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 279 | 120 | 220 | 0 | 627 | 1232 | 35 | 7135.59 | 15645.59 | 75.8
Total KWH | 0 | 1350720 | 508800 | 0 | 0 | 0 | 0 | 0 | 8834400 | 0 | 6816710 | 259920 | 146880 | 1935936 | 1269600 | 4336462 | 1024008 | 341524 | 799200 | 0 | 0 | 0 | 0 | 0 | 270467 | 7238730 | 0 | 0 | 191032 | 1766400 | 381000 | 361080 | 0 | 10336363.64 | 81545 | 35127 | 590400 | 0 | 74400 | 291045 | 405600 | 47848 | 0 | 0 | 20414 | 1357560 | 244218 | 416640 | 22421818.18 | 1433527 | 0 | 618720 | 22843.8 | 964327 | 5033814 | 0 | 0 | 0 | 25559452 | 134055 | 948436 | 568727 | 8009000 | 4456300 | 7634000 | 1251088 | 490080 | 2940000 | 788976 | 567360 | 2687945 | 2670240 | 154560 | 343760 | 1134300 | 3785280 | 66706 | 382218 | 304976 | 7513000 | 0 | 6376000 | 998000 | 719760 | 3445609.09 | 68181 | 345264 | 0 | 1973760 | 702432 | 3617000 | 0 | 2442350 | 165600 | 357600 | 1564800 | 0 | 12300 | 241160 | 79920 | 177729274.71 | 21394182 | 3779712 | 0 | 152160 | 163840 | 0 | 0 | 0 | 0 | 0 | 181296 | 572400 | 13207273 | 0 | 0 | 0 | 32650909 | 0 | 113084 | 0 | 829344 | 1016448 | 0 | 539185 | 147920 | 285749 | 320352 | 692870 | 166810 | 0 | 363392 | 3604727 | 0 | 3991409 | 0 | 0 | 0 | 9064509 | 0 | 3240 | 0 | 1144145 | 886784 | 118593 | 1124006 | 0 | 350595 | 0 | 39519.6 | 896400 | 4437 | 1667712 | 6109000 | 2836000 | 5323010 | 0 | 12290909 | 25236363.64 | 420000 | 151688285.24 | 329417559.95

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 17-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13852.34 | MW | 12:00 Hr. | Energy Generated |  |  | 329.4176 |  | MKWHr.
| Day Peak Demand |  |  | 13946.34 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.954 |  | MKWHr.
| Evening Peak Generation |  |  | 16200.93 | MW | 21:00 Hr. | Energy Demand |  |  | 332.3716 |  | MKWHr.
| Evening Peak Demand |  |  | 16479.93 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34.3 |  | °C
| Minimum Generation of the Day |  |  | 10323.6 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 945.61 |  | MMCFD
| Maximum Generation of the Day |  |  | 16200.93 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.4416 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.9683 | 0 | 14.0099 | 0 | 0 | 0.19103 | 0 | 0 | 48.1692 | Gas | 125.3212 | Gas | 442891621.9616
| Chattogram Zone |  |  | 5.4505 | 47.9813 | 4.7352 | 0 | 1.3576 | 0.15447 | 0 | 0.0744 | 59.7534 | Coal | 105.969 | Coal | 685667872.4194
| Cumilla Zone |  |  | 29.1699 | 0 | 5.8466 | 0 | 0 | 0.38222 | 3.7853 | 0 | 39.184 | HFO | 34.454 | HFO | 579780306.006
| Mymensingh Zone |  |  | 0 | 0 | 2.1679 | 0 | 0 | 0.25346 | 0 | 0 | 2.4214 | HSD | 0.35059 | HSD | 10826373.6
| Sylhet Zone |  |  | 28.1332 | 0 | 0 | 0 | 0 | 0.068181 | 0 | 0 | 28.2014 | Hydro | 1.3576 | Hydro | 135756
| Khulna Zone |  |  | 3.7797 | 13.2073 | 0.4973 | 0 | 0 | 0.5724 | 21.3942 | 0 | 39.4509 | Solar | 4.0606 | Solar | 64554508.222
| Barishal Zone |  |  | 8.159 | 43.6363 | 2.0877 | 0 | 0 | 0.004437 | 0 | 0 | 53.8874 | Import | 57.8304 | Import | 337038794.52
| Rajshahi Zone |  |  | 16.6606 | 0 | 3.0985 | 0 | 0 | 1.3799 | 32.6509 | 0 | 53.7899 | Wind | 0.0744 | Wind | 1094424
| Rangpur Zone |  |  | 0 | 1.1441 | 2.0108 | 0.35059 | 0 | 1.0545 | 0 | 0 | 4.56
| Total |  |  | 125.3212 | 105.969 | 34.454 | 0.35059 | 1.3576 | 4.0606 | 57.8304 | 0.0744 | 329.4176
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 442891621.9616 |  | Hydro | 135756
|  |  |  | Coal | 685667872.4194 |  | Solar | 64554508.222
|  |  |  | HFO | 579780306.006 |  | Import | 337038794.52
|  |  |  | HSD | 10826373.6 |  | Wind | 1094424
[5 empty] | Total: | 212,19,89,656 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.3942 | Peak Hr Flow | 907.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 44716200 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.6509 | Peak Hr Flow | 1457.93 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2063 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.7853 | Peak Hr Flow | 172.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2562 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 57.8304 | Peak Hr Flow | 2536.93 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 20 |  | 5883
|  |  |  | Chattogram |  | 60 |  | 1588
|  |  |  | Cumilla |  | 0 |  | 1556
|  |  |  | Mymensingh |  | 132 |  | 1122
|  |  |  | Sylhet |  | 0 |  | 624
|  |  |  | Khulna |  | 55 |  | 2032
|  |  |  | Barishal |  | 0 |  | 522
|  |  |  | Rajshahi |  | 0 |  | 1644
|  |  |  | Rangpur |  | 0 |  | 861
|  |  |  | Total |  | 267 |  | 15832
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:03 | Srinagar 132/33kV S/S Tr-01 LT is restored.
|  | 08:03 | Srinagar 132/33kV S/S Tr-02 LT is restored.
| 08:22 | 11:46 | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 LT Scheduled S/D Due to Ds-1209S maintenance
due to red-hot.
| 08:28 | 11:39 | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 HT Scheduled S/D Due to DS-1209s maintenance
due to red-hot.
| 08:43 | 11:34 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Scheduled S/D Due to DS-1209S maintenance due to
red-hot.
| 08:59 | 14:10 | Barapukuria-Bogura 230 kV Ckt-2 Project Work S/D from Barapukuria 230/132/33kV end Due to
Project work ERS
| 09:44 |  | Chowmuhani 230/132/33kV S/S ATR-02 LT Scheduled S/D Due to AVR Replacement.
| 09:44 |  | Chowmuhani 230/132/33kV S/S ATR-02 HT Scheduled S/D Due to AVR Replacement.
| 09:53 | 17:49 | Chowmuhani 230/132/33kV S/S Korerhat-04 Scheduled S/D Due to Relay Replacement.
| 09:56 | 14:12 | Barapukuria-Bogura 230 kV Ckt-2 Scheduled S/D from Bogura 400/230kV end Due to Conductor
Shifting from Exiting line tower to ERS tower
| 10:05 | 13:06 | Sonargaon 132/33kV S/S OPSL(IEL-2) Forced S/D Due to NLDC instruction
| 10:06 | 13:53 | Chowmuhani 230/132/33kV S/S TR1-415T LT Forced S/D Due to Project equipment shift.
| 10:06 | 13:53 | Chowmuhani 230/132/33kV S/S TR1-415T HT Forced S/D Due to Project equipment shift.
| 10:16 | 21:54 | BSRM-Cumilla(N) 230 kV Ckt-1 Project Work S/D from Feni 230/132kV end Due to 230kV SAS &
DFDR witnessing
| 10:48 | 13:36 | Feni 230/132kV S/S ATR-3 LT Project Work S/D Due to water supply system pipe installation
& spray nozzle installation.
| 10:48 | 13:36 | Feni 230/132kV S/S ATR-3 HT Project Work S/D Due to water supply system pipe installation
& spray nozzle installation.
| 11:55 | 20:14 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-1 Scheduled S/D Due to Conductor
Shifting from Exiting line tower to ERS tower
| 11:55 | 20:14 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Scheduled S/D Due to Conductor
Shifting from Exiting line tower to ERS tower
| 12:00 |  | Day Peak Generation is 13846 MW.
| 13:16 | 15:48 | Bhangura 132/33kV S/S Tr-2(413T) LT Forced S/D Due to Red Hot
| 13:17 | 15:47 | Bhangura 132/33kV S/S Tr-2(413T) HT Forced S/D Due to Red Hot
| 15:02 | 17:44 | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to 33 kV Nabinagar feeder R phase bus | [7 empty] | 100.0MW load
|  |  | loop connecting work | [7 empty] | interrup.
| 15:02 | 17:45 | Kabirpur 132/33kV S/S XFR, T-2 LT Scheduled S/D
| 15:21 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- ST
| 15:39 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- GT
| 16:57 | 18:25 | Srinagar 132/33kV S/S Tr-02 LT Scheduled S/D Due to Redhot maintenance in 33Kv bus-2 by | [7 empty] | 12.0MW load
|  |  | PBS. | [7 empty] | interrup.
| 16:58 | 18:23 | Srinagar 132/33kV S/S Tr-02 HT Scheduled S/D Due to Redhot maintenance in 33Kv bus-2 by | [7 empty] | 12.0MW load
|  |  | PBS. | [7 empty] | interrup.
| 21:05 | 22:58 | Sylhet 132/33kV S/S T1 LT Scheduled S/D Due to 33KV Upashahar feeder Bus side D/S | [7 empty] | 15.0MW load
|  |  | (Y-Phase) Red hot maintanance by S&D-2 (BPDB). | [7 empty] | interrup.
| 21:06 | 22:58 | Sylhet 132/33kV S/S T1 HT Scheduled S/D Due to 33KV Upashahar feeder Bus side D/S | [7 empty] | 15.0MW load
|  |  | (Y-Phase) Red hot maintanance by S&D-2 (BPDB). | [7 empty] | interrup.
| 21:19 | 22:20 | Narshingdi 132/33kV S/S T-2 HT Scheduled S/D Due to Narsingdi -1, PBS 33kV Mohishasura | [7 empty] | 20.0MW load
|  |  | feeder OC&EF Tripp then T-2 33kV incomer B-phase DS fingers Flashing and Damage. | [7 empty] | interrup.
| 21:20 | 22:20 | Narshingdi 132/33kV S/S T-2 LT Scheduled S/D Due to Narsingdi -1, PBS 33kV Mohishasura | [7 empty] | 20.0MW load
|  |  | feeder OC&EF Tripp then T-2 33kV incomer B-phase DS fingers Flashing and Damage. | [7 empty] | interrup.
| 23:48 | 00:22 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing 33kv OC/EF protection Relay relays Due
to Heavy Rain and Stormy Weather
| 00:28 | 00:41 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing 33kv OC/EF Relay relays Due to
Shaistaganj Feeder Trip
| 01:19 | 02:01 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Tripped from Brahmanbaria 132/33kV end showing | [7 empty] | 30.0MW load
|  |  | Distance relay relays. and from Shahjibazar 132/33kV end showing Distance Relay relays | [7 empty] | interrup.
|  |  | Due to Stormy Weather | [7 empty] | Brahmanbaria
132/33kV end
| 02:32 | 03:30 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 Tripped from Sirajganj 132/33kV end showing
Distance relay relays Due to Thundering.
| 02:59 | 03:26 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 Tripped from Bog-Sherpur 132/33kV end showing
Micom P443 relays Due to unknown
| 03:17 |  | Around 15 MW interruption occurred under Jamalpur and Sherpur grid due to tripping of
RPCL-Muktagacha ckt-1 and ckt-2 showing distance relay caused by bad weather.
| 03:38 |  | RPCL-Muktagacha ckt-1 and ckt-2 were switched ON. Now no interruption is occurring under
Jamalpur and Sherpur grid s/s.
| 05:32 |  | Tangail 132/33kV S/S Tr-1 HT Tripped showing 50-51(MMLG01, MCGG), K-50(MVAJ), 86X(MVAJ).
relays Due to 33kV Shakhipur feeder fault.
| 05:32 |  | Tangail 132/33kV S/S Tr-2 HT Tripped showing 50-51(MMLG01, MCGG), K-50(MVAJ), 86X(MVAJ).
relays Due to 33kV Shakhipur feeder fault.
| 05:32 |  | Tangail 132/33kV S/S Tr-1 LT Tripped showing REF615(ABB) relays Due to 33kV Shakhipur
feeder fault .
| 05:32 |  | Tangail 132/33kV S/S Tr-2 LT Tripped showing REF615(ABB) relays Due to 33kV Shakhipur
feeder fault .
| 05:32 |  | Around 42 MW interruption is occurring under Tangail grid s/s due to tripping of T-1 and
T-2 transformer showing overcurrent & earth-fault relay caused by a faulty feeder
(Sokhipur PBS) trial, which caused trip-coil burn in 33 kV incomer breaker.
| 06:00 |  | Minimum Generation: 11514 MW.
| 07:03 | 07:27 | Jamalpur-Mymensingh 132kV Ckt-2 Tripped from Jamalpur 132/33kV end showing Micom relays
Due to O/C, E/F
| 07:20 |  | Sylhet (South) S/S Trafo-2 LT Scheduled S/D Due to 33kv bus section- 2 feeder work | [7 empty] | 24.0MW load
interrup.
| 07:21 |  | Sylhet (South) S/S Trafo-2 HT Scheduled S/D Due to 33kv bus section- 2 feeder work | [7 empty] | 24.0MW load
interrup.
| 07:39 |  | Purbasadipur 230/132/33kV S/S AIS Old T-4 Transformer LT Scheduled S/D Due to Heat sink
maintenance at Khanshama 33kV feeder
| 07:40 |  | Purbasadipur 230/132/33kV S/S AIS Old T-4 Transformer HT Scheduled S/D Due to Heat sink
maintenance at Khanshama 33kV feeder
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 17-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 367 | 8834400 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1024008 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 296 | 7238730 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 259920 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 147 | 1269600 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 341524 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 270467 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 381000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 361080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 42 | 508800 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 277 | 4336462 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 115 | 1935936 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1350720 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 799200 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 191032 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 16 | 146880 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 415 | 10336363.64 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 253 | 6816710 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1766400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2475 | 48169232.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 22843.8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 134055 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 618720 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 55 | 1357560 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 216 | 5033814 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 67 | 964327 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 39 | 405600 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 32 | 291045 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 16 | 416640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 48 | 590400 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20414 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 35127 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 47848 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 50 | 244218 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 15 | 81545 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 145 | 1433527 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 25559452 | U2 on AGC
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 74400 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1000 | 22421818.18 | AGC
Chattogram Area Total |  |  |  |  | 4898.863 | 2965 | 59753353.98
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 0 | 2940000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 356 | 4456300 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 345 | 7634000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 300 | 8009000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 30 | 788976 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 46 | 490080 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 568727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1251088 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 147 | 948436 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 304976 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 146 | 2687945 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 188 | 2670240 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 172 | 3785280 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 66706 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 18 | 343760 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 108 | 1134300 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 16 | 154560 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 69 | 567360 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 382218 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 2015 | 39183952
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12300 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 1564800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 357600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 241160 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 79920 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 165600 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 125 | 2421380
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 68181 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 998000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 719760 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 143 | 3445609.09 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 153 | 3617000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 702432 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1973760 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2442350 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 345264 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7513000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 327 | 6376000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1238 | 28201356.09
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 907 | 21394182 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 28 | 152160 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 27 | 163840 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 144 | 3779712 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 181296 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 572400 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 585 | 13207273 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1706 | 39450863
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 664 | 12290909 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 1667712 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2836000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1220 | 25236363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5323010 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 420000 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 276 | 6109000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4437 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2664 | 53887431.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 320352 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 33 | 113084 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 147920 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 150 | 3604727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 170 | 3991409 | Liquid fuel shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 362 | 9064509 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 166810 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52 | 285749 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 83 | 539185 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1016448 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 829344 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 3240 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1457.93 | 32650909 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 363392 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 692870 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2585.93 | 53789948
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 165 | 350595 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 48 | 1144145 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 1124006 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 39519.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 886784 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 118593 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 896400 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 427 | 4560042.6
Eastern Grid Total |  |  |  |  | 17418.042 | 8818 | 177729274.71
Western Grid Total |  |  |  |  | 11852.195 | 7382.93 | 151688285.24
National Grid Total |  |  |  |  | 29270.237 | 16200.93 | 329417559.95
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 17-05-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10561.42 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5003.7 | MW
i) Dhaka area |  |  | 5863.42 |  | MW | i) Khulna area |  |  |  | 1976.6 | MW
ii) Chattogram area |  |  | 1528 |  | MW | ii) Barishal area |  |  |  | 521.7 | MW
iii) Cumilla area |  |  | 1556 |  | MW | iii) Rajshahi area |  |  |  | 1644.4 | MW
iv) Mymensingh area |  |  | 990 |  | MW | iv) Rangpur area |  |  |  | 861 | MW
v) Sylhet area |  |  | 624 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15565.12 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 8 | 18:30 | 67 | Hasnabad | 101 | 23:00 | 133 | Natore | 158 | 21:00
2 | AKSML | 137.2 | 15:00 | 68 | Hathazari | 100 | 19:00 | 134 | Nawabganj | 68 | 23:00
3 | Aftabnagar | 44 | 00:00 | 69 | Hatirjheel | 57 | 15:00 | 135 | Netrakona | 131 | 00:00
4 | Agargaon | 126 | 13:00 | 70 | Ishurdi | 95 | 21:00 | 136 | New | 82 | 15:00
5 | Agrabad | 82 | 15:00 | 71 | Jaldhaka | 73 | 20:00 | 137 | Niamatpur | 80 | 22:00
6 | Amnura | 31 | 00:00 | 72 | Jamalpur | 98 | 15:00 | 138 | Noapara | 50 | 01:00
7 | Ashuganj | 93 | 00:00 | 73 | Jashore | 163 | 20:00 | 139 | PHP | 11 | 17:00
8 | BSRM | 204 | 18:30 | 74 | Jhenaidah | 130 | 19:30 | 140 | Pabna | 113 | 01:00
9 | Bagerhat | 87 | 01:00 | 75 | Joydebpur | 173 | 19:00 | 141 | Palashbari | 124 | 20:00
10 | Bajitpur | 88 | 18:30 | 76 | Joypurhat | 74 | 00:00 | 142 | Panchagarh | 62 | 20:00
11 | Bakerganj | 12 | 21:00 | 77 | Juldah | 15 | 10:00 | 143 | Patiya | 10 | 06:00
12 | Bakulia | 108 | 23:00 | 78 | KSRM | 13 | 09:00 | 144 | Patuakhali | 79 | 22:00
13 | Banani | 56 | 13:00 | 79 | Kabirpur | 223 | 00:00 | 145 | Payra | 38 | 01:00
14 | Bangabhaban | 21 | 11:00 | 80 | Kachua | 104 | 23:00 | 146 | Postogola | 59 | 00:00
15 | Barapukuria | 71 | 20:00 | 81 | Kaliganj | 22 | 19:30 | 147 | Pubail | 31 | 22:00
16 | Barguna | 24 | 21:00 | 82 | Kallyanpur | 123 | 19:00 | 148 | Purbachal | 37 | 14:00
17 | Barishal | 114 | 13:00 | 83 | Kalurghat | 47 | 15:00 | 149 | Purbasadipur | 137 | 20:00
18 | Barishal-230 | 116 | 22:00 | 84 | Kamrangirchar | 86 | 13:00 | 150 | Rahanpur | 41 | 00:00
19 | Baroaulia | 70 | 00:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 39 | 11:00
20 | Baroirhat | 63 | 19:00 | 86 | Kasba | 41 | 23:00 | 152 | Rajbari | 95 | 20:00
21 | Bashundhara | 198 | 19:30 | 87 | Kazla | 117 | 01:00 | 153 | Rajendrapur | 129 | 15:00
22 | BashundharaCement | 8 | 12:00 | 88 | Keranigonj | 93 | 19:30 | 154 | Rajshahi | 141 | 21:00
23 | Beanibazar | 78 | 21:00 | 89 | Khagrachori | 36 | 19:00 | 155 | Rajshahi-230 | 96 | 23:00
24 | Benapole | 66 | 19:00 | 90 | Khulna | 73 | 13:00 | 156 | Ramganj | 124 | 21:00
25 | Bhaluka | 179 | 18:30 | 91 | Khulshi | 193 | 20:00 | 157 | Rampur | 48 | 23:00
26 | Bhandaria | 61 | 22:00 | 92 | Kishoreganj | 95 | 17:00 | 158 | Rangamati | 19 | 19:30
27 | Bhangura | 44 | 20:00 | 93 | Kodda | 329 | 21:00 | 159 | Rangpur | 140 | 19:30
28 | Bheramara(GK) | 77 | 19:30 | 94 | Kulaura | 52 | 20:00 | 160 | Ruppur | 4.6 | 15:00
29 | Bhulta | 227 | 15:00 | 95 | Kurigram | 52 | 19:30 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 88 | 23:00 | 96 | Kushtia | 179 | 20:00 | 162 | Saidpur | 95 | 20:00
31 | Bogura | 177 | 19:30 | 97 | Laksam | 35 | 02:00 | 163 | Santhia | 40 | 21:00
32 | Borhanuddin | 96 | 00:00 | 98 | Lakshmipur | 44 | 00:00 | 164 | Satkhira | 144 | 00:00
33 | Brahmanbaria | 139 | 19:30 | 99 | Lalbag | 85 | 13:00 | 165 | Satmasjid | 108 | 19:00
34 | Cantonment | 120 | 13:00 | 100 | Lalmonirhat | 46 | 18:00 | 166 | Savar | 230 | 21:00
35 | Chandina | 21 | 02:00 | 101 | MI_Cement | 16 | 01:00 | 167 | SevenRings | 15.59 | 02:00
36 | Chandpur | 96 | 22:00 | 102 | Madanganj | 44 | 00:00 | 168 | ShahCement | 43 | 01:00
37 | Chandraghona | 39 | 19:00 | 103 | Madaripur | 134 | 22:00 | 169 | Shahjadpur | 87 | 00:00
38 | Chapai | 80 | 21:00 | 104 | Madartek | 86 | 00:00 | 170 | Shahjibazar | 119 | 22:00
39 | Charsaidpur | 40 | 15:00 | 105 | Madunaghat | 58 | 21:00 | 171 | Shahmirpur | 65 | 23:00
40 | Chauddagram | 81 | 22:00 | 106 | Magura | 75 | 21:00 | 172 | Shariatpur | 102 | 22:00
41 | Chhatak | 37 | 21:00 | 107 | Mahasthangarh | 80 | 20:00 | 173 | Sherpur | 106 | 18:30
42 | Chowmuhani | 163 | 22:00 | 108 | Maijdee | 57 | 23:00 | 174 | Shikalbaha | 31 | 09:00
43 | Chuadanga | 131 | 19:00 | 109 | Manikganj | 144 | 19:00 | 175 | Shitalakhya | 94 | 13:00
44 | Coxsbazar | 138 | 22:00 | 110 | Maniknagar | 81 | 19:00 | 176 | Sholosohor | 50 | 15:00
45 | Cumilla(N) | 130 | 18:30 | 111 | Matarbari | 50 | 23:00 | 177 | Shomvuganj | 19 | 20:00
46 | Cumilla(S) | 184 | 20:00 | 112 | Matuail | 82 | 12:00 | 178 | Shyampur | 190 | 10:00
47 | Daganbhuiyan | 46 | 23:00 | 113 | Metrorail_Motijheel | 22 | 12:00 | 179 | Siddhirganj | 134 | 18:30
48 | Daudkandi | 154 | 21:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 112 | 20:00
49 | DhakaUniversity | 94 | 12:00 | 115 | Millgate | 105 | 15:00 | 181 | Sonargaon | 152 | 23:00
50 | Dhamrai | 130 | 19:00 | 116 | Mirpur | 162 | 19:00 | 182 | Sreemongol | 87 | 20:00
51 | Dhanmondi | 107.4 | 13:00 | 117 | Mirsorai | 45 | 03:00 | 183 | Sreepur | 96 | 21:00
52 | Dohazari | 90 | 06:00 | 118 | Mirzapur | 50 | 17:00 | 184 | Srinagar | 54.8 | 22:00
53 | Faridpur | 198 | 22:00 | 119 | Mithapukur | 60 | 20:00 | 185 | Sunamganj | 60 | 20:00
54 | Fatullah | 98 | 16:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 62 | 22:00
55 | Fenchuganj | 46 | 21:00 | 121 | Mogbazar | 105.2 | 16:00 | 187 | Sylhet-132 | 126 | 19:00
56 | Feni | 112 | 19:30 | 122 | Mongla | 50 | 06:00 | 188 | TK | 27 | 00:00
57 | GPH | 2 | 00:00 | 123 | Motijheel | 51 | 13:00 | 189 | Tangail | 148 | 17:00
58 | Ghatail | 76 | 14:00 | 124 | Muktagacha | 27 | 19:00 | 190 | Taraganj | 25 | 20:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 125 | 22:00 | 191 | Tasnim | 33 | 19:00
60 | Ghorashal-230 | 114 | 02:00 | 126 | Muradnagar | 50 | 23:00 | 192 | Thakurgaon | 106 | 19:30
61 | Goalpara | 45 | 01:00 | 127 | Mymensingh | 173 | 19:30 | 193 | Tongi | 175 | 00:00
62 | Gollamari | 120 | 23:00 | 128 | Nabinagar | 88 | 12:00 | 194 | Ullahpara | 41 | 20:00
63 | Gopalganj | 123 | 20:00 | 129 | Naogaon | 141 | 21:00 | 195 | Ullon | 47 | 00:00
64 | Gulshan | 136 | 15:00 | 130 | Narail | 64 | 20:00 | 196 | Uttara | 101 | 17:00
65 | Halishahar | 111 | 15:00 | 131 | Narinda | 74 | 13:00 | 197 | UttaraNew | 59 | 00:00
66 | HaripurSBU | 140 | 04:00 | 132 | Narshingdi | 193 | 00:00 | 198 | Zigatola | 96 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 17-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15195.2 | 121 |  | 15321.65
1:00 | 14111 | 66 |  | 14180
2:00 | 13190 | 67 |  | 13260
3:00 | 12530 | 57 |  | 12590
4:00 | 11832 | 46 |  | 11880
5:00 | 10628 | 40 |  | 10670
6:00 | 10323.6 | 0 |  | 10323.6
7:00 | 10837.04 | 0 |  | 10837.04
8:00 | 11000.92 | 0 |  | 11000.92
9:00 | 11482.48 | 40 |  | 11524.48
10:00 | 12282.01 | 52 |  | 12336.01
11:00 | 12898.69 | 91 |  | 12993.69
12:00 | 13852.34 | 90 |  | 13946.34
13:00 | 14327.07 | 112 |  | 14444.07
14:00 | 14504.3 | 80 |  | 14588.3
15:00 | 14664.65 | 81 |  | 14749.65
16:00 | 14472.24 | 155 |  | 14634.24
17:00 | 14487.27 | 159 |  | 14653.27
18:00 | 14439.59 | 180 |  | 14627.59
19:00 | 15445.52 | 626 |  | 16099.52
19:30 | 15705.27 | 377 |  | 16099.27
20:00 | 16151.68 | 286 |  | 16450.68
21:00 | 16200.93 | 267 |  | 16479.93
22:00 | 15871.29 | 190 |  | 16070.29
23:00 | 15645.59 | 148 |  | 15800.59
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 17-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8281 | 6914.2 | 15195.2 | DAILY GENERATION CURVE
00:30 | 7962.5 | 6690.6 | 14653.1
01:00 | 7644 | 6467 | 14111 | 17-05-2026
01:30 | 7390 | 6260.5 | 13650.5
02:00 | 7136 | 6054 | 13190
02:30 | 6970.5 | 5889.5 | 12860
03:00 | 6805 | 5725 | 12530
03:30 | 6557.5 | 5623.5 | 12181
04:00 | 6310 | 5522 | 11832
04:30 | 5978 | 5252 | 11230
05:00 | 5646 | 4982 | 10628
05:30 | 5553.035 | 4922.765 | 10475.8
06:00 | 5460.07 | 4863.53 | 10323.6
06:30 | 5604.62 | 4975.7 | 10580.32
07:00 | 5749.17 | 5087.87 | 10837.04
07:30 | 5696 | 5222.98 | 10918.98
08:00 | 5642.83 | 5358.09 | 11000.92
08:30 | 5726.875 | 5514.825 | 11241.7
09:00 | 5810.92 | 5671.56 | 11482.48
09:30 | 6084.995 | 5797.25 | 11882.245
10:00 | 6359.07 | 5922.94 | 12282.01
10:30 | 6621.95 | 5968.4 | 12590.35
11:00 | 6884.83 | 6013.86 | 12898.69
11:30 | 7205.43 | 6170.085 | 13375.515
12:00 | 7526.03 | 6326.31 | 13852.34
12:30 | 7623.79 | 6465.915 | 14089.705
13:00 | 7721.55 | 6605.52 | 14327.07
13:30 | 7755.47 | 6660.215 | 14415.685
14:00 | 7789.39 | 6714.91 | 14504.3
14:30 | 7872.955 | 6711.52 | 14584.475
15:00 | 7956.52 | 6708.13 | 14664.65
15:30 | 7931.43 | 6637.015 | 14568.445
16:00 | 7906.34 | 6565.9 | 14472.24
16:30 | 7918.02 | 6561.735 | 14479.755
17:00 | 7929.7 | 6557.57 | 14487.27
17:30 | 7921.155 | 6542.275 | 14463.43
18:00 | 7912.61 | 6526.98 | 14439.59
18:30 | 8220.305 | 6722.25 | 14942.555
19:00 | 8528 | 6917.52 | 15445.52
19:30 | 8710 | 6995.27 | 15705.27
20:00 | 8862 | 7289.68 | 16151.68
20:30 | 8840 | 7336.305 | 16176.305 |  | Executive Engineer
21:00 | 8818 | 7382.93 | 16200.93 |  | Network Operation Division
21:30 | 8759.5 | 7276.61 | 16036.11
22:00 | 8701 | 7170.29 | 15871.29
22:30 | 8605.5 | 7152.94 | 15758.44
23:00 | 8510 | 7135.59 | 15645.59

## En-Curve
QF-LDC-12
Date | 17-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3476 | 1698 | 896 | 0 | 168 | 1456 | 60 | 4872 | 0 | 712 | 1857.2 | 0 | 0 | 0 | 121 | DAILY ENERGY CURVE
00:30 | 3380.5 | 1620.5 | 895.5 | 0 | 165 | 1446 | 60 | 4745 | 0 | 585.5 | 1755.1 | 0 | 0 | 0 | 93.5 | 17-05-2026
01:00 | 3285 | 1543 | 895 | 0 | 162 | 1436 | 60 | 4618 | 0 | 459 | 1653 | 0 | 0 | 0 | 66
01:30 | 3317 | 1622 | 895 | 0 | 160 | 1431 | 60 | 4521 | 0 | 276 | 1367.5 | 0 | 0 | 1 | 66.5 | Energy Generated | 329.4176 |  | MKWHr
02:00 | 3349 | 1701 | 895 | 0 | 158 | 1426 | 60 | 4424 | 0 | 93 | 1082 | 0 | 0 | 2 | 67 | Energy not Served | 2.954 |  | MKWHr
02:30 | 3345.5 | 1723.5 | 830 | 0 | 157 | 1435.5 | 60 | 4396 | 0 | 50.5 | 861 | 0 | 0 | 1 | 62 | Total Energy Requirement | 332.3716 |  | MKWHr
03:00 | 3342 | 1746 | 765 | 0 | 156 | 1445 | 60 | 4368 | 0 | 8 | 640 | 0 | 0 | 0 | 57
03:30 | 3363.5 | 1654 | 765 | 0 | 155 | 1426.5 | 60 | 4299.5 | 0 | 8 | 449.5 | 0 | 0 | 0 | 51.5
04:00 | 3385 | 1562 | 765 | 0 | 154 | 1408 | 60 | 4231 | 0 | 8 | 259 | 0 | 0 | 0 | 46
04:30 | 3290.5 | 1517 | 765 | 0 | 152 | 1331 | 60 | 3942 | 0 | 4 | 168.5 | 0 | 0 | 0 | 43
05:00 | 3196 | 1472 | 765 | 0 | 150 | 1254 | 60 | 3653 | 0 | 0 | 78 | 0 | 0 | 0 | 40
05:30 | 3227 | 1477 | 836 | 0 | 137 | 1217.5 | 60 | 3431.5 | 14.8 | 0 | 74 | 0 | 0 | 1 | 20
06:00 | 3258 | 1482 | 907 | 0 | 124 | 1181 | 60 | 3210 | 29.6 | 0 | 70 | 0 | 0 | 2 | 0
06:30 | 3400.5 | 1555 | 907 | 0 | 127 | 1201 | 60 | 3195.5 | 55.32 | 0 | 78 | 0 | 0 | 1 | 0
07:00 | 3543 | 1628 | 907 | 0 | 130 | 1221 | 60 | 3181 | 81.04 | 0 | 86 | 0 | 0 | 0 | 0
07:30 | 3483 | 1623 | 907.5 | 0 | 133 | 1226 | 60 | 3263 | 141.98 | 0 | 81.5 | 0 | 0 | 0 | 0
08:00 | 3423 | 1618 | 908 | 0 | 136 | 1231 | 60 | 3345 | 202.92 | 0 | 77 | 0 | 0 | 0 | 0
08:30 | 3410 | 1625.75 | 908 | 0 | 138 | 1233.13 | 60 | 3415 | 344.82 | 0 | 107 | 0 | 0 | 0 | 20
09:00 | 3397 | 1633.5 | 908 | 0 | 140 | 1235.26 | 60 | 3485 | 486.72 | 0 | 137 | 0 | 0 | 0 | 40
09:30 | 3464 | 1647.5 | 907.5 | 0 | 140 | 1228.155 | 60 | 3754 | 518.59 | 0 | 162.5 | 0 | 0 | 0 | 46
10:00 | 3531 | 1661.5 | 907 | 0 | 140 | 1221.05 | 60 | 4023 | 550.46 | 0 | 188 | 0 | 0 | 0 | 52
10:30 | 3544.5 | 1643 | 907.5 | 0 | 141 | 1218.045 | 60 | 4247.5 | 547.305 | 16 | 263.5 | 0 | 0 | 2 | 71.5
11:00 | 3558 | 1624.5 | 908 | 0 | 142 | 1215.04 | 60 | 4472 | 544.15 | 32 | 339 | 0 | 0 | 4 | 91
11:30 | 3632.5 | 1641.25 | 908 | 0 | 149 | 1270.165 | 60 | 4508.5 | 555.85 | 84.75 | 559.5 | 0 | 0 | 6 | 90.5
12:00 | 3707 | 1658 | 908 | 0 | 156 | 1325.29 | 60 | 4545 | 567.55 | 137.5 | 780 | 0 | 0 | 8 | 90
12:30 | 3675.5 | 1615 | 907.5 | 0 | 160 | 1385.425 | 60 | 4586 | 547.78 | 197 | 945 | 0 | 0 | 10.5 | 101
13:00 | 3644 | 1572 | 907 | 0 | 164 | 1445.56 | 60 | 4627 | 528.01 | 256.5 | 1110 | 0 | 0 | 13 | 112
13:30 | 3641.5 | 1583 | 907 | 0 | 167 | 1446.58 | 60 | 4595 | 531.855 | 281.25 | 1193 | 0 | 0 | 9.5 | 96
14:00 | 3639 | 1594 | 907 | 0 | 170 | 1447.6 | 60 | 4563 | 535.7 | 306 | 1276 | 0 | 0 | 6 | 80
14:30 | 3647 | 1648 | 907.5 | 0 | 170 | 1454.465 | 60 | 4618.5 | 471.01 | 315.5 | 1285 | 0 | 0 | 7.5 | 80.5
15:00 | 3655 | 1702 | 908 | 0 | 170 | 1461.33 | 60 | 4674 | 406.32 | 325 | 1294 | 0 | 0 | 9 | 81
15:30 | 3613 | 1698.5 | 907.5 | 0 | 170 | 1458.435 | 60 | 4693.5 | 341.01 | 328 | 1289.5 | 0 | 0 | 9 | 118
16:00 | 3571 | 1695 | 907 | 0 | 170 | 1455.54 | 60 | 4713 | 275.7 | 331 | 1285 | 0 | 0 | 9 | 155
16:30 | 3612 | 1672 | 907.5 | 0 | 171 | 1452.92 | 57.5 | 4737 | 199.835 | 367 | 1296.5 | 0 | 0 | 6.5 | 157
17:00 | 3653 | 1649 | 908 | 0 | 172 | 1450.3 | 55 | 4761 | 123.97 | 403 | 1308 | 0 | 0 | 4 | 159
17:30 | 3603.5 | 1637.5 | 908 | 0 | 167 | 1453.145 | 55 | 4699.5 | 72.285 | 462 | 1400 | 0 | 0 | 5.5 | 169.5
18:00 | 3554 | 1626 | 908 | 0 | 162 | 1455.99 | 55 | 4638 | 20.6 | 521 | 1492 | 0 | 0 | 7 | 180
18:30 | 3598 | 1617.5 | 908 | 0 | 165 | 1454.255 | 55 | 4693 | 10.3 | 621 | 1754.5 | 60 | 0 | 6 | 403
19:00 | 3642 | 1609 | 908 | 0 | 168 | 1452.52 | 55 | 4748 | 0 | 721 | 2017 | 120 | 0 | 5 | 626
19:30 | 3579 | 1537 | 907 | 0 | 178 | 1453.27 | 55 | 4892 | 0 | 719 | 2309 | 70 | 0 | 6 | 377
20:00 | 3734 | 1646 | 907 | 0 | 184 | 1452.68 | 55 | 4929 | 0 | 743 | 2333 | 165 | 0 | 3 | 286
20:30 | 3709.5 | 1626 | 907 | 0 | 178 | 1455.305 | 55 | 4973 | 0 | 755.5 | 2350.5 | 165 | 0 | 1.5 | 276.5
21:00 | 3685 | 1606 | 907 | 0 | 172 | 1457.93 | 55 | 5017 | 0 | 768 | 2368 | 165 | 0 | 0 | 267
21:30 | 3680.5 | 1626 | 907.5 | 0 | 174 | 1451.11 | 55 | 4973 | 0 | 757 | 2329.5 | 82.5 | 0 | 0 | 228.5
22:00 | 3676 | 1646 | 908 | 0 | 176 | 1444.29 | 55 | 4929 | 0 | 746 | 2291 | 0 | 0 | 0 | 190
22:30 | 3673.5 | 1632 | 907.5 | 0 | 177 | 1446.94 | 55 | 4897 | 0 | 747.5 | 2222 | 0 | 0 | 0 | 169
23:00 | 3671 | 1618 | 907 | 0 | 178 | 1449.59 | 55 | 4865 | 0 | 749 | 2153 | 0 | 0 | 0 | 148
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 17-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 145 | 15 | 570 | 106 | 1228 | -334 | Ishurdi-Ghorashal Ckt-1 | Export | 3091200
1:00 | 151 | 9 | 624 | 102 | 1464 | 400
2:00 | 133 | 4 | 540 | 72 | 1370 | 394 |  | Import | 0
3:00 | 98 | 4 | 484 | 56 | 1234 | 356
4:00 | 101 | -3 | 446 | 28 | 1234 | 310 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 74 | -22 | 430 | 20 | 810 | 266
6:00 | 126 | -34 | 552 | 48 | 904 | 262 |  | Import | 0
7:00 | 130 | -29 | 566 | 70 | 1068 | 302
8:00 | 150 | -25 | 618 | 124 | 1272 | 302 | Sirajganj-Sreepur Ckt-1 | Export | 3106000
9:00 | 185 | -9 | 692 | 130 | 1464 | 422
10:00 | 198 | 4 | 716 | 180 | 1648 | 478 |  | Import | 0
11:00 | 167 | 9 | 590 | 170 | 1536 | 528
12:00 | 151 | 10 | 588 | 150 | 1534 | 490 | Sirajganj-Sreepur Ckt-2 | Export | 3139000
13:00 | 134 | -1 | 570 | 126 | 1554 | 450
14:00 | 141 | -2 | 610 | 140 | 1544 | 480 |  | Import | 0
15:00 | 137 | 6 | 630 | 164 | 1656 | 502
16:00 | 132 | 11 | 598 | 188 | 1642 | 498 | Gopalganj-Aminbazar Ckt-1 | Export | 17170000
17:00 | 126 | 7 | 554 | 152 | 1584 | 500
18:00 | 128 | 10 | 544 | 138 | 1524 | 510 |  | Import | 0
18:30 | 156 | 19 | 626 | 168 | 1686 | 560
19:00 | 143 | 18 | 612 | 200 | 1610 | 516 | Gopalganj-Aminbazar Ckt-2 | Export | 18210000
19:30 | 110 | 11 | 514 | 176 | 1396 | 460
20:00 | 96 | 1 | 522 | 166 | 1432 | 404 |  | Import | 0
21:00 | 105 | 2 | 538 | 148 | 1420 | 418
22:00 | 95 | -6 | 468 | 84 | 1382 | 392 |  | Total Export | 44716200
23:00 | 95 | -6 | 490 | 90 | 1432 | 350 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 17-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 393 | 05:00 | 365 | 15:00 | Madunaghat | 399 | 05:00 | 389 | 11:00
Amtali | 415 | 06:00 | 403 | 12:00 | Meghnaghat | 396 | 06:00 | 367 | 16:00
Ashuganj | 422 | 5:00 | 387 | 11:00 | Payra | 414 | 05:00 | 406 | 00:00
Bhulta | 414 | 05:00 | 380 | 11:00 | Rahanpur | 409 | 06:00 | 391 | 13:00
Bibiana | 401 | 05:00 | 385 | 16:00 | Rampal | 399 | 05:00 | 381 | 15:00
BIPTC | 402 | 05:00 | 387 | 23:00
Bogura | 399 | 05:00 | 376 | 13:00
Gopalganj | 400 | 05:00 | 380 | 15:00
Kaliakoir | 389 | 06:00 | 361 | 16:00
Korerhat | 400 | 06:00 | 383 | 16:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 234 | 05:00 | 214 | 16:00 | Jhenaidah | 224 | 05:00 | 210 | 20:00
AKSML | 232 | 06:00 | 222.3 | 16:00 | Kachua | 225 | 06:00 | 217 | 04:00
Aminbazar | 235 | 05:00 | 216 | 12:00 | Kaliakoir | 239 | 05:00 | 220 | 11:00
Ashuganj | 238 | 05:00 | 220 | 12:00 | Keranigonj | 230 | 07:00 | 212 | 16:00
Ashuganj-400 | 238 | 05:00 | 220 | 12:00 | Khulna(S) | 229 | 05:00 | 213 | 16:00
Baghabari | 235 | 05:00 | 224 | 13:00 | Korerhat | 227 | 06:00 | 217 | 16:00
Barapukuria | 232 | 06:00 | 206 | 12:00 | Madunaghat | 230 | 05:00 | 224 | 12:00
Barapukuria-230 | 232 | 06:00 | 206 | 12:00 | Madunaghat-400 | 232 | 06:00 | 226 | 11:00
Barishal | 226 | 06:00 | 220 | 00:00 | Maniknagar | 232 | 06:00 | 212 | 12:00
Bheramara | 235 | 04:00 | 221 | 11:00 | Meghnaghat | 237 | 05:00 | 223 | 10:00
Bhulta | 235 | 05:00 | 214 | 11:00 | Meghnaghat-400 | 234 | 05:00 | 217 | 11:00
Bibiana | 240 | 05:00 | 228 | 19:00 | Mirsorai | 233 | 06:00 | 224 | 16:00
BIPTC | 236 | 04:00 | 222 | 11:00 | Naogaon | 224 | 05:00 | 203 | 20:00
Bogura | 241 | 05:00 | 226 | 12:00 | Purbasadipur | 235 | 01:00 | 203 | 12:00
Bogura-400 | 241 | 05:00 | 226 | 12:00 | Rajshahi | 233 | 05:00 | 220 | 13:00
Borhanuddin | 230 | 08:00 | 226 | 00:00 | Rampal | 226 | 05:00 | 214 | 13:00
BSRM | 227 | 06:00 | 218 | 16:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 226 | 06:00 | 218 | 02:00 | Rampura | 235 | 05:00 | 211 | 16:00
Cumilla(N) | 232 | 05:00 | 218 | 11:00 | Shikalbaha | 229 | 07:00 | 221 | 11:00
Faridpur | 221 | 06:00 | 212 | 00:00 | Shyampur | 233 | 05:00 | 214 | 11:00
Fenchuganj | 241 | 06:00 | 229 | 19:30 | Siddhirganj | 233 | 06:00 | 215 | 12:00
Feni | 227 | 06:00 | 217 | 12:00 | Sirajgonj | 242 | 05:00 | 232 | 15:00
Ghorashal | 235 | 05:00 | 220 | 00:00 | Sreepur | 232 | 05:00 | 215 | 15:00
Ghorashal-230 | 235 | 05:00 | 212 | 11:00 | Tongi | 224 | 07:00 | 213 | 11:00
Gopalganj | 222 | 05:00 | 212 | 19:30
GPH | 230 | 06:00 | 222 | 15:00
Haripur | 234 | 05:00 | 214 | 11:00
Hasnabad | 230 | 07:00 | 213 | 12:00
Hathazari | 228 | 07:00 | 222 | 11:00
Ishurdi | 236 | 05:00 | 224 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 140 | 05:00 | 123 | 12:00 | Madunaghat | 134 | 05:00 | 130 | 10:00
Agargaon | 137 | 05:00 | 123 | 15:00 | Magura | 128 | 09:00 | 119 | 20:00
Agrabad | 133 | 07:00 | 129 | 12:00 | Mahasthangarh | 140 | 02:00 | 126 | 12:00
AKS | 131 | 07:00 | 126 | 16:00 | Maijdee | 125 | 06:00 | 121 | 02:00
Aminbazar | 133 | 04:00 | 120 | 15:00 | Manikganj | 133 | 05:00 | 122 | 11:00
Amnura | 135 | 05:00 | 127 | 11:00 | Maniknagar | 137 | 06:00 | 122 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 121 | 00:00 | 115 | 19:00
Ashuganj-230 | 142 | 05:00 | 130 | 16:00 | Matuail | 136.5 | 05:00 | 123 | 12:00
Bagerhat | 122 | 08:00 | 113 | 19:30 | Metrorail_Motijheel | 137 | 06:00 | 122 | 16:00
Bajitpur | 135 | 05:00 | 121 | 16:00 | Metrorail_Uttara | 137 | 05:00 | 121 | 10:00
Bakerganj | 132 | 18:00 | 128 | 00:00 | Millgate | 138 | 04:00 | 122 | 12:00
Bakulia | 134 | 04:00 | 130 | 11:00 | Mirpur | 133 | 05:00 | 119 | 15:00
Banani | 139 | 05:00 | 122 | 15:00 | Mirzapur | 136 | 04:00 | 123 | 11:00
Bangabhaban | 137 | 06:00 | 122 | 11:00 | Mithapukur | 139 | 01:00 | 122 | 12:00
Barapukuria | 137 | 07:00 | 121 | 12:00 | MI_Cement | 133 | 06:00 | 120 | 10:00
Barguna | 132 | 18:30 | 127 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 18:30 | 126 | 11:00 | Mogbazar | 142 | 06:00 | 123 | 16:00
Barishal-230 | 131 | 06:00 | 127 | 11:00 | Mongla | 123 | 09:00 | 113 | 16:00
Baroaulia | 132 | 06:00 | 129 | 10:00 | Motijheel | 137 | 06:00 | 122 | 11:00
Baroirhat | 132 | 06:00 | 126 | 02:00 | Muktagacha | 134 | 02:00 | 117 | 15:00
Bashundhara | 139 | 04:00 | 121 | 11:00 | Munshiganj | 131 | 08:00 | 121 | 12:00
BashundharaCement | 133 | 10:00 | 122 | 12:00 | Muradnagar | 134 | 06:00 | 120 | 12:00
Beanibazar | 132 | 06:00 | 122 | 18:30 | Mymensingh | 133 | 02:00 | 111 | 20:00
Benapole | 126 | 04:00 | 115 | 16:00 | Nabinagar | 138 | 05:00 | 121 | 16:00
Bhaluka | 135 | 01:00 | 119 | 19:00 | Naogaon | 140 | 04:00 | 122 | 20:00
Bhandaria | 129 | 19:00 | 120 | 01:00 | Narail | 127 | 06:00 | 119 | 19:30
Bhangura | 136 | 04:00 | 128 | 15:00 | Narinda | 137 | 06:00 | 122 | 12:00
Bheramara | 136 | 04:00 | 130 | 20:00 | Narshingdi | 137 | 05:00 | 117 | 15:00
Bheramara(GK) | 135 | 04:00 | 130 | 12:00 | Natore | 135 | 05:00 | 127 | 12:00
Bhulta | 132 | 06:00 | 119 | 16:00 | Nawabganj | 137 | 06:00 | 123 | 16:00
Bog-Sherpur | 140 | 05:00 | 128 | 12:00 | Netrakona | 126 | 04:00 | 108 | 20:00
Bogura | 141 | 02:00 | 130 | 12:00 | New | 137 | 04:00 | 123 | 11:00
Bogura-230 | 141 | 05:00 | 130 | 12:00 | Niamatpur | 134 | 04:00 | 125 | 20:00
Brahmanbaria | 134 | 05:00 | 123 | 19:30 | Noapara | 128 | 05:00 | 118 | 16:00
Cantonment | 137 | 05:00 | 123 | 11:00 | Pabna | 135 | 05:00 | 127 | 15:00
Chandina | 134 | 06:00 | 125 | 12:00 | Palashbari | 137 | 01:00 | 122 | 12:00
Chandpur | 130 | 18:30 | 124 | 01:00 | Panchagarh | 139 | 01:00 | 122 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 134 | 06:00 | 130 | 12:00 | Patiya | 133 | 06:00 | 129 | 11:00
Chapai | 132 | 07:00 | 125 | 20:00 | Patuakhali | 132 | 18:30 | 127 | 11:00
Charsaidpur | 135 | 05:00 | 122 | 12:00 | Payra | 135 | 14:00 | 131 | 22:00
Chauddagram | 130 | 05:00 | 124 | 12:00 | PHP | 131 | 06:00 | 126 | 02:00
Chhatak | 130 | 05:00 | 118 | 20:00 | Postogola | 134 | 05:00 | 122 | 12:00
Chowmuhani | 125 | 05:00 | 122 | 00:00 | Pubail | 134 | 05:00 | 124 | 19:30
Chuadanga | 128 | 05:00 | 116 | 19:30 | Purbachal | 140 | 04:00 | 121 | 11:00
Coxsbazar | 124 | 15:00 | 115 | 00:00 | Purbasadipur | 139 | 01:00 | 119 | 12:00
Cumilla(N) | 135 | 05:00 | 125 | 12:00 | Rahanpur | 135 | 06:00 | 129 | 12:00
Cumilla(S) | 131 | 06:00 | 122 | 13:00 | Rahanpur-400 | 135 | 05:00 | 129 | 13:00
Daganbhuiyan | 129 | 06:00 | 123 | 12:00 | Rahim | 137 | 05:00 | 123 | 15:00
Daudkandi | 133 | 06:00 | 117 | 12:00 | Rajbari | 126 | 06:00 | 117 | 20:00
DhakaUniversity | 139 | 05:00 | 122 | 16:00 | Rajendrapur | 137 | 02:00 | 119 | 16:00
Dhamrai | 140 | 05:00 | 123 | 16:00 | Rajshahi | 132 | 18:30 | 124 | 13:00
Dhanmondi | 140 | 05:00 | 123 | 16:00 | Rajshahi-230 | 133 | 04:00 | 126 | 13:00
Dohazari | 129 | 00:00 | 125 | 12:00 | Ramganj | 125 | 18:00 | 118 | 02:00
Faridpur | 128 | 06:00 | 122 | 00:00 | Rampur | 133 | 05:00 | 128 | 11:00
Fatullah | 139 | 06:00 | 125 | 12:00 | Rampura | 140 | 05:00 | 122 | 16:00
Fenchuganj | 138 | 06:00 | 131 | 00:00 | Rangamati | 133 | 04:00 | 129 | 10:00
Feni | 128 | 04:00 | 124 | 16:00 | Rangpur | 137 | 06:00 | 124 | 12:00
Feni-230 | 130 | 06:00 | 124 | 12:00 | Ruppur | 136 | 05:00 | 130 | 15:00
Ghatail | 132 | 03:00 | 116 | 15:00 | Saidpur | 140 | 01:00 | 119 | 12:00
Ghorashal | 142 | 05:00 | 127 | 14:00 | Santhia | 136 | 05:00 | 129 | 14:00
Goalpara | 131 | 05:00 | 119 | 19:30 | Satkhira | 123 | 05:00 | 113 | 20:00
Gollamari | 129 | 05:00 | 121 | 19:30 | Satmasjid | 138 | 06:00 | 122 | 16:00
Gopalganj | 129 | 05:00 | 121 | 00:00 | Savar | 130 | 04:00 | 118 | 15:00
Gopalganj-400 | 132 | 05:00 | 125 | 19:30 | SevenRings | 142 | 05:00 | 127 | 16:00
Gulshan | 139 | 05:00 | 122 | 12:00 | ShahCement | 135 | 05:00 | 122 | 12:00
Halishahar | 134 | 06:00 | 129 | 11:00 | Shahjadpur | 138 | 02:00 | 131 | 15:00
Haripur | 137 | 06:00 | 123 | 16:00 | Shahjibazar | 136 | 06:00 | 124 | 19:30
HaripurSBU | 135 | 05:00 | 123 | 16:00 | Shahmirpur | 134 | 06:00 | 130 | 10:00
Hasnabad | 132 | 05:00 | 120 | 11:00 | Shariatpur | 129 | 06:00 | 122 | 00:00
Hathazari | 133 | 07:00 | 130 | 00:00 | Sherpur | 132 | 03:00 | 113 | 07:00
Hatirjheel | 140 | 05:00 | 122 | 16:00 | Shikalbaha | 124 | 02:00 | 120 | 11:00
Ishurdi | 137 | 04:00 | 131 | 13:00 | Shikalbaha-230 | 136 | 06:00 | 131 | 11:00
Jaldhaka | 138 | 01:00 | 118 | 12:00 | Shitalakhya | 133 | 06:00 | 120 | 10:00
Jamalpur | 132 | 01:00 | 115 | 19:30 | Sholosohor | 133 | 05:00 | 128 | 18:30
Jashore | 126 | 05:00 | 115 | 20:00 | Shomvuganj | 130 | 06:00 | 115 | 16:00
Jhenaidah | 129 | 05:00 | 121 | 19:30 | Shyampur | 138 | 06:00 | 125 | 12:00
Jhenaidah-230 | 131 | 05:00 | 122 | 20:00 | Shyampur-230 | 139 | 05:00 | 127 | 12:00
Joydebpur | 140 | 04:00 | 121 | 16:00 | Siddhirganj | 136 | 05:00 | 124 | 12:00
Joypurhat | 139 | 03:00 | 124 | 12:00 | Sirajganj | 138 | 05:00 | 126 | 12:00
Juldah | 133 | 00:00 | 130 | 03:00 | Sonargaon | 135 | 06:00 | 122 | 00:00
Kabirpur | 139 | 05:00 | 119 | 11:00 | Sreemongol | 135 | 00:00 | 125 | 19:00
Kachua | 128 | 06:00 | 123 | 03:00 | Sreepur | 135 | 04:00 | 123 | 19:00
Kaliakoir | 144 | 05:00 | 128 | 19:00 | Srinagar | 138 | 05:00 | 123 | 16:00
Kaliganj | 131 | 06:00 | 121 | 20:00 | SSM | 137 | 07:00 | 132 | 11:00
Kallyanpur | 133 | 04:00 | 120 | 15:00 | Sunamganj | 127 | 06:00 | 117 | 19:00
Kalurghat | 135 | 06:00 | 130 | 12:00 | Sylhet | 132 | 06:00 | 124 | 19:00
Kamrangirchar | 134 | 06:00 | 117 | 15:00 | Sylhet-132 | 131 | 06:00 | 124 | 19:30
Kaptai | 136 | 6:00 | 132 | 11:00 | Tangail | 136 | 04:00 | 119 | 15:00
Kasba | 134 | 06:00 | 120 | 00:00 | Taraganj | 140 | 01:00 | 121 | 12:00
Kazla | 137 | 06:00 | 122 | 13:00 | Tasnim | 135 | 05:00 | 121 | 15:00
Keranigonj | 137 | 05:00 | 124 | 16:00 | Thakurgaon | 140 | 01:00 | 120 | 12:00
Khagrachori | 131 | 06:00 | 126 | 00:00 | TK | 134 | 05:00 | 129 | 11:00
Khulna | 127 | 06:00 | 118 | 20:00 | Tongi | 133 | 07:00 | 123 | 00:00
Khulna(S) | 130 | 05:00 | 122 | 16:00 | Ullahpara | 138 | 05:00 | 128 | 12:00
Khulshi | 132 | 04:00 | 127 | 12:00 | Ullon | 140 | 05:00 | 122 | 16:00
Kishoreganj | 134 | 06:00 | 120 | 16:00 | Uttara | 136 | 05:00 | 120 | 11:00
Kodda | 135 | 00:00 | 127 | 10:00 | UttaraNew | 137 | 05:00 | 121 | 11:00
Korerhat | 133 | 06:00 | 128 | 16:00 | Zigatola | 137 | 06:00 | 124 | 16:00
KSRM | 133 | 01:00 | 130 | 11:00
Kulaura | 137 | 06:00 | 129 | 19:00
Kurigram | 140 | 01:00 | 116 | 12:00
Kushtia | 131 | 06:00 | 126 | 15:00
Laksam | 127 | 06:00 | 122 | 03:00
Lakshmipur | 125 | 06:00 | 121 | 02:00
Lalbag | 132 | 09:00 | 124 | 12:00
Lalmonirhat | 135 | 01:00 | 122 | 13:00
Madanganj | 132 | 07:00 | 122 | 12:00
Madaripur | 130 | 05:00 | 125 | 00:00
Madartek | 139 | 05:00 | 123 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division