## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 18-05-2026 | [28 empty] | Date: | 18-05-2026 | [28 empty] | Date: | 18-05-2026 | [28 empty] | Date: | 18-05-2026 | [28 empty] | Date: | 18-05-2026 | [17 empty] | Date: | 18-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [17 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 280 | 0 | 0 | 115 | 92 | 293 | 55 | 35 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 123 | 20 | 21 | 0 | 440 | 0 | 0 | 29 | 0 | 0 | 48 | 38 | 0 | 0 | 0 | 0 | 55 | 16 | 26 | 835 | 98 | 0 | 20 | 0 | 66 | 217 | 0 | 0 | 0 | 1160 | 0 | 26 | 0 | 275 | 357 | 345 | 51 | 46 | 0 | 33 | 69 | 146 | 183 | 0 | 19 | 85 | 174 | 37 | 0 | 23 | 305 | 0 | 356 | 42 | 30 | 138 | 0 | 17 | 0 | 86 | 30 | 153 | 0 | 101 | 17 | 9 | 78 | 0 | 0 | 0 | 0 | 8203 | 907 | 141 | 0 | 23 | 33 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 582 | 0 | 0 | 0 | 1422.76 | 0 | 33 | 0 | 113 | 113 | 0 | 73 | 18 | 8 | 0 | 0 | 26 | 0 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 48 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 124 | 220 | 0 | 616 | 1205 | 35 | 7074.76 | 15277.76 | 75.79
01:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 226 | 0 | 0 | 115 | 60 | 293 | 55 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 0 | 0 | 86 | 20 | 21 | 0 | 390 | 0 | 0 | 16 | 0 | 0 | 17 | 38 | 0 | 0 | 0 | 0 | 55 | 14 | 26 | 772 | 0 | 0 | 19 | 0 | 64 | 217 | 0 | 0 | 0 | 1160 | 0 | 26 | 0 | 275 | 358 | 345 | 51 | 47 | 0 | 33 | 0 | 147 | 155 | 0 | 18 | 17 | 168 | 43 | 0 | 23 | 300 | 0 | 381 | 42 | 30 | 136 | 0 | 17 | 0 | 86 | 30 | 154 | 0 | 101 | 17 | 9 | 77 | 0 | 0 | 0 | 0 | 7593 | 923 | 142 | 0 | 23 | 12 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 582 | 0 | 0 | 0 | 1446.61 | 0 | 33 | 0 | 113 | 113 | 0 | 0 | 18 | 8 | 0 | 0 | 26 | 0 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 48 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 124 | 220 | 0 | 617 | 1100 | 17 | 6878.61 | 14471.61 | 75.77
02:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 284 | 0 | 0 | 115 | 15 | 293 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 51 | 20 | 21 | 0 | 440 | 0 | 0 | 12 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 15 | 26 | 786 | 0 | 0 | 19 | 0 | 66 | 217 | 0 | 0 | 0 | 1160 | 0 | 26 | 0 | 275 | 356 | 345 | 51 | 46 | 0 | 33 | 0 | 147 | 34 | 0 | 18 | 0 | 162 | 25 | 0 | 23 | 300 | 0 | 374 | 42 | 30 | 139 | 0 | 17 | 0 | 43 | 30 | 152 | 0 | 101 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 7285 | 924 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 1449.84 | 0 | 0 | 0 | 70 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 50 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 275 | 124 | 220 | 0 | 619 | 1000 | 17 | 6530.84 | 13815.84 | 75.75
03:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 243 | 0 | 0 | 115 | 0 | 293 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 20 | 21 | 0 | 375 | 0 | 0 | 12 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 16 | 26 | 773 | 0 | 0 | 19 | 0 | 65 | 219 | 0 | 0 | 0 | 1140 | 0 | 25 | 0 | 275 | 356 | 345 | 51 | 47 | 0 | 33 | 0 | 147 | 0 | 0 | 18 | 0 | 156 | 8 | 0 | 23 | 305 | 0 | 374 | 42 | 30 | 140 | 0 | 17 | 0 | 84 | 30 | 150 | 0 | 101 | 0 | 9 | 45 | 0 | 0 | 0 | 0 | 6995 | 924 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 1444.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 276 | 124 | 220 | 0 | 619 | 955 | 0 | 6065.09 | 13060.09 | 75.73
04:00 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 231 | 0 | 0 | 98 | 0 | 45 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 20 | 21 | 0 | 370 | 0 | 0 | 13 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 15 | 28 | 777 | 0 | 0 | 19 | 0 | 17 | 219 | 0 | 0 | 0 | 1159 | 0 | 0 | 0 | 300 | 357 | 345 | 51 | 47 | 0 | 34 | 0 | 147 | 0 | 0 | 18 | 0 | 154 | 8 | 0 | 23 | 300 | 0 | 374 | 42 | 30 | 134 | 0 | 17 | 0 | 86 | 30 | 150 | 0 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6607 | 924 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 0 | 0 | 0 | 1344.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 124 | 220 | 0 | 617 | 930 | 0 | 5873.29 | 12480.29 | 75.71
05:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 230 | 0 | 0 | 60 | 0 | 15 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 0 | 0 | 20 | 21 | 0 | 360 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 29 | 739 | 0 | 0 | 6 | 0 | 0 | 219 | 0 | 0 | 0 | 1074 | 0 | 0 | 0 | 330 | 357 | 345 | 51 | 48 | 0 | 34 | 0 | 147 | 0 | 0 | 18 | 0 | 148 | 0 | 0 | 23 | 305 | 0 | 374 | 42 | 30 | 135 | 0 | 17 | 0 | 83 | 30 | 152 | 0 | 101 | 0 | 9 | 8 | 0 | 0 | 0 | 0 | 6344 | 924 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512 | 0 | 0 | 0 | 1225.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247 | 124 | 220 | 0 | 618 | 880 | 0 | 5616.65 | 11960.65 | 75.69
06:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 281 | 0 | 0 | 17 | 0 | 15 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 1 | 0 | 20 | 21 | 0 | 460 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 55 | 0 | 11 | 757 | 0 | 0 | 3 | 0 | 0 | 218 | 0 | 0 | 0 | 948 | 1 | 0 | 0 | 330 | 357 | 345 | 51 | 48 | 0 | 34 | 0 | 148 | 0 | 0 | 18 | 0 | 144 | 0 | 6 | 7 | 300 | 0 | 376 | 42 | 30 | 135 | 0 | 17 | 0 | 83 | 30 | 155 | 0 | 102 | 0 | 0 | 0 | 0 | 0.02 | 0.05 | 0 | 6274.28 | 924 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.95 | 386 | 0 | 0 | 0 | 978.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 3 | 0 | 0 | 2.13 | 160 | 0 | 160 | 0 | 0 | 0 | 393 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.05 | 0 | 272 | 124 | 220 | 0 | 616 | 790 | 0 | 5241.31 | 11515.59 | 75.67
07:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 304 | 0 | 0 | 23 | 0 | 15 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 3 | 0 | 20 | 21 | 0 | 460 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91 | 55 | 0 | 26 | 840 | 0 | 0 | 6 | 0 | 0 | 218 | 0 | 0 | 0 | 955 | 3 | 0 | 0 | 300 | 357 | 345 | 51 | 43 | 0 | 34 | 0 | 146 | 0 | 0 | 14 | 0 | 110 | 0 | 5 | 0 | 305 | 0 | 375 | 42 | 30 | 156 | 0 | 17 | 0 | 85 | 30 | 155 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | 6411.13 | 923 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 375 | 0 | 0 | 0 | 976.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.61 | 16 | 0 | 0 | 0.53 | 160 | 0 | 160 | 0 | 0 | 0 | 411 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0 | 170 | 124 | 220 | 0 | 648 | 820 | 0 | 5237.27 | 11648.4 | 75.65
08:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 296 | 0 | 0 | 34 | 0 | 15 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 8 | 0 | 20 | 21 | 0 | 450 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94 | 55 | 0 | 8 | 880 | 0 | 0 | 6 | 0 | 0 | 217 | 0 | 0 | 0 | 952 | 4 | 0 | 0 | 325 | 357 | 345 | 51 | 18 | 0 | 10 | 0 | 144 | 0 | 0 | 19 | 0 | 128 | 0 | 24 | 0 | 305 | 0 | 375 | 42 | 30 | 155 | 3 | 17 | 0 | 82 | 30 | 152 | 0 | 101 | 0 | 0 | 0 | 0 | 0.27 | 1.99 | 0 | 6440.2 | 924 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 373 | 0 | 0 | 0 | 979.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.58 | 36 | 0 | 0 | 3.45 | 160 | 0 | 160 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 36 | 0.3 | 0 | 191 | 124 | 220 | 0 | 654 | 920 | 0 | 5455.26 | 11895.46 | 75.63
09:00 | 0 | 5 | 25 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 264 | 0 | 0 | 37 | 0 | 60 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 1 | 0 | 20 | 21 | 0 | 430 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.01 | 55 | 0 | 2 | 860 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1006 | 0 | 0 | 0 | 392 | 357 | 345 | 51 | 11 | 0 | 10 | 0 | 144 | 0 | 0 | 19 | 0 | 120 | 0 | 50 | 0 | 300 | 0 | 375 | 42 | 30 | 153 | 2 | 17 | 0 | 85 | 30 | 154 | 0 | 101 | 0 | 8 | 0 | 0 | 0.24 | 30.56 | 0 | 6566.81 | 924 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 397 | 0 | 0 | 0 | 977.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.23 | 30 | 0 | 0 | 10.4 | 160 | 0 | 160 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 81 | 0.4 | 0 | 202 | 124 | 220 | 0 | 652 | 990 | 0 | 5556.39 | 12123.2 | 75.61
10:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 283 | 10 | 0 | 52 | 12 | 95 | 45 | 4 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 20 | 0 | 20 | 21 | 0 | 445 | 0 | 0 | 12 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 4.13 | 55 | 0 | 2 | 835 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1102 | 17 | 0 | 0 | 386 | 357 | 345 | 51 | 11 | 0 | 10 | 0 | 142 | 0 | 0 | 18 | 0 | 126 | 0 | 64 | 0 | 305 | 0 | 362 | 42 | 30 | 148 | 3 | 17 | 0 | 85 | 30 | 154 | 0 | 101 | 0 | 8 | 0 | 0 | 0.6 | 45.7 | 0 | 6822.43 | 924 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 450 | 0 | 0 | 0 | 977.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.29 | 89 | 0 | 0 | 18.42 | 160 | 0 | 160 | 0 | 0 | 0 | 369 | 0 | 2.16 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 116 | 0.64 | 0 | 206 | 124 | 220 | 0 | 644 | 970 | 0 | 5739.8 | 12562.23 | 75.59
11:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 306 | 17 | 0 | 34 | 20 | 95 | 45 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 32 | 12 | 20 | 0 | 0 | 470 | 0 | 0 | 12 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 2.33 | 55 | 0 | 2 | 780 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1105 | 15 | 0 | 0 | 388 | 357 | 342 | 51 | 10 | 0 | 30 | 0 | 146 | 0 | 2 | 17 | 0 | 118 | 0 | 73 | 0 | 305 | 0 | 362 | 42 | 30 | 144 | 10 | 17 | 0 | 85 | 30 | 152 | 0 | 102 | 0 | 25 | 0 | 0 | 0.78 | 10.87 | 0 | 6835.98 | 924 | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 450 | 0 | 0 | 0 | 1119.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.51 | 101 | 0 | 0 | 57 | 160 | 0 | 160 | 0 | 0 | 0 | 406 | 0 | 4.86 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 188 | 0.34 | 0 | 191 | 124 | 220 | 0 | 644 | 950 | 0 | 6021.4 | 12857.38 | 75.58
12:00 | 0 | 22 | 25 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 306 | 17 | 2 | 37 | 28 | 300 | 45 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 312 | 0 | 0 | 32 | 30 | 20 | 0 | 0 | 490 | 0 | 0 | 12 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 2 | 855 | 0 | 0 | 19 | 0 | 0 | 217 | 0 | 0 | 0 | 1180 | 16 | 5 | 0 | 370 | 356 | 342 | 51 | 28 | 0 | 34 | 1 | 145 | 0 | 9 | 18 | 0 | 122 | 0 | 38 | 0 | 305 | 0 | 364 | 42 | 30 | 155 | 2 | 17 | 0 | 85 | 30 | 153 | 0 | 102 | 0 | 25 | 0 | 0 | 0.8 | 3.92 | 0 | 7306.72 | 924 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 511 | 0 | 0 | 0 | 1277.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.01 | 80 | 0 | 0 | 39.1 | 160 | 0 | 160 | 0 | 0 | 0 | 405 | 0 | 2.99 | 0 | 48 | 0 | 25 | 0 | 0 | 0 | 0 | 5.4 | 145 | 0.28 | 5 | 234 | 124 | 220 | 0 | 645 | 980 | 0 | 6283.75 | 13590.47 | 75.57
13:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 274 | 0 | 17 | 74 | 15 | 300 | 50 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 27 | 51 | 19 | 21 | 0 | 415 | 0 | 0 | 12 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1.56 | 55 | 0 | 9 | 795 | 0 | 0 | 19 | 0 | 0 | 221 | 0 | 0 | 0 | 1161 | 17 | 21 | 0 | 305 | 356 | 345 | 51 | 46 | 0 | 33 | 17 | 144 | 7 | 15 | 19 | 0 | 104 | 1 | 69 | 0 | 300 | 0 | 364 | 42 | 30 | 145 | 6 | 17 | 0 | 85 | 30 | 153 | 0 | 102 | 0 | 55 | 16 | 0 | 2.25 | 11.3 | 0 | 7222.11 | 924 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 500 | 0 | 0 | 0 | 1513.04 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 33.32 | 68 | 0 | 0 | 12.23 | 160 | 0 | 160 | 0 | 0 | 0 | 374 | 0 | 0.86 | 0 | 48 | 0 | 19 | 30 | 0 | 0 | 0 | 2.5 | 144 | 0.69 | 48 | 214 | 120 | 220 | 0 | 646 | 1010 | 12 | 6484.64 | 13706.75 | 75.56
14:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 294 | 0 | 17 | 93 | 15 | 300 | 55 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 11 | 68 | 19 | 21 | 0 | 480 | 0 | 0 | 12 | 0 | 6 | 17 | 0 | 0 | 0 | 0 | 3.47 | 55 | 0 | 5 | 770 | 0 | 0 | 19 | 0 | 0 | 216 | 0 | 0 | 0 | 1185 | 15 | 35 | 0 | 300 | 357 | 345 | 51 | 47 | 0 | 33 | 17 | 144 | 16 | 0 | 19 | 0 | 136 | 8 | 62 | 0 | 305 | 0 | 363 | 42 | 30 | 145 | 1 | 17 | 0 | 85 | 30 | 154 | 0 | 102 | 2 | 56 | 16 | 0 | 1.2 | 25.23 | 0 | 7391.9 | 924 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 638 | 0 | 0 | 0 | 1513.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.5 | 43 | 0 | 0 | 48.8 | 160 | 0 | 160 | 0 | 0 | 0 | 398 | 0 | 4.45 | 0 | 48 | 0 | 15 | 34 | 0 | 0 | 0 | 2.1 | 143 | 0.35 | 38 | 211 | 120 | 180 | 0 | 644 | 975 | 17 | 6589.9 | 13981.8 | 75.55
15:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 302 | 0 | 17 | 78 | 15 | 300 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 22 | 68 | 18 | 21 | 0 | 460 | 0 | 0 | 12 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 3.28 | 55 | 0 | 2 | 930 | 0 | 0 | 19 | 0 | 0 | 217 | 0 | 0 | 0 | 1163 | 11 | 12 | 0 | 270 | 357 | 345 | 51 | 46 | 0 | 33 | 7 | 142 | 0 | 0 | 19 | 0 | 140 | 0 | 50 | 0 | 310 | 0 | 363 | 42 | 30 | 155 | 0 | 17 | 0 | 52 | 28 | 153 | 0 | 102 | 17 | 56 | 16 | 0 | 1.2 | 13 | 0 | 7382.48 | 924 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 837 | 0 | 0 | 0 | 1514.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.52 | 34 | 0 | 0 | 37.38 | 150 | 0 | 140 | 0 | 0 | 0 | 398 | 0 | 3.44 | 0 | 48 | 0 | 9 | 34 | 0 | 0 | 0 | 2.6 | 50 | 0.47 | 16 | 278 | 120 | 220 | 0 | 647 | 1034 | 17 | 6740.67 | 14123.15 | 75.54
16:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 263 | 0 | 17 | 78 | 20 | 300 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 14 | 74 | 18 | 21 | 0 | 430 | 0 | 0 | 12 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 1.96 | 55 | 0 | 3 | 930 | 0 | 0 | 19 | 0 | 0 | 216 | 0 | 0 | 0 | 1160 | 7 | 12 | 0 | 270 | 357 | 345 | 51 | 47 | 0 | 33 | 16 | 143 | 0 | 0 | 19 | 0 | 134 | 0 | 34 | 0 | 300 | 0 | 363 | 42 | 30 | 147 | 3 | 17 | 0 | 52 | 28 | 153 | 0 | 102 | 17 | 56 | 16 | 0 | 0.9 | 19.56 | 0 | 7252.42 | 924 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 1003 | 0 | 0 | 0 | 1572.08 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 6.86 | 28 | 0 | 0 | 24.85 | 150 | 0 | 140 | 0 | 0 | 0 | 376 | 0 | 2.11 | 0 | 47 | 0 | 5 | 29 | 0 | 0 | 0 | 0.8 | 35 | 0.19 | 14 | 250 | 120 | 220 | 0 | 647 | 1100 | 17 | 6908.89 | 14161.31 | 75.53
17:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 216 | 0 | 17 | 78 | 60 | 300 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 297 | 0 | 0 | 1 | 105 | 18 | 0 | 0 | 360 | 0 | 0 | 13 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0.58 | 55 | 0 | 5 | 930 | 28 | 0 | 19 | 0 | 0 | 215 | 0 | 0 | 0 | 1160 | 4 | 12 | 0 | 280 | 340 | 280 | 51 | 44 | 0 | 33 | 22 | 142 | 40 | 8 | 19 | 0 | 140 | 16 | 12 | 0 | 305 | 0 | 306 | 42 | 30 | 124 | 2 | 17 | 0 | 52 | 28 | 154 | 0 | 104 | 17 | 18 | 76 | 0 | 0.3 | 7.93 | 0 | 7175.81 | 924 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 1153 | 0 | 0 | 0 | 1588.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 150 | 0 | 140 | 0 | 0 | 0 | 331 | 0 | 0.11 | 0 | 48 | 0 | 7 | 34 | 0 | 0 | 0 | 0.5 | 23 | 0.05 | 14 | 180 | 100 | 180 | 0 | 614 | 996 | 17 | 6649.49 | 13825.3 | 75.52
18:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 271 | 35 | 17 | 78 | 60 | 300 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 35 | 299 | 0 | 0 | 0 | 105 | 18 | 21 | 0 | 420 | 0 | 0 | 24 | 0 | 19 | 0 | 38 | 0 | 0 | 0 | 0.13 | 55 | 0 | 8 | 765 | 32 | 0 | 19 | 5 | 0 | 216 | 0 | 0 | 0 | 1009 | 1 | 12 | 0 | 250 | 280 | 240 | 51 | 43 | 0 | 30 | 36 | 143 | 46 | 18 | 19 | 0 | 132 | 16 | 3 | 23 | 295 | 0 | 302 | 42 | 30 | 127 | 0 | 17 | 0 | 51 | 30 | 153 | 0 | 104 | 17 | 9 | 83 | 0 | 0.07 | 0 | 0 | 7045.2 | 924 | 140 | 0 | 9 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1143 | 0 | 0 | 0 | 1587.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.12 | 140 | 0 | 140 | 0 | 0 | 0 | 385 | 0 | 0.07 | 0 | 48 | 0 | 2 | 39 | 0 | 0 | 0 | 0.5 | 8 | 0 | 14 | 181 | 100 | 180 | 0 | 613 | 846 | 17 | 6539.45 | 13584.65 | 75.52
19:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 277 | 35 | 17 | 93 | 104 | 292 | 55 | 35 | 108 | 0 | 0 | 0 | 0 | 0 | 35 | 285 | 0 | 0 | 0 | 124 | 18 | 21 | 0 | 400 | 0 | 0 | 53 | 0 | 2 | 16 | 54 | 0 | 0 | 0 | 0 | 55 | 0 | 5 | 1000 | 40 | 0 | 19 | 17 | 10 | 217 | 0 | 0 | 0 | 1150 | 0 | 63 | 0 | 315 | 325 | 342 | 51 | 44 | 0 | 33 | 66 | 144 | 63 | 17 | 19 | 50 | 150 | 43 | 0 | 23 | 305 | 0 | 354 | 42 | 30 | 144 | 0 | 17 | 0 | 51 | 28 | 154 | 0 | 104 | 17 | 9 | 83 | 0 | 0 | 0 | 0 | 8148 | 923 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1029 | 0 | 0 | 0 | 1586.82 | 0 | 0 | 0 | 35 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 49 | 109 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 171 | 100 | 180 | 0 | 620 | 780 | 17 | 6522.82 | 14670.82 | 75.51
19:30 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 245 | 35 | 17 | 115 | 45 | 277 | 55 | 35 | 108 | 0 | 0 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 400 | 0 | 0 | 53 | 0 | 1 | 3 | 41 | 0 | 0 | 0 | 0 | 55 | 0 | 5 | 1000 | 32 | 0 | 19 | 17 | 30 | 218 | 0 | 0 | 0 | 1160 | 0 | 12 | 0 | 393 | 352 | 345 | 51 | 47 | 0 | 35 | 69 | 144 | 60 | 17 | 19 | 17 | 158 | 43 | 0 | 23 | 300 | 0 | 356 | 42 | 30 | 130 | 0 | 17 | 0 | 51 | 25 | 152 | 0 | 102 | 17 | 9 | 83 | 0 | 0 | 0 | 0 | 8084 | 924 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 956 | 0 | 0 | 0 | 1592.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 49 | 50 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 120 | 220 | 0 | 627 | 770 | 0 | 6392.6 | 14476.6
20:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 212 | 35 | 17 | 115 | 45 | 95 | 30 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 290 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 330 | 0 | 0 | 55 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 6 | 900 | 16 | 0 | 19 | 17 | 0 | 218 | 0 | 0 | 0 | 1160 | 0 | 12 | 0 | 380 | 357 | 345 | 51 | 48 | 0 | 36 | 65 | 145 | 17 | 18 | 19 | 17 | 160 | 34 | 0 | 0 | 300 | 0 | 356 | 42 | 30 | 129 | 0 | 17 | 0 | 51 | 28 | 153 | 0 | 102 | 17 | 9 | 83 | 0 | 0 | 0 | 0 | 7467 | 923 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 933 | 0 | 0 | 0 | 1589.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 49 | 62 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 120 | 220 | 0 | 615 | 786 | 0 | 6317.76 | 13784.76 | 75.51
21:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 302 | 35 | 0 | 115 | 45 | 45 | 30 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 307 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 465 | 0 | 0 | 55 | 0 | 6 | 49 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 8 | 910 | 0 | 0 | 19 | 0 | 0 | 218 | 0 | 0 | 0 | 1160 | 0 | 12 | 0 | 393 | 357 | 345 | 51 | 48 | 0 | 36 | 16 | 148 | 17 | 17 | 19 | 0 | 168 | 8 | 0 | 0 | 300 | 0 | 356 | 42 | 30 | 149 | 0 | 17 | 0 | 51 | 28 | 154 | 0 | 102 | 17 | 9 | 86 | 0 | 0 | 0 | 0 | 7589 | 924 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 838 | 0 | 0 | 0 | 1589.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 49 | 70 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 120 | 220 | 0 | 644 | 900 | 0 | 6462.94 | 14051.94 | 75.5
22:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 309 | 35 | 0 | 115 | 45 | 45 | 30 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 303 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 480 | 0 | 0 | 53 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 14 | 930 | 0 | 0 | 19 | 0 | 0 | 220 | 0 | 0 | 0 | 1163 | 0 | 12 | 0 | 285 | 357 | 345 | 51 | 48 | 0 | 37 | 17 | 148 | 17 | 18 | 19 | 0 | 170 | 8 | 0 | 0 | 300 | 0 | 320 | 42 | 30 | 156 | 0 | 17 | 0 | 51 | 28 | 152 | 0 | 102 | 17 | 9 | 78 | 0 | 0 | 0 | 0 | 7505 | 923 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 875 | 0 | 0 | 0 | 1461.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 49 | 70 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 120 | 220 | 0 | 746 | 998 | 0 | 6576.8 | 14081.8 | 75.5
23:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 324 | 35 | 0 | 115 | 45 | 45 | 30 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 324 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 500 | 0 | 0 | 42 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 18 | 930 | 0 | 0 | 19 | 0 | 0 | 217 | 0 | 0 | 0 | 1224 | 0 | 12 | 0 | 285 | 358 | 345 | 51 | 48 | 0 | 37 | 16 | 100 | 16 | 0 | 19 | 0 | 174 | 8 | 0 | 0 | 305 | 0 | 308 | 42 | 30 | 156 | 0 | 0 | 0 | 51 | 20 | 150 | 0 | 102 | 17 | 9 | 78 | 0 | 0 | 0 | 0 | 7490 | 924 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995 | 0 | 0 | 0 | 1463.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 50 | 70 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 120 | 220 | 0 | 847 | 1106 | 0 | 6920.62 | 14410.62 | 75.49
Total KWH | 0 | 1391040 | 793920 | 0 | 0 | 0 | 0 | 0 | 8812800 | 0 | 6839390 | 259560 | 149760 | 1929456 | 683520 | 4111145 | 1153530 | 263180 | 601920 | 0 | 0 | 0 | 0 | 0 | 218419 | 7290794 | 0 | 0 | 164360 | 1563600 | 465600 | 444240 | 0 | 10357272.73 | 0 | 0 | 530880 | 0 | 98400 | 308863 | 208656 | 0 | 0 | 0 | 24680 | 1311780 | 70255 | 314400 | 20392727.27 | 235855 | 0 | 324960 | 39018.6 | 298582 | 5315835 | 0 | 0 | 0 | 26710906 | 121770 | 389745 | 0 | 7565000 | 8790300 | 8146000 | 1250356 | 959040 | 0 | 754272 | 370560 | 3417013 | 645600 | 153720 | 465640 | 99180 | 3450240 | 238291 | 474845 | 185568 | 7299000 | 0 | 8635000 | 993000 | 725280 | 3471954.55 | 31335 | 377568 | 0 | 1639680 | 664320 | 3495000 | 0 | 2443150 | 204840 | 412800 | 919200 | 0 | 8200 | 129500 | 0 | 172606272.15 | 22325091 | 3686688 | 0 | 42720 | 50688 | 0 | 0 | 0 | 0 | 0 | 25344 | 644400 | 16843635 | 0 | 0 | 0 | 32852727 | 0 | 0 | 0 | 252096 | 375360 | 0 | 27648 | 21309 | 13963 | 245232 | 599960 | 33434 | 0 | 278544 | 3759455 | 0 | 3894527 | 0 | 0 | 0 | 9136436 | 0 | 21360 | 0 | 1154182 | 692492 | 77689 | 985699 | 0 | 0 | 0 | 24985.68 | 975600 | 4477 | 504192 | 5214000 | 2882000 | 5308430 | 0 | 15752727 | 23384727.27 | 180000 | 152271817.95 | 324878090.1

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 19-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-05-2026 | during | 19-05-2026 | during | 19-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 375 | 370 | 412 | 412 | 392 | 392 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 45 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 312 | 285 | 335 | 335 | 315 | 315 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 8 | 8 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 0 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 28 | 104 | 149.36 | 149.36 | 90 | 128 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 18 | 33 | 33 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 21 | 14 | 14 | 14 | 14 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 50 | 52.19 | 52.19 | 25 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 300 | 292 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 37 | 93 | 149 | 149 | 133 | 133 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 22 | 105 | 105 | 105 | 50 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 162 | 162 | 18 | 36 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 2 | 17 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 490 | 400 | 584 | 584 | 490 | 490 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 306 | 277 | 718 | 718 | 310 | 310 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 30 | 124 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2110 | 2424 | 5781.22 | 5749.22 | 2427 | 2620
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 0 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 16 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 55 | 55 | 55 | 55 | 55 | 55 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 217 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 10 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 54 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 16 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 5 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 12 | 53 | 108 | 108 | 18 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0 | 0 | 4.01 | 0 | 4.01 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 40 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1180 | 1150 | 1224 | 1224 | 1204 | 1204 | Can't Start AGC
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 7 | 2 | 0 | 2 | 0 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 855 | 1000 | 930 | 1000 | 930 | 1000 | AGC
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2363 | 2638 | 3731.87 | 3862.86 | 3051.37 | 3210.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 356 | 325 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 342 | 342 | 342.01 | 342.01 | 342.01 | 342.01 | FGMO not available
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 370 | 315 | 393 | 393 | 350 | 350 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 34 | 33 | 41.65 | 41.65 | 36 | 36 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 28 | 44 | 52.82 | 52.82 | 48 | 48 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 5 | 63 | 150 | 150 | 25 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 23 | 40 | 40 | 40 | 40 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 145 | 144 | 163 | 163 | 140 | 140 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 63 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 122 | 150 | 84 | 80 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 43 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 50 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 17 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 1 | 66 | 115 | 115 | 17 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 38 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1519 | 1748 | 2546.19 | 2477.19 | 1936.02 | 2056.02
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-05-2026 | during | 19-05-2026 | during | 19-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.8 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 0 | 83 | 90 | 90 | 90 | 90 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 25 | 9 | 30 | 30 | 10 | 10 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 3.92 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 29.72 | 109 | 402.2 | 354 | 202.7 | 129
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 144 | 163 | 163 | 147 | 147 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 153 | 154 | 155 | 155 | 155 | 155 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 28 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 51 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 102 | 104 | 102 | 102 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 364 | 354 | 250 | 250 | 250 | 250 | Plant availability less
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1285 | 1229 | 1244 | 1244 | 1164 | 1164
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 923 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 32 | 32 | 30 | 30 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 151 | 143 | 410 | 410 | 165 | 165 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 88 | 0 | 95 | 0 | 95 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 511 | 1029 | 1234.2 | 1234.2 | 1194 | 1194 | U-2 Under Maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1674 | 2095 | 3591.2 | 3496.2 | 2621.1 | 2526.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 645 | 620 | 700 | 800 | 700 | 800 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 5 | 24 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 124 | 100 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 980 | 780 | 1244 | 1244 | 1184 | 1184 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 17 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 234 | 171 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.28 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2208.28 | 1892 | 2862 | 2961 | 2649 | 2785
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 53.01 | 0 | 48 | 0 | 48 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 160 | 140 | 214 | 214 | 161 | 161 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 160 | 140 | 220 | 220 | 160 | 160 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 405 | 367 | 413.79 | 413.79 | 372.41 | 372.41 | AGC
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 26 | 26 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0.03 | 0.03 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 92 | 92 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 10 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.99 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1277.97 | 1586.82 | 1435.88 | 1435.88 | 1356 | 1356 | Can't Start AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 39.1 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 80 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2178.07 | 2278.82 | 3210.57 | 2995.87 | 2579.14 | 2449.44
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 49 | 50 | 50 | 50 | 50 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 99 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.4 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 109 | 115 | 115 | 35 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 25 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 145 | 0 | 140.71 | 0 | 140.71 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 223.4 | 257 | 474.71 | 298 | 374.71 | 278
System Total |  |  |  |  | 28823.2 | 29270.237 | 13590.47 | 14670.82 | 23843.96 | 23438.34 | 17005.04 | 17217.92
Forecast Scenario (19-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14000 |  | 0 |  | 14000
|  |  |  | 1:00 | 13590 |  | 0 |  | 13590
|  |  |  | 2:00 | 13120 |  | 0 |  | 13120
|  |  |  | 3:00 | 12960 |  | 0 |  | 12960
|  |  |  | 4:00 | 12840 |  | 0 |  | 12840
|  |  |  | 5:00 | 12570 |  | 0 |  | 12570
|  |  |  | 6:00 | 12390 |  | 0 |  | 12390
|  |  |  | 7:00 | 12640 |  | 0 |  | 12640
|  |  |  | 8:00 | 12520 |  | 0 |  | 12520
|  |  |  | 9:00 | 12710 |  | 0 |  | 12710
|  |  |  | 10:00 | 13290 |  | 0 |  | 13290
|  |  |  | 11:00 | 13720 |  | 0 |  | 13720
|  |  |  | 12:00 | 14150 |  | 0 |  | 14150
|  |  |  | 13:00 | 14470 |  | 0 |  | 14470
|  |  |  | 14:00 | 14640 |  | 0 |  | 14640
|  |  |  | 15:00 | 14810 |  | 0 |  | 14810
|  |  |  | 16:00 | 14780 |  | 0 |  | 14780
|  |  |  | 17:00 | 14570 |  | 0 |  | 14570
|  |  |  | 18:00 | 14570 |  | 0 |  | 14570
|  |  |  | 18:30 | 15150 |  | 0 |  | 15150
|  |  |  | 19:00 | 16040 |  | 0 |  | 16040
|  |  |  | 19:30 | 16250 |  | 0 |  | 16250
|  |  |  | 20:00 | 16200 |  | 0 |  | 16200
|  |  |  | 21:00 | 16200 |  | 0 |  | 16200
|  |  |  | 22:00 | 16160 |  | 0 |  | 16160
|  |  |  | 23:00 | 15900 |  | 0 |  | 15900
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 14150.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0 |  |  |  | 0
Probable Maximum Demand at Evening Peak: |  |  | 16250.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16052.99 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 338.36742 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:08 hrs on 19-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 18-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13590.47 | MW | 12:00 Hr. | Energy Generated |  |  | 324.8781 |  | MKWHr.
| Day Peak Demand |  |  | 13684.47 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.637 |  | MKWHr.
| Evening Peak Generation |  |  | 14670.82 | MW | 19:00 Hr. | Energy Demand |  |  | 327.5151 |  | MKWHr.
| Evening Peak Demand |  |  | 14974.82 | MW | 19:00 Hr. | Maximum Temperature |  |  | 32.7 |  | °C
| Minimum Generation of the Day |  |  | 11515.59 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 930.31 |  | MMCFD
| Maximum Generation of the Day |  |  | 15277.76 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.9357 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.2101 | 0 | 13.119 | 0 | 0 | 0.16436 | 0 | 0 | 47.4935 | Gas | 129.5994 | Gas | 454342159.4201
| Chattogram Zone |  |  | 5.6302 | 47.1036 | 2.0171 | 0 | 1.3118 | 0.14645 | 0 | 0.0984 | 56.3076 | Coal | 109.4529 | Coal | 711154042.5176
| Cumilla Zone |  |  | 31.3476 | 0 | 2.0827 | 0 | 0 | 0.47485 | 3.4502 | 0 | 37.3554 | HFO | 21.9606 | HFO | 362002336.082
| Mymensingh Zone |  |  | 0 | 0 | 1.5368 | 0 | 0 | 0.1377 | 0 | 0 | 1.6745 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 29.744 | 0 | 0 | 0 | 0 | 0.031335 | 0 | 0 | 29.7753 | Hydro | 1.3118 | Hydro | 131178
| Khulna Zone |  |  | 3.6867 | 16.8436 | 0.11875 | 0 | 0 | 0.6444 | 22.3251 | 0 | 43.6186 | Solar | 3.8269 | Solar | 60543894.9736
| Barishal Zone |  |  | 8.1904 | 44.3515 | 0.68419 | 0 | 0 | 0.004477 | 0 | 0 | 53.2306 | Import | 58.6281 | Import | 338749205.16
| Rajshahi Zone |  |  | 16.7904 | 0 | 0.72381 | 0 | 0 | 1.1451 | 32.8527 | 0 | 51.5121 | Wind | 0.0984 | Wind | 1447464
| Rangpur Zone |  |  | 0 | 1.1542 | 1.6782 | 0 | 0 | 1.0783 | 0 | 0 | 3.9106
| Total |  |  | 129.5994 | 109.4529 | 21.9606 | 0 | 1.3118 | 3.8269 | 58.6281 | 0.0984 | 324.8781
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 454342159.4201 |  | Hydro | 131178
|  |  |  | Coal | 711154042.5176 |  | Solar | 60543894.9736
|  |  |  | HFO | 362002336.082 |  | Import | 338749205.16
|  |  |  | HSD | 0 |  | Wind | 1447464
[5 empty] | Total: | 192,83,70,280 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.3251 | Peak Hr Flow | 923.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 45789181.82 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.8527 | Peak Hr Flow | 1586.82 MW at 19:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2501 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.4502 | Peak Hr Flow | 150.00 MW at 19:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 3118 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 58.6281 | Peak Hr Flow | 2659.82 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 30 |  | 5951
|  |  |  | Chattogram |  | 100 |  | 1512
|  |  |  | Cumilla |  | 0 |  | 1455
|  |  |  | Mymensingh |  | 161 |  | 1128
|  |  |  | Sylhet |  | 0 |  | 573
|  |  |  | Khulna |  | 0 |  | 1022
|  |  |  | Barishal |  | 0 |  | 511
|  |  |  | Rajshahi |  | 0 |  | 1392
|  |  |  | Rangpur |  | 0 |  | 909
|  |  |  | Total |  | 291 |  | 14453
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:01 | Purbasadipur 230/132/33kV S/S AIS Old T-4 Transformer HT is restored.
|  | 08:02 | Purbasadipur 230/132/33kV S/S AIS Old T-4 Transformer LT is restored.
| 08:34 | 09:46 | Mithapukur 132/33kV S/S TR-1(404T) LT Forced S/D Due to Red hot in isolator clam | [7 empty] | 14.5MW load
interrup.
| 08:48 | 19:32 | BSRM-Cumilla(N) 230 kV Ckt-2 Project Work S/D from Feni 230/132kV end Due to Witness Work
of SAS & DFDR
| 08:49 | 19:31 | Korerhat 400/230/132kV S/S Feni -2 Project Work S/D Due to Project work
| 09:06 | 17:49 | Keraniganj-Nawabganj 132kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to
OPGW maintenance work. and from Nawabganj 132/33kV end Due to OPGW Maintenance.
| 09:32 | 12:08 | Korerhat 400/230/132kV S/S Meghnaghat-1 Project Work S/D Due to Project work
| 09:32 | 12:09 | Madunaghat-Meghnaghat 400kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to 400
kV Korerhat ckt- 01 shutdown instructed by NLDC.
|  | 09:35 | Sylhet (South) S/S Trafo-2 HT is restored.
|  | 09:35 | Sylhet (South) S/S Trafo-2 LT is restored.
| 10:31 | 12:24 | Aminbazar-Meghnaghat 400kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to for
maintenance work
|  | 10:45 | Tangail 132/33kV S/S Tr-1 HT is restored.
|  | 10:45 | Tangail 132/33kV S/S Tr-1 LT is restored.
| 11:15 | 16:47 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-1 Scheduled S/D Due to Conductor
Shifting from Exiting line tower to ERS tower
| 11:15 | 16:47 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Scheduled S/D Due to Conductor
Shifting from Exiting line tower to ERS tower
| 11:25 | 12:42 | Kabirpur 132/33kV S/S XFR, T-I LT Scheduled S/D Due to 33 kV bus maintenance. | [7 empty] | 70.0MW load
interrup.
| 11:25 | 12:41 | Kabirpur 132/33kV S/S XFR, T-I HT Scheduled S/D | [7 empty] | 70.0MW load
interrup.
| 12:00 | 13:47 | Bhulta 132/33kV S/S GT2 HT Scheduled S/D Due to 33 kV side Cable's heat srink leakage. | [7 empty] | 45.0MW load
interrup.
| 12:19 | 16:15 | Madunaghat-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to
Instruction by NLDC
| 12:20 | 16:16 | Korerhat 400/230/132kV S/S Meghnaghat-2 Project Work S/D Due to Project work
| 13:31 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U2
| 15:50 | 17:21 | BIPTC S/S 10CF22 Forced S/D Due to Corrective maintenance
|  | 15:57 | Chowmuhani 230/132/33kV S/S ATR-02 HT is restored.
|  | 15:57 | Chowmuhani 230/132/33kV S/S ATR-02 LT is restored.
| 16:19 | 17:19 | Purbasadipur 230/132/33kV S/S AIS Old T-4 Transformer HT Scheduled S/D Due to 33kv PBS | [7 empty] | 20.0MW load
|  |  | feeder maintenance. | [7 empty] | interrup.
| 17:05 | 21:56 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 Forced S/D Due to instructed by NLDC
AE sir due to reduce system voltage
| 17:05 | 21:57 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Forced S/D Due to instructed by NLDC
AE sir due to reduce system voltage
| 17:11 | 21:57 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-1 Forced S/D Due to instructed by
NLDC AE sir due to reduce system voltage
| 17:11 | 21:57 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Forced S/D Due to instructed by
NLDC AE sir due to reduce system voltage
|  | 17:42 | Tangail 132/33kV S/S Tr-2 HT is restored.
| 17:42 | 17:50 | Kasba 132/33kV S/S TR-1 LT Forced S/D Due to SD for pbs grounding wire repair | [7 empty] | 10.0MW load
interrup.
|  | 17:42 | Tangail 132/33kV S/S Tr-2 LT is restored.
| 17:50 | 20:03 | Kasba 132/33kV S/S TR-1 HT Scheduled S/D | [7 empty] | 14.0MW load
interrup.
|  | 18:43 | Sonargaon 132/33kV S/S Bashundhara Line is restored.
| 20:06 | 20:10 | Barishal 132/33kV S/S T-2 (415T) LT Tripped showing Instt. O/V, Definte O/C relays Due to | [7 empty] | 30.0MW load
|  |  | 33kV Dopdopia WZPDCL feeder fault | [7 empty] | interrup.
| 20:10 | 20:40 | Madanganj 132/33kV S/S GT-2 LT Tripped showing 132 kv Side o/c and E/F 33 KV side phase | [7 empty] | 25.0MW load
|  |  | instant fault Fault in PBS line relays Due to Heavy rain and storm | [7 empty] | interrup.
| 20:10 | 20:37 | Madanganj 132/33kV S/S GT-2 HT Tripped showing 132 KV side o/c and E/F 33 kv side phase | [7 empty] | 25.0MW load
|  |  | instant fault Fault in PBS line relays Due to Heavy rain and storm | [7 empty] | interrup.
| 20:21 | 22:24 | Bhandaria 132/33kV S/S Transformer-2 LT Tripped showing Over current and earth fault | [7 empty] | 6.0MW load
|  |  | relays Due to Oxilary transformer DS pin insulator Blust | [7 empty] | interrup.
| 20:21 | 22:21 | Bhandaria 132/33kV S/S Transformer-1 LT Tripped showing Over current and earth fault | [7 empty] | 6.0MW load
|  |  | relays Due to Oxilary transformer DS pin insulator Blust | [7 empty] | interrup.
| 20:41 | 21:49 | Kasba 132/33kV S/S TR-1 HT Scheduled S/D Due to for grounding maintenance at 33 kV switch | [7 empty] | 18.0MW load
|  |  | yard. | [7 empty] | interrup.
| 20:41 | 21:49 | Kasba 132/33kV S/S TR-1 LT Scheduled S/D Due to for grounding maintenance at 33 kV switch | [7 empty] | 18.0MW load
|  |  | yard. | [7 empty] | interrup.
| 21:28 | 22:20 | Bhandaria 132/33kV S/S Transformer-1 HT Forced S/D Due to Oxilary transformer DS pin | [7 empty] | 6.0MW load
|  |  | insulator Blust | [7 empty] | interrup.
| 21:28 | 22:23 | Bhandaria 132/33kV S/S Transformer-2 HT Forced S/D Due to Auxilary transformer DS pin | [7 empty] | 6.0MW load
|  |  | insulator Blust | [7 empty] | interrup.
| 21:39 | 22:23 | Jhenaidah-Kushtia 132kV Ckt-1 Tripped from Kushtia 132/33kV end showing SOTF Optd
relays.
| 21:40 | 22:25 | Jhenaidah 132/33kV S/S Jhenaidah-Kushtia 132kV Circuit-1(L1) Tripped showing Distance
Relay, E/F relays.
| 23:17 | 01:12 | Chauddagram 132/33kV S/S 132 kv T-1 HT Scheduled S/D Due to Red hot maintenance for PBS | [7 empty] | 40.0MW load
|  |  | end. | [7 empty] | interrup.
| 23:17 | 01:12 | Chauddagram 132/33kV S/S 132 kv T-1 LT Scheduled S/D Due to Red hot maintenance for PBS | [7 empty] | 40.0MW load
|  |  | end | [7 empty] | interrup.
| 05:33 |  | Mymensingh 132/33kV S/S Transformer-1 (404T) LT Scheduled S/D Due to To perform high
temperature mitigate works of 132kV B-Bus DS Net-1 and T-1 (404T).
| 05:33 |  | Mymensingh 132/33kV S/S Transformer-1 (404T) HT Scheduled S/D Due to To perform high
temperature mitigate works of 132kV B-Bus DS Net-1 and T-1 (404T).
| 05:45 |  | Mymensingh-Netrokona 132kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end Due to To
perform high temperature mitigate works of 132kV B-Bus DS Net-1 and T-1 (404T).
| 06:00 |  | Minimum Generation: 12262 MW
| 06:36 |  | Kalurghat 132/33kV S/S TRFO-02(516T) LT Scheduled S/D Due to High temperature
| 06:36 |  | Aminbazar-Kallyanpur 132kV Ckt-2 Scheduled S/D from Kallyanpur 132/33kV end Due to OPGW
Maintenance Work
| 06:53 |  | Mymensingh 132/33kV S/S Bus B Scheduled S/D Due to To perform high temperature mitigate
works of 132kV B-Bus DS Net-1 R-phase and T-1 (404T) R-phase.
| 07:06 |  | Full load interruption has been occurring in Kurigram Grid S/S due to 132 kV bus shutdown
for high temperature maintenance work.
| 07:06 |  | Kurigram-Lalmonirhat 132kV Ckt-1 Forced S/D from Kurigram 132/33kV end Due to 132kv bus | [7 empty] | 50.0MW load
|  |  | B phase Red hot | [7 empty] | interrup. Kurigram
132/33kV end
| 07:06 |  | Lalmonirhat-Rangpur 132 kV Ckt-2 Forced S/D from Kurigram 132/33kV end Due to 132kv bus B | [7 empty] | 50.0MW load
|  |  | phase Red hot | [7 empty] | interrup. Kurigram
132/33kV end
| 07:15 |  | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat Forced S/D Due to Kurigram bus maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 18-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 370 | 8812800 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1153530 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 285 | 7290794 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 259560 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 104 | 683520 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 263180 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 218419 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 465600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 444240 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 793920 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 292 | 4111145 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 93 | 1929456 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1391040 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 601920 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 164360 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 149760 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 10357272.73 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 277 | 6839390 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 124 | 1563600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2424 | 47493506.73
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 39018.6 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 121770 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 324960 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 55 | 1311780 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5315835 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 10 | 298582 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 54 | 208656 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 16 | 308863 | plant availability zero
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 5 | 314400 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 53 | 530880 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24680 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 70255 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 40 | 235855 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1150 | 26710906 | U2 on AGC
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 2 | 98400 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1000 | 20392727.27 | AGC
Chattogram Area Total |  |  |  |  | 4898.863 | 2638 | 56307567.87
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 0 | 0 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 325 | 8790300 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 342 | 8146000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 315 | 7565000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 33 | 754272 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 44 | 959040 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1250356 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 63 | 389745 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 185568 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 144 | 3417013 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 63 | 645600 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 150 | 3450240 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 238291 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 465640 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 50 | 99180 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 17 | 153720 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 66 | 370560 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 474845 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1748 | 37355370
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 83 | 919200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 412800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 129500 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 204840 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 109 | 1674540
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 31335 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 993000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 725280 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 144 | 3471954.55 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 154 | 3495000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 28 | 664320 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 51 | 1639680 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 104 | 2443150 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 377568 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7299000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 354 | 8635000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1229 | 29775287.55
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 923 | 22325091 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 42720 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 50688 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 143 | 3686688 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 25344 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 644400 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1029 | 16843635 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2095 | 43618566
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 620 | 15752727 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 24 | 504192 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 100 | 2882000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 780 | 23384727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 180 | 5308430 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 180000 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 171 | 5214000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4477 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1892 | 53230553.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 245232 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 21309 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 140 | 3759455 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 140 | 3894527 | Liquid fuel shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 367 | 9136436 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 33434 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 13963 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 27648 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 10 | 375360 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 252096 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 21360 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1586.82 | 32852727 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 278544 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 599960 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2278.82 | 51512051
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1154182 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 985699 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 24985.68 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 109 | 692492 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 77689 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 975600 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 257 | 3910647.68
Eastern Grid Total |  |  |  |  | 17418.042 | 8148 | 172606272.15
Western Grid Total |  |  |  |  | 11852.195 | 6522.82 | 152271817.95
National Grid Total |  |  |  |  | 29270.237 | 14670.82 | 324878090.1
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 18-05-2026
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10328.21 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3834.9 | MW
i) Dhaka area |  |  | 5921.01 |  | MW | i) Khulna area |  |  |  | 1022.5 | MW
ii) Chattogram area |  |  | 1412.2 |  | MW | ii) Barishal area |  |  |  | 511 | MW
iii) Cumilla area |  |  | 1455 |  | MW | iii) Rajshahi area |  |  |  | 1392.4 | MW
iv) Mymensingh area |  |  | 967 |  | MW | iv) Rangpur area |  |  |  | 909 | MW
v) Sylhet area |  |  | 573 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14163.11 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 7 | 05:00 | 67 | Hasnabad | 99 | 00:00 | 133 | Natore | 164 | 00:00
2 | AKSML | 98.4 | 02:00 | 68 | Hathazari | 95 | 20:00 | 134 | Nawabganj | 64.2 | 00:00
3 | Aftabnagar | 44 | 00:00 | 69 | Hatirjheel | 55 | 13:00 | 135 | Netrakona | 115 | 22:00
4 | Agargaon | 124 | 13:00 | 70 | Ishurdi | 86 | 00:00 | 136 | New | 81.6 | 12:00
5 | Agrabad | 78 | 14:00 | 71 | Jaldhaka | 77 | 19:00 | 137 | Niamatpur | 76 | 00:00
6 | Amnura | 31 | 00:00 | 72 | Jamalpur | 92 | 13:00 | 138 | Noapara | 48 | 02:00
7 | Ashuganj | 92 | 23:00 | 73 | Jashore | 172 | 14:00 | 139 | PHP | 13 | 21:00
8 | BSRM | 192 | 00:00 | 74 | Jhenaidah | 119 | 00:00 | 140 | Pabna | 105 | 00:00
9 | Bagerhat | 87 | 03:00 | 75 | Joydebpur | 157 | 00:00 | 141 | Palashbari | 114 | 19:30
10 | Bajitpur | 79 | 19:00 | 76 | Joypurhat | 60 | 00:00 | 142 | Panchagarh | 57 | 19:00
11 | Bakerganj | 12.6 | 21:00 | 77 | Juldah | 15.5 | 11:00 | 143 | Patiya | 11 | 02:00
12 | Bakulia | 102 | 00:00 | 78 | KSRM | 13 | 10:00 | 144 | Patuakhali | 76 | 19:30
13 | Banani | 52.4 | 15:00 | 79 | Kabirpur | 272 | 18:30 | 145 | Payra | 36 | 01:00
14 | Bangabhaban | 19 | 10:00 | 80 | Kachua | 101 | 00:00 | 146 | Postogola | 58 | 00:00
15 | Barapukuria | 63 | 19:00 | 81 | Kaliganj | 22 | 00:00 | 147 | Pubail | 30 | 19:00
16 | Barguna | 24 | 00:00 | 82 | Kallyanpur | 120 | 00:00 | 148 | Purbachal | 35 | 19:00
17 | Barishal | 118 | 13:00 | 83 | Kalurghat | 55 | 22:00 | 149 | Purbasadipur | 132 | 20:00
18 | Barishal-230 | 112 | 00:00 | 84 | Kamrangirchar | 86 | 13:00 | 150 | Rahanpur | 39 | 00:00
19 | Baroaulia | 67 | 21:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 30 | 12:00
20 | Baroirhat | 69 | 20:00 | 86 | Kasba | 40 | 22:00 | 152 | Rajbari | 92 | 00:00
21 | Bashundhara | 198 | 19:00 | 87 | Kazla | 115 | 13:00 | 153 | Rajendrapur | 124 | 23:00
22 | BashundharaCement | 6 | 00:00 | 88 | Keranigonj | 90 | 19:00 | 154 | Rajshahi | 138 | 00:00
23 | Beanibazar | 76 | 00:00 | 89 | Khagrachori | 36 | 19:00 | 155 | Rajshahi-230 | 94 | 00:00
24 | Benapole | 70 | 14:00 | 90 | Khulna | 68 | 13:00 | 156 | Ramganj | 122 | 00:00
25 | Bhaluka | 168 | 20:00 | 91 | Khulshi | 206 | 21:00 | 157 | Rampur | 48 | 00:00
26 | Bhandaria | 61 | 00:00 | 92 | Kishoreganj | 112 | 23:00 | 158 | Rangamati | 17 | 22:00
27 | Bhangura | 39 | 00:00 | 93 | Kodda | 331 | 19:00 | 159 | Rangpur | 136 | 19:00
28 | Bheramara(GK) | 73 | 00:00 | 94 | Kulaura | 46 | 19:30 | 160 | Ruppur | 4.4 | 16:00
29 | Bhulta | 218 | 15:00 | 95 | Kurigram | 60 | 19:00 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 86 | 00:00 | 96 | Kushtia | 174 | 00:00 | 162 | Saidpur | 89 | 20:00
31 | Bogura | 165 | 20:00 | 97 | Laksam | 37 | 14:00 | 163 | Santhia | 36 | 00:00
32 | Borhanuddin | 97 | 00:00 | 98 | Lakshmipur | 44 | 20:00 | 164 | Satkhira | 136 | 19:00
33 | Brahmanbaria | 131 | 00:00 | 99 | Lalbag | 84 | 13:00 | 165 | Satmasjid | 105 | 19:00
34 | Cantonment | 120 | 18:30 | 100 | Lalmonirhat | 52 | 18:30 | 166 | Savar | 228 | 19:00
35 | Chandina | 23 | 19:00 | 101 | MI_Cement | 13.2 | 17:00 | 167 | SevenRings | 18.69 | 03:00
36 | Chandpur | 92 | 00:00 | 102 | Madanganj | 47 | 19:00 | 168 | ShahCement | 44 | 01:00
37 | Chandraghona | 39 | 19:00 | 103 | Madaripur | 127 | 00:00 | 169 | Shahjadpur | 85 | 13:00
38 | Chapai | 79 | 23:00 | 104 | Madartek | 85 | 00:00 | 170 | Shahjibazar | 117 | 23:00
39 | Charsaidpur | 45 | 17:00 | 105 | Madunaghat | 57 | 00:00 | 171 | Shahmirpur | 67 | 01:00
40 | Chauddagram | 81 | 19:30 | 106 | Magura | 72 | 00:00 | 172 | Shariatpur | 99 | 00:00
41 | Chhatak | 35 | 20:00 | 107 | Mahasthangarh | 79 | 00:00 | 173 | Sherpur | 106 | 17:00
42 | Chowmuhani | 162 | 20:00 | 108 | Maijdee | 57 | 00:00 | 174 | Shikalbaha | 29.5 | 00:00
43 | Chuadanga | 126 | 00:00 | 109 | Manikganj | 140 | 19:30 | 175 | Shitalakhya | 90.1 | 16:00
44 | Coxsbazar | 138 | 14:00 | 110 | Maniknagar | 79 | 00:00 | 176 | Sholosohor | 50 | 19:00
45 | Cumilla(N) | 125 | 01:00 | 111 | Matarbari | 54 | 07:00 | 177 | Shomvuganj | 16 | 19:00
46 | Cumilla(S) | 173 | 00:00 | 112 | Matuail | 82 | 12:00 | 178 | Shyampur | 162 | 01:00
47 | Daganbhuiyan | 46 | 19:00 | 113 | Metrorail_Motijheel | 28 | 18:30 | 179 | Siddhirganj | 132 | 18:00
48 | Daudkandi | 157 | 20:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 120 | 20:00
49 | DhakaUniversity | 96 | 13:00 | 115 | Millgate | 105 | 12:00 | 181 | Sonargaon | 152 | 00:00
50 | Dhamrai | 118 | 21:00 | 116 | Mirpur | 158 | 19:30 | 182 | Sreemongol | 66 | 19:30
51 | Dhanmondi | 106.5 | 13:00 | 117 | Mirsorai | 48 | 11:00 | 183 | Sreepur | 93 | 18:30
52 | Dohazari | 101 | 05:00 | 118 | Mirzapur | 45 | 00:00 | 184 | Srinagar | 51.8 | 19:00
53 | Faridpur | 194 | 00:00 | 119 | Mithapukur | 50 | 21:00 | 185 | Sunamganj | 58 | 22:00
54 | Fatullah | 98 | 15:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 66 | 19:30
55 | Fenchuganj | 47 | 00:00 | 121 | Mogbazar | 100.2 | 15:00 | 187 | Sylhet-132 | 111 | 00:00
56 | Feni | 111 | 00:00 | 122 | Mongla | 51 | 04:00 | 188 | TK | 24 | 18:30
57 | GPH | 1 | 00:00 | 123 | Motijheel | 49 | 13:00 | 189 | Tangail | 178 | 00:00
58 | Ghatail | 82 | 01:00 | 124 | Muktagacha | 30 | 18:30 | 190 | Taraganj | 22 | 19:30
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 120 | 00:00 | 191 | Tasnim | 37 | 15:00
60 | Ghorashal-230 | 117 | 12:00 | 126 | Muradnagar | 50 | 19:30 | 192 | Thakurgaon | 101 | 20:00
61 | Goalpara | 42 | 07:00 | 127 | Mymensingh | 148 | 19:00 | 193 | Tongi | 155 | 11:00
62 | Gollamari | 122 | 00:00 | 128 | Nabinagar | 89 | 18:30 | 194 | Ullahpara | 38 | 00:00
63 | Gopalganj | 119.2 | 00:00 | 129 | Naogaon | 140 | 00:00 | 195 | Ullon | 46 | 00:00
64 | Gulshan | 130 | 14:00 | 130 | Narail | 63 | 00:00 | 196 | Uttara | 96 | 16:00
65 | Halishahar | 100.5 | 09:00 | 131 | Narinda | 74 | 13:00 | 197 | UttaraNew | 56 | 00:00
66 | HaripurSBU | 142 | 01:00 | 132 | Narshingdi | 191 | 19:30 | 198 | Zigatola | 93 | 18:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 18-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15277.76 | 108 |  | 15390.62
1:00 | 14471.61 | 90 |  | 14565.61
2:00 | 13815.84 | 68 |  | 13886.84
3:00 | 13060.09 | 58 |  | 13121.09
4:00 | 12480.29 | 57 |  | 12540.29
5:00 | 11960.65 | 20 |  | 11981.65
6:00 | 11515.59 | 58 |  | 11576.59
7:00 | 11648.4 | 24 |  | 11673.4
8:00 | 11895.46 | 28 |  | 11924.46
9:00 | 12123.2 | 48 |  | 12173.2
10:00 | 12562.23 | 78 |  | 12644.23
11:00 | 12857.38 | 93 |  | 12954.38
12:00 | 13590.47 | 90 |  | 13684.47
13:00 | 13706.75 | 83 |  | 13793.75
14:00 | 13981.8 | 59 |  | 14043.8
15:00 | 14123.15 | 96 |  | 14223.15
16:00 | 14161.31 | 138 |  | 14305.52
17:00 | 13825.3 | 122 |  | 13952.3
18:00 | 13584.65 | 136 |  | 13726.65
19:00 | 14670.82 | 291 |  | 14974.82
19:30 | 14476.6 | 290 |  | 14779.6
20:00 | 13784.76 | 302 |  | 14100.76
21:00 | 14051.94 | 247 |  | 14309.94
22:00 | 14081.8 | 209 |  | 14299.8
23:00 | 14410.62 | 134 |  | 14550.62
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 18-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8203 | 7074.76 | 15277.76 | DAILY GENERATION CURVE
00:30 | 7898 | 6976.685 | 14874.685
01:00 | 7593 | 6878.61 | 14471.61 | 18-05-2026
01:30 | 7439 | 6704.725 | 14143.725
02:00 | 7285 | 6530.84 | 13815.84
02:30 | 7140 | 6297.965 | 13437.965
03:00 | 6995 | 6065.09 | 13060.09
03:30 | 6801 | 5969.19 | 12770.19
04:00 | 6607 | 5873.29 | 12480.29
04:30 | 6475.5 | 5744.97 | 12220.47
05:00 | 6344 | 5616.65 | 11960.65
05:30 | 6309.14 | 5428.98 | 11738.12
06:00 | 6274.28 | 5241.31 | 11515.59
06:30 | 6342.705 | 5239.29 | 11581.995
07:00 | 6411.13 | 5237.27 | 11648.4
07:30 | 6425.665 | 5346.265 | 11771.93
08:00 | 6440.2 | 5455.26 | 11895.46
08:30 | 6503.505 | 5505.825 | 12009.33
09:00 | 6566.81 | 5556.39 | 12123.2
09:30 | 6694.62 | 5648.095 | 12342.715
10:00 | 6822.43 | 5739.8 | 12562.23
10:30 | 6829.205 | 5880.6 | 12709.805
11:00 | 6835.98 | 6021.4 | 12857.38
11:30 | 7071.35 | 6152.575 | 13223.925
12:00 | 7306.72 | 6283.75 | 13590.47
12:30 | 7264.415 | 6384.195 | 13648.61
13:00 | 7222.11 | 6484.64 | 13706.75
13:30 | 7307.005 | 6537.27 | 13844.275
14:00 | 7391.9 | 6589.9 | 13981.8
14:30 | 7387.19 | 6665.285 | 14052.475
15:00 | 7382.48 | 6740.67 | 14123.15
15:30 | 7317.45 | 6824.78 | 14142.23
16:00 | 7252.42 | 6908.89 | 14161.31
16:30 | 7214.115 | 6779.19 | 13993.305
17:00 | 7175.81 | 6649.49 | 13825.3
17:30 | 7110.505 | 6594.47 | 13704.975
18:00 | 7045.2 | 6539.45 | 13584.65
18:30 | 7596.6 | 6531.135 | 14127.735
19:00 | 8148 | 6522.82 | 14670.82
19:30 | 8084 | 6392.6 | 14476.6
20:00 | 7467 | 6317.76 | 13784.76
20:30 | 7528 | 6390.35 | 13918.35 |  | Executive Engineer
21:00 | 7589 | 6462.94 | 14051.94 |  | Network Operation Division
21:30 | 7547 | 6519.87 | 14066.87
22:00 | 7505 | 6576.8 | 14081.8
22:30 | 7497.5 | 6748.71 | 14246.21
23:00 | 7490 | 6920.62 | 14410.62

## En-Curve
QF-LDC-12
Date | 18-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3691 | 1669 | 907 | 0 | 174 | 1422.76 | 55 | 4753 | 0 | 692 | 1914 | 0 | 0 | 0 | 108 | DAILY ENERGY CURVE
00:30 | 3695 | 1613.5 | 915 | 0 | 171 | 1434.685 | 55 | 4669.5 | 0 | 599 | 1722 | 0 | 0 | 0 | 99 | 18-05-2026
01:00 | 3699 | 1558 | 923 | 0 | 168 | 1446.61 | 55 | 4586 | 0 | 506 | 1530 | 0 | 0 | 0 | 90
01:30 | 3710.5 | 1591.5 | 923.5 | 0 | 165 | 1448.225 | 55 | 4528 | 0 | 358 | 1363.5 | 0 | 0 | 0.5 | 79 | Energy Generated | 324.8781 |  | MKWHr
02:00 | 3722 | 1625 | 924 | 0 | 162 | 1449.84 | 55 | 4470 | 0 | 210 | 1197 | 0 | 0 | 1 | 68 | Energy not Served | 2.637 |  | MKWHr
02:30 | 3697 | 1596 | 924 | 0 | 159 | 1446.965 | 55 | 4431.5 | 0 | 158 | 969.5 | 0 | 0 | 1 | 63 | Total Energy Requirement | 327.5151 |  | MKWHr
03:00 | 3672 | 1567 | 924 | 0 | 156 | 1444.09 | 55 | 4393 | 0 | 106 | 742 | 0 | 0 | 1 | 58
03:30 | 3687 | 1555 | 924 | 0 | 155 | 1394.19 | 55 | 4389.5 | 0 | 101.5 | 506 | 0 | 0 | 3 | 57.5
04:00 | 3702 | 1543 | 924 | 0 | 154 | 1344.29 | 55 | 4386 | 0 | 97 | 270 | 0 | 0 | 5 | 57
04:30 | 3721.5 | 1540 | 924 | 0 | 151 | 1284.97 | 55 | 4252.5 | 0 | 76.5 | 212.5 | 0 | 0 | 2.5 | 38.5
05:00 | 3741 | 1537 | 924 | 0 | 148 | 1225.65 | 55 | 4119 | 0 | 56 | 155 | 0 | 0 | 0 | 20
05:30 | 3773.5 | 1601 | 924 | 0 | 146 | 1101.865 | 55 | 3968 | 9.755 | 35.5 | 123.5 | 0 | 0 | 0 | 39
06:00 | 3806 | 1665 | 924 | 0 | 144 | 978.08 | 55 | 3817 | 19.51 | 15 | 92 | 0 | 0 | 0 | 58
06:30 | 3815.5 | 1693.5 | 923.5 | 0 | 127 | 977.535 | 55 | 3837.5 | 35.96 | 20 | 96.5 | 0 | 0 | 0 | 41
07:00 | 3825 | 1722 | 923 | 0 | 110 | 976.99 | 55 | 3858 | 52.41 | 25 | 101 | 0 | 0 | 0 | 24
07:30 | 3823 | 1692 | 923.5 | 0 | 119 | 978.01 | 55 | 3938 | 111.92 | 25 | 106.5 | 0 | 0 | 0 | 26
08:00 | 3821 | 1662 | 924 | 0 | 128 | 979.03 | 55 | 4018 | 171.43 | 25 | 112 | 0 | 0 | 0 | 28
08:30 | 3832 | 1627.5 | 924 | 0 | 124 | 978.495 | 55 | 4087 | 216.835 | 27.5 | 137 | 0 | 0 | 0 | 38
09:00 | 3843 | 1593 | 924 | 0 | 120 | 977.96 | 55 | 4156 | 262.24 | 30 | 162 | 0 | 0 | 0 | 48
09:30 | 3828.5 | 1609.5 | 924 | 0 | 123 | 977.925 | 55 | 4205.5 | 373.79 | 42 | 202.5 | 0 | 0 | 1 | 63
10:00 | 3814 | 1626 | 924 | 0 | 126 | 977.89 | 55 | 4255 | 485.34 | 54 | 243 | 0 | 0 | 2 | 78
10:30 | 3833 | 1636.5 | 924 | 0 | 122 | 1048.54 | 55 | 4211 | 559.765 | 64 | 253.5 | 0 | 0 | 2.5 | 85.5
11:00 | 3852 | 1647 | 924 | 0 | 118 | 1119.19 | 55 | 4167 | 634.19 | 74 | 264 | 0 | 0 | 3 | 93
11:30 | 3862 | 1672 | 924 | 0 | 120 | 1198.58 | 55 | 4310 | 582.845 | 89.5 | 405 | 0 | 0 | 5 | 91.5
12:00 | 3872 | 1697 | 924 | 0 | 122 | 1277.97 | 55 | 4453 | 531.5 | 105 | 546 | 0 | 0 | 7 | 90
12:30 | 3807.5 | 1659 | 924 | 0 | 113 | 1395.505 | 55 | 4413.5 | 501.605 | 115 | 657.5 | 0 | 0 | 7 | 86.5
13:00 | 3743 | 1621 | 924 | 0 | 104 | 1513.04 | 55 | 4374 | 471.71 | 125 | 769 | 0 | 0 | 7 | 83
13:30 | 3759.5 | 1644.5 | 924 | 0 | 120 | 1513.37 | 55 | 4422.5 | 487.905 | 142 | 769 | 0 | 0 | 6.5 | 71
14:00 | 3776 | 1668 | 924 | 0 | 136 | 1513.7 | 55 | 4471 | 504.1 | 159 | 769 | 0 | 0 | 6 | 59
14:30 | 3747 | 1670.5 | 924 | 0 | 138 | 1513.98 | 55 | 4704 | 412.995 | 159 | 721 | 0 | 0 | 7 | 77.5
15:00 | 3718 | 1673 | 924 | 0 | 140 | 1514.26 | 55 | 4937 | 321.89 | 159 | 673 | 0 | 0 | 8 | 96
15:30 | 3697.5 | 1630.5 | 924 | 0 | 137 | 1543.17 | 55 | 5037 | 273.56 | 164 | 674 | 0 | 0 | 6.5 | 117
16:00 | 3677 | 1588 | 924 | 0 | 134 | 1572.08 | 55 | 5137 | 225.23 | 169 | 675 | 0 | 0 | 5 | 138
16:30 | 3560.5 | 1489.5 | 924 | 0 | 137 | 1580.055 | 55 | 5109 | 147.25 | 237 | 746.5 | 0 | 0 | 7.5 | 130
17:00 | 3444 | 1391 | 924 | 0 | 140 | 1588.03 | 55 | 5081 | 69.27 | 305 | 818 | 0 | 0 | 10 | 122
17:30 | 3417 | 1456 | 924 | 0 | 136 | 1587.895 | 55 | 4843 | 43.08 | 357.5 | 871 | 0 | 0 | 14.5 | 129
18:00 | 3390 | 1521 | 924 | 0 | 132 | 1587.76 | 55 | 4605 | 16.89 | 410 | 924 | 0 | 0 | 19 | 136
18:30 | 3511.5 | 1526.5 | 923.5 | 0 | 141 | 1587.29 | 55 | 4702 | 8.445 | 443 | 1219 | 0 | 0 | 10.5 | 213.5
19:00 | 3633 | 1532 | 923 | 0 | 150 | 1586.82 | 55 | 4799 | 0 | 476 | 1514 | 0 | 0 | 2 | 291
19:30 | 3767 | 1524 | 924 | 0 | 158 | 1592.6 | 55 | 4742 | 0 | 409 | 1304 | 0 | 0 | 1 | 290
20:00 | 3692 | 1422 | 923 | 0 | 160 | 1589.76 | 55 | 4614 | 0 | 391 | 938 | 0 | 0 | 0 | 302
20:30 | 3762.5 | 1545.5 | 923.5 | 0 | 164 | 1589.85 | 55 | 4646 | 0 | 391 | 838 | 0 | 0 | 3 | 274.5
21:00 | 3833 | 1669 | 924 | 0 | 168 | 1589.94 | 55 | 4678 | 0 | 391 | 738 | 0 | 0 | 6 | 247
21:30 | 3769.5 | 1686.5 | 923.5 | 0 | 169 | 1525.87 | 55 | 4809.5 | 0 | 391 | 734 | 0 | 0 | 3 | 228
22:00 | 3706 | 1704 | 923 | 0 | 170 | 1461.8 | 55 | 4941 | 0 | 391 | 730 | 0 | 0 | 0 | 209
22:30 | 3682.5 | 1717.5 | 923.5 | 0 | 172 | 1462.71 | 42.5 | 5140 | 0 | 391 | 714.5 | 0 | 0 | 0 | 171.5
23:00 | 3659 | 1731 | 924 | 0 | 174 | 1463.62 | 30 | 5339 | 0 | 391 | 699 | 0 | 0 | 0 | 134
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 18-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 97 | -7 | 432 | 50 | 1416 | 344 | Ishurdi-Ghorashal Ckt-1 | Export | 3178181.82
1:00 | 102 | -11 | 450 | 50 | 1430 | 372
2:00 | 98 | -14 | 476 | 56 | 1352 | 352 |  | Import | 0
3:00 | 82 | -21 | 432 | 70 | 1206 | 296
4:00 | 104 | -9 | 434 | 42 | 1270 | 348 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 89 | -14 | 348 | 2 | 1118 | 334
6:00 | 74 | -14 | 356 | 54 | 902 | 376 |  | Import | 0
7:00 | 76 | -10 | 364 | 66 | 952 | 348
8:00 | 106 | 0 | 430 | 92 | 1250 | 430 | Sirajganj-Sreepur Ckt-1 | Export | 3142000
9:00 | 131 | 15 | 466 | 128 | 1344 | 478
10:00 | 146 | 17 | 520 | 152 | 1408 | 522 |  | Import | 0
11:00 | 161 | 22 | 586 | 196 | 1484 | 576
12:00 | 142 | 4 | 574 | 180 | 1398 | 488 | Sirajganj-Sreepur Ckt-2 | Export | 3149000
13:00 | 128 | 3 | 544 | 128 | 1414 | 500
14:00 | 131 | 3 | 610 | 180 | 1562 | 586 |  | Import | 0
15:00 | 137 | 17 | 600 | 204 | 1744 | 666
16:00 | 149 | 19 | 608 | 194 | 1874 | 772 | Gopalganj-Aminbazar Ckt-1 | Export | 18140000
17:00 | 183 | 32 | 656 | 186 | 1908 | 742
18:00 | 212 | 45 | 708 | 198 | 1928 | 786 |  | Import | 0
18:30 | 238 | 46 | 772 | 220 | 2108 | 830
19:00 | 177 | 27 | 600 | 148 | 1724 | 736 | Gopalganj-Aminbazar Ckt-2 | Export | 18180000
19:30 | 144 | 14 | 516 | 96 | 1714 | 706
20:00 | 158 | 15 | 566 | 114 | 1962 | 776 |  | Import | 0
21:00 | 147 | 11 | 560 | 116 | 1822 | 722
22:00 | 150 | 12 | 554 | 130 | 1968 | 684 |  | Total Export | 45789181.82
23:00 | 151 | 11 | 560 | 150 | 1986 | 646 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 18-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 386 | 05:00 | 358 | 15:00 | Madunaghat | 396 | 06:00 | 383 | 16:00
Amtali | 412 | 06:00 | 405 | 15:00 | Meghnaghat | 387 | 06:00 | 358 | 15:00
Ashuganj | 415 | 6:00 | 380 | 15:00 | Payra | 413 | 05:00 | 407 | 15:00
Bhulta | 408 | 05:00 | 370 | 15:00 | Rahanpur | 409 | 06:00 | 383 | 19:30
Bibiana | 399 | 05:00 | 381 | 16:00 | Rampal | 399 | 06:00 | 382 | 13:00
BIPTC | 401 | 19:00 | 386 | 00:00
Bogura | 399 | 06:00 | 367 | 19:30
Gopalganj | 397 | 06:00 | 375 | 16:00
Kaliakoir | 381 | 05:00 | 353 | 16:00
Korerhat | 395 | 06:00 | 374 | 16:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 231 | 06:00 | 208 | 16:00 | Jhenaidah | 231 | 18:30 | 210 | 15:00
AKSML | 229.9 | 13:00 | 220.8 | 16:00 | Kachua | 226 | 10:00 | 218 | 16:00
Aminbazar | 231 | 06:00 | 210 | 15:00 | Kaliakoir | 234 | 05:00 | 211 | 15:00
Ashuganj | 236 | 06:00 | 212 | 15:00 | Keranigonj | 230 | 06:00 | 207 | 16:00
Ashuganj-400 | 236 | 06:00 | 212 | 15:00 | Khulna(S) | 232 | 20:00 | 211 | 13:00
Baghabari | 234 | 06:00 | 221 | 15:00 | Korerhat | 227 | 10:00 | 219 | 16:00
Barapukuria | 230 | 03:00 | 203 | 19:30 | Madunaghat | 229 | 06:00 | 223 | 15:00
Barapukuria-230 | 230 | 03:00 | 203 | 19:30 | Madunaghat-400 | 231 | 07:00 | 223 | 16:00
Barishal | 226 | 20:00 | 217 | 15:00 | Maniknagar | 231 | 05:00 | 208 | 16:00
Bheramara | 234 | 05:00 | 220 | 16:00 | Meghnaghat | 237 | 04:00 | 223 | 15:00
Bhulta | 232 | 05:00 | 208 | 15:00 | Meghnaghat-400 | 232 | 07:00 | 213 | 15:00
Bibiana | 239 | 06:00 | 226 | 16:00 | Mirsorai | 230 | 00:00 | 217 | 16:00
BIPTC | 237 | 18:00 | 219 | 15:00 | Naogaon | 219 | 06:00 | 199 | 19:30
Bogura | 240 | 06:00 | 220 | 19:30 | Purbasadipur | 229 | 01:00 | 201 | 19:30
Bogura-400 | 240 | 06:00 | 220 | 19:30 | Rajshahi | 232 | 07:00 | 217 | 14:00
Borhanuddin | 230 | 20:00 | 225 | 15:00 | Rampal | 232 | 20:00 | 213 | 13:00
BSRM | 228 | 10:00 | 219 | 16:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 226 | 13:00 | 219 | 14:00 | Rampura | 233 | 06:00 | 206 | 16:00
Cumilla(N) | 229 | 06:00 | 213 | 15:00 | Shikalbaha | 227 | 07:00 | 220 | 15:00
Faridpur | 222 | 19:00 | 210 | 15:00 | Shyampur | 231 | 06:00 | 209 | 15:00
Fenchuganj | 240 | 05:00 | 229 | 16:00 | Siddhirganj | 228 | 05:00 | 209 | 15:00
Feni | 225 | 06:00 | 213 | 15:00 | Sirajgonj | 241 | 05:00 | 228 | 15:00
Ghorashal | 230 | 01:00 | 210 | 15:00 | Sreepur | 232 | 05:00 | 210 | 15:00
Ghorashal-230 | 232 | 06:00 | 207 | 15:00 | Tongi | 226 | 04:00 | 206 | 15:00
Gopalganj | 230 | 20:00 | 210 | 16:00
GPH | 227 | 13:00 | 222 | 17:00
Haripur | 232 | 06:00 | 209 | 15:00
Hasnabad | 230 | 05:00 | 208 | 16:00
Hathazari | 227 | 04:00 | 220 | 15:00
Ishurdi | 235 | 05:00 | 220 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 05:00 | 120 | 15:00 | Madunaghat | 133 | 00:00 | 129 | 16:00
Agargaon | 134 | 05:00 | 119 | 16:00 | Magura | 138 | 18:30 | 120 | 13:00
Agrabad | 132 | 07:00 | 126 | 15:00 | Mahasthangarh | 137 | 05:00 | 123 | 19:30
AKS | 130 | 00:00 | 125 | 15:00 | Maijdee | 126 | 10:00 | 121 | 02:00
Aminbazar | 131 | 06:00 | 114 | 15:00 | Manikganj | 130 | 00:00 | 119 | 16:00
Amnura | 134 | 06:00 | 123 | 19:30 | Maniknagar | 136 | 05:00 | 120 | 15:00
Ashuganj | 145 | 06:00 | 128 | 15:00 | Matarbari | 120 | 13:00 | 113 | 14:00
Ashuganj-230 | 145 | 06:00 | 128 | 15:00 | Matuail | 133.5 | 06:00 | 121 | 15:00
Bagerhat | 136 | 20:00 | 112 | 16:00 | Metrorail_Motijheel | 136 | 06:00 | 120 | 15:00
Bajitpur | 139 | 05:00 | 118 | 15:00 | Metrorail_Uttara | 134 | 07:00 | 119 | 16:00
Bakerganj | 132 | 18:30 | 127 | 23:00 | Millgate | 135 | 05:00 | 117 | 15:00
Bakulia | 134 | 04:00 | 128 | 14:00 | Mirpur | 130 | 05:00 | 116 | 16:00
Banani | 137 | 06:00 | 120 | 15:00 | Mirzapur | 134 | 05:00 | 120 | 15:00
Bangabhaban | 135 | 05:00 | 119 | 16:00 | Mithapukur | 137 | 06:00 | 121 | 19:30
Barapukuria | 136 | 01:00 | 119 | 19:30 | MI_Cement | 133 | 06:00 | 120 | 15:00
Barguna | 138 | 14:00 | 126 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 20:00 | 125 | 16:00 | Mogbazar | 135 | 07:00 | 121 | 15:00
Barishal-230 | 132 | 20:00 | 125 | 15:00 | Mongla | 135 | 20:00 | 113 | 16:00
Baroaulia | 132 | 00:00 | 129 | 20:00 | Motijheel | 136 | 06:00 | 119 | 16:00
Baroirhat | 130 | 07:00 | 124 | 16:00 | Muktagacha | 131 | 03:00 | 113 | 18:30
Bashundhara | 137 | 05:00 | 117 | 15:00 | Munshiganj | 132 | 05:00 | 119 | 15:00
BashundharaCement | 135 | 07:00 | 121 | 15:00 | Muradnagar | 131 | 06:00 | 119 | 15:00
Beanibazar | 132 | 06:00 | 124 | 19:00 | Mymensingh | 133 | 01:00 | 112 | 22:00
Benapole | 136 | 18:30 | 113 | 13:00 | Nabinagar | 135 | 05:00 | 119 | 15:00
Bhaluka | 135 | 05:00 | 118 | 15:00 | Naogaon | 136 | 01:00 | 120 | 19:30
Bhandaria | 130 | 21:00 | 118 | 15:00 | Narail | 140 | 18:30 | 118 | 15:00
Bhangura | 135 | 06:00 | 125 | 15:00 | Narinda | 136 | 05:00 | 120 | 15:00
Bheramara | 137 | 18:30 | 129 | 16:00 | Narshingdi | 141 | 06:00 | 115 | 15:00
Bheramara(GK) | 137 | 18:00 | 129 | 15:00 | Natore | 134 | 04:00 | 124 | 15:00
Bhulta | 127 | 09:00 | 117 | 15:00 | Nawabganj | 135 | 06:00 | 118 | 16:00
Bog-Sherpur | 138 | 06:00 | 126 | 15:00 | Netrakona | 132 | 00:00 | 114 | 12:00
Bogura | 138 | 01:00 | 128 | 15:00 | New | 135 | 06:00 | 119 | 15:00
Bogura-230 | 139 | 06:00 | 126 | 19:30 | Niamatpur | 133 | 06:00 | 122 | 19:30
Brahmanbaria | 140 | 03:00 | 121 | 23:00 | Noapara | 136 | 20:00 | 117 | 15:00
Cantonment | 134 | 06:00 | 120 | 15:00 | Pabna | 134 | 06:00 | 125 | 15:00
Chandina | 132 | 06:00 | 123 | 15:00 | Palashbari | 135 | 05:00 | 120 | 19:30
Chandpur | 130 | 00:00 | 123 | 15:00 | Panchagarh | 141 | 02:00 | 121 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 133 | 05:00 | 129 | 15:00 | Patiya | 133 | 19:00 | 127 | 16:00
Chapai | 133 | 07:00 | 124 | 21:00 | Patuakhali | 131 | 18:00 | 127 | 12:00
Charsaidpur | 132 | 06:00 | 120 | 15:00 | Payra | 135 | 18:30 | 131 | 23:00
Chauddagram | 129 | 06:00 | 123 | 15:00 | PHP | 129 | 06:00 | 124 | 16:00
Chhatak | 130 | 06:00 | 120 | 19:00 | Postogola | 133 | 05:00 | 116 | 15:00
Chowmuhani | 126 | 11:00 | 122 | 02:00 | Pubail | 141 | 05:00 | 120 | 15:00
Chuadanga | 138 | 18:30 | 115 | 16:00 | Purbachal | 136 | 05:00 | 117 | 15:00
Coxsbazar | 124 | 01:00 | 115 | 14:00 | Purbasadipur | 136 | 01:00 | 118 | 19:30
Cumilla(N) | 131 | 06:00 | 123 | 15:00 | Rahanpur | 135 | 06:00 | 126 | 19:30
Cumilla(S) | 131 | 06:00 | 123 | 19:30 | Rahanpur-400 | 135 | 06:00 | 126 | 19:30
Daganbhuiyan | 128 | 10:00 | 124 | 15:00 | Rahim | 134 | 06:00 | 121 | 16:00
Daudkandi | 128 | 05:00 | 116 | 15:00 | Rajbari | 128 | 19:30 | 118 | 15:00
DhakaUniversity | 137 | 05:00 | 120 | 15:00 | Rajendrapur | 134 | 05:00 | 116 | 15:00
Dhamrai | 134 | 06:00 | 121 | 15:00 | Rajshahi | 138 | 00:00 | 122 | 15:00
Dhanmondi | 134.6 | 06:00 | 121.5 | 15:00 | Rajshahi-230 | 133 | 06:00 | 124 | 14:00
Dohazari | 130 | 19:00 | 125 | 14:00 | Ramganj | 125 | 19:00 | 120 | 02:00
Faridpur | 130 | 19:00 | 122 | 15:00 | Rampur | 132 | 06:00 | 126 | 15:00
Fatullah | 138 | 06:00 | 115 | 15:00 | Rampura | 137 | 06:00 | 120 | 15:00
Fenchuganj | 139 | 06:00 | 131 | 16:00 | Rangamati | 132 | 08:00 | 127 | 15:00
Feni | 129 | 10:00 | 125 | 15:00 | Rangpur | 137 | 01:00 | 120 | 19:30
Feni-230 | 130 | 10:00 | 125 | 16:00 | Ruppur | 136 | 08:00 | 128 | 15:00
Ghatail | 131 | 03:00 | 114 | 18:00 | Saidpur | 136 | 06:00 | 121 | 18:00
Ghorashal | 141 | 04:00 | 123 | 15:00 | Santhia | 135 | 06:00 | 127 | 15:00
Goalpara | 138 | 20:00 | 121 | 13:00 | Satkhira | 136 | 20:00 | 114 | 15:00
Gollamari | 137 | 20:00 | 121 | 13:00 | Satmasjid | 133 | 05:00 | 119 | 16:00
Gopalganj | 134 | 20:00 | 120 | 15:00 | Savar | 129 | 04:00 | 114 | 15:00
Gopalganj-400 | 141 | 07:00 | 124 | 16:00 | SevenRings | 142 | 06:00 | 123 | 15:00
Gulshan | 135 | 04:00 | 119 | 16:00 | ShahCement | 132 | 06:00 | 120 | 15:00
Halishahar | 133 | 07:00 | 127 | 15:00 | Shahjadpur | 138 | 04:00 | 130 | 14:00
Haripur | 134 | 06:00 | 122 | 15:00 | Shahjibazar | 141 | 05:00 | 121 | 23:00
HaripurSBU | 134 | 06:00 | 122 | 16:00 | Shahmirpur | 136 | 19:00 | 128 | 16:00
Hasnabad | 132 | 04:00 | 117 | 16:00 | Shariatpur | 132 | 20:00 | 122 | 15:00
Hathazari | 133 | 06:00 | 129 | 16:00 | Sherpur | 135 | 03:00 | 110 | 20:00
Hatirjheel | 137 | 06:00 | 120 | 15:00 | Shikalbaha | 124 | 00:00 | 131 | 7:00
Ishurdi | 137 | 06:00 | 129 | 15:00 | Shikalbaha-230 | 135 | 07:00 | 130 | 15:00
Jaldhaka | 135 | 06:00 | 116 | 19:00 | Shitalakhya | 133 | 06:00 | 114 | 15:00
Jamalpur | 135 | 03:00 | 112 | 23:00 | Sholosohor | 132 | 19:00 | 127 | 16:00
Jashore | 136 | 18:30 | 114 | 15:00 | Shomvuganj | 133 | 00:00 | 115 | 15:00
Jhenaidah | 139 | 18:30 | 122 | 13:00 | Shyampur | 135 | 04:00 | 124 | 16:00
Jhenaidah-230 | 139 | 19:00 | 122 | 15:00 | Shyampur-230 | 138 | 06:00 | 124 | 16:00
Joydebpur | 139 | 05:00 | 118 | 15:00 | Siddhirganj | 134 | 05:00 | 122 | 15:00
Joypurhat | 134 | 05:00 | 121 | 19:30 | Sirajganj | 135 | 05:00 | 123 | 16:00
Juldah | 133 | 01:00 | 128 | 15:00 | Sonargaon | 131 | 07:00 | 119 | 15:00
Kabirpur | 134 | 05:00 | 114 | 15:00 | Sreemongol | 138 | 03:00 | 124 | 23:00
Kachua | 128 | 18:00 | 123 | 16:00 | Sreepur | 137 | 05:00 | 121 | 15:00
Kaliakoir | 139 | 05:00 | 124 | 15:00 | Srinagar | 135 | 06:00 | 120 | 16:00
Kaliganj | 138 | 18:30 | 120 | 13:00 | SSM | 132 | 00:00 | 132 | 00:00
Kallyanpur | 130 | 05:00 | 115 | 15:00 | Sunamganj | 128 | 01:00 | 118 | 21:00
Kalurghat | 133 | 05:00 | 128 | 16:00 | Sylhet | 133 | 06:00 | 125 | 19:00
Kamrangirchar | 135 | 06:00 | 114 | 15:00 | Sylhet-132 | 131 | 06:00 | 125 | 19:00
Kaptai | 135 | 1:00 | 131 | 16:00 | Tangail | 133 | 04:00 | 115 | 18:30
Kasba | 131 | 06:00 | 118 | 15:00 | Taraganj | 136 | 05:00 | 117 | 19:30
Kazla | 134 | 05:00 | 119 | 16:00 | Tasnim | 132 | 06:00 | 119 | 15:00
Keranigonj | 136 | 06:00 | 121 | 16:00 | Thakurgaon | 139 | 01:00 | 119 | 19:30
Khagrachori | 132 | 09:00 | 127 | 15:00 | TK | 133 | 11:00 | 129 | 22:00
Khulna | 138 | 20:00 | 118 | 15:00 | Tongi | 134 | 04:00 | 120 | 15:00
Khulna(S) | 138 | 20:00 | 121 | 13:00 | Ullahpara | 135 | 04:00 | 125 | 15:00
Khulshi | 131 | 01:00 | 124 | 16:00 | Ullon | 137 | 06:00 | 121 | 15:00
Kishoreganj | 134 | 03:00 | 117 | 15:00 | Uttara | 135 | 05:00 | 116 | 15:00
Kodda | 135 | 19:00 | 120 | 16:00 | UttaraNew | 134 | 06:00 | 117 | 15:00
Korerhat | 131 | 03:00 | 127 | 15:00 | Zigatola | 135 | 06:00 | 120 | 16:00
KSRM | 133 | 00:00 | 128 | 15:00
Kulaura | 138 | 06:00 | 129 | 23:00
Kurigram | 136 | 01:00 | 113 | 19:30
Kushtia | 138 | 18:30 | 125 | 13:00
Laksam | 127 | 10:00 | 122 | 15:00
Lakshmipur | 126 | 10:00 | 122 | 01:00
Lalbag | 134 | 05:00 | 122 | 16:00
Lalmonirhat | 134 | 06:00 | 120 | 16:00
Madanganj | 133 | 04:00 | 121 | 15:00
Madaripur | 132 | 19:30 | 126 | 00:00
Madartek | 135 | 05:00 | 119 | 15:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division