## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID BANGLADESH PLC
SYSTEM OPERATION DATA
Month: April 2026
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2026-04-01 |  | 2026-03-01 |  | 2025-04-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 15199 | 2026-04-20 | 14856.09 | 2026-03-11 | 16365.8 | 2025-04-24 | 16794 | 2025-07-23
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 19:30 Hr. |  | 21:00 Hr.
2 | Minimum Generation (MW) | 7093.7 | 2026-04-29 | 5964.82 | 2026-03-22 | 9058.19 | 2025-04-29 | - | -
|  |  | 08:00 Hr. |  | 06:00 Hr. |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 15199 | 2026-04-20 | 14856.09 | 2026-03-11 | 16365.8 | 2025-04-24 | 16794 | 2025-07-23
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 19:30 Hr. |  | 21:00 Hr.
4 | Maximum Day Peak Generation (MW) | 14194.78 | 2026-04-23 | 13333.42 | 2026-03-11 | 14594.67 | 2025-04-24 | 14965.88 | 2025-09-30
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 Hr.
5 | Maximum Evening Peak Demand (MW) Estimated | 16895.43 | 2026-04-23 | 14960.09 | 2026-03-11 | 16510.8 | 2025-04-24 | 17200 | 2024-04-29
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 19:30 Hr. |  | 21:00
6 | Average Generation (MW) at Evening Peak | 13883.6437 |  | 12524.5352 |  | 14342.7523 |  | - | -
7 | Average Generation (MW) at Day Peak | 12874.9397 |  | 11174.6671 |  | 12823.5187 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 935 | 2026-04-27 | 924 | 2026-03-30 | 924 | 2025-04-28 | 980 | 2026-02-20
|  |  | 11:30 |  | 17:00 |  | 12:00 |  | 0:30
9 | Maximum Power Import from Tripura, India (MW) | 213 | 2026-04-22 | 187 | 2026-03-11 | 106 | 2025-04-20 | 213 | 4/22/26
|  |  | 16:00 |  | 14:00 |  | 22:00 |  | 16:00
10 | Maximum Load Shed (MW) at Evening Peak | 2086 | 2026-04-22 | 100 | 2026-03-11 | 1491 | 45773 | 4395 | 04/10/2022
|  |  | 20:00 Hr. |  | 21:00 Hr. |  | 21:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 14467.04 | 2026-04-22 | 14856.09 | 2026-03-11 | 14440.43 | 45773 | 14965 | 2024-05-16
|  |  | 20:00 Hr. |  | 21:00 Hr. |  | 21:00 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 35 | 2026-04-10 | 10 | 2026-03-03 | 0 | 45748 | - | -
|  |  | 19:30 Hr. |  | 19:30 Hr. |  | 20:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 12714.59 | 2026-04-10 | 12957.59 | 2026-03-03 | 12576 | 45748 | - | -
|  |  | 19:30 Hr. |  | 19:30 Hr. |  | 20:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 2493 | 2026-04-22 | 369 | 2026-03-16 | 196 | 45759 | - | -
|  |  | 12:00 |  | 12:00 Hr. |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 13116.11 | 2026-04-22 | 11578 | 2026-03-16 | 13140 | 45759 | - | -
|  |  | 12:00 |  | 12:00 Hr. |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 62 | 2026-04-03 | 90 | 2026-03-09 | 0 | 45748 | - | -
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 13369.18 | 2026-04-03 | 12641.8 | 2026-03-09 | 10576.14 | 45748 | - | -
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 24 |  | 9 |  | 16 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 23 |  | 11 |  | 17 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 961.1528 |  | 885.5136 |  | 1417.8481 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 17.9504 |  | 14.9241 |  | 50.0825 |  | - | -
22 | Net Generation of BPDB (MKWH) | 943.2024 |  | 870.5895 |  | 1367.7656 |  | - | -
23 | Net Generation of IPP (MKWH) | 2382.4425 |  | 2322.2578 |  | 3367.4554 |  | - | -
23b | Net Generation by Generation Companies | 4165.6817 |  | 3481.2826 |  | 2738.0106
24 | Net Generation of REB (MKWH) | 47.8268 |  | 49.7992 |  | 116.0982 |  | - | -
25 | Net Generation of Rental Power Plant (MKWH) | 70.7437 |  | 54.0965 |  | 225.7863 |  | - | -
26 | Total Net Generation (MKHWh) (Excluding Import) | 7609.897 |  | 6778.0256 |  | 7815.1161 |  | - | -
27 | Energy Generation by Gas (MKWH) | 3680.8197 |  | 3548.1844 |  | 4009.324 |  | - | -
28 | Energy Generation by Diesel (MKWH) | 20.2439 |  | 0 |  | 219.8468 |  | - | -
29 | Energy Generation by Furnace Oil (MKWH) | 934.0014 |  | 438.8774 |  | 1171.3858 |  | - | -
30 | Energy Generation by Hydro (MKWH) | 44.552 |  | 56.2631 |  | 0.70868 |  | - | -
31 | Energy Generation by Solar (MKWH) | 124.9061 |  | 120.8884 |  | 149.0391 |  | 149.04 | 2026-04-25
31b | Energy Generation by Wind (MKWH) | 6.2407 |  | 3.7781 |  | 0.1 |  | - | -
32 | Energy Generation by Coal (MKWH) | 2817.0837 |  | 2624.9585 |  | 2314.7942 |  | 3144.92 | 2025-08-25
33 | Enegry Import from India (MKWH) | 1466.7946 |  | 1524.069 |  | 1413.5762 |  | - | -
34 | Monthly Load Factor (%) | 83.1071 |  | 75.2472 |  | 78.7446 |  | 86.52 | 2026-09-25

## QF-LDC-22
QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: April 2026
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 15199 | 2026-04-20 | 21:00 Hr.
Generation Period
| Dhaka | MW | 5715.89
| Chattogram | MW | 1498
| Cumilla | MW | 1319
| Mymensingh | MW | 1009
| Sylhet | MW | 497
a) | Total supply in East zone | MW | 10038.89
| Khulna | MW | 1652.3
| Barisal | MW | 402.8
| Rajshahi | MW | 1708.6
| Rangpur | MW | 818
b) | Total supply in West zone | MW | 4581.7
c) | Total supply in both zone ( a+b) | MW | 14620.59
Ref: | 27.21.0000.603.16.087.20.976 | Date: 14/05/2026
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month: April 2026
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Maximum power Export through EWI/ NO-1
| a) Ishurdi end | AMPS | 627 | 2026-04-16 | 14:00
|  | MW | 262
| b) Ghorashal end | AMPS | 82 | 29/04/2026 | 8:00
|  | MW | 21
18 | Maximum power Import through EWI/ NO-1 |  |  | -
| a) Ishurdi end | AMPS | 88 | 29/04/2026 | 7:00
|  | MW | 18
| b) Ghorashal end | AMPS | 625 | 2026-04-16 | 22:00
|  | MW | 237
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ishurdi end | MWh | 4357.45 | 2026-04-16 | N/A
| b) Ghorashal end | MWh | 29.43 | 2026-04-29
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ishurdi end | MWh | 26.76 | 2026-04-29
| b) Ghorashal end | MWh | 3921.7 | 2026-04-16 | N/A
21 | Total Energy Export through EWI/ NO-1
| a) Ishurdi end | MWh | 88888.72
| b) Ghorashal end | MWh | 36.18
22 | Total Energy Import through EWI/ NO-1
| a) Ishurdi end | MWh | 35.12
| b) Ghorashal end | MWh | 86222.06
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Maximum power Export through EWI/ NO-2
| a) Sirajganj end | AMPS | 2000 | 2026-04-16
|  | MW | 810
| b) Sreepur end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
25 | Maximum power Import through EWI/ NO-2 |  | - | -
| a) Serajganj end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
| b) Sreepur end | AMPS | - | - | -
|  | MW | -
26 | Daily Maximum Energy Export through EWI/NO-2
| a) Sirajganj end | MWh | 8384 | 2026-04-13
| b) Sreepur end | MWh | 0
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Sirajganj end | MWh | 0 | - | -
| b) Sreepur end | MWh | - | - | -
28 | Total Energy Export through EWI/ NO-2
| a) Sirajganj end | MWh | 328152 | - | -
| b) Sreepur end | MWh | 0 | - | -
29 | Total Energy Import through EWI/ NO-2
| a) Sirajganj end | MWh | 0 | - | -
| b) Sreepur end | MWh | 318589.1 | - | -
30 | Transmission loss of EWI/ NO-2 | % | 2.91 | - | -
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 3182 | 2026-04-15 | 21:00
|  | MW | 2142
| b) Aminbazar end | AMPS | 0
|  | MW | 0
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | 0
|  | MW | 0
| b) Aminbazar end | AMPS | 3175 | 2026-04-16 | 21:00
|  | MW | 2141
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 48300 | 2026-04-17 | N/A
| a) Aminbazar end | MWh | 0
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0 | - | N/A
| a) Aminbazar end | MWh | 48133 | 2026-04-17
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 1109630
| b) Aminbazar end (ckt-1 ) | MWh | 0
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0
| b) Aminbazar end (ckt-2 ) | MWh | 1104441
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.468
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: April 2026
| Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH) |  |  | 0.094444
Dhaka (North) Grid Circle : | [10 empty] | 0.0097222
Aminbazar 400/230/132kV | 230/132kv Tr-02 | 2026-04-26 17:03 | 2026-04-26 20:56 | 0.16181 | T | 33KV Auxiliary Bus Ph to Ph short Diff (R, Y, B) ph trip General trip | 0 | 0 | No interruption |  | 0.0097222
Bhaluka 132/33kV | 01. Transformer- 01 | 2026-04-02 01:19 | 2026-04-02 01:33 | 0.0097222 | T | Thundering 50/51/50N/51N trip | 30 | 7 | Power interruption |  | 0.0069444
Bhaluka 132/33kV | 02. Transformer- 02 | 2026-04-02 01:19 | 2026-04-02 01:33 | 0.0097222 | T | Thundering 50/51/50N/51N trip | 30 | 7 | Power interruption |  | 0.063194
Bhaluka 132/33kV | 01. Transformer- 01 | 2026-04-02 01:40 | 2026-04-02 01:58 | 0.0125 | T | Thundering 50/51/50N/51N trip,df/dt,59(O/V) trip. | 0 | 0 | No interruption |  | 0.024306
Bhaluka 132/33kV | 02. Transformer- 02 | 2026-04-02 01:40 | 2026-04-02 01:58 | 0.0125 | T | Thundering 50/51/50N/51N trip,df/dt,59(O/V) trip. | 0 | 0 | No interruption |  | 0.14931
Jamalpur 132/33kV | T-4 | 2026-04-27 07:04 | 2026-04-27 08:34 | 0.0625 | T | Over voltage Lockout | 0 | 0 | No interruption |  | 0.081944
Jamalpur 132/33kV | T-4 | 2026-04-29 07:24 | 2026-04-29 07:48 | 0.016667 | T | Over voltage Locout operate | 0 | 0 | No interruption |  | 0.091667
Kishoreganj 132/33kV | Tr-1 (404T) | 2026-04-07 01:40 | 2026-04-07 02:40 | 0.041667 | T | Bajitpur feedr 33 kv breaker to bus DS loop joint out. P40 Agile | 28 | 28 | Power interruption
Kishoreganj 132/33kV | Tr-2 (414T) | 2026-04-07 01:40 | 2026-04-07 02:40 | 0.041667 | T | Bajitpur feeder 33 kv breaker to bus DS loop joint out P 40 agile | 28 | 28 | Power interruption |  | 0.11042
Kishoreganj 132/33kV | Tr-1 (404T) | 2026-04-18 16:34 | 2026-04-18 17:13 | 0.027083 | T | PDB 33 KV Mollapara feeder trip P40 Agile | 15 | 9.75 | Power interruption |  | 0.035417
Kishoreganj 132/33kV | Tr-2 (414T) | 2026-04-18 16:34 | 2026-04-18 17:13 | 0.027083 | T | PDB 33 KV Mollapara feeder trip P40 Agile | 15 | 9.75 | Power interruption
Mirzapur 132/33kV | Transformer-01(E05) | 2026-04-09 11:11 | 2026-04-09 11:35 | 0.016667 | T | 33 KV Jamurki Feeder CT Brust SIPROTEC 7SJ85 | 21 | 8.4 | Power interruption
Mirzapur 132/33kV | Transformer-01(E05) | 2026-04-22 20:56 | 2026-04-22 23:28 | 0.10556 | T | PBS Jamurki feeder fualt. OC OPTD 86.1 & 86.2 Trip relay. | 20 | 50.6667 | Power interruption
Muktagacha 132/33kV | T-1(404T) | 2026-04-27 06:37 | 2026-04-27 08:18 | 0.070139 | T | 24-overexitation 0/v relay | 0 | 0 | No interruption
Muktagacha 132/33kV | T-2(414T) | 2026-04-27 06:37 | 2026-04-27 08:18 | 0.070139 | T | Over voltage Over excitation | 0 | 0 | No interruption
Muktagacha 132/33kV | T-3(424T) | 2026-04-27 06:37 | 2026-04-27 08:18 | 0.070139 | T | Over voltage Over excitation | 0 | 0 | No interruption
Muktagacha 132/33kV | T-1(404T) | 2026-04-29 07:10 | 2026-04-29 07:49 | 0.027083 | T | over excitation | 0 | 0 | No interruption
Muktagacha 132/33kV | T-2(414T) | 2026-04-29 07:10 | 2026-04-29 07:53 | 0.029861 | T | 24 over voltage | 0 | 0 | No interruption
Muktagacha 132/33kV | T-3(424T) | 2026-04-29 07:10 | 2026-04-29 07:53 | 0.029861 | T | 24 over voltage | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-1 | 2026-04-27 05:08 | 2026-04-27 08:42 | 0.14861 | T | 81 trip REF 630 | 20 | 71.3333 | Power interruption
Rajendrapur 132/33kV | MTR-2 | 2026-04-27 05:08 | 2026-04-27 08:42 | 0.14861 | T | 81 trip REF 630 | 9 | 32.1 | Power interruption
Rajendrapur 132/33kV | MTR-3 | 2026-04-27 05:08 | 2026-04-27 08:42 | 0.14861 | T | 81 trip REF630 | 9 | 32.1 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2026-04-05 12:14 | 2026-04-05 19:01 | 0.28264 | T | Differential trip R&Y phase 7UT61 Differential relay | 0 | 0 | No interruption
Sreepur 230/132/33kV | 230/132 kV T-1 | 2026-04-27 06:02 | 2026-04-27 09:01 | 0.12431 | T | Over Voltage 86.1 and 86.2 | 0 | 0 | No interruption
Sreepur 230/132/33kV | 230/132 kV T-2 | 2026-04-27 06:02 | 2026-04-27 09:30 | 0.14444 | T | Over Voltage 86.1 86.2 | 5 | 17.3333 | Power interruption
Aminbazar 400/230/132kV | 230/132kv Tr-03 | 2026-04-06 17:09 | 2026-04-06 19:36 | 0.10208 | E/O | For Red Hot remove | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 132kV Bus 2 | 2026-04-25 06:30 | 2026-04-25 08:46 | 0.094444 | E/O | DS 102S Maintenance | 60 | 136 | Power interruption
Kishoreganj 132/33kV | Tr-1 (404T) | 2026-04-16 09:02 | 2026-04-16 09:16 | 0.0097222 | E/O | Emergency maint.work | 4 | 0.93333 | Power interruption
Nabinagar 132/33kV | T-1 | 2026-04-25 06:18 | 2026-04-25 06:32 | 0.0097222 | E/O | কালিয়াকৈর গ্রিড উপকেন্দ্রে Bus Shifting জনিত কারনে অপারেশন করা হয়। | 8 | 1.8667 | Power interruption
Nabinagar 132/33kV | T-1 | 2026-04-25 08:40 | 2026-04-25 08:50 | 0.0069444 | E/O | কালিয়াকৈর গ্রিড উপকেন্দ্রে Bus Shifting জনিত কারনে অপারেশন করা হয়। | 8 | 1.3333 | Power interruption
Sherpur 132/33kV | Transformer- 02 | 2026-04-11 20:52 | 2026-04-11 21:33 | 0.028472 | E/O | 33KV BUS Side, SPBS Bay-03 Feeder Rad Hot Remove Work. | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2026-04-07 11:54 | 2026-04-07 13:03 | 0.047917 | E/O | 33kV feeder DS Repair (S/D taken by PBS) | 0 | 0 | No interruption
Tangail 132/33kV | Tr-2 | 2026-04-01 20:55 | 2026-04-01 22:26 | 0.063194 | E/O | 33kv t-1 bus section isolator red hot | 40 | 60.6667 | Power interruption
Tangail 132/33kV | Tr-1 | 2026-04-01 20:56 | 2026-04-01 22:26 | 0.0625 | E/O | 33kv t-1 bus section isolator red hot | 40 | 60 | Power interruption
|  |  | Total : | 1900-01-01 06:21 |  | Unserved Energy: |  | 562.2333
Dhaka (South) Grid Circle :
Hasnabad 132/33kV | 132/33kV 404 T-1 | 2026-04-01 20:28 | 2026-04-01 21:04 | 0.025 | T | O/C Overcurrent Relay | 31 | 18.6 | Power interruption
Hasnabad 132/33kV | 132/33kV 424 T-5 | 2026-04-01 20:28 | 2026-04-01 21:04 | 0.025 | T | O/C Overcurrent Relay | 31 | 18.6 | Power interruption
Hasnabad 132/33kV | 132/33kV 404 T-1 | 2026-04-28 07:07 | 2026-04-28 08:37 | 0.0625 | T | 132Kv Main bus trip by bus bar protection differential relay operate Busbar protection relay. | 28 | 42 | Power interruption
Hasnabad 132/33kV | 132/33kV 424 T-5 | 2026-04-28 07:07 | 2026-04-28 08:39 | 0.063889 | T | 132Kv Main bus trip by bus bar protection differential relay operate Busbar protection relay | 28 | 42.9333 | Power interruption
Hasnabad 132/33kV | 132/33kV 414 T-2 | 2026-04-28 07:07 | 2026-04-28 08:41 | 0.065278 | T | 132Kv Main bus trip by bus bar protection differential relay operate Busbar protection relay | 12 | 18.8 | Power interruption
Hasnabad 230/132kV | AUTO TR-1 | 2026-04-28 07:08 | 2026-04-28 08:41 | 0.064583 | T | 132kV BUS fault 2OC/EF | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-3 | 2026-04-28 07:08 | 2026-04-28 08:40 | 0.063889 | T | 132kV BUS fault Trip relay 186.1 Trip relay 186.2 | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-2 | 2026-04-28 07:08 | 2026-04-29 08:42 | 1899-12-31 01:34 | T | 132kV BUS fault 2OC/EF | 0 | 0 | No interruption
Hasnabad 230/132kV | Bus-1 | 2026-04-29 10:01 | 2026-04-29 16:32 | 0.27153 | T | BUS-1 CVT blust 1) BUS-1 pro (DISC) 2) BUS-2 pro (check) 3) 86B1 4) 86B4 5) Trip relay BUS-1 | 0 | 0 | No interruption
Keranigonj 230/132/33kV | TR-1 | 2026-04-23 02:56 | 2026-04-23 03:07 | 0.0076389 | T | Overcurrent Earth fault by 33kV Ati bazar feeder fault. 86 | 47 | 8.6167 | Power interruption
Madanganj 132/33kV | GT-2 | 2026-04-21 23:26 | 2026-04-22 00:22 | 0.038889 | T | No relay operated | 22 | 20.5333 | Power interruption
Madanganj 132/33kV | GT-2 | 2026-04-26 17:15 | 2026-04-26 19:13 | 0.081944 | T | Heavy Storm and rain Phase instants fault | 10 | 19.6667 | Power interruption
Munshiganj 132/33kV | Transformer-1 | 2026-04-19 15:04 | 2026-04-19 15:31 | 0.01875 | T | Banco 33kv line-1 CB flashing DIR O/C TRIP | 47.5 | 21.375 | Power interruption
Munshiganj 132/33kV | Transformer-2 | 2026-04-19 15:04 | 2026-04-19 15:31 | 0.01875 | T | Banco 33kv line-1 CB flashing DIR O/C TRIP | 47.5 | 21.375 | Power interruption
Munshiganj 132/33kV | Transformer-1 | 2026-04-29 19:04 | 2026-04-29 19:16 | 0.0083333 | T | PBS faulty None | 39 | 7.8 | Power interruption
Munshiganj 132/33kV | Transformer-2 | 2026-04-29 19:04 | 2026-04-29 19:16 | 0.0083333 | T | PBS faulty None | 39 | 7.8 | Power interruption
Narshingdi 132/33kV | T-2 | 2026-04-28 09:36 | 2026-04-28 10:10 | 0.023611 | T | 33kV feeder tripped by Over current REF 630 | 5 | 2.8333 | Power interruption
Nawabganj 132/33kV | TR-2 | 2026-04-07 22:29 | 2026-04-07 22:40 | 0.0076389 | T | Over current Over current relay | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-2 | 2026-04-15 17:08 | 2026-04-15 17:26 | 0.0125 | T | Due to 33 kV Agla feeder fault Lockout relay, Over current protection relay | 0 | 0 | No interruption
Postogola 132/33kV | GT-2 | 2026-04-26 17:19 | 2026-04-26 21:21 | 0.16806 | T | GT-2 tripped due to over flux RET670 | 0 | 0 | No interruption
Postogola 132/33kV | GT-1 | 2026-04-26 17:19 | 2026-04-26 18:20 | 0.042361 | T | GT-1 tripped due to over flux 46 RET670 | 46 | 46.7667 | Power interruption
Rampura 230/132kV | NLDC Trafo | 2026-04-04 06:29 | 2026-04-04 06:58 | 0.020139 | T | N/A O/C ST-2 | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-2 | 2026-04-20 09:16 | 2026-04-20 09:33 | 0.011806 | T | due to PBS 33KV Borpa Feeder Source side isolator finger burnt TR/P relay,DIR O/C & E/F Relay | 30 | 8.5 | Power interruption
Srinagar 132/33kV | Tr-01 | 2026-04-21 22:14 | 2026-04-21 22:30 | 0.011111 | T | Fault Occurred in 33KV PBS Feder no-02 Lockout Relay-01 & 02 Overcurrent Protection Relay | 0 | 0 | No interruption
Srinagar 132/33kV | Tr-02 | 2026-04-21 22:14 | 2026-04-21 22:30 | 0.011111 | T | Fault Occurred in 33KV PBS Feder no-02 Lockout Relay-01 & 02 Overcurrent Protection Relay | 0 | 0 | No interruption
Srinagar 132/33kV | Tr-01 | 2026-04-28 03:10 | 2026-04-28 03:16 | 0.0041667 | T | Fault Occurred in 33KV feeder-1 Lockout Relay-01 Overcurrent Protection Relay | 0 | 0 | No interruption
Srinagar 132/33kV | Tr-02 | 2026-04-28 03:10 | 2026-04-28 03:16 | 0.0041667 | T | Fault Occurred in 33KV feeder-1 Lockout Relay-01 Overcurrent Protection Relay | 0 | 0 | No interruption
Srinagar 132/33kV | Tr-01 | 2026-04-29 11:51 | 2026-04-29 12:00 | 0.00625 | T | Fault occur in 33 KV Feeder-02 Lockout Relay-01, 02 Overcurrent Protection Relay | 0 | 0 | No interruption
Srinagar 132/33kV | Tr-02 | 2026-04-29 11:51 | 2026-04-29 12:00 | 0.00625 | T | Fault in 33 KV Feeder-02 Lockout Relay-01, 02 Overcorrect Protection Relay | 0 | 0 | No interruption
Bhulta 132/33kV | GT2 | 2026-04-04 10:00 | 2026-04-04 17:37 | 0.31736 | E/O | for Narayanganj pbs-02 purbachal feeder faulty section work. | 0 | 0 | No interruption
Ghorashal 230kV | TARFO-2 | 2026-04-27 13:24 | 2026-04-27 14:55 | 0.063194 | E/O | CT B phase Red hot maintenance. | 65 | 98.5833 | Power interruption
Haripur 230/132kV | 132KV Bhult | 2026-04-05 15:30 | 2026-04-05 15:40 | 0.0069444 | E/O | Transformer Load management. | 0 | 0 | No interruption
Hasnabad 132/33kV | 132kV Main Bus | 2026-04-28 07:50 | 2026-04-30 19:33 | 1900-01-01 11:43 | E/O | 132Kv Main bus trip by bus bar protection differential relay operate and line and transformer shift to 132kv Reserve bus. 132kv R bus restore, main shutdown and system normal. | 0 | 0 | No interruption
Munshiganj 132/33kV | Transformer-2 | 2026-04-22 17:33 | 2026-04-22 18:08 | 0.024306 | E/O | Shutdown to replace damaged VCB of BANCO ckt-1 | 60 | 35 | Power interruption
Nawabganj 132/33kV | TR-1 | 2026-04-20 07:09 | 2026-04-20 11:13 | 0.16944 | E/O | Redhot maintenance. | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-2 | 2026-04-02 12:10 | 2026-04-02 13:43 | 0.064583 | E/O | Red hot maintenance At 33 KV side Annondah Bazer Feeder | 65 | 100.75 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2026-04-20 12:45 | 2026-04-20 13:49 | 0.044444 | E/O | Due to pbs 33kv Borpa feeder isolator finger changing | 60 | 64 | Power interruption
|  |  | Total : | 1900-01-04 09:32 |  | Unserved Energy: |  | 604.5333
Chattogram Grid Circle :
Dohazari 132/33kV | Power Transformer -T-1 | 2026-04-02 07:57 | 2026-04-02 08:37 | 0.027778 | T | T-01 Sec. Trip Due to Bashkali 33kv Feeder. Siemence Relay | 28 | 18.6667 | Power interruption
Juldah 132/33kV | 132/33 KV 406T T-1 | 2026-04-18 20:28 | 2026-04-21 14:41 | 1900-01-01 18:13 | T | Due to the explosion of the R-phase cable on the 33 KV side of the transformer. Over Current relay. | 0 | 0 | No interruption
Madunaghat 132/33kV | TR-1(507T) | 2026-04-23 05:49 | 2026-04-23 06:27 | 0.026389 | T | Due to Mohora-2 feeder fault REF-615 | 20 | 12.6667 | Power interruption
Madunaghat 132/33kV | TR-1(507T) | 2026-04-26 20:08 | 2026-04-26 21:29 | 0.05625 | T | Due to 33 kv feeder fault REL 615 | 29 | 39.15 | Power interruption
Bakulia 132/33kV | T-2 (412T) | 2026-04-27 06:03 | 2026-04-27 07:15 | 0.05 | E/O | 33KV side Y-phase terminal point emergency Hot Spot maintenance work. | 0 | 0 | No interruption
Bakulia 132/33kV | T-1 (402T) | 2026-04-27 07:17 | 2026-04-27 08:10 | 0.036806 | E/O | Hot Spot Maintenance work. | 0 | 0 | No interruption
Chandraghona 132/33kV | TR-01(406T) | 2026-04-07 18:01 | 2026-04-07 18:15 | 0.0097222 | E/O | WASA 33KV feeder underground cable maintenance | 25 | 5.8333 | Power interruption
Halishahar 132/33kV | 405T(TR-1) | 2026-04-07 11:54 | 2026-04-07 12:36 | 0.029167 | E/O | Due to remove bird nest from T-1 33 kV side gantry. | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-01 | 2026-04-28 12:49 | 2026-04-30 16:39 | 1900-01-01 03:50 | E/O | DC problem. | 0 | 0 | No interruption
Juldah 132/33kV | 132/33 KV 406T T-1 | 2026-04-20 11:16 | 2026-04-21 14:39 | 1899-12-31 03:23 | E/O | 132/33 KV transformer T-1 was tripped and and termination cable (R-Phase) was burnt . Now it needs to be replaced . | 0 | 0 | No interruption
Madunaghat 400/230kV | ATR-2 7106T | 2026-04-09 15:49 | 2026-04-19 11:18 | 1900-01-08 19:29 | E/O | Due to SF6 Leakage. Section ES (R phase). | 0 | 0 | No interruption
Mirsorai 230/33kV | TR-1, 718T | 2026-04-27 13:48 | 2026-04-27 13:48 | 0 | E/O | For protection,SPMD | 0 | 0 | No interruption
Patiya 132/33kV | TRAFO-01 | 2026-04-04 09:28 | 2026-04-04 11:42 | 0.093056 | E/O | Emergency maint.work | 0 | 0 | No interruption
Patiya 132/33kV | BUS I | 2026-04-26 20:35 | 2026-04-26 22:11 | 0.066667 | E/O | Pbs 33 kv fedeer load side redhot maintenance. | 12 | 19.2 | Power interruption
Sholosohor 132/33kV | TRAFO-02 | 2026-04-01 12:13 | 2026-04-01 15:15 | 0.12639 | E/O | Disk replacement work at 33kV feeder sholoshahar-2 isolator by BPDB | 0 | 0 | No interruption
|  |  | Total : | 1900-01-15 09:27 |  | Unserved Energy: |  | 95.5167
Cumilla Grid Circle :
Cumilla(S) 132/33kV | TR-3 | 2026-04-28 10:59 | 2026-04-28 11:44 | 0.03125 | T | 33KV PDB feeder fault REF615 | 2 | 1.5 | Power interruption
Cumilla(S) 132/33kV | TR-4 | 2026-04-28 10:59 | 2026-04-28 11:44 | 0.03125 | T | Kotbari PDB Feeder fault REF615 | 2 | 1.5 | Power interruption
Cumilla(S) 132/33kV | TR-3 | 2026-04-29 13:17 | 2026-04-29 13:32 | 0.010417 | T | 33 KV Kotbari feeder fault. C.B. Not trip. REF- 615 | 30 | 7.5 | Power interruption
Cumilla(S) 132/33kV | TR-4 | 2026-04-29 13:17 | 2026-04-29 13:34 | 0.011806 | T | 33 KV Kotbari feeder fault. C.B. Not trip. REF 615 | 29 | 8.2167 | Power interruption
Feni 132/33kV | T-2(415T) | 2026-04-28 11:09 | 2026-04-28 12:09 | 0.041667 | T | fault Inst,O/C. | 26 | 26 | Power interruption
Kulaura 132/33kV | TR-1 AB | 2026-04-07 04:12 | 2026-04-07 08:02 | 0.15972 | T | Natural disasters Differential Protection relay, Over current protection relay. | 8 | 30.6667 | Power interruption
Shahjibazar 132/33kV | TR-04 | 2026-04-04 00:44 | 2026-04-04 00:55 | 0.0076389 | T | Bisic Feeder CT Blast Trip Relay-1 | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2026-04-04 11:18 | 2026-04-04 11:25 | 0.0048611 | T | Shayestaganj Feeder Trip 33 kv OC/EF Protection Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2026-04-05 12:38 | 2026-04-05 12:50 | 0.0083333 | T | Shayestaganj Feeder Earth fault 33 kv OC/EF protection Relay | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2026-04-26 17:24 | 2026-04-26 17:56 | 0.022222 | T | Shaistaganj Feeder Over Curent Earth Fault. Gen. Trip,Non Dir OC DMT Trip | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2026-04-26 17:25 | 2026-04-26 17:56 | 0.021528 | T | Habiganj Bypass Feeder Over Current Earth. Trip Relay-1, General Trip, Y&B PH Trip, Non Dir OC | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2026-04-26 23:09 | 2026-04-26 23:22 | 0.0090278 | T | Madhabpur-1 feeder fault General Trip, Y PH Trip, B PH Trip, Non Dir EF | 0 | 0 | No interruption
Chandina 132/33kV | TR-2 | 2026-04-23 12:30 | 2026-04-23 18:33 | 0.25208 | E/O | As per written aplication by Md. Sakib Ahmmed (AE) PDB. | 0 | 0 | No interruption
Chandina 132/33kV | TR-3 | 2026-04-26 23:00 | 2026-04-26 23:39 | 0.027083 | E/O | For Pbs fedder R phase DS red hot problem | 0 | 0 | No interruption
Chandina 132/33kV | TR-3 | 2026-04-29 13:28 | 2026-04-29 14:14 | 0.031944 | E/O | For Red Hot problem at 33 kv R phase bus DS | 4 | 3.0667 | Power interruption
Chandpur 132/33kV | 422T(T-5) | 2026-04-04 07:40 | 2026-04-04 10:05 | 0.10069 | E/O | Maintenance | 0 | 0 | No interruption
Chauddagram 132/33kV | 132 kv T-2 | 2026-04-01 13:40 | 2026-04-01 16:39 | 0.12431 | E/O | 33 kV DS Problem. | 30 | 89.5 | Power interruption
Chowmuhani 230/132/33kV | TR1-415T | 2026-04-12 22:55 | 2026-04-12 23:55 | 0.041667 | E/O | Maijdee 33kV BUS DS redhot maintenance. | 30 | 30 | Power interruption
Daganbhuiyan 132/33kV | Transformer-2 | 2026-04-27 18:32 | 2026-04-27 20:02 | 0.0625 | E/O | for 33KV Bus Red hot Maintenance(PBS) | 11 | 16.5 | Power interruption
Kachua 230/132/33kV | TR-1 | 2026-04-27 10:35 | 2026-04-27 12:30 | 0.079861 | E/O | Emergency Maint.work | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-2 | 2026-04-28 16:33 | 2026-04-28 18:12 | 0.06875 | E/O | Red hot Maintenance | 0 | 0 | No interruption
Sunamganj 132/33kV | Tr-1 | 2026-04-26 14:35 | 2026-04-26 15:25 | 0.034722 | E/O | Shutdown due to PDB Busbar maintenance | 0 | 0 | No interruption
Sylhet (South) | Trafo-2 | 2026-04-21 15:08 | 2026-04-21 16:43 | 0.065972 | E/O | 33 kv PBS loop connection works. | 5 | 7.9167 | Power interruption
|  |  | Total : | 1899-12-31 05:59 |  | Unserved Energy: |  | 222.3667
Khulna Grid Circle :
Barishal 132/33kV | T-2 (415T) | 2026-04-07 00:24 | 2026-04-07 00:29 | 0.0034722 | T | 33 kV dopdopia 1 feeder fault. Lockout relay | 20 | 1.6667 | Power interruption
Barishal 132/33kV | T-1 (405T) | 2026-04-29 11:32 | 2026-04-29 11:34 | 0.0013889 | T | WZPDCL 33kV feeder fault - Dopdapia 2 Definite O/C, instt O/C, instt E/F | 17 | 0.56667 | Power interruption
Barishal 230/132kV | T-4 | 2026-04-16 18:29 | 2026-04-16 20:14 | 0.072917 | T | 33 kv Rahmatpur feeder trip P142 | 40 | 70 | Power interruption
Barishal 230/132kV | T-5 | 2026-04-16 18:29 | 2026-04-16 21:09 | 0.11111 | T | 33kv Rahmatpur feeder trip P142 | 40 | 106.6667 | Power interruption
Barishal 230/132kV | T-4 | 2026-04-19 19:00 | 2026-04-19 19:31 | 0.021528 | T | due to 33kv Jhalakhati Feeder R-Phase Burn out Over current relay | 37 | 19.1167 | Power interruption
Barishal 230/132kV | T-5 | 2026-04-19 19:00 | 2026-04-19 20:12 | 0.05 | T | due to 33kv Jhalakhati Feeder R-Phase Burn out O/C | 37 | 44.4 | Power interruption
Barishal 230/132kV | ATR-2 | 2026-04-29 16:15 | 2026-04-29 18:06 | 0.077083 | T | WTI Trip LV RET670 | 0 | 0 | No interruption
Benapole 132/33kV | Transformer-1(406T) | 2026-04-29 12:07 | 2026-04-29 12:17 | 0.0069444 | T | Benapole Sharsha 33 KV feeder Trip due to heavy wind REF630 | 26 | 4.3333 | Power interruption
Khulna (C) | TR-1 425T | 2026-04-07 00:08 | 2026-04-07 00:26 | 0.0125 | T | Pbs sadar feeder fault OC/EF | 5 | 1.5 | Power interruption
Khulna (C) | Tr-2 415 T | 2026-04-07 00:08 | 2026-04-07 00:30 | 0.015278 | T | Pbs sadar feeder fault OC/EF | 5 | 1.8333 | Power interruption
Khulna (C) | Tr-3 405T | 2026-04-08 22:58 | 2026-04-08 23:17 | 0.013194 | T | 33 kv khalispur feeder fault Earth fault ( Inst.) | 12 | 3.8 | Power interruption
Khulna (C) | Tr-3 405T | 2026-04-09 07:45 | 2026-04-09 18:11 | 0.43472 | T | Winding temperature 26W4, 86T | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2026-04-29 10:58 | 2026-04-29 11:45 | 0.032639 | T | Khulna PBS and Paikgasa Feeder fault. O/C | 22 | 17.2333 | Power interruption
Mongla 132/33kV | T-2 | 2026-04-28 17:21 | 2026-04-28 18:38 | 0.053472 | T | Protection rely | 1 | 1.2833 | Power interruption
Noapara 132/33kV | T-1 | 2026-04-16 14:47 | 2026-04-16 15:03 | 0.011111 | T | Due REB-1 Feeder over current & earth fault SIEMENS SIPROTEC-7SJ81 Protection: 50N/51N IMDT> Pick up Protection: 50/51 DMT: Operate | 6 | 1.6 | Power interruption
Noapara 132/33kV | T-2 | 2026-04-16 14:47 | 2026-04-16 15:03 | 0.011111 | T | Due REB-1 Feeder over current & earth fault SIEMENS SIPROTEC-7SJ81 Protection: 50N/51N IMDT> Pick up Protection: 50/51 DMT: Operate | 6 | 1.6 | Power interruption
Barishal 230/132kV | T-5 | 2026-04-17 18:13 | 2026-04-17 18:15 | 0.0013889 | T | Sound on 33kv Busbar DS B-phase | 0 | 0 | No interruption
Benapole 132/33kV | Transformer-1(406T) | 2026-04-06 08:28 | 2026-04-06 08:44 | 0.011111 | E/O | To remove bird nest from 33 KV side structure. | 0 | 0 | No interruption
Borhanuddin 230/33kV | Tr-Load | 2026-04-10 07:10 | 2026-04-10 10:45 | 0.14931 | E/O | Incomer red hot maintains | 55 | 197.0833 | Power interruption
Gollamari 132/33kV | Tr-1 | 2026-04-23 06:35 | 2026-04-25 14:45 | 1900-01-01 08:10 | E/O | Wzpdcl cable trench burn. | 0 | 0 | No interruption
Gollamari 132/33kV | Tr-2 | 2026-04-23 06:35 | 2026-04-23 08:38 | 0.085417 | E/O | Wzpdcl cable trench burn | 80 | 164 | Power interruption
Gopalganj 132/33kV | T2 | 2026-04-02 09:43 | 2026-04-02 13:36 | 0.16181 | E/O | Relay protection test | 0 | 0 | No interruption
Gopalganj 132/33kV | T1 | 2026-04-02 13:54 | 2026-04-02 17:49 | 0.16319 | E/O | Protection maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 20:11 |  | Unserved Energy: |  | 636.6833
HVDC Grid Circle :
Ishurdi 132/33kV | 132/33 kV T-3 | 2026-04-29 12:20 | 2026-04-29 13:02 | 0.029167 | T | 33kv feeder fault micom | 27 | 18.9 | Power interruption
Jhenaidah 132/33kV | Transformer T-3 | 2026-04-14 06:47 | 2026-04-14 09:12 | 0.10069 | T | O/C time Over current relay | 28 | 67.6667 | Power interruption
Jhenaidah 132/33kV | Transformer T-2 | 2026-04-14 09:43 | 2026-04-14 09:43 | 0 | T | Transofmer diff: 1:87T | 29 | 0 | Power interruption
Kushtia 132/33kV | T-3 | 2026-04-18 20:19 | 2026-04-18 20:38 | 0.013194 | T | HV O/C Protection relay | 103 | 32.6167 | Power interruption
Kushtia 132/33kV | T2 | 2026-04-30 00:13 | 2026-04-30 00:36 | 0.015972 | T | Inter Lock | 36 | 13.8 | Power interruption
Kushtia 132/33kV | T-3 | 2026-04-30 00:13 | 2026-04-30 00:33 | 0.013889 | T | Inter Lock Inter Lock | 26 | 8.6667 | Power interruption
BIPTC | 10CF25 | 2026-04-01 14:33 | 2026-04-01 15:20 | 0.032639 | T | Tripped by Capacitor bank 1 T1 Current Unbalance at B & Y Phase. | 0 | 0 | No interruption
BIPTC | 20DF21 | 2026-04-06 10:50 | 2026-04-06 12:21 | 0.063194 | T | C1 Unbalance 60/61 instant L2 Trip | 0 | 0 | No interruption
BIPTC | 10CF15 | 2026-04-09 08:43 | 2026-04-09 10:44 | 0.084028 | T | Tripped by Capacitor Unbalance B Phase. | 0 | 0 | No interruption
BIPTC | 20DF11 | 2026-04-10 22:54 | 2026-04-11 11:40 | 0.53194 | T | Tripped | 0 | 0 | No interruption
BIPTC | 10CF14 | 2026-04-20 07:00 | 2026-04-20 10:43 | 0.15486 | T | Tripped | 0 | 0 | No interruption
BIPTC | 20DF13 | 2026-04-02 10:48 | 2026-04-02 15:46 | 0.20694 | E/O | Shutdown was taken for buchholz relay's oil leakage maintenance work on CB | 0 | 0 | No interruption
BIPTC | 10CF15 | 2026-04-09 10:02 | 2026-04-09 10:44 | 0.029167 | E/O | 0 | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-2(413T) | 2026-04-10 19:58 | 2026-04-10 20:58 | 0.041667 | E/O | Red Hot | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-1(403T) | 2026-04-14 21:09 | 2026-04-14 22:04 | 0.038194 | E/O | Red Hot In 33KV Tr-1 BKR | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-2(413T) | 2026-04-26 20:12 | 2026-04-26 21:08 | 0.038889 | E/O | red hot 33 kv side | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-1(403T) | 2026-04-27 00:08 | 2026-04-27 00:51 | 0.029861 | E/O | 33 kv bua red hot remove | 0 | 0 | No interruption
Jashore 132/33kV | T-1 | 2026-04-23 06:06 | 2026-04-23 08:04 | 0.081944 | E/O | Redhot Maintanance to Auxiliary Tx. (East) | 30 | 59 | Power interruption
Jhenaidah 132/33kV | Transformer T-3 | 2026-04-19 06:24 | 2026-04-19 08:22 | 0.081944 | E/O | 33kV CB B-Phase Redhot Maintenance. | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-1 | 2026-04-20 07:35 | 2026-04-20 09:40 | 0.086806 | E/O | 33kV PBS BUS SECTION DS-3 Redhot Maintenance work. | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-1 | 2026-04-20 16:35 | 2026-04-20 18:55 | 0.097222 | E/O | Change the conductor of 'Y' phage busbar at bus section-3, 33KV under the T-1A. | 45 | 105 | Power interruption
Jhenaidah 132/33kV | Transformer T-1 | 2026-04-27 06:34 | 2026-04-27 08:19 | 0.072917 | E/O |  | 15 | 26.25 | Power interruption
Kushtia 132/33kV | T-1 | 2026-04-01 22:51 | 2026-04-01 23:36 | 0.03125 | E/O | Red Hot Maintenance of PBS Bus Section Coupler | 60 | 45 | Power interruption
Kushtia 132/33kV | T-3 | 2026-04-23 15:34 | 2026-04-23 17:16 | 0.070833 | E/O | Bus Conductor change | 61 | 103.7 | Power interruption
Pabna 132/33kV | T-2 | 2026-04-02 09:25 | 2026-04-02 17:05 | 0.31944 | E/O | None | 0 | 0 | No interruption
Pabna 132/33kV | T-3 | 2026-04-21 16:15 | 2026-04-21 17:25 | 0.048611 | E/O |  | 12 | 14 | Power interruption
Shahjadpur 132/33kV | T-1(405T) | 2026-04-18 19:41 | 2026-04-19 08:59 | 0.55417 | E/O | Red-hot maintenance work. | 0 | 0 | No interruption
Ullahpara 132/33kV | Power Transformer -1 | 2026-04-09 11:49 | 2026-04-09 15:25 | 0.15 | E/O | Emergency Maintenance. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 00:28 |  | Unserved Energy: |  | 494.6
Bogura Grid Circle:
Bog-Sherpur 132/33kV | Transformer-3 (424T) | 2026-04-03 08:16 | 2026-04-03 12:25 | 0.17292 | T | Water entered the PRD box. Trip Relay K31, K32 XFR. Auxiliary Relay (K13-14) | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-1 (404T) | 2026-04-12 13:33 | 2026-04-12 14:33 | 0.041667 | T | 33 kV feeder fault OVERCURRENT PROTECTION P142 | 36 | 36 | Power interruption
Bog-Sherpur 132/33kV | Transformer-2 (414T) | 2026-04-12 13:33 | 2026-04-12 14:34 | 0.042361 | T | 33 kV feeder fault OVERCURRENT PROTECTION P142 | 36 | 36.6 | Power interruption
Bog-Sherpur 132/33kV | Transformer-1 (404T) | 2026-04-26 16:41 | 2026-04-27 16:27 | 0.99028 | T | Not Finding DIFFERENTIAL PROTECTION P632 | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-1 | 2026-04-13 23:00 | 2026-04-13 23:29 | 0.020139 | T | due to birgram 33kv pbs-2 t-1 33 kv SIMENSe SIPROTEC 7SJ81 | 50 | 24.1667 | Power interruption
Niamatpur 132/33kV | Transformer-2 (417T) | 2026-04-03 14:45 | 2026-04-03 15:14 | 0.020139 | T | PBS, Niamatpur-2 33kv CT Burst. SIPROTEC 7SJ81 | 44 | 21.2667 | Power interruption
Niamatpur 132/33kV | Transformer-2 (417T) | 2026-04-19 00:30 | 2026-04-19 01:40 | 0.048611 | T | Overvolt SIEMENS | 28 | 32.6667 | Power interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2026-04-23 01:10 | 2026-04-23 01:26 | 0.011111 | T | O/C, E/F | 21 | 5.6 | Power interruption
Rahanpur 132/33kV | TR-1 404T | 2026-04-19 00:26 | 2026-04-19 01:09 | 0.029861 | T | Agile | 0 | 0 | No interruption
Rahanpur 132/33kV | TR-2 (414T) | 2026-04-19 00:26 | 2026-04-19 01:11 | 0.03125 | T | Agile | 3 | 2.25 | Power interruption
Sirajganj 132/33kV | T2-(425) | 2026-04-01 05:30 | 2026-04-01 17:56 | 0.51806 | T | 33KV T2-T3 Bus Coupler Sky Wire depart or fall on. Differential Relay- R, Y, B | 12 | 149.2 | Power interruption
Sirajganj 132/33kV | T1-(415) | 2026-04-01 17:30 | 2026-04-01 17:57 | 0.01875 | T | 33KV T2-T3 Bus Coupler Sky Wire depart or fall on. O/C IDMT R & Y Phase | 20 | 9 | Power interruption
Sirajganj 132/33kV | T4-(445) | 2026-04-01 17:30 | 2026-04-01 18:01 | 0.021528 | T | 33KV T2-T3 Bus Coupler Sky Wire depart or fall on. O/C R & Y & B Phase | 22 | 11.3667 | Power interruption
Sirajganj 132/33kV | T1-(415) | 2026-04-05 08:48 | 2026-04-05 09:00 | 0.0083333 | T | 33kV Kamarkhand Feeder SPBS-2 tripped at this time due to E/F>,E/F>>,O/C>,O/C>>. O/C E/F | 30 | 6 | Power interruption
Sirajganj 132/33kV | T2-(425) | 2026-04-05 08:48 | 2026-04-05 09:00 | 0.0083333 | T | 33kV Kamarkhand Feeder SPBS-2 tripped at this time due to E/F>,E/F>>,O/C>,O/C>>. O/C E/F | 30 | 6 | Power interruption
Sirajganj 132/33kV | T3-(435) | 2026-04-29 06:13 | 2026-04-29 09:32 | 0.13819 | T | heavy storm. 132/33 kV T4-(445) HT Tripped showing 87-Differential Relay relays and Relay Signal: 87 Dif> Trip, 87 Dif>> Trip, at CP Signal: Transformer Main-1 87T1 Trip, Transformer Main-1 general trip. signals | 0 | 0 | No interruption
Amnura 132/33kV | T-1 (406T) | 2026-04-19 14:03 | 2026-04-19 17:24 | 0.13958 | E/O | Oil leakage. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132/33 KV T-5, 424T | 2026-04-30 11:07 | 2026-04-30 13:19 | 0.091667 | E/O | Emergency cable maintenance. | 5 | 11 | Power interruption
Bogura 400/230kV | ATR-02 | 2026-04-12 14:40 | 2026-04-12 16:37 | 0.08125 | E/O | Temperature meter change | 0 | 0 | No interruption
Jaldhaka 132/33kV | 406T-1 | 2026-04-17 11:25 | 2026-04-17 12:03 | 0.026389 | E/O | 33 kV PBS Dimla feeder sky wire maintenance work | 15 | 9.5 | Power interruption
Joypurhat 132/33kV | Transformer T-1 (407 T) | 2026-04-27 07:16 | 2026-04-27 08:52 | 0.066667 | E/O | Due to 33kv bus side loop jumper maintenence.(Baliatoir feeder). | 7 | 11.2 | Power interruption
Joypurhat 132/33kV | Transformer T-2 (417 T) | 2026-04-27 07:17 | 2026-04-27 08:53 | 0.066667 | E/O | Due to 33kv bus side loop jumper maintenence.(Baliatoir feeder). | 0 | 0 | No interruption
Lalmonirhat 132/33kV | T-2 (415T) | 2026-04-24 09:04 | 2026-04-24 11:41 | 0.10903 | E/O | Redhot in T2 T3 33KV bus section | 12 | 31.4 | Power interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2026-04-04 10:41 | 2026-04-04 12:51 | 0.090278 | E/O | pirob 33 kV feeder redhot. | 30 | 65 | Power interruption
Mahasthangarh 132/33kV | 406T MTR1 | 2026-04-07 22:45 | 2026-04-08 01:48 | 0.12708 | E/O | NESCO 33kV feeder redhot work. | 24 | 73.2 | Power interruption
Mithapukur 132/33kV | TR-1(404T) | 2026-04-12 08:26 | 2026-04-12 09:52 | 0.059722 | E/O | Maintenance work on a 33kv pbs feeder due to a red hot condition. | 35 | 50.1667 | Power interruption
Mithapukur 132/33kV | TR-2 (414T) | 2026-04-27 11:51 | 2026-04-27 12:42 | 0.035417 | E/O |  | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-2 (417T) | 2026-04-04 07:24 | 2026-04-04 09:46 | 0.098611 | E/O | PBS 33kv Busber red hot maintenance | 35 | 82.8333 | Power interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2026-04-22 21:41 | 2026-04-23 00:20 | 0.11042 | E/O | Red hot maintenance. | 10 | 26.5 | Power interruption
Palashbari 132/33kV | TR2-404T | 2026-04-21 13:57 | 2026-04-21 14:48 | 0.035417 | E/O | Red hot maintenence | 30 | 25.5 | Power interruption
Rajshahi 132/33kV | Transformer T-2(415T) | 2026-04-15 07:02 | 2026-04-15 09:01 | 0.082639 | E/O | 33 kV Poba & Mohonpur feeder red hot maintenance work. | 15 | 29.75 | Power interruption
Rajshahi 132/33kV | Transformer T-2(415T) | 2026-04-19 07:35 | 2026-04-19 09:50 | 0.09375 | E/O | T2 -T3 33 KV Section Bus DS Post Insulator Change . | 25 | 56.25 | Power interruption
Rajshahi 132/33kV | Transformer T-3 (425T) | 2026-04-19 07:36 | 2026-04-19 09:20 | 0.072222 | E/O | None | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-3 (425T) | 2026-04-29 12:38 | 2026-04-29 14:18 | 0.069444 | E/O | Bagha feeder faulty | 28 | 46.6667 | Power interruption
Sirajganj 132/33kV | T2-(425) | 2026-04-01 18:28 | 2026-04-01 19:29 | 0.042361 | E/O | 33KV T2-T3 Bus Coupler Sky Wire depart or fall on work. | 25 | 25.4167 | Power interruption
Sirajganj 132/33kV | T3-(435) | 2026-04-01 18:28 | 2026-04-01 19:31 | 0.04375 | E/O | 33KV T2-T3 Bus Coupler Sky Wire depart or fall on work. | 25 | 26.25 | Power interruption
Sirajganj 132/33kV | T4-(445) | 2026-04-04 10:27 | 2026-04-04 13:56 | 0.14514 | E/O | Emergency 33kv DS work for changing damaged part. | 0 | 0 | No interruption
Sirajganj 132/33kV | T3-(435) | 2026-04-09 10:08 | 2026-04-09 11:24 | 0.052778 | E/O | For repair work due to the Y phase riser wire coming off the 33 kV busbar of the Kazipur 33 kV feeder | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 20:41 |  | Unserved Energy: |  | 910.75
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 1900-02-04 00:39 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: April 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Kallyanpur-02 | 2026-04-27 06:12 | 2026-04-27 07:09 | 0.039583 | T | Over Voltage | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 01 | 2026-04-27 05:11 | 2026-04-27 07:28 | 0.095139 | T | O ver voltage Trip | 18 | 41.1 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 02 | 2026-04-27 05:11 | 2026-04-27 07:28 | 0.095139 | T | Over voltage Trip | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 01 | 2026-04-27 05:11 | 2026-04-27 08:59 | 0.15833 | T | Over voltage trip | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 02 | 2026-04-27 05:11 | 2026-04-27 08:59 | 0.15833 | T | Over voltage Trip | 0 | 0 | No interruption
Bhaluka 132/33kV | Sreepur Ckt- 01 | 2026-04-27 07:27 | 2026-04-27 08:39 | 0.05 | T | CB open by NLDC | 0 | 0 | No interruption
Bhaluka 132/33kV | Sreepur Ckt- 02 | 2026-04-27 07:27 | 2026-04-27 09:12 | 0.072917 | T | CB Open by NLDC | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Lalbag Ckt-02 | 2026-04-01 20:13 | 2026-04-01 21:28 | 0.052083 | T | প্রচন্ড ঝড় বৃষ্ট্রি | 0 | 0 | No interruption
Kishoreganj 132/33kV | Mymensingh Ckt-1 | 2026-04-24 12:54 | 2026-04-24 13:09 | 0.010417 | T | Zone 1 & zone 3 trip, phase B &C, distance 100.4 km | 39 | 9.75 | Power interruption
Kishoreganj 132/33kV | Bajitpur Ckt-1 | 2026-04-28 07:46 | 2026-04-28 09:04 | 0.054167 | T | Tripped | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Sector-18 | 2026-04-27 06:03 | 2026-04-27 09:12 | 0.13125 | T | Over Voltage. | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Sector-18 | 2026-04-29 23:49 | 2026-04-29 23:54 | 0.0034722 | T | Over Voltage | 0 | 0 | No interruption
Mirzapur 132/33kV | Mirzapur-Tangail-ckt-2A(E04) | 2026-04-27 05:10 | 2026-04-27 08:49 | 0.15208 | T | Storm and rain system Over Voltage | 34 | 124.1 | Power interruption
Muktagacha 132/33kV | Ghatail-1 | 2026-04-27 05:12 | 2026-04-27 10:37 | 0.22569 | T | Over voltage | 0 | 0 | No interruption
Muktagacha 132/33kV | Ghatail-2 | 2026-04-27 05:12 | 2026-04-27 06:36 | 0.058333 | T | Over voltage | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-1 | 2026-04-27 05:12 | 2026-04-27 09:17 | 0.17014 | T | Over voltage | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-2 | 2026-04-27 05:12 | 2026-04-27 06:36 | 0.058333 | T | O/v | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Kishoreganj Ckt-1 | 2026-04-24 12:58 | 2026-04-24 13:12 | 0.0097222 | T | Tripped | 39 | 9.1 | Power interruption
Sreepur 230/132/33kV | Sreepur-Ashuganj Ckt-2 | 2026-04-06 13:00 | 2026-04-06 17:19 | 0.17986 | T | Distance Trip | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Sirajganj Ckt-1 | 2026-04-18 16:42 | 2026-04-18 16:55 | 0.0090278 | T | Distance relay trip | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Sirajganj Ckt-2 | 2026-04-22 20:53 | 2026-04-22 22:38 | 0.072917 | T | Distance Trip | 0 | 0 | No interruption
Tangail 132/33kV | Kaliakair-1 | 2026-04-26 16:00 | 2026-04-26 16:24 | 0.016667 | T | Main Protection Operated Distance-Trip | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Basundhara Ckt-1 | 2026-04-01 10:17 | 2026-04-01 10:51 | 0.023611 | T | Tripped | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2026-04-27 05:38 | 2026-04-27 07:22 | 0.072222 | T | Tripped | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2026-04-29 07:33 | 2026-04-29 07:45 | 0.0083333 | T | Bad weather and over voltage | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2026-04-29 08:08 | 2026-04-29 10:30 | 0.098611 | T | bad Weather and over voltage | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Manikgonj Power Plant-01 | 2026-04-12 13:01 | 2026-04-12 14:00 | 0.040972 | E/O | DS Maintenance | 0 | 0 | No interruption
Bajitpur 132/33kV | Ashuganj Ckt-2 | 2026-04-21 14:54 | 2026-04-21 15:42 | 0.033333 | E/O | Emergency maint.work | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-01 | 2026-04-27 04:56 | 2026-04-27 09:22 | 0.18472 | E/O | open due to over voltage | 0 | 0 | No interruption
Jamalpur 132/33kV | 132KV UMPL Ckt-01 | 2026-04-27 05:20 | 2026-04-27 09:33 | 0.17569 | E/O | Open due to over voltage | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-02 | 2026-04-27 06:42 | 2026-04-27 06:46 | 0.0027778 | E/O | Open due to over voltage | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Tangail-1 | 2026-04-25 06:08 | 2026-04-25 09:06 | 0.12361 | E/O | DS 102S Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Sector-18 | 2026-04-27 06:05 | 2026-04-27 09:12 | 0.12986 | E/O | Fault rectification. | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Sector-18 | 2026-04-29 06:55 | 2026-04-29 11:35 | 0.19444 | E/O | Over voltage | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Sirajganj Ckt-1 | 2026-04-16 06:16 | 2026-04-16 10:08 | 0.16111 | E/O | DS Connector Repair At sirajganj end. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 02:57 |  | Unserved Energy: |  | 184.05
Dhaka (South) Grid Circle :
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2026-04-16 00:10 | 2026-04-16 00:39 | 0.020139 | T | Bad weather | 0 | 0 | No interruption
Haripur 230/132kV | Ullon (Maniknagar-2) | 2026-04-07 09:00 | 2026-04-07 09:30 | 0.020833 | T | Unknown. | 0 | 0 | No interruption
Hasnabad 132/33kV | Fatulla (Pre-Brahmongaon) | 2026-04-28 07:07 | 2026-04-28 08:45 | 0.068056 | T | 132Kv Main bus trip by bus bar protection differential relay operate | 65 | 106.1667 | Power interruption
Hasnabad 132/33kV | Shitallakhya | 2026-04-28 07:07 | 2026-04-28 08:36 | 0.061806 | T | 132Kv Main bus trip by bus bar protection differential relay operate | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 1 | 2026-04-01 20:19 | 2026-04-02 21:31 | 1899-12-31 01:12 | T | SOTF trip & Zone -01 trip | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 2 | 2026-04-01 20:28 | 2026-04-02 21:31 | 1899-12-31 01:03 | T | Zone - 3 trip | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 1 | 2026-04-07 20:13 | 2026-04-08 11:34 | 0.63958 | T | SOTF trip & Zone-01 trip | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Nawabganj Ckt. 1 | 2026-04-26 17:14 | 2026-04-26 18:42 | 0.061111 | T | 50/67N earth fault trip & Zone-1 trip | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 1 | 2026-04-26 17:14 | 2026-04-26 17:14 | 0 | T | SOTF & Zone -1 trip | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Lalbagh Ckt. 3 | 2026-04-26 17:26 | 2026-04-26 18:46 | 0.055556 | T | SOTF & Zone-1 trip | 66 | 88 | Power interruption
Keranigonj 230/132/33kV | 132 kV Nawabganj Ckt. 1 | 2026-04-29 19:04 | 2026-04-29 21:07 | 0.085417 | T | Due to OPGW wire Broken with flashing at 230 kV Aminbazar Ckt-01, Aminbazar ckt-02. | 17 | 34.85 | Power interruption | ok
Keranigonj 230/132/33kV | 132 kV Nawabganj Ckt. 2 | 2026-04-29 19:04 | 2026-04-29 20:35 | 0.063194 | T | Due to OPGW wire Broken with flashing at 230 kV Aminbazar Ckt-01, Aminbazar ckt-02. | 17 | 25.7833 | Power interruption | ok
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 1 | 2026-04-29 19:04 | 2026-04-30 08:01 | 0.53958 | T | Due to OPGW wire Broken with flashing at 230 kV Aminbazar Ckt-01, Aminbazar ckt-02. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 2 | 2026-04-29 19:04 | 2026-04-30 13:03 | 0.74931 | T | Due to OPGW wire Broken with flashing at 230 kV Aminbazar Ckt-01, Aminbazar ckt-02. | 0 | 0 | No interruption
Nawabganj 132/33kV | Keraniganj-1 | 2026-04-26 17:15 | 2026-04-26 18:44 | 0.061806 | T | Extreme strom, DISTANCE TRIP Z-1, | 0 | 0 | No interruption
Rampura 230/132kV | Moghbazar-02 | 2026-04-01 20:28 | 2026-04-01 21:20 | 0.036111 | T | Thunder Storm (Hatirjhil GIS SS) | 19 | 16.4667 | Power interruption
Shitalakhya 132/33kV | 132 kV Hasnabad | 2026-04-29 11:57 | 2026-04-30 00:14 | 0.51181 | T | E/F R phase | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Fatullah-2(E05) | 2026-04-01 08:38 | 2026-04-02 02:02 | 0.725 | T | Stormy weather | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Shyampur old-2(E10) | 2026-04-01 08:38 | 2026-04-01 09:04 | 0.018056 | T | Stormy weather | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT1 | 2026-04-07 09:02 | 2026-04-07 12:47 | 0.15625 | T | U/N | 0 | 0 | No interruption
|  |  | Total : | 1900-01-04 23:13 |  | Unserved Energy: |  | 271.2667
Chattogram Grid Circle :
Baroaulia 132/33kV | AKSPL | 2026-04-02 11:58 | 2026-04-02 12:36 | 0.026389 | T | None | 0 | 0 | No interruption
Baroaulia 132/33kV | Hat-1 | 2026-04-07 02:01 | 2026-04-07 10:52 | 0.36875 | T | Due to Thunderstorm | 0 | 0 | No interruption
Coxsbazar 132/33kV | Doh-Cox Ckt-2 | 2026-04-07 02:56 | 2026-04-07 03:42 | 0.031944 | T | Tripped | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-2 | 2026-04-07 03:01 | 2026-04-07 03:41 | 0.027778 | T | Due to stormy weather and thundering | 0 | 0 | No interruption
Dohazari 132/33kV | 100 MW PPP | 2026-04-29 11:35 | 2026-04-29 23:58 | 0.51597 | T | Due to R phase LA blast . | 0 | 0 | No interruption
GPH 230/33kV | HATHAZARI | 2026-04-16 03:25 | 2026-04-16 03:59 | 0.023611 | T | Tropped | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Ananda Bazar Ckt-1 | 2026-04-09 10:40 | 2026-04-09 11:11 | 0.021528 | T | Transient fault. | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Ananda Bazar Ckt-1 | 2026-04-09 10:40 | 2026-04-09 11:11 | 0.021528 | T | Transient fault. | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Julda Ckt. line | 2026-04-11 15:58 | 2026-04-11 18:07 | 0.089583 | T | Transient fault | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2026-04-11 15:58 | 2026-04-11 18:10 | 0.091667 | T | Due to bad weather. | 0 | 0 | No interruption
Khagrachori 132/33kV | RANGAMATI-2 | 2026-04-28 13:21 | 2026-04-28 13:25 | 0.0027778 | T | Thundering | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-AKSPL Line | 2026-04-02 11:58 | 2026-04-02 12:18 | 0.013889 | T | N/A | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Sikalbaha ckt | 2026-04-07 02:53 | 2026-04-07 03:25 | 0.022222 | T | Bad weather | 0 | 0 | No interruption
Rampur 230/132/33 | Anandabazar-1 | 2026-04-14 13:38 | 2026-04-14 15:13 | 0.065972 | T | Distance Trip | 0 | 0 | No interruption
Hathazari 230/132/33kV | Raojan-02 | 2026-04-28 12:07 | 2026-04-28 12:07 | 0 | E/O | DC problem. | 0 | 0 | No interruption
Hathazari 230/132/33kV | Raojan-01 | 2026-04-28 12:58 | 2026-04-28 14:26 | 0.061111 | E/O | DC problem. | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Madunaghat CKT-2 | 2026-04-20 10:48 | 2026-04-25 05:47 | 1900-01-03 18:59 | E/O | As per instruction from NLDC AE(299725) | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Madunaghat CKT-2 | 2026-04-25 12:36 | 2026-05-02 08:59 | 1900-01-05 20:23 | E/O | as per instruction of nldc | 0 | 0 | No interruption
|  |  | Total : | 1900-01-12 00:36 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-2 | 2026-04-04 00:32 | 2026-04-04 00:42 | 0.0069444 | T | Heavy thunder storm. | 24 | 4 | Power interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-1 | 2026-04-14 02:22 | 2026-04-14 03:05 | 0.029861 | T | None | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-2 | 2026-04-18 15:05 | 2026-04-22 21:33 | 1900-01-03 06:28 | T | Tripped | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-1 | 2026-04-18 15:17 | 2026-04-18 15:30 | 0.0090278 | T | Tripped | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-1 | 2026-04-18 15:18 | 2026-04-18 15:35 | 0.011806 | T | Tripped | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-2 | 2026-04-25 13:25 | 2026-04-25 13:38 | 0.0090278 | T | Tripped | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-1 | 2026-04-28 07:37 | 2026-04-28 10:34 | 0.12292 | T | None | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-2 | 2026-04-28 07:37 | 2026-04-28 10:35 | 0.12361 | T | Tripped | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Kachua | 2026-04-26 18:47 | 2026-04-26 19:41 | 0.0375 | T | B-ph, zone1, SOTF, | 7 | 6.3 | Power interruption
Cumilla(S) 132/33kV | Chowddagram-2 | 2026-04-28 10:42 | 2026-04-28 11:45 | 0.04375 | T | Zone-1, AR Operated | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2026-04-04 00:33 | 2026-04-04 02:05 | 0.063889 | T | Bad Weather. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Kulaura-2 | 2026-04-14 21:01 | 2026-04-14 21:37 | 0.025 | T | Bad weather | 0 | 0 | No interruption
Feni 132/33kV | Feni Ckt-1 | 2026-04-18 11:27 | 2026-04-18 15:30 | 0.16875 | T | Due increase Sag | 0 | 0 | No interruption
Feni 132/33kV | Feni Ckt-3 | 2026-04-28 11:25 | 2026-04-28 12:44 | 0.054861 | T | Fault | 0 | 0 | No interruption
Feni 230/132kV | Feni-1 | 2026-04-18 11:27 | 2026-04-18 15:32 | 0.17014 | T | Due to fault at 33kv side at Feni 132/33 kv substation | 0 | 0 | No interruption
Kasba 132/33kV | Muradnagar-Kasba Ckt-1 | 2026-04-26 18:01 | 2026-04-26 18:43 | 0.029167 | T | Bad weather | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-01 | 2026-04-14 02:24 | 2026-04-14 03:08 | 0.030556 | T | Stormy weather | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2026-04-18 15:04 | 2026-04-22 21:31 | 1900-01-03 06:27 | T | Bad Weather | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-01 | 2026-04-18 15:17 | 2026-04-18 15:30 | 0.0090278 | T | Bad Weather | 0 | 0 | No interruption
Shahjibazar 132/33kV | BPDB 60 MW | 2026-04-18 15:31 | 2026-04-18 16:23 | 0.036111 | T | Bad weather | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shajibazar-Sreemongal Ckt-01 | 2026-04-24 11:52 | 2026-04-24 12:02 | 0.0069444 | T | N/A | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shajibazar-Sreemongal Ckt-02 | 2026-04-24 11:52 | 2026-04-24 12:05 | 0.0090278 | T | N/A | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2026-04-25 13:25 | 2026-04-25 13:38 | 0.0090278 | T | Bad Weather | 0 | 0 | No interruption
Shahjibazar 132/33kV | SPCL 86 MW | 2026-04-27 06:08 | 2026-04-27 06:33 | 0.017361 | T | Heavy Rain with Thundering | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-01 | 2026-04-28 07:37 | 2026-04-28 10:36 | 0.12431 | T | Stormy Weather | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2026-04-28 07:37 | 2026-04-28 10:36 | 0.12431 | T | Stormy Weather | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-2 | 2026-04-15 03:15 | 2026-04-15 03:54 | 0.027083 | T | Power swing fault is caught by Distance relay | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal-Fenchugonj circuit-1 | 2026-04-19 02:26 | 2026-04-19 03:24 | 0.040278 | T | distance relay phase A | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal - Shahjibazar circuit-1 | 2026-04-24 11:52 | 2026-04-24 12:02 | 0.0069444 | T | Tripped | 0 | 0 | No interruption
Sreemongol 132/33kV | sreemangal-Shahjibazar circuit-2 | 2026-04-24 11:52 | 2026-04-24 12:03 | 0.0076389 | T | Tripped | 0 | 0 | No interruption
Sunamganj 132/33kV | Chhatak-Sunamgonj CKT-2 | 2026-04-13 19:46 | 2026-04-13 19:55 | 0.00625 | T | Tripped | 18.5 | 2.775 | Power interruption
Sunamganj 132/33kV | Chhatak-Sunamgonj CKT-1 | 2026-04-13 19:46 | 2026-04-13 19:55 | 0.00625 | T | Tripped | 18.5 | 2.775 | Power interruption
Sunamganj 132/33kV | Chhatak-Sunamgonj CKT-2 | 2026-04-14 22:24 | 2026-04-14 22:40 | 0.011111 | T | Tripped due to severe storm | 44 | 11.7333 | Power interruption
Sunamganj 132/33kV | Chhatak-Sunamgonj CKT-1 | 2026-04-19 01:19 | 2026-04-19 01:40 | 0.014583 | T | Tripped chhatak-sunamgonj CKT-1 from sylhet for northwester | 19 | 6.65 | Power interruption
Sunamganj 132/33kV | Chhatak-Sunamgonj CKT-2 | 2026-04-19 01:19 | 2026-04-19 01:40 | 0.014583 | T | Tripped chhatak-sunamgonj CKT-2 from sylhet for northwester | 19 | 6.65 | Power interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2026-04-04 04:41 | 2026-04-04 05:41 | 0.041667 | T | Distance protection Operated Signal | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2026-04-13 19:44 | 2026-04-13 19:54 | 0.0069444 | T | Heavy Thundering | 26 | 4.3333 | Power interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2026-04-14 22:26 | 2026-04-14 22:41 | 0.010417 | T | Distance Relay | 25 | 6.25 | Power interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2026-04-19 01:20 | 2026-04-19 01:41 | 0.014583 | T | Thundering | 20 | 7 | Power interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-1 | 2026-04-04 00:42 | 2026-04-04 15:03 | 0.59792 | E/O | OPGW disconnected due to heavy thunder storm between 81 & 82 tower | 0 | 0 | No interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-2 | 2026-04-04 00:43 | 2026-04-04 15:03 | 0.59722 | E/O | OPGW disconnected due to heavy thunder storm between 81 & 82 tower | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-2 | 2026-04-17 06:12 | 2026-04-17 10:01 | 0.15903 | E/O | Emergency Maintenance | 0 | 0 | No interruption
Chandina 132/33kV | Cumilla (N) Line-1 | 2026-04-23 13:09 | 2026-04-23 17:00 | 0.16042 | E/O | Due to Maintenance work at cumilla north-1 line bay. | 0 | 0 | No interruption
Chandpur 132/33kV | 33 kV T-5 section | 2026-04-04 07:40 | 2026-04-04 10:05 | 0.10069 | E/O | Maintenance | 25 | 60.4167 | Power interruption
Chandpur 132/33kV | 33 kV T-2 section | 2026-04-27 14:45 | 2026-04-27 15:10 | 0.017361 | E/O | Maintenance work by BPDB | 12 | 5 | Power interruption
Daganbhuiyan 132/33kV | Chowmuhuni ckt-1 | 2026-04-23 10:10 | 2026-04-23 10:10 | 0 | E/O | Replacing Panel Chowmuhuni S/S. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2026-04-04 02:06 | 2026-04-04 12:52 | 0.44861 | E/O | OPGW Maintenance | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2026-04-04 00:41 | 2026-04-04 14:52 | 0.59097 | E/O | Line Fault Removal. | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2026-04-04 10:27 | 2026-04-09 19:35 | 1900-01-04 09:08 | E/O | Line Fault Removal. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-17 01:44 |  | Unserved Energy: |  | 123.8833
Khulna Grid Circle :
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2026-04-06 23:36 | 2026-04-07 01:32 | 0.080556 | T | Over voltage | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2026-04-30 00:10 | 2026-04-30 01:34 | 0.058333 | T | Over Voltage | 0 | 0 | No interruption
Barishal 230/132kV | Madaripur ckt-01 | 2026-04-08 17:40 | 2026-04-08 17:54 | 0.0097222 | T | Overcurrent | 0 | 0 | No interruption
Barishal 230/132kV | Madaripur ckt-01 | 2026-04-28 14:08 | 2026-04-28 21:59 | 0.32708 | T | Distance Relay | 0 | 0 | No interruption
Gollamari 132/33kV | E05 Gollamari-Khulna(S) Line-2 | 2026-04-29 11:06 | 2026-04-29 11:28 | 0.015278 | T | Thundering | 0 | 0 | No interruption
Gopalganj 132/33kV | Gopalganj North-1 | 2026-04-28 13:05 | 2026-04-28 13:21 | 0.011111 | T | Thundering | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- Noapara-2 | 2026-04-06 22:57 | 2026-04-07 01:23 | 0.10139 | T | Transmission line fault | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- Noapara-2 | 2026-04-29 21:52 | 2026-04-29 23:14 | 0.056944 | T | Heavy rain and Storm. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-1 | 2026-04-16 13:42 | 2026-04-16 13:58 | 0.011111 | T | Earth Fault | 0 | 0 | No interruption
Khulna(S) 230/132kV | Gallamari Ckt-2 | 2026-04-29 11:06 | 2026-04-29 11:29 | 0.015972 | T | Thundering | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 2 | 2026-04-06 22:57 | 2026-04-07 01:24 | 0.10208 | T | Distance Relay Trip | 0 | 0 | No interruption
Noapara 132/33kV | Jashore-1 | 2026-04-14 11:37 | 2026-04-14 12:26 | 0.034028 | T | Distance Relay Trip | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 2 | 2026-04-16 14:07 | 2026-04-16 15:15 | 0.047222 | T | Distance Relay Trip | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 2 | 2026-04-29 21:52 | 2026-04-29 23:10 | 0.054167 | T | Distance Relay Trip | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-1 (L-1) | 2026-04-16 13:42 | 2026-04-16 13:56 | 0.0097222 | T | Earth fault | 0 | 0 | No interruption
Barishal 230/132kV | Madaripur ckt-01 | 2026-04-28 14:08 | 2026-04-28 21:59 | 0.32708 | E/O | Conductor torn out | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2026-04-12 15:22 | 2026-04-16 00:14 | 1900-01-02 08:52 | E/O | Due to line overload, the breaker of the Rooppur line has been kept open as per NLDC instructions. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-1 | 2026-04-28 11:38 | 2026-04-28 13:15 | 0.067361 | E/O | Emergency Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Rupsha Ckt-1 | 2026-04-28 13:46 | 2026-04-28 18:46 | 0.20833 | E/O | Emergency Maintenance | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-1 (L-1) | 2026-04-28 11:38 | 2026-04-28 13:15 | 0.067361 | E/O | R ফেজে ঘুড়ির সুতা অপসারণ | 0 | 0 | No interruption
|  |  | Total : | 1900-01-03 23:23 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi 132/33kV | 132 kV Rupppur-2 | 2026-04-19 02:05 | 2026-04-19 08:44 | 0.27708 | T | Tripped | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Baghabari Line | 2026-04-21 18:02 | 2026-04-21 20:28 | 0.10139 | T | Tripped | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Pabna | 2026-04-22 12:59 | 2026-04-22 13:37 | 0.026389 | T | Tripped | 0 | 0 | No interruption
Jashore 132/33kV | NOA-1(L3) | 2026-04-14 11:37 | 2026-04-14 12:27 | 0.034722 | T | Trip | 0 | 0 | No interruption
Jashore 132/33kV | JH-2(L1) | 2026-04-16 12:50 | 2026-04-16 13:07 | 0.011806 | T | Distance trip | 0 | 0 | No interruption
Jashore 132/33kV | BEN-2 | 2026-04-30 00:11 | 2026-04-30 00:26 | 0.010417 | T | Trip | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah1-Jhenaidah2,132kV Circuit-2(L3) | 2026-04-03 13:24 | 2026-04-03 14:01 | 0.025694 | T | Tripped | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Shahjadpur Line | 2026-04-08 21:36 | 2026-04-08 22:30 | 0.0375 | T | Tripped | 0 | 0 | No interruption
Ruppur 132/11kV | 132kv Ishurdi Line-2 | 2026-04-19 02:04 | 2026-04-19 12:56 | 0.45278 | T | Tripped | 0 | 0 | No interruption
Shahjadpur 132/33kV | 132 KV Shahjadpur-Pabna | 2026-04-22 13:04 | 2026-04-22 14:19 | 0.052083 | T | None | 8 | 10 | Power interruption
Shahjadpur 132/33kV | 132 KV Shahjadpur-Bghabari-1 | 2026-04-26 12:55 | 2026-04-26 13:04 | 0.00625 | T | N/A | 0 | 0 | No interruption
Ullahpara 132/33kV | Baghabari ckt | 2026-04-01 17:31 | 2026-04-01 18:34 | 0.04375 | T | Storm and rain | 0 | 0 | No interruption
Ullahpara 132/33kV | Shahjadpur Ckt | 2026-04-01 17:31 | 2026-04-01 18:32 | 0.042361 | T | Storm and Rain | 0 | 0 | No interruption
Kushtia 132/33kV | Kushtia-Jhenaida | 2026-04-29 03:45 | 2026-04-29 04:59 | 0.051389 | T | Distance Relay (F21) and Overcurrent Relay (F67). | 0 | 0 | No interruption
Kushtia 132/33kV | Kushtia-Jhenaida | 2026-04-29 09:37 | 2026-04-29 12:54 | 0.13681 | T | Siemens 7SA87 | 27 | 88.65 | Power interruption
BIPTC | Baharampur-3 | 2026-04-11 17:47 | 2026-04-12 01:17 | 0.3125 | E/O | Shutdown is taken from Baharampur end | 0 | 0 | No interruption
Ruppur 132/11kV | 132kv Ishurdi Line-2 | 2026-04-19 08:33 | 2026-04-19 12:56 | 0.18264 | E/O | Emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 19:20 |  | Unserved Energy: |  | 98.65
Bogura Grid Circle:
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt2 | 2026-04-26 10:54 | 2026-04-26 12:21 | 0.060417 | T | Zone 01Trip | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt1 | 2026-04-29 06:49 | 2026-04-29 07:12 | 0.015972 | T | Earth fault | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt2 | 2026-04-29 06:49 | 2026-04-29 07:14 | 0.017361 | T | Earth fault | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt1 | 2026-04-29 12:06 | 2026-04-29 12:06 | 0 | T | None | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt2 | 2026-04-29 12:06 | 2026-04-29 12:38 | 0.022222 | T | Tripped | 0 | 0 | No interruption
Bogura 230/132kV | Confidance UN-2 | 2026-04-27 04:02 | 2026-04-27 07:10 | 0.13056 | T | stormy weather | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Kurigram-Lalmonirhat Ckt | 2026-04-29 04:52 | 2026-04-29 06:17 | 0.059028 | T | Heavy thurstorm happening | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Kurigram-Lalmonirhat | 2026-04-29 04:50 | 2026-04-29 06:22 | 0.063889 | T | STORM | 0 | 0 | No interruption
Purbasadipur 230/132/33kV | Saidpur Line-1 | 2026-04-27 01:40 | 2026-04-27 02:47 | 0.046528 | T | Thundering | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV Raj(new)-1 | 2026-04-02 10:08 | 2026-04-02 10:23 | 0.010417 | T | Trip | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Taraganj-1 | 2026-04-14 14:01 | 2026-04-14 14:20 | 0.013194 | T | Tripped | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Teesta Solar-1 | 2026-04-25 22:33 | 2026-04-25 23:36 | 0.04375 | T | storm and thundering | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Jaldhaka CKT-02 | 2026-04-26 14:14 | 2026-04-26 14:28 | 0.0097222 | T | Tripped | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Purbosadipur CKT-01 | 2026-04-27 01:40 | 2026-04-27 02:36 | 0.038889 | T | Tripped | 0 | 0 | No interruption
Sirajganj 132/33kV | Ullapara -1 | 2026-04-27 03:30 | 2026-04-27 04:10 | 0.027778 | T | Tripped | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Rangpur CKT-01 | 2026-04-14 14:01 | 2026-04-14 14:22 | 0.014583 | T | Tripped | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Bogura Ckt-1 | 2026-04-11 09:50 | 2026-04-11 10:40 | 0.034722 | E/O | Emergency maint.work | 0 | 0 | No interruption
Bogura 132/33kV | New Bogura-1 | 2026-04-22 11:25 | 2026-04-22 13:10 | 0.072917 | E/O | SF6 Gas Leakage Maintenance work | 0 | 0 | No interruption
Bogura 230/132kV | Sherpur 132 KV Line-1 | 2026-04-11 09:51 | 2026-04-11 10:40 | 0.034028 | E/O | 132kV Line issue at Sherpur(Bogura) 132kV end | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2026-04-10 06:05 | 2026-04-10 22:19 | 0.67639 | E/O | Reduce system voltage | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2026-04-10 06:05 | 2026-04-10 22:19 | 0.67639 | E/O | Reduce system voltage. | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2026-04-12 08:45 | 2026-04-13 17:16 | 1899-12-31 08:31 | E/O | as Direction by NLDC | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2026-04-13 20:11 | 2026-04-13 21:05 | 0.0375 | E/O | Due to reduce system voltage. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2026-04-13 20:11 | 2026-04-13 21:05 | 0.0375 | E/O | Due to reduce system voltage. | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2026-04-20 06:49 | 2026-04-26 00:42 | 1900-01-04 17:53 | E/O | Instruction by NLDC Dhaka. Increase system voltage. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2026-04-27 04:12 | 2026-04-27 18:04 | 0.57778 | E/O | Reduce system voltage | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2026-04-27 04:12 | 2026-04-27 18:04 | 0.57778 | E/O | Reduce system voltage | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2026-04-29 03:33 | 2026-05-01 21:10 | 1900-01-01 17:37 | E/O | Dear sir Kaliakoir ckt- 01 & 02 has been shutdown instructed by NLDC XEN sir due to reduce system voltage . Date: 29-04-2026 Time: 03:33 am Previous voltage : 414/242 kV After S/D voltage : 410/240 kV Thank you Bogura 400/230kV GIS Grid Sub-Station | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2026-04-29 03:33 | 2026-05-01 21:10 | 1900-01-01 17:37 | E/O | Dear sir Kaliakoir ckt- 01 & 02 has been shutdown instructed by NLDC XEN sir due to reduce system voltage . Date: 29-04-2026 Time: 03:33 am Previous voltage : 414/242 kV After S/D voltage : 410/240 kV Thank you Bogura 400/230kV GIS Grid Sub-Station | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2026-04-29 17:55 | 2026-04-29 21:56 | 0.16736 | E/O | Emergency maint.work | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Bogura Ckt-1 | 2026-04-15 09:57 | 2026-04-15 14:36 | 0.19375 | E/O | Insulator change work from Joypurhat Grid end. | 0 | 0 | No interruption
Niamatpur 132/33kV | 132kV Rahanpur Ckt-1 | 2026-04-26 10:20 | 2026-04-26 17:30 | 0.29861 | E/O | Extra sound at inside of rahanpur ckt 1 Y phase breaker. | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Niamatpur 132 KV Line Ckt-01 | 2026-04-26 11:13 | 2026-04-26 17:32 | 0.26319 | E/O | Emergency maint.work | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV PPP 50 Mw | 2026-04-02 17:32 | 2026-04-04 20:11 | 1900-01-01 02:39 | E/O | Maintenance Work By Peaking Power Plant | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Jaldhaka CKT-01 | 2026-04-15 12:39 | 2026-04-15 13:12 | 0.022917 | E/O | For Jaldhaka end sub-station work | 0 | 0 | No interruption
Sirajgonj 230 | Sreepur-01 | 2026-04-16 06:14 | 2026-04-16 10:10 | 0.16389 | E/O | For D/S Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-18 02:06 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1900-03-06 01:19 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
| Ashuganj-2 | 2024-11-13 12:06 | 2024-11-13 12:18

## QF-LDC-25
QF-LDC-25
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:April 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | 230 kv Bus 01 | 2026-04-05 12:10 | 2026-04-05 14:33 | 2:23 | S/O | Due to Redhot maintenance of Bus DS841S | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Bus-2 (400kV) | 2026-04-18 07:30 | 2026-04-18 18:15 | 10:45 | S/O | Connect with existing Bus | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Bus-2 (400kV) | 2026-04-19 08:45 | 2026-04-19 17:55 | 9:10 | S/O | Bay Extension | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Bus-1 (400kV) | 2026-04-20 08:33 | 2026-04-20 21:46 | 13:13 | S/O | Scheduled IDRNPP project work | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Bus-1 (400kV) | 2026-04-21 09:45 | 2026-04-21 14:59 | 5:14 | S/O | Bay Extension | 0 | 0 | No interruption
Bhaluka 132/33kV | Bus A | 2026-04-16 07:02 | 2026-04-16 09:16 | 2:14 | S/O | High temperature maintenance. | 0 | 0 | No interruption
Bhaluka 132/33kV | Bus B | 2026-04-16 09:40 | 2026-04-16 10:32 | 0:52 | S/O | High temperature maintenance. | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-2 | 2026-04-13 07:58 | 2026-04-13 10:45 | 2:47 | S/O | Red hot maintenance by PBS. | 0 | 0 | No interruption
Dhamrai 132/33kV | 33 KV Bus Section-02 | 2026-04-13 08:06 | 2026-04-13 10:40 | 2:34 | S/O | Red hot maintenance work by obs. | 50 | 128.3333 | Power interruption
Dhamrai 132/33kV | Transformer-1 | 2026-04-25 06:06 | 2026-04-25 08:46 | 2:40 | S/O | Kaliakoir end bus shift | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-1 | 2026-04-25 08:38 | 2026-04-25 08:46 | 0:08 | S/O | Kaliakoir end bus shift. | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-2 | 2026-04-25 08:38 | 2026-04-25 08:46 | 0:08 | S/O | Kaliakoir end bus shift | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-1 | 2026-04-27 13:23 | 2026-04-27 15:29 | 2:06 | S/O | Due to PBS 33 KV radio feeder riser clamp maintenance | 50 | 105 | Power interruption
Jamalpur 132/33kV | T-4 | 2026-04-15 11:45 | 2026-04-23 19:48 | 200:03 | S/O | Project work for transformer painting. | 0 | 0 | No interruption
Jamalpur 132/33kV | T-2 | 2026-04-18 07:05 | 2026-04-18 09:02 | 1:57 | S/O | 33kv bus work | 45 | 87.75 | Power interruption
Jamalpur 132/33kV | T-3 | 2026-04-25 11:42 | 2026-04-25 11:42 | 0:00 | S/O | Project work. | 0 | 0 | No interruption
Joydebpur 132/33kV | GT-2 | 2026-04-04 09:08 | 2026-04-04 14:01 | 4:53 | S/O | 33 kV Bus Maintenance by PBS. | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-3 | 2026-04-11 18:50 | 2026-04-11 20:35 | 1:45 | S/O | None | 60 | 105 | Power interruption
Kabirpur 132/33kV | XFR, T-I | 2026-04-11 18:53 | 2026-04-11 20:32 | 1:39 | S/O | Redhot maintenance of 33 kV bus | 95 | 156.75 | Power interruption
Kaliakoir 400/230/132kV | 400/132kV TR-3 | 2026-04-18 15:34 | 2026-04-18 15:57 | 0:23 | S/O | Due to High temperature of DS-181S . | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 132kV Bus 2 | 2026-04-24 06:38 | 2026-04-24 09:04 | 2:26 | S/O | Bus DS Maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 132kV Bus 2 | 2026-04-27 08:52 | 2026-04-27 18:41 | 9:49 | S/O | DS-142S of 400/132kv ATR-1 maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/132kV TR1 | 2026-04-27 08:55 | 2026-04-27 14:10 | 5:15 | S/O | DS-142s maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/132kV TR-3 | 2026-04-28 06:05 | 2026-04-28 07:19 | 1:14 | S/O | Bus Ds maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 132 kV Bus-1 | 2026-04-28 06:10 | 2026-04-28 11:50 | 5:40 | S/O | Bus DS maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/132kV TR2 | 2026-04-28 07:33 | 2026-04-28 08:19 | 0:46 | S/O | Bus DS maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 132kV Bus 2 | 2026-04-28 15:51 | 2026-04-28 15:57 | 0:06 | S/O | 230/132kv Transformer on | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-2 (414T) | 2026-04-01 11:49 | 2026-04-06 17:40 | 125:51 | S/O | Transformer Painting work | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-3 (424T) | 2026-04-07 14:18 | 2026-04-11 15:10 | 96:52 | S/O | T3 painting work. | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-2 (414T) | 2026-04-16 07:20 | 2026-04-16 09:16 | 1:56 | S/O | 33kv bajitpur incoming loops change | 15 | 29 | Power interruption
Kishoreganj 132/33kV | Tr-3 (424T) | 2026-04-27 15:21 | 2026-04-27 15:25 | 0:04 | S/O | Parallel operation | 5 | 0.33333 | Power interruption
Mirpur 132/33kV | Main Bus | 2026-04-08 08:38 | 2026-04-08 17:08 | 8:30 | S/O | Gantry Structure Painting works. | 0 | 0 | No interruption
Mirpur 132/33kV | Reserve Bus | 2026-04-09 09:30 | 2026-04-09 17:04 | 7:34 | S/O | Gantry Structure Painting of Reserve Bus. | 0 | 0 | No interruption
Mirzapur 132/33kV | Transformer-01(E05) | 2026-04-24 05:52 | 2026-04-24 09:53 | 4:01 | S/O | Existing LILO Line ( Mirzapur-Tangail- kaliakair) | 30 | 120.5 | Power interruption
Mirzapur 132/33kV | Transformer-02(E07) | 2026-04-24 05:59 | 2026-04-24 09:54 | 3:55 | S/O | Existing LILO Line ( Mirzapur-Tangail- kaliakair) | 25 | 97.9167 | Power interruption
Mymensingh 132/33kV | Bus A | 2026-04-10 06:51 | 2026-04-10 12:20 | 5:29 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Bus B | 2026-04-11 07:26 | 2026-04-11 11:02 | 3:36 | S/O | Maint.work | 100 | 360 | Power interruption
Nabinagar 132/33kV | T-1 | 2026-04-03 09:14 | 2026-04-11 18:30 | 201:16 | S/O | 230kV Ghorashal-Ishwardi reconductoring work purpose. | 0 | 0 | No interruption
Nabinagar 132/33kV | T-1 | 2026-04-11 15:10 | 2026-04-11 18:30 | 3:20 | S/O | Red hot maintenance | 0 | 0 | No interruption
Nabinagar 132/33kV | Bus Section-1 | 2026-04-11 15:10 | 2026-04-11 18:30 | 3:20 | S/O | Red hot maintenance | 0 | 0 | No interruption
Nabinagar 132/33kV | Main Bus-2 | 2026-04-12 15:39 | 2026-04-12 19:33 | 3:54 | S/O | Stability test | 0 | 0 | No interruption
Nabinagar 132/33kV | T-1 | 2026-04-26 08:45 | 2026-04-26 20:40 | 11:55 | S/O | clamp connector replacement due to red hot maintenance | 0 | 0 | No interruption
Pubail 132/33kV | TRX-2 | 2026-04-18 10:18 | 2026-04-18 12:17 | 1:59 | S/O | Ct maintenance | 0 | 0 | No interruption
Pubail 132/33kV | TRX-1 | 2026-04-18 12:22 | 2026-04-18 14:12 | 1:50 | S/O | 33kV CT Maintenance. | 0 | 0 | No interruption
Savar 132/33kV | T-1 | 2026-04-22 09:45 | 2026-04-22 17:20 | 7:35 | S/O | Transformer painting works. | 0 | 0 | No interruption
Savar 132/33kV | T-1 | 2026-04-23 08:50 | 2026-04-23 18:04 | 9:14 | S/O | Painting works | 0 | 0 | No interruption
Savar 132/33kV | T-1 | 2026-04-24 10:04 | 2026-04-24 17:08 | 7:04 | S/O | Painting works. | 0 | 0 | No interruption
Savar 132/33kV | T-2 | 2026-04-25 10:37 | 2026-04-25 19:00 | 8:23 | S/O | Painting | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-I | 2026-04-25 10:40 | 2026-04-25 18:59 | 8:19 | S/O | Redhot maintenance | 0 | 0 | No interruption
Savar 132/33kV | T-1 | 2026-04-26 10:30 | 2026-04-26 14:45 | 4:15 | S/O | Maint.work | 0 | 0 | No interruption
Savar 132/33kV | T-2 | 2026-04-26 10:32 | 2026-04-26 14:45 | 4:13 | S/O | Maint.work | 0 | 0 | No interruption
Tongi 230/132/33kV | T-1 | 2026-04-23 07:37 | 2026-04-23 07:56 | 0:19 | S/O | DESCO | 0 | 0 | No interruption
Tongi 230/132/33kV | T-03 | 2026-04-23 08:05 | 2026-04-23 08:52 | 0:47 | S/O | Shutdown taken by Desco | 0 | 0 | No interruption
|  |  | Total : | 1900-02-02 09:41 |  | Unserved Energy: |  | 1190.5833
Dhaka (South) Grid Circle :
Ghorashal 230kV | TARFO-2 | 2026-04-11 09:57 | 2026-04-11 15:10 | 5:13 | S/O | CT oil leakage, Loop change, Red hot maintenance. | 70 | 365.1667 | Power interruption
Haripur 230/132kV | 132kV Bus Coupler | 2026-04-04 08:21 | 2026-04-04 11:10 | 2:49 | S/O | Red Hot Maintenance. | 0 | 0 | No interruption
Haripur 230/132kV | Auto TR-1 | 2026-04-05 07:01 | 2026-04-07 16:03 | 57:02 | S/O | Maint.work | 0 | 0 | No interruption
Haripur 230/132kV | 132kV Reserve Bus Sec-1 | 2026-04-05 07:18 | 2026-04-10 12:23 | 125:05 | S/O | Maint.work | 0 | 0 | No interruption
Haripur 230/132kV | Auto TR-1 | 2026-04-08 06:38 | 2026-04-08 07:11 | 0:33 | S/O | Maint.work | 0 | 0 | No interruption
Haripur 230/132kV | Auto TR-2 | 2026-04-08 07:17 | 2026-04-10 12:21 | 53:04 | S/O | Maint.work | 0 | 0 | No interruption
Haripur 230/132kV | 132kV Reserve Bus Sec-2 | 2026-04-08 07:18 | 2026-04-10 12:23 | 53:05 | S/O | Maint.work | 0 | 0 | No interruption
Haripur 230/132kV | 132kV Bus Coupler | 2026-04-08 07:18 | 2026-04-10 12:23 | 53:05 | S/O | Maint.work | 0 | 0 | No interruption
Haripur 230/132kV | Auto TR-1 | 2026-04-18 07:11 | 2026-04-18 10:35 | 3:24 | S/O | High temperature maintenance. | 0 | 0 | No interruption
Haripur 230/132kV | 132kV Main Bus Sec-1 | 2026-04-18 07:35 | 2026-04-18 12:21 | 4:46 | S/O | High temperature maintenance. | 0 | 0 | No interruption
Haripur 230/132kV | Auto TR-2 | 2026-04-18 10:40 | 2026-04-18 12:34 | 1:54 | S/O | Corrective maintenance of different high temperature junction points of ATR-2 230and 132 kV bays. | 0 | 0 | No interruption
Haripur 230/132kV | 132kV Main Bus Sec-2 | 2026-04-18 11:00 | 2026-04-18 12:20 | 1:20 | S/O | Corrective maintenance of different high temperature junction points of ATR-2 132 kV bays. | 0 | 0 | No interruption
Haripur 230/132kV | 132kV Bus Coupler | 2026-04-18 11:00 | 2026-04-18 12:20 | 1:20 | S/O | Corrective maintenance of different high temperature junction points of ATR-2 230and 132 kV bays. | 0 | 0 | No interruption
Hasnabad 132/33kV | 33kv Reserve Bus | 2026-04-24 08:07 | 2026-04-24 12:59 | 4:52 | S/O | Nawabganj -2 R.Bus maintenance and Dohar, sreenagar red hot maintenance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV | ATR-3 | 2026-04-06 11:38 | 2026-04-22 15:43 | 388:05 | S/O | GIS compartment maintenance work. this 132 kv part of the transformer is not operantional since 03.01.2025 because of termination blast (b phase) at gis end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | ATR-3 | 2026-04-21 09:03 | 2026-04-21 15:54 | 6:51 | S/O | ATR-03 132kV GIS Cable terminal module commissioning work | 0 | 0 | No interruption
Maniknagar 132/33kV | Transformer GT-1 | 2026-04-17 07:34 | 2026-04-17 11:10 | 3:36 | S/O | DPDC 33/11 KV upgradation work | 0 | 0 | No interruption
Meghnaghat 400/230kV | ATR -03 | 2026-04-24 11:05 | 2026-04-24 18:12 | 7:07 | S/O | Project work | 0 | 0 | No interruption
Narshingdi 132/33kV | T-3 | 2026-04-01 12:13 | 2026-04-01 14:04 | 1:51 | S/O | Bus-1 DS Maintanance | 0 | 0 | No interruption
Narshingdi 132/33kV | T-4 | 2026-04-26 22:35 | 2026-04-26 23:43 | 1:08 | S/O | Redhot maintenance | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-2 | 2026-04-16 07:04 | 2026-04-16 13:59 | 6:55 | S/O | BAY 105, 132 kV TR-02, Y Phase PT replacement. | 0 | 0 | No interruption
Siddhirganj 132/33kV | T-2 | 2026-04-03 07:03 | 2026-04-03 09:10 | 2:07 | S/O | Due to auxiliary transformer-2 Painting Work. | 0 | 0 | No interruption
Siddhirganj 132/33kV | T-2 | 2026-04-10 08:15 | 2026-04-10 08:55 | 0:40 | S/O | 33 kV meter replacement | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-2 | 2026-04-30 14:57 | 2026-04-30 16:30 | 1:33 | S/O | Due to PBS 33KV source side Langalband feeder's blade change work. | 55 | 85.25 | Power interruption
Srinagar 132/33kV | Tr-01 | 2026-04-27 22:05 | 2026-04-27 23:15 | 1:10 | S/O | Red hot maintenance at 33kv bus feeder 04. | 20 | 23.3333 | Power interruption
|  |  | Total : | 1900-01-31 20:35 |  | Unserved Energy: |  | 473.75
Chattogram Grid Circle :
Baroirhat 132/33kV | TR-1, 406T | 2026-04-02 07:14 | 2026-04-02 09:36 | 2:22 | S/O | Maintenance work | 0 | 0 | No interruption
Baroirhat 132/33kV | TR-2, 416T | 2026-04-02 09:52 | 2026-04-02 12:30 | 2:38 | S/O | Maintenance work | 0 | 0 | No interruption
Dohazari 132/33kV | Power Transformer -T-1 | 2026-04-08 12:11 | 2026-04-08 13:36 | 1:25 | S/O | 33KV Bus Isolator Maintenance | 5 | 7.0833 | Power interruption
Khulshi 132/33kV | 425T(BSRM) | 2026-04-09 08:09 | 2026-04-10 11:41 | 27:32 | S/O | Maintenance and power shifting. | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-3(7103T) | 2026-04-19 09:47 | 2026-04-19 17:07 | 7:20 | S/O | Protection Witness | 0 | 0 | No interruption
Patiya 132/33kV | TRAFO-02 | 2026-04-21 19:59 | 2026-04-21 20:39 | 0:40 | S/O | Meter test | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 17:57 |  |  |  | 7.0833
Cumilla Grid Circle :
Beanibazar 132/33kV | 132 KV Transformer TR-01 | 2026-04-08 10:00 | 2026-04-08 14:15 | 4:15 | S/O | Tan-delta rest | 0 | 0 | No interruption
Beanibazar 132/33kV | 132KV Transformer TR-02 | 2026-04-08 14:38 | 2026-04-08 16:47 | 2:09 | S/O | Tan delta test | 0 | 0 | No interruption
Chandpur 132/33kV | 412T (T-2) | 2026-04-26 21:16 | 2026-04-26 22:14 | 0:58 | S/O | Maintainace Work at 33kv Side | 5 | 4.8333 | Power interruption
Chandpur 132/33kV | 422T(T-5) | 2026-04-26 21:16 | 2026-04-26 22:14 | 0:58 | S/O | Maintainace Work at 33kv Side | 0 | 0 | No interruption
Chauddagram 132/33kV | 132 kv T-2 | 2026-04-01 09:15 | 2026-04-01 13:30 | 4:15 | S/O | Leakage repair of NIFPS valve. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | ATR-02 | 2026-04-21 08:31 | 2026-04-21 17:41 | 9:10 | S/O | Painting the blast wall of Transformer | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | ATR-02 | 2026-04-22 08:11 | 2026-04-22 17:28 | 9:17 | S/O | Blast wall Painting | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | ATR-02 | 2026-04-23 08:42 | 2026-04-23 16:24 | 7:42 | S/O | Fire wall painting | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | TR3-435T | 2026-04-24 14:38 | 2026-04-24 16:30 | 1:52 | S/O | TR-03 CRP Relocation Work. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV T-03 | 2026-04-09 05:28 | 2026-04-09 09:42 | 4:14 | S/O | Winding & oil temperature meter maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-2 | 2026-04-29 17:12 | 2026-04-29 19:12 | 2:00 | S/O |  | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-2 | 2026-04-30 08:16 | 2026-04-30 17:30 | 9:14 | S/O | Transformer replacement work | 0 | 0 | No interruption
Daudkandi 132/33kV | Transformer-1 | 2026-04-26 21:56 | 2026-04-26 23:20 | 1:24 | S/O | Red hot maintenance by PBS-3 at 33 kV switchyard | 0 | 0 | No interruption
Feni 132/33kV | T-1(405T) | 2026-04-01 09:18 | 2026-04-01 13:24 | 4:06 | S/O | T-2,132kV GCB Replace work | 0 | 0 | No interruption
Feni 132/33kV | Bus-1 | 2026-04-01 09:40 | 2026-04-01 12:36 | 2:56 | S/O | For T2 132KV breaker replacement work | 0 | 0 | No interruption
Feni 132/33kV | T-1(405T) | 2026-04-04 07:24 | 2026-04-04 09:59 | 2:35 | S/O | For bpdb request. | 0 | 0 | No interruption
Feni 132/33kV | Bus-1 | 2026-04-04 07:24 | 2026-04-04 09:59 | 2:35 | S/O | For bpdb | 32 | 82.6667 | Power interruption
Feni 132/33kV | T-1(405T) | 2026-04-06 07:20 | 2026-04-06 14:16 | 6:56 | S/O | For T2 132KV breaker replacement work | 0 | 0 | No interruption
Feni 132/33kV | T-2(415T) | 2026-04-30 06:29 | 2026-04-30 14:04 | 7:35 | S/O | Red Hot maintenance at B-Phase 33KV loop Dead end clamp | 24 | 182 | Power interruption
Feni 230/132kV | ATR-1 | 2026-04-20 12:45 | 2026-04-20 14:43 | 1:58 | S/O | TRANSFORMER OIL LEAKAGE CHECK | 0 | 0 | No interruption
Feni 230/132kV | ATR-3 | 2026-04-20 14:51 | 2026-04-20 16:41 | 1:50 | S/O | INSPECTION OIL leakage and rust | 0 | 0 | No interruption
Feni 230/132kV | ATR-2 | 2026-04-21 09:22 | 2026-04-21 17:04 | 7:42 | S/O | Oil leakage and painting work | 0 | 0 | No interruption
Feni 230/132kV | ATR-2 | 2026-04-22 09:12 | 2026-04-22 17:53 | 8:41 | S/O | Oil Leakage and Rast check works | 0 | 0 | No interruption
Feni 230/132kV | ATR-2 | 2026-04-23 09:02 | 2026-04-25 17:22 | 56:20 | S/O | Painting works on going by project | 0 | 0 | No interruption
Kachua 230/132/33kV | TR-1 | 2026-04-05 11:31 | 2026-04-05 17:24 | 5:53 | S/O |  | 8 | 47.0667 | Power interruption
Kachua 230/132/33kV | TR-2 | 2026-04-06 09:59 | 2026-04-06 16:02 | 6:03 | S/O | DFDR test | 0 | 0 | No interruption
Kachua 230/132/33kV | ATR-1 | 2026-04-07 09:50 | 2026-04-07 15:10 | 5:20 | S/O | DFDR Test | 0 | 0 | No interruption
Kachua 230/132/33kV | ATR-2 | 2026-04-07 15:18 | 2026-04-07 17:21 | 2:03 | S/O | DFDR test | 0 | 0 | No interruption
Kachua 230/132/33kV | ATR-1 | 2026-04-08 11:21 | 2026-04-08 16:32 | 5:11 | S/O | DC mixup | 0 | 0 | No interruption
Kachua 230/132/33kV | Main Bus-2 (132 kV) | 2026-04-08 12:26 | 2026-04-08 19:51 | 7:25 | S/O | DFDR test | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 AB | 2026-04-08 09:07 | 2026-04-08 11:01 | 1:54 | S/O | PBS Bus DS Redhot maintenance | 18 | 34.2 | Power interruption
Kulaura 132/33kV | TR-1 AB | 2026-04-25 08:01 | 2026-04-25 09:14 | 1:13 | S/O | PBS bus DS redhot maintenance | 18 | 21.9 | Power interruption
Lakshmipur 132/33kV | Transformer-1 | 2026-04-30 12:09 | 2026-04-30 15:58 | 3:49 | S/O | Transformer has taken Shutdown due to fix Red Hot Problem. | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-01 | 2026-04-20 12:55 | 2026-04-20 15:25 | 2:30 | S/O | 33kv DS Maintenance work. | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-02 | 2026-04-20 15:40 | 2026-04-20 16:46 | 1:06 | S/O | 33kv DS maintenance work | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-01 | 2026-04-30 11:20 | 2026-04-30 12:36 | 1:16 | S/O | project work | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-02 | 2026-04-30 13:40 | 2026-04-30 14:40 | 1:00 | S/O | 33 Kv DS Maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2026-04-01 08:48 | 2026-04-01 09:50 | 1:02 | S/O | Shutdown Taken by pdb for redhot maintenance. | 60 | 62 | Power interruption
Shahjibazar 132/33kV | TR-04 | 2026-04-07 09:01 | 2026-04-07 09:40 | 0:39 | S/O | Redhot Maintenance by pdb | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2026-04-19 16:12 | 2026-04-19 17:16 | 1:04 | S/O | Redhot maintenance | 40 | 42.6667 | Power interruption
Shahjibazar 132/33kV | TR-04 | 2026-04-24 08:28 | 2026-04-24 18:15 | 9:47 | S/O | Work by Energypac | 70 | 684.8333 | Power interruption
Sylhet (South) | Trafo-2 | 2026-04-27 12:21 | 2026-04-27 13:55 | 1:34 | S/O | for 33 kv broken loop connection. | 0 | 0 | No interruption
Sylhet 132/33kV | T2 | 2026-04-16 07:11 | 2026-04-16 09:08 | 1:57 | S/O | Botteshwar feeder 33 KV Bus side DS Maintenance purpose. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-08 05:28 |  |  |  | 1162.1667
Khulna Grid Circle :
Amtali 400/132kV | BUS-1 | 2026-04-08 10:14 | 2026-04-08 17:16 | 7:02 | S/O | Maint.work | 0 | 0 | No interruption
Amtali 400/132kV | BUS-1 | 2026-04-10 08:25 | 2026-04-10 17:04 | 8:39 | S/O | DS problem | 0 | 0 | No interruption
Barishal 230/132kV | T-5 | 2026-04-04 07:49 | 2026-04-04 09:20 | 1:31 | S/O | Hot spot maintenance | 0 | 0 | No interruption
Barishal 230/132kV | T-4 | 2026-04-04 09:39 | 2026-04-04 12:27 | 2:48 | S/O | Hotspot maintenance | 0 | 0 | No interruption
Barishal 230/132kV | T-5 | 2026-04-08 15:49 | 2026-04-08 17:15 | 1:26 | S/O | Nobogram feeder work | 29 | 41.5667 | Power interruption
Barishal 230/132kV | T-5 | 2026-04-20 07:04 | 2026-04-20 10:57 | 3:53 | S/O | T-5 33kv Clamp change,Noise problem of 33 kv Bus DS & Nut bolt tigting | 25 | 97.0833 | Power interruption
Barishal 230/132kV | T-4 | 2026-04-20 16:14 | 2026-04-20 16:53 | 0:39 | S/O | For installation of a new spring charging motor for the 33 kV breaker. | 0 | 0 | No interruption
Barishal 230/132kV | ATR-1 | 2026-04-25 12:24 | 2026-04-25 13:38 | 1:14 | S/O | Oil Refill of Aux-1 | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-2 | 2026-04-11 07:12 | 2026-04-11 09:33 | 2:21 | S/O | Hot Spot maintenance | 0 | 0 | No interruption
Goalpara 132/33kV | T-6 | 2026-04-06 23:10 | 2026-04-07 12:05 | 12:55 | S/O | Maint.work | 0 | 0 | No interruption
Goalpara 132/33kV | T1 | 2026-04-17 07:32 | 2026-04-17 11:12 | 3:40 | S/O | High temperature rised in both side of Txr-1. Main works by nut-bolt tighting in the both side clamp | 0 | 0 | No interruption
Goalpara 132/33kV | T-5 | 2026-04-24 06:48 | 2026-04-24 09:54 | 3:06 | S/O | Shutdown taken by Wzpdcl for 33kv chandanimohol fedder redhot maintenance | 20 | 62 | Power interruption
Goalpara 132/33kV | T-6 | 2026-04-24 06:48 | 2026-04-24 09:54 | 3:06 | S/O | Shutdown taken by Wzpdcl for 33kv chandanimohol fedder redhot maintenance | 0 | 0 | No interruption
Goalpara 132/33kV | T1 | 2026-04-24 06:48 | 2026-04-24 09:54 | 3:06 | S/O | Shutdown taken by Wzpdcl for 33kv chandanimohol fedder redhot maintenance | 0 | 0 | No interruption
Gollamari 132/33kV | Tr-2 | 2026-04-10 08:09 | 2026-04-10 09:31 | 1:22 | S/O | PBS Tetultala Feeder Maintenance | 20 | 27.3333 | Power interruption
Gollamari 132/33kV | Tr-1 | 2026-04-15 08:41 | 2026-04-15 16:50 | 8:09 | S/O | Project work:132kv T-1 painting | 0 | 0 | No interruption
Gollamari 132/33kV | Tr-1 | 2026-04-16 08:03 | 2026-04-16 15:35 | 7:32 | S/O | Paint Work | 0 | 0 | No interruption
Gollamari 132/33kV | Tr-1 | 2026-04-17 08:02 | 2026-04-17 11:34 | 3:32 | S/O | Paint job | 0 | 0 | No interruption
Gollamari 132/33kV | Tr-2 | 2026-04-18 08:02 | 2026-04-18 18:06 | 10:04 | S/O | Maint.work | 0 | 0 | No interruption
Gollamari 132/33kV | Tr-2 | 2026-04-19 07:32 | 2026-04-19 17:01 | 9:29 | S/O | Maint.work | 0 | 0 | No interruption
Gollamari 132/33kV | Tr-1 | 2026-04-20 08:31 | 2026-04-20 10:24 | 1:53 | S/O |  | 0 | 0 | No interruption
Gopalganj 132/33kV | T1 | 2026-04-20 07:06 | 2026-04-20 09:37 | 2:31 | S/O | Red hot Maintenance | 17 | 42.7833 | Power interruption
Gopalganj 400/132kV | ATR-02 | 2026-04-01 10:05 | 2026-04-01 16:30 | 6:25 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Bus-01 | 2026-04-29 08:25 | 2026-04-30 00:09 | 15:44 | S/O | Maint.work | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2026-04-08 08:24 | 2026-04-08 10:57 | 2:33 | S/O | Hot spot maintenance | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2026-04-09 07:37 | 2026-04-09 08:55 | 1:18 | S/O | Wzpdcl | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2026-04-26 09:08 | 2026-04-26 16:45 | 7:37 | S/O | Due to x-former painting work | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2026-04-27 08:17 | 2026-04-27 17:17 | 9:00 | S/O | Due to x-former painting work | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2026-04-28 08:10 | 2026-04-28 17:46 | 9:36 | S/O | Project work | 0 | 0 | No interruption
Khulna(S) 230/132kV | 230 KV Main Bus 2 | 2026-04-29 10:47 | 2026-04-29 12:56 | 2:09 | S/O | control card change | 0 | 0 | No interruption
Mongla 132/33kV | T-2 | 2026-04-07 06:29 | 2026-04-07 12:19 | 5:50 | S/O | 33KV Bus PT change by Pbs. | 20 | 116.6667 | Power interruption
Narail 132/33kV | TR1 (403-T) | 2026-04-05 06:49 | 2026-04-05 08:52 | 2:03 | S/O | Red hot maintenance work in 33KV bus section -০1 ( 04 no feeder at source side) . This shutdown taken by jpbs-2 | 28 | 57.4 | Power interruption
Narail 132/33kV | TR1 (403-T) | 2026-04-11 07:01 | 2026-04-11 09:07 | 2:06 | S/O | Incomer-01 Yphase DS Red Hot Maintenance | 20 | 42 | Power interruption
Noapara 132/33kV | T-1 | 2026-04-09 09:29 | 2026-04-09 17:26 | 7:57 | S/O | project work (painting). | 0 | 0 | No interruption
Noapara 132/33kV | T-1 | 2026-04-10 08:41 | 2026-04-10 17:30 | 8:49 | S/O | Maint.work | 0 | 0 | No interruption
Noapara 132/33kV | T-1 | 2026-04-11 08:57 | 2026-04-11 16:20 | 7:23 | S/O | T-1 Transformer S/D Due to Painting Work. | 0 | 0 | No interruption
Noapara 132/33kV | T-2 | 2026-04-12 08:19 | 2026-04-12 17:48 | 9:29 | S/O | Maint.work | 0 | 0 | No interruption
Noapara 132/33kV | T-2 | 2026-04-13 08:21 | 2026-04-13 17:06 | 8:45 | S/O | Maint.work | 0 | 0 | No interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-01 | 2026-04-01 11:01 | 2026-04-01 11:01 | 0:00 | S/O | Maintenance | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-2 | 2026-04-08 10:46 | 2026-04-08 12:21 | 1:35 | S/O | Red hot maintenance | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-1 | 2026-04-08 12:42 | 2026-04-08 14:31 | 1:49 | S/O | Rajbari PBS red hot maintenance. | 0 | 0 | No interruption
Satkhira 132/33kV | Transformer-1 (T-1) | 2026-04-11 08:23 | 2026-04-11 10:56 | 2:33 | S/O | Maint.work | 62 | 158.1 | Power interruption
Satkhira 132/33kV | Transformer-2 (T-2) | 2026-04-11 08:23 | 2026-04-11 10:56 | 2:33 | S/O | Maint.work | 38 | 96.9 | Power interruption
Shariatpur 132/33kV | T1-406T | 2026-04-15 08:31 | 2026-04-15 11:59 | 3:28 | S/O | Emergency Maintenance Work | 0 | 0 | No interruption
Shariatpur 132/33kV | T2-416T | 2026-04-15 12:17 | 2026-04-15 15:26 | 3:09 | S/O | Emergency Maintenance work. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-08 05:49 |  | Unserved Energy : |  | 741.8333
HVDC Grid Circle
Bhangura 132/33kV | Tr-1(403T) | 2026-04-11 08:10 | 2026-04-11 17:53 | 9:43 | S/O | Project work for bus 2 | 30 | 291.5 | Power interruption
Bhangura 132/33kV | Tr-2(413T) | 2026-04-11 08:11 | 2026-04-11 17:53 | 9:42 | S/O | Project shutdown for bus 2 work | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-2(413T) | 2026-04-12 09:30 | 2026-04-12 18:19 | 8:49 | S/O | Maint.work | 0 | 0 | No interruption
Jashore 132/33kV | T-3 | 2026-04-02 09:23 | 2026-04-02 17:18 | 7:55 | S/O | Due to project work. | 0 | 0 | No interruption
Jashore 132/33kV | T-3 | 2026-04-03 07:45 | 2026-04-03 18:08 | 10:23 | S/O | Maint.work | 0 | 0 | No interruption
Jashore 132/33kV | T-3 | 2026-04-04 08:20 | 2026-04-04 18:13 | 9:53 | S/O | Maint.work | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-1 | 2026-04-10 07:58 | 2026-04-10 17:39 | 9:41 | S/O | Maint.work | 20 | 193.6667 | Power interruption
Jhenaidah 132/33kV | Transformer T-2 | 2026-04-11 07:58 | 2026-04-11 14:36 | 6:38 | S/O | New T2A DS installation | 15 | 99.5 | Power interruption
Kushtia 132/33kV | T-3 | 2026-04-01 09:21 | 2026-04-15 14:48 | 341:27 | S/O | Maint.work | 0 | 0 | No interruption
Kushtia 132/33kV | T-1 | 2026-04-12 15:29 | 2026-04-12 17:17 | 1:48 | S/O | Maint.work | 35 | 63 | Power interruption
Kushtia 132/33kV | T-1 | 2026-04-16 13:53 | 2026-04-30 12:46 | 334:53 | S/O | Maint.work | 0 | 0 | No interruption
Magura 132/33kV | 132 kV Bus-A (Main) | 2026-04-10 07:05 | 2026-04-10 09:20 | 2:15 | S/O | Red hot maintenance | 30 | 67.5 | Power interruption
Pabna 132/33kV | T-2 | 2026-04-19 07:40 | 2026-04-19 14:50 | 7:10 | S/O | None | 14 | 100.3333 | Power interruption
BIPTC | 10CF16 | 2026-04-05 10:46 | 2026-04-06 16:46 | 30:00 | S/O | For Maintenance work | 0 | 0 | No interruption
BIPTC | 20DF21 | 2026-04-06 11:22 | 2026-04-06 12:21 | 0:59 | S/O | For Maintenance work | 0 | 0 | No interruption
BIPTC | 20DF11 | 2026-04-11 09:59 | 2026-04-11 11:40 | 1:41 | S/O | Corrective Maintenance. | 0 | 0 | No interruption
BIPTC | 10CF14 | 2026-04-20 10:12 | 2026-04-20 10:43 | 0:31 | S/O | Corrective Maintenance | 0 | 0 | No interruption
BIPTC | 20DF43 | 2026-04-22 11:05 | 2026-04-22 12:38 | 1:33 | S/O | For CB Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-02-01 03:01 |  | Unserved Energy : |  | 815.5
Bogura Grid Circle:
Amnura 132/33kV | T-2 (416T) | 2026-04-07 08:44 | 2026-04-09 17:20 | 56:36 | S/O | Oil Leakage Maintenance Works | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 230/132KV T-06, 723T | 2026-04-07 09:34 | 2026-04-07 18:17 | 8:43 | S/O | Oil lekage maintenance. | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 230/132 KV T-02, 713T | 2026-04-08 09:30 | 2026-04-08 16:43 | 7:13 | S/O | Oil leakage maintenance work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132/33 KV T-4, 444T | 2026-04-10 18:12 | 2026-04-10 19:51 | 1:39 | S/O |  | 30 | 49.5 | Power interruption
Barapukuria 230/132/33kV | 132/33 KV T-5, 424T | 2026-04-25 11:11 | 2026-04-25 13:12 | 2:01 | S/O | 33 kv under ground cable fault. | 0 | 0 | No interruption
Bogura 230/132kV | T-03 | 2026-04-10 14:50 | 2026-04-10 17:17 | 2:27 | S/O | Oil Refilling | 0 | 0 | No interruption
Bogura 400/230kV | ATR-01 | 2026-04-06 10:17 | 2026-04-06 19:50 | 9:33 | S/O | FDS ( Sergi) R.Disc Maintenance | 0 | 0 | No interruption
Bogura 400/230kV | ATR-01 | 2026-04-07 09:17 | 2026-04-07 14:36 | 5:19 | S/O | Oil Leakage Maintenance | 0 | 0 | No interruption
Chapai 132/33kV | T-2 (415T) | 2026-04-07 15:18 | 2026-04-07 15:43 | 0:25 | S/O | T-01 bay upgrading | 0 | 0 | No interruption
Lalmonirhat 132/33kV | T-1 (425T) | 2026-04-09 15:02 | 2026-04-09 16:59 | 1:57 | S/O | 33KV Bus Maintenance | 20 | 39 | Power interruption
Lalmonirhat 132/33kV | T-2 (415T) | 2026-04-09 15:02 | 2026-04-09 16:55 | 1:53 | S/O | 33KV Bus Maintenance. | 10 | 18.8333 | Power interruption
Lalmonirhat 132/33kV | T-2 (415T) | 2026-04-30 09:30 | 2026-04-30 12:32 | 3:02 | S/O | 132 KV CB change | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2026-04-26 13:56 | 2026-04-26 16:16 | 2:20 | S/O | 33 kv Prib feeder source side red hot | 35 | 81.6667 | Power interruption
Mithapukur 132/33kV | TR-1(404T) | 2026-04-27 10:24 | 2026-04-27 11:24 | 1:00 | S/O | Energy meter change. | 0 | 0 | No interruption
Naogaon 132/33kV | T-4 | 2026-04-13 12:32 | 2026-04-16 17:05 | 76:33 | S/O | Project work | 0 | 0 | No interruption
Naogaon 132/33kV | Main Bus | 2026-04-19 16:34 | 2026-04-19 16:34 | 0:00 | S/O | 132kV main Bus shut down for Bogura ckt-1&2 cable termanation work. | 0 | 0 | No interruption
Panchagarh 132/33kV | T-1(407T) | 2026-04-02 09:10 | 2026-04-02 12:00 | 2:50 | S/O | Red hot Maintenance of 33 kv Bus section-01 (S/D of T-1 Transformer) | 0 | 0 | No interruption
Saidpur 132/33kV | TR-01 | 2026-04-01 10:15 | 2026-04-01 11:55 | 1:40 | S/O | QF- GMD-39 and as the instruction of ALDC Bogura (499264) | 0 | 0 | No interruption
Saidpur 132/33kV | TR-01 | 2026-04-19 12:50 | 2026-04-19 13:58 | 1:08 | S/O | QF- GMD-39 and as the instruction of ALDC Bogura (499264) | 0 | 0 | No interruption
Sirajganj 132/33kV | T4-(445) | 2026-04-07 10:06 | 2026-04-07 12:51 | 2:45 | S/O | 33KV Tarash feeder CT Re-installation work | 20 | 55 | Power interruption
|  |  | Total : | 1900-01-06 21:04 |  | Unserved Energy : |  | 244
Others :Nil
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 3083:35 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:April 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV | Aminbazar Ckt-2 | 2026-04-03 07:19 | 2026-04-03 18:43 | 11:24 | S/O | Deep Cleaning of Disc Insulator. | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-2 | 2026-04-08 22:44 | 2026-04-09 10:30 | 11:46 | S/O | Shut down due to Titas gas Line Leakage Rectification. | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-1 | 2026-04-11 07:40 | 2026-04-11 18:38 | 10:58 | S/O | Deep Cleaning of Disc Insulator | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-2 | 2026-04-18 07:23 | 2026-04-18 16:00 | 8:37 | S/O | Deep cleaning | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Keranigonj-02 | 2026-04-05 11:55 | 2026-04-05 15:06 | 3:11 | S/O | Due to redhot maintenance of Bus-1 DS841S | 0 | 0 | No interruption
Bajitpur 132/33kV | Ashuganj Ckt-1 | 2026-04-03 09:48 | 2026-04-03 18:39 | 8:51 | S/O | Maint.work | 0 | 0 | No interruption
Bajitpur 132/33kV | Ashuganj Ckt-1 | 2026-04-04 09:48 | 2026-04-04 10:30 | 0:42 | S/O | Maint.work | 0 | 0 | No interruption
Bajitpur 132/33kV | Ashuganj Ckt-2 | 2026-04-04 10:31 | 2026-04-04 18:44 | 8:13 | S/O | Maint.work | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 01 | 2026-04-11 07:18 | 2026-04-11 11:17 | 3:59 | S/O | Work on Mymensingh end | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 01 | 2026-04-16 06:39 | 2026-04-16 10:29 | 3:50 | S/O | High temperature maintenance. | 0 | 0 | No interruption
Bhaluka 132/33kV | Sreepur Ckt- 02 | 2026-04-16 07:26 | 2026-04-16 08:34 | 1:08 | S/O | High temperature maintenance. | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 01 | 2026-04-16 08:38 | 2026-04-16 09:22 | 0:44 | S/O | High temperature maintenance. | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-02 | 2026-04-22 11:16 | 2026-04-22 13:13 | 1:57 | S/O | Work for Mymensingh grid | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2026-04-03 09:39 | 2026-04-03 12:03 | 2:24 | S/O | Maint.work | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-1 | 2026-04-24 05:42 | 2026-04-24 09:55 | 4:13 | S/O | Maint.work | 60 | 253 | Power interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2026-04-25 05:34 | 2026-04-25 08:53 | 3:19 | S/O | Project Work. | 30 | 99.5 | Power interruption
Kabirpur 132/33kV | Kadda-1 | 2026-04-09 13:47 | 2026-04-09 15:18 | 1:31 | S/O | Cutting trees on the line of kadda circuit -1 | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -1 | 2026-04-03 08:21 | 2026-04-03 15:16 | 6:55 | S/O | Disc Cleaning. (ES Close 9.26) | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Tongi-2 | 2026-04-03 08:25 | 2026-04-03 17:45 | 9:20 | S/O | Disc Cleaning. (ES Close : 9.29) | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Bibiyana 2 | 2026-04-05 07:02 | 2026-04-05 07:43 | 0:41 | S/O | shutdown taken by NLDC | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Tangail-2 | 2026-04-24 06:09 | 2026-04-24 09:50 | 3:41 | S/O | DS Maintenance. | 0 | 0 | No interruption
Kodda 132/33kV | Summit 149 MW PS | 2026-04-01 13:36 | 2026-04-01 15:03 | 1:27 | S/O | Red hot maintenance | 0 | 0 | No interruption
Kodda 132/33kV | RPCL 100 MW PS | 2026-04-13 07:10 | 2026-04-13 09:00 | 1:50 | S/O | Red Hot Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Sector-18 | 2026-04-07 09:06 | 2026-04-07 17:51 | 8:45 | S/O | Maint.work | 0 | 0 | No interruption
Mirpur 132/33kV | Aminbazar-2 | 2026-04-10 08:30 | 2026-04-10 17:21 | 8:51 | S/O | Gantry structure & equipment painting work. | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Sector-18 | 2026-04-13 09:07 | 2026-04-13 16:42 | 7:35 | S/O | Shutdown applied for Gantry structure painting work. | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Sector-18 | 2026-04-29 23:55 | 2026-04-30 04:13 | 4:18 | S/O | System Over Voltage | 0 | 0 | No interruption
Mirzapur 132/33kV | Mirzapur-Tangail-ckt-1(E03) | 2026-04-24 05:36 | 2026-04-24 09:51 | 4:15 | S/O | Existing LILO Line ( Mirzapur-Tangail- kaliakair) | 30 | 127.5 | No interruption
Mirzapur 132/33kV | Mirzapur-Tangail-ckt-2B(E03) | 2026-04-24 06:00 | 2026-04-24 06:00 | 0:00 | S/O | Existing LILO Line ( Mirzapur-Tangail- kaliakair) | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Bhaluka Ckt-1 | 2026-04-11 07:18 | 2026-04-11 11:18 | 4:00 | S/O | Maint.work | 0 | 0 | No interruption
Nabinagar 132/33kV | Nabinagar-Dhamrai Ckt-1 | 2026-04-03 09:15 | 2026-04-03 12:27 | 3:12 | S/O | 230kV Ghorashal-Ishwardi reconductoring work purpose. | 0 | 0 | No interruption
Nabinagar 132/33kV | Nabinagar-Dhamrai Ckt-2 | 2026-04-03 09:15 | 2026-04-03 12:28 | 3:13 | S/O | 230kV Ghorashal-Ishwardi reconductoring work purpose. | 0 | 0 | No interruption
Netrakona 132/33kV | Mymensingh-Netrokona Ckt-1 | 2026-04-27 10:18 | 2026-04-27 13:41 | 3:23 | S/O | Energy meter replacement. | 0 | 0 | No interruption
Netrakona 132/33kV | Mymensingh-Netrokona Ckt-2 | 2026-04-27 13:42 | 2026-04-27 16:42 | 3:00 | S/O | Energy meter replacement. | 0 | 0 | No interruption
Pubail 132/33kV | Ghorasal-1 | 2026-04-03 08:58 | 2026-04-03 12:13 | 3:15 | S/O | Line Maintenance Work | 0 | 0 | No interruption
Pubail 132/33kV | Joydebpur-2 | 2026-04-03 09:48 | 2026-04-03 12:03 | 2:15 | S/O | Line Maintenance Work | 0 | 0 | No interruption
Pubail 132/33kV | Joydebpur-1 | 2026-04-24 05:44 | 2026-04-24 09:54 | 4:10 | S/O | line maintenance | 0 | 0 | No interruption
Pubail 132/33kV | Ghorasal-2 | 2026-04-24 05:47 | 2026-04-24 10:17 | 4:30 | S/O | line maintenance | 0 | 0 | No interruption
Pubail 132/33kV | Joydebpur-2 | 2026-04-25 05:35 | 2026-04-25 08:52 | 3:17 | S/O | line maintenance | 0 | 0 | No interruption
Pubail 132/33kV | Ghorasal-1 | 2026-04-25 05:39 | 2026-04-25 08:51 | 3:12 | S/O | line mainteance | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-2 | 2026-04-16 07:27 | 2026-04-16 08:34 | 1:07 | S/O | Redhot Maintenancce | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2026-04-08 09:58 | 2026-04-08 16:05 | 6:07 | S/O | Project shutdown | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Uttara 3rd Phase Ckt | 2026-04-24 15:16 | 2026-04-24 17:11 | 1:55 | S/O | Shutdown taken by NLDC | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Basundhara Ckt-1 | 2026-04-29 09:53 | 2026-05-01 12:03 | 50:10 | S/O | for Navy construction works | 0 | 0 | No interruption
|  |  | Total : | 1900-01-09 01:11 |  | Unserved Energy: |  | 480
Dhaka (South) Grid Circle :
Ghorashal 230kV | Ghorashal GIS- AIS Ckt-1 | 2026-04-05 11:27 | 2026-04-05 13:48 | 2:21 | S/O | Old Ghorasha-Ishwardi Tower dismantle work. | 0 | 0 | No interruption
Haripur 230/132kV | Meghnaghat-1 | 2026-04-20 06:26 | 2026-04-20 09:14 | 2:48 | S/O | Other end | 0 | 0 | No interruption
Hasnabad 132/33kV | Shitallakhya | 2026-04-22 15:30 | 2026-04-22 16:04 | 0:34 | S/O | shut down by NLDC | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 2 | 2026-04-05 11:30 | 2026-04-05 15:05 | 3:35 | S/O | Aminbazar end BUS DS redhot maintenance work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 1 | 2026-04-27 10:58 | 2026-04-27 10:58 | 0:00 | S/O | For conductor repair work at Hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 1 | 2026-04-29 21:51 | 2026-04-30 08:01 | 10:10 | S/O | Broken OPGW Inspection | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 2 | 2026-04-29 21:51 | 2026-04-30 13:03 | 15:12 | S/O | Broken OPGW Inspection | 0 | 0 | No interruption
Meghnaghat 230/132kV | Meghnaghat-Haripur-01 | 2026-04-20 06:33 | 2026-04-20 09:10 | 2:37 | S/O | Red hot maintenance work in line ds | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-2 | 2026-04-20 11:24 | 2026-04-20 13:11 | 1:47 | S/O | 400 kV Korerhat ckt- 2 shutdown instructed by NLDC. | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-02 | 2026-04-23 06:18 | 2026-04-23 06:29 | 0:11 | S/O | Order by nldc | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-01 | 2026-04-23 06:36 | 2026-04-23 08:08 | 1:32 | S/O | Order by NLDC | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-01 | 2026-04-02 07:25 | 2026-04-02 19:33 | 12:08 | S/O | OPGW change purpose Tower No_83 to 85 | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 04:55 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Baroaulia 132/33kV | Hat-2 | 2026-04-17 07:51 | 2026-04-18 01:00 | 17:09 | S/O | Maintenance work at hathazari end | 0 | 0 | No interruption
Baroaulia 132/33kV | Hat-1 | 2026-04-25 06:36 | 2026-04-25 12:33 | 5:57 | S/O | Maintenance work at hathazari end | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Kaptai Ckt-02 | 2026-04-09 08:31 | 2026-04-09 15:06 | 6:35 | S/O | Insulator disk change work | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Ananda Bazar Ckt-2 | 2026-04-21 10:27 | 2026-04-21 11:53 | 1:26 | S/O | Meter accuracy test | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Ananda Bazar Ckt-1 | 2026-04-21 14:20 | 2026-04-21 14:43 | 0:23 | S/O | Maintenance work | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Ananda Bazar Ckt-1 | 2026-04-27 07:12 | 2026-04-27 11:15 | 4:03 | S/O | Line parameters check | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroaulia-02 | 2026-04-17 08:10 | 2026-04-18 01:02 | 16:52 | S/O | Maintenance work | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroaulia-01 | 2026-04-25 06:38 | 2026-04-25 12:33 | 5:55 | S/O | Maintenance work | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2026-04-22 08:33 | 2026-04-22 15:39 | 7:06 | S/O | Due to Armouring work between 4-5 No Tower. | 0 | 0 | No interruption
Kalurghat 132/33kV | MODUNAGHAT-01 | 2026-04-09 09:12 | 2026-04-09 19:14 | 10:02 | S/O | Line repair maintenance | 0 | 0 | No interruption
Rangamati 132/33kV | Chandraghona Ckt-02 | 2026-04-01 09:44 | 2026-04-01 12:05 | 2:21 | S/O | Red hot temperature maintenance. | 0 | 0 | No interruption
Shikalbaha 230/132kV | Anwara-2 | 2026-04-16 15:34 | 2026-04-16 15:34 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 05:49 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-2 | 2026-04-15 06:15 | 2026-04-15 08:20 | 2:05 | S/O | Line Rerouting work | 25 | 52.0833 | Power interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-1 | 2026-04-17 06:04 | 2026-04-17 08:08 | 2:04 | S/O | Line re-routing work | 25 | 49.5 | Power interruption
Bibiana 400/230kV | Bibi-Kalia Ckt-I | 2026-04-01 09:38 | 2026-04-01 17:22 | 7:44 | S/O | Emergency Maintenance | 0 | 0 | No interruption
Bibiana 400/230kV | Bibi-Kalia Ckt-II | 2026-04-05 07:10 | 2026-04-05 19:44 | 12:34 | S/O | EM | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Kachua Ckt-1 | 2026-04-01 11:28 | 2026-04-01 18:24 | 6:56 | S/O | Due to kachua ss maintenance work | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Kachua Ckt-2 | 2026-04-02 10:00 | 2026-04-02 18:52 | 8:52 | S/O | 132 kV Chandpur-Kachua Ckt- 2 S/D due to kachua ss maintenance work. | 0 | 0 | No interruption
Chandpur 132/33kV | 100MW(GT) Power Plant Incomer (T4) | 2026-04-21 08:54 | 2026-04-21 14:22 | 5:28 | S/O | Maintenance work by BPDB | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 01 | 2026-04-01 05:39 | 2026-04-01 10:58 | 5:19 | S/O | For 132kV Breaker Maintenance Work. | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 02 | 2026-04-01 06:25 | 2026-04-07 08:33 | 146:08 | S/O | For 132kV Breaker Maintenance Work. | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 01 | 2026-04-07 06:15 | 2026-04-07 09:35 | 3:20 | S/O | Shutdown for remove jumpering. | 15 | 50 | Power interruption
Chowmuhani 230/132/33kV | Feni line-01 | 2026-04-23 10:08 | 2026-04-23 10:08 | 0:00 | S/O | For replacing existing panel and integrating new panel | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | Lakshmipur-02 | 2026-04-24 11:22 | 2026-04-24 13:15 | 1:53 | S/O | CB Pressure gauge issue | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Kachua | 2026-04-02 10:09 | 2026-04-02 19:12 | 9:03 | S/O | Working on Kachua end. | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Kachua | 2026-04-29 14:50 | 2026-04-29 18:21 | 3:31 | S/O | Spring charge maintenance. | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Chowmuhani Ckt-2 | 2026-04-24 14:24 | 2026-04-24 15:44 | 1:20 | S/O | For Project Work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2026-04-15 06:26 | 2026-04-15 08:15 | 1:49 | S/O | Biyanibazar End maintenace Work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2026-04-17 05:59 | 2026-04-17 08:11 | 2:12 | S/O | project work at Sylhet South SS end. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2026-04-29 14:33 | 2026-04-29 18:29 | 3:56 | S/O | Beanibazar Grid SS end work | 0 | 0 | No interruption
Feni 132/33kV | Feni Ckt-3 | 2026-04-01 09:31 | 2026-04-01 13:36 | 4:05 | S/O | For T2 132KV breaker replacement work | 0 | 0 | No interruption
Feni 132/33kV | Feni Ckt-4 | 2026-04-01 09:31 | 2026-04-01 13:39 | 4:08 | S/O | For T2 132KV breaker replacement work | 0 | 0 | No interruption
Feni 132/33kV | Feni-Lanka HFO PS | 2026-04-01 09:35 | 2026-04-01 13:57 | 4:22 | S/O | For T2 132KV breaker replacement work | 0 | 0 | No interruption
Feni 132/33kV | Feni-Lanka HFO PS | 2026-04-06 06:55 | 2026-04-06 13:49 | 6:54 | S/O | For T2 132KV breaker replacement work | 0 | 0 | No interruption
Feni 132/33kV | Feni Ckt-3 | 2026-04-06 08:11 | 2026-04-06 14:14 | 6:03 | S/O | For T2 132KV breaker replacement work | 0 | 0 | No interruption
Feni 132/33kV | Feni Ckt-4 | 2026-04-06 08:16 | 2026-04-06 14:16 | 6:00 | S/O | For T2 132KV breaker replacement work | 0 | 0 | No interruption
Feni 132/33kV | Feni Ckt-2 | 2026-04-18 13:16 | 2026-04-18 15:32 | 2:16 | S/O | For BPDB Required | 0 | 0 | No interruption
Feni 230/132kV | Feni-3 | 2026-04-01 09:29 | 2026-04-01 13:36 | 4:07 | S/O | Braker replacement at Feni 132/33kV Grid end. | 0 | 0 | No interruption
Feni 230/132kV | Feni-4 | 2026-04-01 09:30 | 2026-04-01 13:38 | 4:08 | S/O | Braker replacement at Feni 132/33kV Grid end. | 0 | 0 | No interruption
Feni 230/132kV | Feni-3 | 2026-04-06 08:12 | 2026-04-06 13:35 | 5:23 | S/O | Due to breaker replacement at Feni 132 kv grid substation end | 0 | 0 | No interruption
Feni 230/132kV | Feni-4 | 2026-04-06 08:17 | 2026-04-06 13:39 | 5:22 | S/O | Due to breaker replacement at Feni 132kv substation end | 0 | 0 | No interruption
Feni 230/132kV | Feni-2 | 2026-04-18 13:18 | 2026-04-18 15:33 | 2:15 | S/O | Due to work at feni 132/33 kv grid end | 0 | 0 | No interruption
Kachua 230/132/33kV | Laksam CKT-2 | 2026-04-01 10:50 | 2026-04-01 18:01 | 7:11 | S/O | DFDR Test. | 0 | 0 | No interruption
Kachua 230/132/33kV | Chandpur CKT-1 | 2026-04-01 11:40 | 2026-04-01 18:24 | 6:44 | S/O | DFDR Test. | 0 | 0 | No interruption
Kachua 230/132/33kV | Chandpur CKT-2 | 2026-04-02 09:59 | 2026-04-02 18:57 | 8:58 | S/O | DFDR test | 0 | 0 | No interruption
Kachua 230/132/33kV | Cumilla South CKT | 2026-04-02 10:09 | 2026-04-02 19:12 | 9:03 | S/O | DFDR test. | 0 | 0 | No interruption
Kachua 230/132/33kV | Cumilla North CKT | 2026-04-08 11:26 | 2026-04-08 20:14 | 8:48 | S/O | DFDR test | 0 | 0 | No interruption
Kachua 230/132/33kV | Cumilla South CKT | 2026-04-29 14:52 | 2026-04-29 18:20 | 3:28 | S/O | CB spring charge work | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-Ashuganj Ckt-03 | 2026-04-02 10:30 | 2026-04-02 10:30 | 0:00 | S/O | Line Shifting works. | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-01 | 2026-04-21 09:35 | 2026-04-22 21:30 | 35:55 | S/O | OPGW repairing | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2026-04-21 10:49 | 2026-04-22 21:31 | 34:42 | S/O | opgw repairing work | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shajibazar-Sreemongal Ckt-01 | 2026-04-28 16:44 | 2026-04-28 17:14 | 0:30 | S/O | N/A | 0 | 0 | No interruption
Sunamganj 132/33kV | Chhatak-Sunamgonj CKT-1 | 2026-04-07 06:07 | 2026-04-07 08:36 | 2:29 | S/O | Due to chhatak-Sunamgonj ckt-1 maintenance | 12 | 29.8 | Power interruption
Sunamganj 132/33kV | Chhatak-Sunamgonj CKT-2 | 2026-04-07 06:07 | 2026-04-07 08:46 | 2:39 | S/O | Due to chhatak-sunamgonj ckt-2 maintenance | 12 | 31.8 | Power interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2026-04-15 06:20 | 2026-04-15 08:14 | 1:54 | S/O | Project Work Of OPGW. | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2026-04-17 06:01 | 2026-04-17 08:11 | 2:10 | S/O | Project Work Of OPGW. | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Biyanibazar 132KV Ckt-1 | 2026-04-19 12:11 | 2026-04-28 18:26 | 222:15 | S/O | Shutdown for project work purpose. | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Biyanibazar 132KV Ckt-2 | 2026-04-19 12:11 | 2026-04-19 12:11 | 0:00 | S/O | Shutdown for project work purpose. | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2026-04-29 14:32 | 2026-04-29 18:27 | 3:55 | S/O | Biyanibazar Line disconnect. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2026-04-07 06:20 | 2026-04-07 09:35 | 3:15 | S/O | Chhatak ckt -2 Breaker Maintenance of Chhatak grid end. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2026-04-07 06:20 | 2026-04-07 08:32 | 2:12 | S/O | Chhatak ckt -2 Breaker Maintenance of Chhatak grid end. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2026-04-08 09:17 | 2026-04-09 19:59 | 34:42 | S/O | Project work Purpose. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-26 22:07 |  | Unserved Energy: |  | 213.1833
Khulna Grid Circle :
Amtali 400/132kV | Amtali - RNPL 400 kV Ckt - 1 | 2026-04-01 15:15 | 2026-04-01 17:54 | 2:39 | S/O | DS problem | 0 | 0 | No interruption
Amtali 400/132kV | Amtali - RNPL 400 kV Ckt - 2 | 2026-04-01 18:03 | 2026-04-01 20:18 | 2:15 | S/O | DS Checking | 0 | 0 | No interruption
Amtali 400/132kV | Amtali - Payra 400 kV Ckt - 1 | 2026-04-17 08:40 | 2026-04-17 09:30 | 0:50 | S/O | DS problem of 8052S | 0 | 0 | No interruption
Amtali 400/132kV | Amtali - RNPL 400 kV Ckt - 2 | 2026-04-22 08:29 | 2026-04-22 16:42 | 8:13 | S/O | RNPL চাহিদা অনুযায়ী Shutdown নেওয়া হয়েছে। | 0 | 0 | No interruption
Amtali 400/132kV | Amtali - RNPL 400 kV Ckt - 2 | 2026-04-23 08:57 | 2026-04-23 20:54 | 11:57 | S/O | RNPL demand | 0 | 0 | No interruption
Amtali 400/132kV | Amtali - RNPL 400 kV Ckt - 1 | 2026-04-27 08:40 | 2026-04-27 11:34 | 2:54 | S/O | RNPL এর পক্ষ থেকে চাওয়া হইছে। | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2026-04-15 10:44 | 2026-04-15 11:08 | 0:24 | S/O | Maintenence works. | 0 | 0 | No interruption
Barishal 230/132kV | Gopalgonj CKT-1 | 2026-04-07 10:23 | 2026-04-07 15:29 | 5:06 | S/O | Shutdown Taken from Gopalgonj | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-NWPGCL | 2026-04-17 08:58 | 2026-04-17 11:23 | 2:25 | S/O | Maintenence works. | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Khulna Central-1 | 2026-04-23 09:43 | 2026-04-23 10:54 | 1:11 | S/O | RedHot Remove to Central end | 0 | 0 | No interruption
Gollamari 132/33kV | E01 Gollamari-Gopalgonj Line - 1 | 2026-04-08 08:18 | 2026-04-08 17:05 | 8:47 | S/O | Conductor Stringing SRTL line | 0 | 0 | No interruption
Gollamari 132/33kV | E07 Gollamari-Gopalgonj Line - 2 | 2026-04-08 08:19 | 2026-04-08 17:05 | 8:46 | S/O | Conductor Stringing SRTL line | 0 | 0 | No interruption
Gollamari 132/33kV | E01 Gollamari-Gopalgonj Line - 1 | 2026-04-24 09:52 | 2026-04-24 14:51 | 4:59 | S/O | Maintenence works. | 0 | 0 | No interruption
Gollamari 132/33kV | E07 Gollamari-Gopalgonj Line - 2 | 2026-04-24 09:53 | 2026-04-24 15:06 | 5:13 | S/O | Maintenence works. | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-1 | 2026-04-08 08:19 | 2026-04-08 17:05 | 8:46 | S/O | ALDC | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-2 | 2026-04-08 08:19 | 2026-04-08 17:06 | 8:47 | S/O | ALDC | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Barisal CKT-01 | 2026-04-07 10:22 | 2026-04-07 15:28 | 5:06 | S/O | Maintenence works. | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2026-04-16 10:10 | 2026-04-19 09:41 | 71:31 | S/O | Maintenence works. | 0 | 0 | No interruption
Khulna (C) | 132kV Central-Goalpara-2 | 2026-04-15 09:05 | 2026-04-16 15:25 | 30:20 | S/O | Due to replacement of distance relay by the SPMD Khulna. | 0 | 0 | No interruption
Khulna (C) | 132kV Central-Goalpara-1 | 2026-04-23 09:44 | 2026-04-23 10:53 | 1:09 | S/O | Red Hot maintenance. | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- Noapara-2 | 2026-04-28 10:51 | 2026-04-28 13:45 | 2:54 | S/O | ঘুড়ির সুতা নামানোর জন্য | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-1 | 2026-04-11 08:24 | 2026-04-11 10:54 | 2:30 | S/O | Maintenence works. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-2 | 2026-04-11 08:24 | 2026-04-11 10:54 | 2:30 | S/O | Maintenence works. | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 2 | 2026-04-28 10:50 | 2026-04-28 13:50 | 3:00 | S/O | According to ALDC's Instruction. | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-1 (L-1) | 2026-04-11 08:23 | 2026-04-11 10:55 | 2:32 | S/O | Maintenence works. | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-2 (L-2) | 2026-04-11 08:23 | 2026-04-11 10:55 | 2:32 | S/O | Maintenence works. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-07 15:16 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Bhangura 132/33kV | Bhangura-Bhagabari ckt-1 | 2026-04-11 08:17 | 2026-04-11 17:43 | 9:26 | S/O | Project shutdown for line 2 and bus work | 30 | 283 | Power interruption
BIPTC | Baharampur-2 | 2026-04-18 10:52 | 2026-04-18 20:56 | 10:04 | S/O | For Maintenance work | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2026-04-30 10:11 | 2026-04-30 18:23 | 8:12 | S/O | Shutdown was taken from Baharampur end | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Rupppur-1 | 2026-04-03 10:05 | 2026-04-03 16:37 | 6:32 | S/O | scapffolding work at 132 ishwardi-ruppur circuit-1 | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Rupppur-2 | 2026-04-04 09:08 | 2026-04-04 17:31 | 8:23 | S/O | Isd-Ghorasal ckt-2 reconductoring purpose scaffolding work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Pabna | 2026-04-05 10:00 | 2026-04-05 15:35 | 5:35 | S/O | For Maintenance work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Rupppur-2 | 2026-04-19 08:45 | 2026-04-19 12:55 | 4:10 | S/O | For Maintenance work | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah-Magura, 132kV Circuit-1(L7) | 2026-04-10 06:51 | 2026-04-10 09:38 | 2:47 | S/O | For Maintenance work | 35 | 97.4167 | Power interruption
Jhenaidah 132/33kV | Jhenaidah-Magura 132kV Circuit-2(L6) | 2026-04-10 06:51 | 2026-04-10 09:38 | 2:47 | S/O | For Maintenance work | 35 | 97.4167 | Power interruption
Magura 132/33kV | Jhenaidah Ckt. -1 | 2026-04-10 07:03 | 2026-04-10 09:38 | 2:35 | S/O | Red hot maintenance | 0 | 0 | No interruption
Magura 132/33kV | Jhenaidah Ckt. - 2 | 2026-04-10 07:04 | 2026-04-10 09:39 | 2:35 | S/O | Red hot maintenance | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Shahjadpur Line | 2026-04-11 08:05 | 2026-04-11 17:36 | 9:31 | S/O | CB Pole Replacement | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Shahjadpur Line | 2026-04-25 17:48 | 2026-04-25 19:17 | 1:29 | S/O | For Maintenance work | 0 | 0 | No interruption
Ruppur 132/11kV | 132kv Ishurdi Line-1 | 2026-04-03 10:03 | 2026-04-03 16:37 | 6:34 | S/O | For Maintenance work | 0 | 0 | No interruption
Ruppur 132/11kV | 132kv Ishurdi Line-2 | 2026-04-04 09:07 | 2026-04-04 17:32 | 8:25 | S/O | For Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 17:05 |  | Unserved Energy: |  | 477.8333
Bogura Grid Circle :
Bogura 132/33kV | New Bogura-1 | 2026-04-27 09:51 | 2026-04-27 13:58 | 4:07 | S/O | SF6 Meter gauge repair | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-2 | 2026-04-16 08:24 | 2026-04-16 15:18 | 6:54 | S/O | Project work at Naogaon S/S. | 0 | 0 | No interruption
Bogura 230/132kV | Bogra 132KV Line-1 | 2026-04-22 11:23 | 2026-04-22 13:10 | 1:47 | S/O | Maintenance work at Bogura 132kV sub-Station | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-1 | 2026-04-23 13:58 | 2026-04-23 19:38 | 5:40 | S/O | RTU commissioning , | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-1 | 2026-04-24 14:48 | 2026-04-24 18:59 | 4:11 | S/O | For Maintenance work | 0 | 0 | No interruption
Bogura 230/132kV | Bogra 132KV Line-1 | 2026-04-27 09:52 | 2026-04-27 13:47 | 3:55 | S/O | Maintenance work at kV Sub-Station | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-1 | 2026-04-28 12:35 | 2026-04-29 21:03 | 32:28 | S/O | Project Work at Naogaon Sub-Station | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-1 | 2026-04-30 10:53 | 2026-04-30 10:53 | 0:00 | S/O | For Maintenance work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Rooppur 400 KV Line-1 | 2026-04-06 10:49 | 2026-04-06 19:48 | 8:59 | S/O | Relay Pannel work rooppur site. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2026-04-22 11:56 | 2026-04-22 16:04 | 4:08 | S/O | Kaliakoir Ckt 1 Aviation Light replacement | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2026-04-25 09:00 | 2026-04-25 17:47 | 8:47 | S/O | Aviation light replace. | 0 | 0 | No interruption
Joypurhat 132/33kV | Naogaon Ckt.-2 | 2026-04-23 13:58 | 2026-04-23 19:41 | 5:43 | S/O | For Maintenance work | 0 | 0 | No interruption
Joypurhat 132/33kV | Naogaon Ckt.-2 | 2026-04-24 14:49 | 2026-04-24 18:56 | 4:07 | S/O | For Maintenance work | 0 | 0 | No interruption
Joypurhat 132/33kV | Naogaon Ckt.-2 | 2026-04-28 12:33 | 2026-04-29 21:04 | 32:31 | S/O | Project Work Naogaon end | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Rangpur-kurigram Ckt | 2026-04-15 08:30 | 2026-04-15 09:38 | 1:08 | S/O | Energy Meter Replacement at Rangpur Grid End. | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Rangpur-kurigram Ckt | 2026-04-21 10:17 | 2026-04-21 18:14 | 7:57 | S/O | RTU Integration with NLDC. | 0 | 0 | No interruption
Mithapukur 132/33kV | Confidence-1 | 2026-04-13 09:55 | 2026-04-13 13:48 | 3:53 | S/O | patching the armor on the conductor | 0 | 0 | No interruption
Mithapukur 132/33kV | Confidence-1 | 2026-04-20 09:46 | 2026-04-20 15:53 | 6:07 | S/O | sky wire stringing from lilo tower | 0 | 0 | No interruption
Mithapukur 132/33kV | Confidence-2 | 2026-04-20 09:46 | 2026-04-20 15:53 | 6:07 | S/O | sky wire sringing | 0 | 0 | No interruption
Mithapukur 132/33kV | Palashbari-1 | 2026-04-22 09:46 | 2026-04-22 14:40 | 4:54 | S/O | For pulling opzw from line tower to gantry structure. | 0 | 0 | No interruption
Mithapukur 132/33kV | Palashbari-2 | 2026-04-22 09:46 | 2026-04-22 14:48 | 5:02 | S/O | For pulling opgw from line tower to gantry structure. | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Bogura Ckt-2 | 2026-04-16 08:26 | 2026-04-16 15:58 | 7:32 | S/O | Project work. | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Bogura Ckt-1 | 2026-04-28 12:35 | 2026-04-29 21:03 | 32:28 | S/O | Naogaon-Bogura Ckt-1 will be shifted from AIS to GIS Bus. That's why EEGBPS Project took this line shutdown for Line and XLPE Cable Pot-Head loop Connection. | 0 | 0 | No interruption
Niamatpur 132/33kV | 132kV Rahanpur Ckt-1 | 2026-04-25 14:58 | 2026-04-25 20:16 | 5:18 | S/O | Commission work of RTU | 0 | 0 | No interruption
Niamatpur 132/33kV | 132kV Rahanpur Ckt-1 | 2026-04-27 09:48 | 2026-04-27 15:38 | 5:50 | S/O | Project work and RTU test | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Rahanpur Ckt-2 | 2026-04-27 15:49 | 2026-04-27 17:09 | 1:20 | S/O | Project work and RTU test | 0 | 0 | No interruption
Panchagarh 132/33kV | Thakurgaon- 2 | 2026-04-18 10:31 | 2026-04-18 18:08 | 7:37 | S/O | RTU Integration with NLDC | 0 | 0 | No interruption
Panchagarh 132/33kV | Thakurgaon- 2 | 2026-04-19 10:00 | 2026-04-19 20:27 | 10:27 | S/O | RTU Integrating with NLDC , Thakurgaon substation | 0 | 0 | No interruption
Panchagarh 132/33kV | Thakurgaon- 2 | 2026-04-20 09:23 | 2026-04-20 14:36 | 5:13 | S/O | RTU integrating with NLDC, tHAKURGAON substation | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Niamatpur 132 KV Line Ckt-01 | 2026-04-25 14:59 | 2026-04-25 20:11 | 5:12 | S/O | For Maintenance work | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Niamatpur 132 KV Line Ckt-01 | 2026-04-27 09:48 | 2026-04-27 15:40 | 5:52 | S/O | As per instruction of ALDC (Bogura) | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Niamatpur 132 KV Line Ckt-02 | 2026-04-27 15:46 | 2026-04-27 17:10 | 1:24 | S/O | For maintenance work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Taraganj-1 | 2026-04-04 08:32 | 2026-04-05 16:19 | 31:47 | S/O | Development work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Taraganj-2 | 2026-04-05 09:21 | 2026-04-06 17:01 | 31:40 | S/O | For Maintenance work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-GTPS | 2026-04-07 10:20 | 2026-04-27 16:55 | 486:35 | S/O | New gantry conductor connection | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Kurigram | 2026-04-15 08:31 | 2026-04-15 09:37 | 1:06 | S/O | Energy meter replace | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Kurigram | 2026-04-21 10:18 | 2026-04-21 18:13 | 7:55 | S/O | For Maintenance work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Confidence-2 | 2026-04-25 10:13 | 2026-04-25 17:37 | 7:24 | S/O | Project work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Confidence-2 | 2026-04-26 08:50 | 2026-04-26 17:22 | 8:32 | S/O | For Maintenance work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Confidence-1 | 2026-04-27 10:20 | 2026-04-27 15:04 | 4:44 | S/O | For Maintenance work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Confidence-2 | 2026-04-27 10:21 | 2026-04-27 15:05 | 4:44 | S/O | For Maintenance work | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Rangpur CKT-01 | 2026-04-04 08:33 | 2026-04-05 16:20 | 31:47 | S/O | For Maintenance work | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Rangpur CKT-02 | 2026-04-05 09:24 | 2026-04-06 17:02 | 31:38 | S/O | For Maintenance work | 0 | 0 | No interruption
Thakurgaon 132/33kV | Panchagar CKT-2 | 2026-04-18 10:30 | 2026-04-18 18:07 | 7:37 | S/O | RTU communication works | 0 | 0 | No interruption
Thakurgaon 132/33kV | Panchagar CKT-2 | 2026-04-19 10:10 | 2026-04-19 20:30 | 10:20 | S/O | RTU Panel commissioning | 0 | 0 | No interruption
Thakurgaon 132/33kV | Panchagar CKT-2 | 2026-04-20 09:20 | 2026-04-20 14:35 | 5:15 | S/O | RTU pannel comissioning work. | 0 | 0 | No interruption
|  |  | Total : | 1900-02-06 05:42 |  | Unserved Energy: |  | 0
Others :Nil
No interruption
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1900-04-03 00:05 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:April 2026
| Area | Previous Month (March' 2026) |  |  |  | Current Month (April'2026)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 38 | 6 | 65 | 109 | 51 | 18 | 57 | 126
2 | Dhaka (South) Grid Circle. | 62 | 22 | 63 | 147 | 49 | 8 | 37 | 94
3 | Chattogram Grid Circle. | 19 | 10 | 33 | 62 | 18 | 15 | 18 | 51
4 | Cumilla Grid Circle. | 40 | 14 | 70 | 124 | 51 | 21 | 93 | 165
5 | Khulna Grid Circle. | 37 | 19 | 68 | 124 | 32 | 11 | 71 | 114
6 | HVDC Grid Circle | 6 | 26 | 13 | 45 | 26 | 19 | 33 | 78
7 | Bogura Grid Circle. | 41 | 29 | 48 | 118 | 32 | 42 | 66 | 140
8 | Others
9 | Total | 243 | 126 | 360 | 729 | 259 | 134 | 375 | 768
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month: April 2026
| Area | Previous Month (March' 2026) |  |  |  | Current Month (April '2026)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 572.4 | 363.87 | 273.67 | 1209.94 | 485.48 | 260.8 | 1670.58 | 2416.86
2 | Dhaka (South) Grid Circle. | 1887.22 | 156.96 | 842.88 | 2887.06 | 577.47 | 298.33 | 473.75 | 1349.55
3 | Chattogram Grid Circle. | 39.93 | 1.33 | 211.76 | 253.02 | 70.48 | 25.03 | 7.08 | 102.59
4 | Cumilla Grid Circle. | 228.3 | 135.28 | 515.52 | 879.1 | 133.85 | 212.4 | 1375.35 | 1721.6
5 | Khulna Grid Circle. | 224.17 | 364.2 | 695.8 | 1284.17 | 275.6 | 361.08 | 741.83 | 1378.51
6 | HVDC Grid Circle | 674.1 | 117.62 | 166.88 | 958.6 | 240.3 | 352.95 | 1293.33 | 1886.58
7 | Bogura Grid Circle. | 286.85 | 549.43 | 387.25 | 1223.53 | 340.12 | 570.63 | 244 | 1154.75
8 | Others | bar: Energy unserved ( MWH ) due to Total; Energy unserved ( MWH ) due to Total
9 | Total | 3912.97 | 1688.69 | 3093.76 | 8695.42 | 2123.3 | 2081.22 | 5805.92 | 10010.44
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-29
QF-LDC-29
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:April 2026
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 18 | 10 | 28 | 6 | 5 | 17 | 1752.82
2 | Dhaka (South) | 5031.6 | 19 | 3 | 22 | 6 | 5 | 11 | 1078.28
3 | Chattogram | 2042 | 5 | 1 | 6 | 1 | 2 | 3 | 102.6
4 | Khulna | 2434 | 16 | 10 | 26 | 8 | 2 | 16 | 1378.5
5 | HVDC | 5954.3 | 11 | 6 | 17 | 3 | 2 | 12 | 1310.1
6 | Bogura | 3145.6 | 27 | 5 | 32 | 6 | 5 | 21 | 1154.75
7 | Cumilla | 2981 | 11 | 9 | 20 | 2 | 6 | 12 | 1384.53
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 8161.58
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.97%
3 | Chattogram | 99.99%
4 | Khulna | 99.98%
5 | HVDC | 99.99%
6 | Bogura | 99.97%
7 | Cumilla | 99.99% | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:April 2026
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 4 | 3 | 7 | 2 | - | 5 | 664.05
2 | Dhaka (South) | 990.29 | - | 5 | - | 5 | 1 | - | 4 | 271.27
3 | Chattogram | 917 | - | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | -
5 | HVDC | 1325 | - | 2 | 5 | 7 | - | - | 7 | 576.48
6 | Bogura | 1803.3 |  | - | - | - | - | - | - | -
7 | Cumilla | 1648.16 | - | 12 | 5 | 17 | 10 | 1 | 6 | 337.07
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 1848.87
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 100%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 99.99%
6 | Bogura | 100%
7 | Cumilla | 99.99% | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:April 2026
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2026-04-01 | 13 | - | 15 | 22 hr 32 min | 1 | 2 hr 25 min
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-32
QF-LDC-32
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:April 2026
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Bhaluka 132/33kV | 2 | 0.019444 | 14
Kishoreganj 132/33kV | 4 | 3:18 | 75.5
Mirzapur 132/33kV | 2 | 2:56 | 59.07
Rajendrapur 132/33kV | 2 | 10:42 | 135.53
Sreepur 230/132/33kV | 1 | 3:28 | 17.3333
Kaliakoir 400/230/132kV | 1 | 0.094444 | 136
Kishoreganj 132/33kV | 1 | 0.0097222 | 0.93333
Nabinagar 132/33kV | 2 | 0.016667 | 3.2
Tangail 132/33kV | 2 | 0.12569 | 120.67
Bhaluka 132/33kV | 1 | 0.095139 | 41.1
Kishoreganj 132/33kV | 1 | 0.010417 | 9.75
Mirzapur 132/33kV | 1 | 0.15208 | 124.1
Mymensingh 132/33kV | 1 | 0.0097222 | 9.1
Dhamrai 132/33kV | 2 | 0.19444 | 233.33
Jamalpur 132/33kV | 1 | 0.08125 | 87.75
Kabirpur 132/33kV | 2 | 0.14167 | 261.75
Kishoreganj 132/33kV | 2 | 0.083333 | 29.33
Mirzapur 132/33kV | 2 | 0.33056 | 218.42
Mymensingh 132/33kV | 1 | 0.15 | 360
Joydebpur 132/33kV | 2 | 0.31389 | 352.5
Mirzapur 132/33kV | 1 | 0.17708 | 127.5
Hasnabad 132/33kV | 5 | 0.24167 | 140.93
Keranigonj 230/132/33kV | 1 | 0.0076389 | 8.6167
Madanganj 132/33kV | 2 | 2:54 | 40.2
Munshiganj 132/33kV | 4 | 1:18 | 58.35
Narshingdi 132/33kV | 1 | 0:34 | 2.8333
Postogola 132/33kV | 1 | 1:01 | 46.7667
Sonargaon 132/33kV | 1 | 0:17 | 8.5
Ghorashal 230kV | 1 | 1:31 | 98.5833
Munshiganj 132/33kV | 1 | 0:35 | 35
Sonargaon 132/33kV | 2 | 2:37 | 164.75
Hasnabad 132/33kV | 1 | 1:38 | 106.1667
Keranigonj 230/132/33kV | 3 | 4:54 | 148.63
Rampura 230/132kV | 1 | 0:52 | 16.4667
Ghorashal 230kV | 1 | 5:13 | 365.1667
Sonargaon 132/33kV | 1 | 1:33 | 85.25
Srinagar 132/33kV | 1 | 1:10 | 23.3333
Dohazari 132/33kV | 1 | 0:40 | 18.6667
Madunaghat 132/33kV | 2 | 1:59 | 51.82
Chandraghona 132/33kV | 1 | 0:14 | 5.8333
Patiya 132/33kV | 1 | 1:36 | 19.2
Dohazari 132/33kV | 1 | 1:25 | 7.0833
Cumilla(S) 132/33kV | 4 | 2:02 | 18.72
Feni 132/33kV | 1 | 1:00 | 26
Kulaura 132/33kV | 1 | 3:50 | 30.6667
Chandina 132/33kV | 1 | 0:46 | 3.0667
Chauddagram 132/33kV | 1 | 2:59 | 89.5
Chowmuhani 230/132/33kV | 1 | 1:00 | 30
Daganbhuiyan 132/33kV | 1 | 1:30 | 16.5
Sylhet (South) | 1 | 1:35 | 7.9167
Beanibazar 132/33kV | 1 | 0:10 | 4
Cumilla(S) 132/33kV | 1 | 0:54 | 6.3
Sunamganj 132/33kV | 5 | 1:16 | 30.58
Sylhet 132/33kV | 3 | 0:46 | 17.58
Chandpur 132/33kV | 2 | 2:50 | 65.42
Chandpur 132/33kV | 1 | 0:58 | 4.8333
Feni 132/33kV | 2 | 10:10 | 264.67
Kachua 230/132/33kV | 1 | 5:53 | 47.0667
Kulaura 132/33kV | 1 | 1:54 | 34.2
Kulaura 132/33kV | 1 | 1:13 | 21.9
Shahjibazar 132/33kV | 3 | 11:53 | 789.5
Beanibazar 132/33kV | 2 | 4:09 | 101.58
Chhatak 132/33kV | 1 | 3:20 | 50
Sunamganj 132/33kV | 2 | 5:08 | 61.6
Barishal 132/33kV | 2 | 0:07 | 2.23
Barishal 230/132kV | 4 | 6:08 | 240.18
Benapole 132/33kV | 1 | 0:10 | 4.3333
Khulna (C) | 4 | 1:46 | 24.37
Mongla 132/33kV | 1 | 1:17 | 1.2833
Noapara 132/33kV | 2 | 0:32 | 3.2
Borhanuddin 230/33kV | 1 | 3:35 | 197.0833
Gollamari 132/33kV | 1 | 2:03 | 164
Barishal 230/132kV | 2 | 5:19 | 138.65
Goalpara 132/33kV | 1 | 3:06 | 62
Gollamari 132/33kV | 1 | 1:22 | 27.3333
Gopalganj 132/33kV | 1 | 2:31 | 42.7833
Mongla 132/33kV | 1 | 5:50 | 116.6667
Narail 132/33kV | 2 | 2:06 | 99.4
Satkhira 132/33kV | 2 | 5:06 | 255
Ishurdi 132/33kV | 1 | 0:42 | 18.9
Jhenaidah 132/33kV | 1 | 2:25 | 67.6667
Kushtia 132/33kV | 3 | 1:02 | 55.08
Jashore 132/33kV | 1 | 1:58 | 59
Jhenaidah 132/33kV | 2 | 4:05 | 131.25
Kushtia 132/33kV | 2 | 2:27 | 148.7
Pabna 132/33kV | 1 | 1:10 | 14
Shahjadpur 132/33kV | 1 | 1:15 | 10
Kushtia 132/33kV | 1 | 3:17 | 88.65
Bhangura 132/33kV | 1 | 9:43 | 291.5
Jhenaidah 132/33kV | 2 | 16:19 | 293.17
Kushtia 132/33kV | 1 | 1:48 | 63
Magura 132/33kV | 1 | 2:15 | 67.5
Pabna 132/33kV | 1 | 7:10 | 100.3333
Bhangura 132/33kV | 1 | 9:26 | 283
Jhenaidah 132/33kV | 2 | 5:34 | 194.83
Bog-Sherpur 132/33kV | 2 | 2:01 | 72.6
Bogura 132/33kV | 1 | 0:29 | 24.1667
Niamatpur 132/33kV | 3 | 1:55 | 59.53
Rahanpur 132/33kV | 1 | 0:45 | 2.25
Sirajganj 132/33kV | 5 | 13:48 | 181.57
Barapukuria 230/132/33kV | 1 | 2:12 | 11
Jaldhaka 132/33kV | 1 | 0:38 | 9.5
Joypurhat 132/33kV | 1 | 1:36 | 11.2
Lalmonirhat 132/33kV | 1 | 2:37 | 31.4
Mahasthangarh 132/33kV | 2 | 5:13 | 138.2
Mithapukur 132/33kV | 1 | 1:26 | 50.1667
Niamatpur 132/33kV | 2 | 5:01 | 109.33
Palashbari 132/33kV | 1 | 0:51 | 25.5
Rajshahi 132/33kV | 3 | 5:54 | 132.67
Sirajganj 132/33kV | 2 | 2:04 | 51.67
Barapukuria 230/132/33kV | 1 | 1:39 | 49.5
Lalmonirhat 132/33kV | 2 | 3:50 | 57.83
Mahasthangarh 132/33kV | 1 | 2:20 | 81.6667
Sirajganj 132/33kV | 1 | 2:45 | 55
| 184 | 340:26 | 10010.4567
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: April-2026
Sl No. | Sub-station | Load (MW) | Date & Time
1 | AKS | 15 | 2026-04-13 07:00
2 | AKSML | 106 | 2026-04-30 11:00
3 | Aftabnagar | 46 | 2026-04-21 19:30
4 | Agargaon | 138 | 2026-04-21 13:00
5 | Agrabad | 80 | 2026-04-22 18:30
6 | Amnura | 52 | 2026-04-15 13:00
7 | Ashuganj | 111 | 2026-04-04 20:00
8 | BSRM | 206 | 2026-04-03 05:00
9 | Bagerhat | 92 | 2026-04-26 18:30
10 | Bajitpur | 100 | 2026-04-20 19:30
11 | Bakerganj | 15 | 2026-04-18 20:00
12 | Bakulia | 104 | 2026-04-26 18:30
13 | Banani | 64 | 2026-04-22 13:00
14 | Bangabhaban | 23 | 2026-04-21 13:00
15 | Barapukuria | 72 | 2026-04-20 22:00
16 | Barguna | 24 | 2026-04-22 22:00
17 | Barishal | 123 | 2026-04-25 12:00
18 | Barishal-230 | 116 | 2026-04-22 22:00
19 | Baroaulia | 74 | 2026-04-04 12:00
20 | Baroirhat | 66 | 2026-04-01 18:30
21 | Bashundhara | 227 | 2026-04-20 18:30
22 | BashundharaCement | 14 | 2026-04-20 19:00
23 | Beanibazar | 84 | 2026-04-16 19:30
24 | Benapole | 82 | 2026-04-18 23:00
25 | Bhaluka | 171 | 2026-04-02 19:00
26 | Bhandaria | 60 | 2026-04-22 22:00
27 | Bhangura | 50 | 2026-04-20 14:00
28 | Bheramara(GK) | 78 | 2026-04-25 18:00
29 | Bhulta | 233 | 2026-04-16 21:00
30 | Bog-Sherpur | 92 | 2026-04-13 21:00
31 | Bogura | 218 | 2026-04-22 22:00
32 | Borhanuddin | 95 | 2026-04-26 19:00
33 | Brahmanbaria | 155 | 2026-04-22 22:00
34 | Cantonment | 160 | 2026-04-06 18:30
35 | Chandina | 46 | 2026-04-21 19:00
36 | Chandpur | 89 | 2026-04-18 19:30
37 | Chandraghona | 42 | 2026-04-07 18:30
38 | Chapai | 90 | 2026-04-13 21:00
39 | Charsaidpur | 44 | 2026-04-05 13:00
40 | Chauddagram | 90 | 2026-04-18 20:00
41 | Chhatak | 40 | 2026-04-18 22:00
42 | Chowmuhani | 174 | 2026-04-26 18:30
43 | Chuadanga | 136 | 2026-04-14 20:00
44 | Coxsbazar | 155 | 2026-04-26 20:00
45 | Cumilla(N) | 137 | 2026-04-18 22:00
46 | Cumilla(S) | 213 | 2026-04-22 16:00
47 | Daganbhuiyan | 43 | 2026-04-03 23:00
48 | Daudkandi | 173 | 2026-04-25 19:30
49 | DhakaUniversity | 100 | 2026-04-21 13:00
50 | Dhamrai | 136 | 2026-04-23 21:00
51 | Dhanmondi | 155.5 | 2026-04-22 13:00
52 | Dohazari | 114 | 2026-04-03 19:30
53 | Faridpur | 199 | 2026-04-22 21:00
54 | Fatullah | 104 | 2026-04-01 16:00
55 | Fenchuganj | 48 | 2026-04-18 21:00
56 | Feni | 117 | 2026-04-26 16:00
57 | GPH | 92 | 2026-04-04 13:00
58 | Ghatail | 98 | 2026-04-01 17:00
59 | Ghorashal | 11 | 2026-04-15 18:00
60 | Ghorashal-230 | 115 | 2026-04-02 19:00
61 | Goalpara | 51 | 2026-04-25 19:30
62 | Gollamari | 114 | 2026-04-21 21:00
63 | Gopalganj | 118.2 | 2026-04-18 22:00
64 | Gulshan | 154 | 2026-04-22 15:00
65 | Halishahar | 108 | 2026-04-26 18:30
66 | HaripurSBU | 140 | 2026-04-08 16:00
67 | Hasnabad | 116 | 2026-04-23 18:30
68 | Hathazari | 96 | 2026-04-26 19:00
69 | Hatirjheel | 56 | 2026-04-22 15:00
70 | Ishurdi | 95 | 2026-04-18 19:30
71 | Jaldhaka | 99 | 2026-04-17 20:00
72 | Jamalpur | 127 | 2026-04-14 21:00
73 | Jashore | 175 | 2026-04-25 19:00
74 | Jhenaidah | 121 | 2026-04-20 20:00
75 | Joydebpur | 176 | 2026-04-22 18:30
76 | Joypurhat | 85 | 2026-04-22 22:00
77 | Juldah | 24 | 2026-04-05 12:00
78 | KSRM | 37 | 2026-04-07 10:00
79 | Kabirpur | 277 | 2026-04-28 10:00
80 | Kachua | 108 | 2026-04-25 19:30
81 | Kaliganj | 36 | 2026-04-03 19:00
82 | Kallyanpur | 132 | 2026-04-23 00:00
83 | Kalurghat | 134 | 2026-04-28 18:30
84 | Kamrangirchar | 88 | 2026-04-21 13:00
85 | Kaptai | N/A | N/A
86 | Kasba | 43 | 2026-04-07 01:00
87 | Kazla | 126 | 2026-04-23 13:00
88 | Keranigonj | 95 | 2026-04-25 20:00
89 | Khagrachori | 36 | 2026-04-04 19:00
90 | Khulna | 94 | 2026-04-18 13:00
91 | Khulshi | 195 | 2026-04-15 21:00
92 | Kishoreganj | 140 | 2026-04-03 20:00
93 | Kodda | 333 | 2026-04-02 15:00
94 | Kulaura | 50 | 2026-04-18 18:30
95 | Kurigram | 70 | 2026-04-02 18:30
96 | Kushtia | 164 | 2026-04-25 18:00
97 | Laksam | 30 | 2026-04-02 21:00
98 | Lakshmipur | 45 | 2026-04-03 15:00
99 | Lalbag | 80 | 2026-04-19 13:00
100 | Lalmonirhat | 69 | 2026-04-02 19:00
101 | MI_Cement | 18.8 | 2026-04-11 10:00
102 | Madanganj | 50 | 2026-04-04 10:00
103 | Madaripur | 127 | 2026-04-18 21:00
104 | Madartek | 100 | 2026-04-25 00:00
105 | Madunaghat | 63 | 2026-04-01 19:00
106 | Magura | 80 | 2026-04-17 19:00
107 | Mahasthangarh | 99 | 2026-04-20 20:00
108 | Maijdee | 50 | 2026-04-03 21:00
109 | Manikganj | 146 | 2026-04-23 22:00
110 | Maniknagar | 85 | 2026-04-21 13:00
111 | Matarbari | 61 | 2026-04-17 19:00
112 | Matuail | 84 | 2026-04-19 13:00
113 | Metrorail_Motijheel | 50 | 2026-04-27 09:00
114 | Metrorail_Uttara | 10 | 2026-04-23 10:00
115 | Millgate | 112 | 2026-04-21 16:00
116 | Mirpur | 176 | 2026-04-25 16:00
117 | Mirsorai | 61 | 2026-04-20 08:00
118 | Mirzapur | 55 | 2026-04-26 01:00
119 | Mithapukur | 68 | 2026-04-03 19:00
120 | Modern | N/A | N/A
121 | Mogbazar | 101.6 | 2026-04-22 15:00
122 | Mongla | 58 | 2026-04-13 18:30
123 | Motijheel | 56 | 2026-04-21 13:00
124 | Muktagacha | 40 | 2026-04-07 19:00
125 | Munshiganj | 141 | 2026-04-22 18:30
126 | Muradnagar | 57 | 2026-04-22 22:00
127 | Mymensingh | 233 | 2026-04-04 20:00
128 | Nabinagar | 41 | 2026-04-30 18:30
129 | Naogaon | 164 | 2026-04-18 20:00
130 | Narail | 68 | 2026-04-18 22:00
131 | Narinda | 82 | 2026-04-20 13:00
132 | Narshingdi | 200 | 2026-04-13 21:00
133 | Natore | 192 | 2026-04-18 19:30
134 | Nawabganj | 80 | 2026-04-25 19:30
135 | Netrakona | 137 | 2026-04-20 19:30
136 | New | 100 | 2026-04-23 09:00
137 | Niamatpur | 120 | 2026-04-13 21:00
138 | Noapara | 49 | 2026-04-26 19:00
139 | PHP | 13 | 2026-04-09 13:00
140 | Pabna | 119 | 2026-04-21 19:00
141 | Palashbari | 136 | 2026-04-17 19:30
142 | Panchagarh | 64 | 2026-04-06 19:00
143 | Patiya | 12 | 2026-04-16 19:30
144 | Patuakhali | 76 | 2026-04-22 22:00
145 | Payra | 50 | 2026-04-16 13:00
146 | Postogola | 61 | 2026-04-24 00:00
147 | Pubail | 37 | 2026-04-27 13:00
148 | Purbachal | 40 | 2026-04-23 15:00
149 | Purbasadipur | 134 | 2026-04-04 13:00
150 | Rahanpur | 44 | 2026-04-13 21:00
151 | Rahim | 50 | 2026-04-08 12:00
152 | Rajbari | 93.5 | 2026-04-26 03:00
153 | Rajendrapur | 137 | 2026-04-23 20:00
154 | Rajshahi | 142 | 2026-04-03 22:00
155 | Rajshahi-230 | 111 | 2026-04-20 21:00
156 | Ramganj | 122 | 2026-04-18 21:00
157 | Rampur | 46 | 2026-04-16 23:00
158 | Rangamati | 21 | 2026-04-02 18:30
159 | Rangpur | 157 | 2026-04-22 22:00
160 | Ruppur | 7 | 2026-04-15 07:00
161 | SSM | 12 | 2026-04-09 01:00
162 | Saidpur | 111 | 2026-04-23 12:00
163 | Santhia | 40 | 2026-04-20 20:00
164 | Satkhira | 143 | 2026-04-01 19:00
165 | Satmasjid | 121 | 2026-04-21 16:00
166 | Savar | 244 | 2026-04-08 15:00
167 | SevenRings | 23.49 | 2026-04-09 13:00
168 | ShahCement | 46 | 2026-04-18 19:30
169 | Shahjadpur | 94 | 2026-04-22 23:00
170 | Shahjibazar | 123 | 2026-04-03 20:00
171 | Shahmirpur | 66 | 2026-04-12 18:30
172 | Shariatpur | 96 | 2026-04-19 00:00
173 | Sherpur | 130 | 2026-04-14 18:30
174 | Shikalbaha | 34 | 2026-04-13 02:00
175 | Shitalakhya | 94.7 | 2026-04-22 18:00
176 | Sholosohor | 50 | 2026-04-06 17:00
177 | Shyampur | 206 | 2026-04-19 13:00
178 | Siddhirganj | 137 | 2026-04-19 12:00
179 | Sirajganj | 150 | 2026-04-20 20:00
180 | Sonargaon | 168 | 2026-04-26 04:00
181 | Sreemongol | 86 | 2026-04-14 22:00
182 | Sreepur | 121 | 2026-04-13 20:00
183 | Srinagar | 61.8 | 2026-04-22 22:00
184 | Sunamganj | 60 | 2026-04-03 20:00
185 | Sylhet | 68 | 2026-04-16 19:00
186 | Sylhet-132 | 133 | 2026-04-16 19:00
187 | TK | 28.5 | 2026-04-16 21:00
188 | Tangail | 206 | 2026-04-14 19:00
189 | Taraganj | 26 | 2026-04-03 19:00
190 | Tasnim | 35 | 2026-04-18 16:00
191 | Thakurgaon | 103 | 2026-04-03 19:30
192 | Tongi | 165 | 2026-04-22 11:00
193 | Ullahpara | 51 | 2026-04-22 22:00
194 | Ullon | 76 | 2026-04-18 15:00
195 | Uttara | 111 | 2026-04-23 16:00
196 | UttaraNew | 91 | 2026-04-27 05:00
197 | Zigatola | 102 | 2026-04-04 13:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID BANGLADESH PLC. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: April 2026
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5973.16 | 2026-04-20 | 19:30
Chattogram | 1628.7 | 2026-04-26 | 18:30
Cumilla | 1519 | 2026-04-02 | 20:00
Mymensingh | 1107 | 2026-04-02 | 19:30
Sylhet | 609 | 2026-04-16 | 21:00
Khulna | 1900.6 | 2026-04-01 | 19:00
Barishal | 528 | 2026-04-22 | 22:00
Rajshahi | 1708.6 | 2026-04-20 | 21:00
Rangpur | 959 | 2026-04-20 | 22:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-35
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: April-2026
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 408 | 2026-04-27 06:00 | 365 | 2026-04-23 12:00
2 | Amtali | 400 | 440 | 2026-04-17 05:00 | 398 | 2026-04-20 13:00
3 | Ashuganj | 400 | N/A | N/A | N/A | N/A
4 | Bhulta | 400 | 425 | 2026-04-27 06:00 | 371 | 2026-04-01 11:00
5 | Bibiana | 400 | 419 | 2026-04-27 06:00 | 390 | 2026-04-26 12:00
6 | BIPTC | 400 | 408 | 2026-04-29 07:00 | 385 | 2026-04-04 13:00
7 | Bogura | 400 | 420 | 2026-04-09 22:00 | 373 | 2026-04-13 21:00
8 | Gopalganj | 400 | 414 | 2026-04-30 05:00 | 379 | 2026-04-20 12:00
9 | Kaliakoir | 400 | 409 | 2026-04-27 06:00 | 357 | 2026-04-20 12:00
10 | Korerhat | 400 | 415 | 2026-04-09 19:30 | 382 | 2026-04-26 12:00
11 | Madunaghat | 400 | 414 | 2026-04-09 20:00 | 385 | 2026-04-21 10:00
12 | Meghnaghat | 400 | 407 | 2026-04-27 06:00 | 367 | 2026-04-20 12:00
13 | Payra | 400 | 420 | 2026-04-07 04:00 | 400 | 2026-04-20 12:00
14 | Rahanpur | 400 | 424 | 2026-04-09 19:30 | 388 | 2026-04-13 21:00
15 | Rampal | 400 | 413 | 2026-04-07 05:00 | 386 | 2026-04-20 13:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 247 | 2026-04-27 06:00 | 213 | 2026-04-18 11:00
2 | AKSML | 230 | 244 | 2026-04-07 02:00 | 219 | 2026-04-18 11:00
3 | Aminbazar | 230 | 248 | 2026-04-27 06:00 | 214 | 2026-04-18 13:00
4 | Ashuganj | 230 | 246 | 2026-04-27 06:00 | 217 | 2026-04-26 12:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 241 | 2026-04-27 05:00 | 224 | 2026-04-21 10:00
7 | Barapukuria | 230 | 240 | 2026-04-29 05:00 | 200 | 2026-04-07 07:00
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 234 | 2026-04-05 13:00 | 217 | 2026-04-26 15:00
10 | Bheramara | 230 | 238 | 2026-04-30 04:00 | 220 | 2026-04-30 19:00
11 | Bhulta | 230 | 245 | 2026-04-27 06:00 | 209 | 2026-04-26 12:00
12 | Bibiana | 230 | 243 | 2026-04-27 05:00 | 226 | 2026-04-18 11:00
13 | BIPTC | 230 | 239 | 2026-04-30 00:00 | 221 | 2026-04-04 18:00
14 | Bogura | 230 | 245 | 2026-04-27 04:00 | 219 | 2026-04-12 07:00
15 | Bogura-400 | 230 | 245 | 2026-04-27 06:00 | 219 | 2026-04-12 07:00
16 | Borhanuddin | 230 | 237 | 2026-04-07 05:00 | 223 | 2026-04-26 03:00
17 | BSRM | 230 | 238 | 2026-04-07 02:00 | 216 | 2026-04-18 11:00
18 | Chowmuhani | 230 | 237 | 2026-04-27 07:00 | 215 | 2026-04-18 11:00
19 | Cumilla(N) | 230 | 240 | 2026-04-27 07:00 | 215 | 2026-04-20 12:00
20 | Faridpur | 230 | 232 | 2026-04-07 22:00 | 210 | 2026-04-20 13:00
21 | Fenchuganj | 230 | 250 | 2026-04-27 06:00 | 229 | 2026-04-18 22:00
22 | Feni | 230 | 238 | 2026-04-07 02:00 | 214 | 2026-04-26 16:00
23 | Ghorashal | 230 | 246 | 2026-04-27 06:00 | 212 | 2026-04-26 14:00
24 | Ghorashal-230 | 230 | 245 | 2026-04-27 06:00 | 209 | 2026-04-26 12:00
25 | Gopalganj | 230 | 231 | 2026-04-30 03:00 | 212 | 2026-04-20 12:00
26 | GPH | 230 | 240 | 2026-04-03 19:00 | 220 | 2026-04-26 11:00
27 | Haripur | 230 | 244 | 2026-04-27 07:00 | 210 | 2026-04-26 12:00
28 | Hasnabad | 230 | 245 | 2026-04-29 07:00 | 211 | 2026-04-18 13:00
29 | Hathazari | 230 | 244 | 2026-04-07 02:00 | 218 | 2026-04-18 10:00
30 | Ishurdi | 230 | 240 | 2026-04-30 00:00 | 223 | 2026-04-12 12:00
31 | Jhenaidah | 230 | 239 | 2026-04-30 00:00 | 213 | 2026-04-20 13:00
32 | Kachua | 230 | 239 | 2026-04-07 02:00 | 215 | 2026-04-18 10:00
33 | Kaliakoir | 230 | 252 | 2026-04-27 06:00 | 217 | 2026-04-18 10:00
34 | Keranigonj | 230 | 245 | 2026-04-27 06:00 | 212 | 2026-04-19 12:00
35 | Khulna(S) | 230 | 239 | 2026-04-30 02:00 | 216 | 2026-04-20 13:00
36 | Korerhat | 230 | 238 | 2026-04-29 08:00 | 217 | 2026-04-18 11:00
37 | Madunaghat | 230 | 243 | 2026-04-03 17:00 | 221 | 2026-04-18 12:00
38 | Madunaghat-400 | 230 | 244 | 2026-04-06 08:00 | 221 | 2026-04-18 12:00
39 | Maniknagar | 230 | 241 | 2026-04-29 08:00 | 208 | 2026-04-26 12:00
40 | Meghnaghat | 230 | 249 | 2026-04-27 07:00 | 218 | 2026-04-26 12:00
41 | Meghnaghat-400 | 230 | 243 | 2026-04-27 06:00 | 213 | 2026-04-26 12:00
42 | Mirsorai | 230 | 242 | 2026-04-03 18:00 | 215 | 2026-04-18 11:00
43 | Naogaon | 230 | 236 | 2026-04-07 17:00 | 202 | 2026-04-21 07:00
44 | Purbasadipur | 230 | 241 | 2026-04-27 06:00 | 201 | 2026-04-23 07:00
45 | Rajshahi | 230 | 238 | 2026-04-30 04:00 | 218 | 2026-04-04 18:00
46 | Rampal | 230 | 237 | 2026-04-07 04:00 | 216 | 2026-04-27 22:00
47 | Rampur | 230 | N/A | N/A | N/A | N/A
48 | Rampura | 230 | 244 | 2026-04-27 06:00 | 206 | 2026-04-26 12:00
49 | Shikalbaha | 230 | 242 | 2026-04-03 17:00 | 217 | 2026-04-18 10:00
50 | Shyampur | 230 | 243 | 2026-04-27 06:00 | 211 | 2026-04-26 12:00
51 | Siddhirganj | 230 | 242 | 2026-04-29 06:00 | 210 | 2026-04-26 12:00
52 | Sirajgonj | 230 | 250 | 2026-04-29 13:00 | 229 | 2026-04-21 10:00
53 | Sreepur | 230 | 244 | 2026-04-27 06:00 | 216 | 2026-04-26 12:00
54 | Tongi | 230 | 245 | 2026-04-27 05:00 | 208 | 2026-04-20 13:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 142 | 2026-04-27 05:00 | 121 | 2026-04-18 12:00
2 | Agargaon | 132 | 141 | 2026-04-07 01:00 | 123 | 2026-04-18 13:00
3 | Agrabad | 132 | 141 | 2026-04-28 13:00 | 125 | 2026-04-16 20:00
4 | AKS | 132 | 140 | 2026-04-07 02:00 | 125 | 2026-04-16 19:30
5 | Aminbazar | 132 | 143 | 2026-04-27 06:00 | 120 | 2026-04-23 12:00
6 | Amnura | 132 | 140 | 2026-04-07 17:00 | 124 | 2026-04-20 13:00
7 | Ashuganj | 132 | N/A | N/A | N/A | N/A
8 | Ashuganj-230 | 132 | 147 | 2026-04-27 04:00 | 132 | 2026-04-26 12:00
9 | Bagerhat | 132 | 140 | 2026-04-30 00:00 | 113 | 2026-04-20 13:00
10 | Bajitpur | 132 | 141 | 2026-04-29 08:00 | 123 | 2026-04-20 19:30
11 | Bakerganj | 132 | 138 | 2026-04-07 18:00 | 125 | 2026-04-27 22:00
12 | Bakulia | 132 | 140 | 2026-04-03 18:30 | 126 | 2026-04-16 19:30
13 | Banani | 132 | 141 | 2026-04-29 07:00 | 120 | 2026-04-18 13:00
14 | Bangabhaban | 132 | 142 | 2026-04-27 06:00 | 119 | 2026-04-26 12:00
0 | Barapukuria | 132 | 140 | 2026-04-26 | 118 | 2026-04-07 07:00
16 | Barguna | 132 | 138 | 2026-04-07 01:00 | 125 | 2026-04-20 12:00
17 | Barishal | 132 | 139 | 2026-04-07 01:00 | 124 | 2026-04-27 23:00
18 | Barishal-230 | 132 | 138 | 2026-04-07 01:00 | 125 | 2026-04-20 12:00
19 | Baroaulia | 132 | 139 | 2026-04-05 18:00 | 126 | 2026-04-16 19:30
20 | Baroirhat | 132 | 136 | 2026-04-03 19:00 | 120 | 2026-04-23 00:00
21 | Bashundhara | 132 | 139 | 2026-04-26 18:00 | 118 | 2026-04-20 13:00
22 | BashundharaCement | 132 | 141 | 2026-04-07 01:00 | 120 | 2026-04-26 08:00
23 | Beanibazar | 132 | 138 | 2026-04-27 06:00 | 120 | 2026-04-16 19:30
24 | Benapole | 132 | 139 | 2026-04-06 23:00 | 110 | 2026-04-01 22:00
25 | Bhaluka | 132 | 148 | 2026-04-27 06:00 | 119 | 2026-04-30 15:00
26 | Bhandaria | 132 | 140 | 2026-04-28 17:00 | 116 | 2026-04-27 22:00
27 | Bhangura | 132 | 139 | 2026-04-27 05:00 | 125 | 2026-04-12 09:00
28 | Bheramara | 132 | 140 | 2026-04-30 04:00 | 129 | 2026-04-09 13:00
29 | Bheramara(GK) | 132 | 139 | 2026-04-30 00:00 | 128 | 2026-04-20 13:00
30 | Bhulta | 132 | 137 | 2026-04-27 06:00 | 116 | 2026-04-26 12:00
31 | Bog-Sherpur | 132 | 143 | 2026-04-27 05:00 | 124 | 2026-04-03 08:00
32 | Bogura | 132 | 144 | 2026-04-27 06:00 | 125 | 2026-04-03 13:00
33 | Bogura-230 | 132 | 143 | 2026-04-27 04:00 | 124 | 2026-04-15 11:00
34 | Brahmanbaria | 132 | 146 | 2026-04-27 06:00 | 120 | 2026-04-20 12:00
35 | Cantonment | 132 | 141 | 2026-04-10 05:00 | 122 | 2026-04-18 12:00
36 | Chandina | 132 | 141 | 2026-04-27 06:00 | 122 | 2026-04-20 12:00
37 | Chandpur | 132 | 139 | 2026-04-09 19:00 | 120 | 2026-04-26 05:00
39 | Chandraghona | 132 | 142 | 2026-04-28 13:00 | 129 | 2026-04-18 16:00
40 | Chapai | 132 | 141 | 2026-04-07 17:00 | 127 | 2026-04-20 06:00
41 | Charsaidpur | 132 | 141 | 2026-04-27 06:00 | 120 | 2026-04-26 12:00
42 | Chauddagram | 132 | 138 | 2026-04-27 07:00 | 120 | 2026-04-26 11:00
43 | Chhatak | 132 | 138 | 2026-04-26 18:00 | 120 | 2026-04-18 21:00
44 | Chowmuhani | 132 | 134 | 2026-04-07 02:00 | 120 | 2026-04-19 02:00
45 | Chuadanga | 132 | 143 | 2026-04-07 21:00 | 114 | 2026-04-01 19:00
46 | Coxsbazar | 132 | 137 | 2026-04-30 04:00 | 104 | 2026-04-16 19:30
47 | Cumilla(N) | 132 | 141 | 2026-04-06 10:00 | 123 | 2026-04-26 11:00
48 | Cumilla(S) | 132 | 141 | 2026-04-27 07:00 | 115 | 2026-04-19 15:00
49 | Daganbhuiyan | 132 | 136 | 2026-04-07 02:00 | 121 | 2026-04-18 11:00
50 | Daudkandi | 132 | 142 | 2026-04-27 06:00 | 112 | 2026-04-20 12:00
51 | DhakaUniversity | 132 | 141 | 2026-04-29 06:00 | 121 | 2026-04-19 10:00
52 | Dhamrai | 132 | 147 | 2026-04-27 06:00 | 118 | 2026-04-18 10:00
53 | Dhanmondi | 132 | 143 | 2026-04-27 06:00 | 124 | 2026-04-18 10:00
54 | Dohazari | 132 | 138 | 2026-04-07 04:00 | 120 | 2026-04-11 06:00
55 | Faridpur | 132 | 136 | 2026-04-30 00:00 | 123 | 2026-04-20 12:00
56 | Fatullah | 132 | 144 | 2026-04-26 18:00 | 120 | 2026-04-23 12:00
57 | Fenchuganj | 132 | 142 | 2026-04-27 06:00 | 128 | 2026-04-18 22:00
58 | Feni | 132 | 138 | 2026-04-06 07:00 | 120 | 2026-04-26 11:00
59 | Feni-230 | 132 | 136 | 2026-04-27 06:00 | 121 | 2026-04-18 11:00
60 | Ghatail | 132 | 147 | 2026-04-27 07:00 | 114 | 2026-04-01 15:00
61 | Ghorashal | 132 | 146 | 2026-04-27 07:00 | 125 | 2026-04-24 01:00
62 | Goalpara | 132 | 144 | 2026-04-30 00:00 | 120 | 2026-04-20 13:00
63 | Gollamari | 132 | 141 | 2026-04-30 00:00 | 121 | 2026-04-20 13:00
64 | Gopalganj | 132 | 139 | 2026-04-30 00:00 | 121 | 2026-04-20 13:00
65 | Gopalganj-400 | 132 | 138 | 2026-04-30 04:00 | 120 | 2026-04-18 21:00
66 | Gulshan | 132 | 141 | 2026-04-27 05:00 | 120 | 2026-04-19 10:00
67 | Halishahar | 132 | 140 | 2026-04-07 03:00 | 126 | 2026-04-16 19:30
68 | Haripur | 132 | 142 | 2026-04-27 06:00 | 124 | 2026-04-18 11:00
69 | HaripurSBU | 132 | 142 | 2026-04-27 06:00 | 124 | 2026-04-18 11:00
70 | Hasnabad | 132 | 145 | 2026-04-26 18:00 | 121 | 2026-04-18 11:00
71 | Hathazari | 132 | 143 | 2026-04-07 02:00 | 128 | 2026-04-18 10:00
72 | Hatirjheel | 132 | 139 | 2026-04-27 05:00 | 120 | 2026-04-19 10:00
73 | Ishurdi | 132 | 141 | 2026-04-30 00:00 | 130 | 2026-04-20 13:00
74 | Jaldhaka | 132 | 140 | 2026-04-29 06:00 | 113 | 2026-04-07 07:00
75 | Jamalpur | 132 | 146 | 2026-04-27 08:00 | 111 | 2026-04-23 22:00
76 | Jashore | 132 | 140 | 2026-04-06 23:00 | 113 | 2026-04-01 22:00
77 | Jhenaidah | 132 | 143 | 2026-04-07 06:00 | 118 | 2026-04-20 13:00
78 | Jhenaidah-230 | 132 | 143 | 2026-04-07 00:00 | 120 | 2026-04-01 19:30
79 | Joydebpur | 132 | 146 | 2026-04-27 07:00 | 120 | 2026-04-26 12:00
80 | Joypurhat | 132 | 142 | 2026-04-27 06:00 | 111 | 2026-04-18 07:00
81 | Juldah | 132 | 141 | 2026-04-03 18:30 | 126 | 2026-04-16 19:30
82 | Kabirpur | 132 | 146 | 2026-04-27 07:00 | 115 | 2026-04-26 12:00
83 | Kachua | 132 | 136 | 2026-04-07 02:00 | 122 | 2026-04-18 10:00
84 | Kaliakoir | 132 | 145 | 2026-04-29 08:00 | 125 | 2026-04-01 15:00
85 | Kaliganj | 132 | 142 | 2026-04-07 21:00 | 118 | 2026-04-01 19:30
86 | Kallyanpur | 132 | 142 | 2026-04-27 06:00 | 120 | 2026-04-15 15:00
87 | Kalurghat | 132 | 141 | 2026-04-07 03:00 | 129 | 2026-04-16 19:30
88 | Kamrangirchar | 132 | 147 | 2026-04-26 18:00 | 117 | 2026-04-26 12:00
89 | Kaptai | 132 | N/A | N/A | N/A | N/A
90 | Kasba | 132 | 141 | 2026-04-27 06:00 | 117 | 2026-04-20 12:00
91 | Kazla | 132 | 143 | 2026-04-27 07:00 | 119 | 2026-04-21 13:00
92 | Keranigonj | 132 | 147 | 2026-04-26 18:00 | 124 | 2026-04-18 10:00
93 | Khagrachori | 132 | 141 | 2026-04-07 03:00 | 125 | 2026-04-19 10:00
94 | Khulna | 132 | 141 | 2026-04-30 00:00 | 120 | 2026-04-20 13:00
95 | Khulna(S) | 132 | 142 | 2026-04-30 00:00 | 121 | 2026-04-20 13:00
96 | Khulshi | 132 | 139 | 2026-04-03 19:00 | 124 | 2026-04-16 19:30
97 | Kishoreganj | 132 | 140 | 2026-04-27 05:00 | 120 | 2026-04-20 19:30
98 | Kodda | 132 | 146 | 2026-04-27 06:00 | 118 | 2026-04-26 12:00
99 | Korerhat | 132 | 138 | 2026-04-07 04:00 | 126 | 2026-04-18 11:00
100 | KSRM | 132 | 140 | 2026-04-03 17:00 | 127 | 2026-04-26 11:00
101 | Kulaura | 132 | 142 | 2026-04-27 07:00 | 127 | 2026-04-18 22:00
102 | Kurigram | 132 | 140 | 2026-04-27 06:00 | 114 | 2026-04-23 07:00
103 | Kushtia | 132 | 139 | 2026-04-30 01:00 | 124 | 2026-04-20 13:00
104 | Laksam | 132 | 138 | 2026-04-27 07:00 | 121 | 2026-04-26 04:00
105 | Lakshmipur | 132 | 134 | 2026-04-07 02:00 | 118 | 2026-04-26 05:00
106 | Lalbag | 132 | 146 | 2026-04-27 06:00 | 123 | 2026-04-02 12:00
107 | Lalmonirhat | 132 | 139 | 2026-04-27 05:00 | 116 | 2026-04-03 08:00
108 | Madanganj | 132 | 141 | 2026-04-07 01:00 | 121 | 2026-04-26 12:00
109 | Madaripur | 132 | 137 | 2026-04-07 22:00 | 125 | 2026-04-26 03:00
110 | Madartek | 132 | 138 | 2026-04-07 21:00 | 120 | 2026-04-19 10:00
111 | Madunaghat | 132 | 141 | 2026-04-03 19:00 | 102 | 2026-04-21 09:00
112 | Magura | 132 | 141 | 2026-04-07 04:00 | 116 | 2026-04-01 19:00
113 | Mahasthangarh | 132 | 143 | 2026-04-27 06:00 | 121 | 2026-04-03 08:00
114 | Maijdee | 132 | 135 | 2026-04-07 02:00 | 119 | 2026-04-19 02:00
115 | Manikganj | 132 | 143 | 2026-04-27 06:00 | 112 | 2026-04-26 12:00
116 | Maniknagar | 132 | 143 | 2026-04-27 06:00 | 119 | 2026-04-26 12:00
117 | Matarbari | 132 | 136 | 2026-04-28 15:00 | 103 | 2026-04-16 19:30
118 | Matuail | 132 | 141 | 2026-04-29 08:00 | 121 | 2026-04-26 12:00
119 | Metrorail_Motijheel | 132 | 143 | 2026-04-27 06:00 | 119 | 2026-04-26 12:00
120 | Metrorail_Uttara | 132 | 147 | 2026-04-27 06:00 | 118 | 2026-04-23 12:00
121 | Millgate | 132 | 147 | 2026-04-27 06:00 | 120 | 2026-04-19 09:00
122 | Mirpur | 132 | 142 | 2026-04-30 00:00 | 119 | 2026-04-12 12:00
123 | Mirzapur | 132 | 147 | 2026-04-27 06:00 | 118 | 2026-04-01 15:00
124 | Mithapukur | 132 | 142 | 2026-04-27 06:00 | 118 | 2026-04-17 10:00
125 | MI_Cement | 132 | 145 | 2026-04-26 18:00 | 118 | 2026-04-18 10:00
126 | Modern | 132 | N/A | N/A | N/A | N/A
127 | Mogbazar | 132 | 140 | 2026-04-03 04:00 | 122 | 2026-04-19 10:00
128 | Mongla | 132 | 140 | 2026-04-30 00:00 | 114 | 2026-04-20 13:00
129 | Motijheel | 132 | 142 | 2026-04-27 06:00 | 119 | 2026-04-26 12:00
130 | Muktagacha | 132 | 147 | 2026-04-27 06:00 | 115 | 2026-04-01 13:00
131 | Munshiganj | 132 | 140 | 2026-04-27 05:00 | 119 | 2026-04-26 12:00
132 | Muradnagar | 132 | 141 | 2026-04-27 07:00 | 116 | 2026-04-20 12:00
133 | Mymensingh | 132 | 148 | 2026-04-27 07:00 | 108 | 2026-04-20 19:30
134 | Nabinagar | 132 | 146 | 2026-04-27 06:00 | 118 | 2026-04-18 10:00
135 | Naogaon | 132 | 143 | 2026-04-27 04:00 | 116 | 2026-04-03 09:00
136 | Narail | 132 | 144 | 2026-04-07 21:00 | 115 | 2026-04-01 19:30
137 | Narinda | 132 | 0 | 2026-04-01 00:00 | N/A | N/A
139 | Narshingdi | 132 | 146 | 2026-04-27 06:00 | 116 | 2026-04-21 11:00
140 | Natore | 132 | 138 | 2026-04-01 12:00 | 123 | 2026-04-17 12:00
141 | Nawabganj | 132 | 147 | 2026-04-26 18:00 | 123 | 2026-04-02 12:00
142 | Netrakona | 132 | 139 | 2026-04-29 08:00 | 111 | 2026-04-20 19:30
143 | New Tongi | 132 | 147 | 2026-04-27 06:00 | 120 | 2026-04-23 12:00
144 | Niamatpur | 132 | 141 | 2026-04-09 03:00 | 125 | 2026-04-20 23:00
145 | Noapara | 132 | 139 | 2026-04-07 00:00 | 117 | 2026-04-20 13:00
146 | Pabna | 132 | 139 | 2026-04-30 00:00 | 125 | 2026-04-05 14:00
147 | Palashbari | 132 | 141 | 2026-04-27 05:00 | 116 | 2026-04-03 08:00
148 | Panchagarh | 132 | 142 | 2026-04-26 14:00 | 120 | 2026-04-07 07:00
149 | Patiya | 132 | 139 | 2026-04-28 13:00 | 123 | 2026-04-16 19:30
150 | Patuakhali | 132 | 137 | 2026-04-07 18:00 | 125 | 2026-04-27 22:00
151 | Payra | 132 | 138 | 2026-04-06 10:00 | 130 | 2026-04-20 12:00
152 | PHP | 132 | 137 | 2026-04-27 08:00 | 123 | 2026-04-18 11:00
153 | Postogola | 132 | 143 | 2026-04-29 08:00 | 120 | 2026-04-18 10:00
154 | Pubail | 132 | 145 | 2026-04-29 08:00 | 123 | 2026-04-26 12:00
155 | Purbachal | 132 | 146 | 2026-04-27 05:00 | 118 | 2026-04-26 12:00
156 | Purbasadipur | 132 | 139 | 2026-04-29 06:00 | 116 | 2026-04-23 07:00
157 | Rahanpur | 132 | 142 | 2026-04-07 17:00 | 129 | 2026-04-21 06:00
158 | Rahanpur-400 | 132 | 143 | 2026-04-19 00:00 | 129 | 2026-04-21 06:00
159 | Rahim | 132 | 141 | 2026-04-27 06:00 | 121 | 2026-04-26 12:00
160 | Rajbari | 132 | 138 | 2026-04-07 08:00 | 118 | 2026-04-20 13:00
161 | Rajendrapur | 132 | 144 | 2026-04-07 20:00 | 119 | 2026-04-30 13:00
162 | Rajshahi | 132 | 135 | 2026-04-07 17:00 | 122 | 2026-04-20 13:00
163 | Rajshahi-230 | 132 | 137 | 2026-04-30 04:00 | 121 | 2026-04-04 20:00
164 | Ramganj | 132 | 135 | 2026-04-07 01:00 | 116 | 2026-04-26 16:00
165 | Rampur | 132 | 140 | 2026-04-03 18:30 | 126 | 2026-04-16 19:30
166 | Rampura | 132 | 139 | 2026-04-26 18:00 | 121 | 2026-04-18 14:00
167 | Rangamati | 132 | 141 | 2026-04-07 03:00 | 127 | 2026-04-26 11:00
168 | Rangpur | 132 | 141 | 2026-04-27 06:00 | 118 | 2026-04-07 07:00
169 | Ruppur | 132 | 140 | 2026-04-08 05:00 | 124 | 2026-04-07 00:00
170 | Saidpur | 132 | 140 | 2026-04-27 05:00 | 115 | 2026-04-07 07:00
171 | Santhia | 132 | 140 | 2026-04-30 00:00 | 128 | 2026-04-20 13:00
172 | Satkhira | 132 | 141 | 2026-04-30 | 114 | 2026-04-20 13:00
173 | Satmasjid | 132 | 141 | 2026-04-30 00:00 | 122 | 2026-04-20 13:00
174 | Savar | 132 | 141 | 2026-04-27 06:00 | 117 | 2026-04-26 14:00
175 | SevenRings | 132 | 146 | 2026-04-29 06:00 | 126 | 2026-04-26 12:00
176 | ShahCement | 132 | 141 | 2026-04-27 06:00 | 120 | 2026-04-26 12:00
177 | Shahjadpur | 132 | 141 | 2026-04-08 03:00 | 130 | 2026-04-03 08:00
178 | Shahjibazar | 132 | 144 | 2026-04-27 06:00 | 121 | 2026-04-18 21:00
179 | Shahmirpur | 132 | 141 | 2026-04-07 03:00 | 126 | 2026-04-16 19:30
180 | Shariatpur | 132 | 138 | 2026-04-07 01:00 | 123 | 2026-04-18 22:00
181 | Sherpur | 132 | 144 | 2026-04-29 07:00 | 106 | 2026-04-20 02:00
182 | Shikalbaha | 132 | 129 | 2026-04-03 18:30 | 129 | 2026-04-03 18:30
183 | Shikalbaha-230 | 132 | 141 | 2026-04-02 18:30 | 127 | 2026-04-16 19:30
184 | Shitalakhya | 132 | 145 | 2026-04-26 18:00 | 118 | 2026-04-18 10:00
185 | Sholosohor | 132 | 140 | 2026-04-05 20:00 | 128 | 2026-04-16 19:30
186 | Shyampur | 132 | 139 | 2026-04-29 08:00 | 118 | 2026-04-19 12:00
187 | Shyampur-230 | 132 | 140 | 2026-04-27 06:00 | 118 | 2026-04-26 12:00
188 | Siddhirganj | 132 | 142 | 2026-04-27 06:00 | 121 | 2026-04-26 12:00
189 | Sirajganj | 132 | 140 | 2026-04-27 05:00 | 123 | 2026-04-03 08:00
190 | Sonargaon | 132 | 140 | 2026-04-07 21:00 | 140 | 2026-04-07 21:00
191 | Sreemongol | 132 | 142 | 2026-04-27 06:00 | 123 | 2026-04-18 21:00
192 | Sreepur | 132 | 144 | 2026-04-27 05:00 | 123 | 2026-04-30 12:00
193 | Srinagar | 132 | 148 | 2026-04-26 18:00 | 123 | 2026-04-18 10:00
194 | SSM | 132 | 142 | 2026-04-02 18:00 | 128 | 2026-04-02 08:00
195 | Sunamganj | 132 | 137 | 2026-04-27 10:00 | 119 | 2026-04-16 21:00
196 | Sylhet | 132 | 139 | 2026-04-27 06:00 | 126 | 2026-04-16 19:30
197 | Sylhet-132 | 132 | 138 | 2026-04-27 07:00 | 126 | 2026-04-16 19:30
198 | Tangail | 132 | 147 | 2026-04-27 06:00 | 114 | 2026-04-01 15:00
199 | Taraganj | 132 | 140 | 2026-04-27 06:00 | 114 | 2026-04-07 07:00
200 | Tasnim | 132 | 140 | 2026-04-07 21:00 | 117 | 2026-04-22 19:00
201 | Thakurgaon | 132 | 141 | 2026-04-18 20:00 | 116 | 2026-04-07 07:00
202 | TK | 132 | 140 | 2026-04-03 18:30 | 128 | 2026-04-16 19:30
203 | Tongi | 132 | 145 | 2026-04-27 07:00 | 120 | 2026-04-23 12:00
204 | Ullahpara | 132 | 141 | 2026-04-27 05:00 | 125 | 2026-04-25 06:00
205 | Ullon | 132 | 144 | 2026-04-26 17:00 | 121 | 2026-04-18 13:00
206 | Uttara | 132 | 147 | 2026-04-27 06:00 | 117 | 2026-04-23 15:00
207 | UttaraNew | 132 | 147 | 2026-04-27 06:00 | 118 | 2026-04-23 12:00
208 | Zigatola | 132 | 147 | 2026-04-26 18:00 | 123 | 2026-04-18 10:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-36
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: April 2026
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Aminbazar 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 04-04-2026 | 12:00 | 417 | 223 | 90.939
Aminbazar 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 04-04-2026 | 12:00 | 417 | 223 | 90.939
Aminbazar 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 520 | 04-04-2026 | 12:00 | 417 | 223 | 90.939
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 325 | 01-04-2026 | 00:00 | 0 | 0 | 0
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 27-04-2026 | 10:00 | 319 | 93 | 63.9
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 27-04-2026 | 10:00 | 319 | 93 | 63.9
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 520 | 02-04-2026 | 15:00 | 157 | 43 | 31.3042
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 520 | 02-04-2026 | 15:00 | 149 | 36 | 29.4783
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 750 | 12-04-2026 | 16:00 | 453 | 19 | 60.4531
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 750 | 21-04-2026 | 07:00 | 360 | 68 | 48.8488
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 750 | 12-04-2026 | 16:00 | 453 | 19 | 60.4531
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 325 | 27-04-2026 | 19:00 | 139 | 58 | 46.3432
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 325 | 27-04-2026 | 19:00 | 139 | 58 | 46.3432
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 325 | 27-04-2026 | 19:00 | 139 | 58 | 46.3432
Gopalganj 400/230kV Grid Sub-Station | ATR-04 | 400/230 | 750 | 27-04-2026 | 06:00 | 136 | 79 | 20.9707
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 520 | 22-04-2026 | 09:00 | 285 | 192 | 66.0848
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 520 | 22-04-2026 | 12:00 | 288 | 234 | 71.3614
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 325 | 26-04-2026 | 06:00 | 294 | 74 | 93.2831
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 325 | 26-04-2026 | 06:00 | 294 | 74 | 93.2831
Madunaghat 400/230kV Grid Sub-Station | ATR-1 7006T | 400/230 | 750 | 10-04-2026 | 13:00 | 402 | 148 | 57.1171
Madunaghat 400/230kV Grid Sub-Station | ATR-2 7106T | 400/230 | 750 | 26-04-2026 | 11:00 | 334 | 149 | 48.7637
Madunaghat 400/230kV Grid Sub-Station | ATR-3 7206T | 400/230 | 750 | 19-04-2026 | 09:00 | 364 | 144 | 52.1931
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 750 | 26-04-2026 | 14:00 | 441 | 168 | 62.9222
Meghnaghat 400/230kV Grid Sub-Station | ATR-2 | 400/230 | 750 | 26-04-2026 | 14:00 | 441 | 167 | 62.8748
Meghnaghat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 750 | 26-04-2026 | 14:00 | 449 | 163 | 63.6895
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 520 | 27-04-2026 | 19:30 | 357 | 61 | 69.6488
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 520 | 27-04-2026 | 19:30 | 353 | 60 | 68.8582
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 325 | 27-04-2026 | 19:00 | 154 | 43 | 49.1971
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 325 | 01-04-2026 | 12:00 | 190 | 60 | 61.3073
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 520 | 14-04-2026 | 21:00 | 173 | 56 | 34.9688
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 520 | 14-04-2026 | 21:00 | 173 | 56 | 34.9688
Koerhat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 1000 | 18-04-2026 | 22:00 | 313 | 1 | 31.3002
Koerhat 400/132kV Grid Sub-Station | ATR-4 | 400/230 | 1000 | 18-04-2026 | 22:00 | 313 | 1 | 31.3002
Koerhat 400/132kV Grid Sub-Station | ATR-2 | 400/132 | 325 | 01-04-2026 | 17:00 | 0 | 0 | 0
Koerhat 400/132kV Grid Sub-Station | ATR-3 | 400/132 | 325 | 18-04-2026 | 22:00 | 147 | 55 | 48.293
Mirsharai 400/230 kV Grid Sub-Station | ATR-1 | 400/230 | 1000 | 14-04-2026 | 17:00 | 0 | 0 | 0
Mirsharai 400/230 kV Grid Sub-Station | ATR-2 | 400/230 | 1000 | 2026-12-04 | 13:00 | 199 | 93 | 21.9659
Ashuganj 400/230 kV GIS Grid Sub-Station | Interbus-1 | 400/230 | 325 |  |  |  |  | 0
Ashuganj 400/230 kV GIS Grid Sub-Station | Interbus-2 | 400/230 | 325 |  |  |  |  | 0
Amtali 400/132kV Grid Sub-Station
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 300 | 21-04-2026 | 14:00 | 206 | 92 | 75.2034
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 300 | 21-04-2026 | 14:00 | 206 | 92 | 75.2034
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 225 | 06-04-2026 | 12:00 | 192 | 60 | 83.2263
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 225 | 06-04-2026 | 12:00 | 192 | 60 | 83.2263
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 225 | 06-04-2026 | 12:00 | 192 | 60 | 83.2263
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 300 | 05-04-2026 | 20:00 | 200 | 140 | 81.377
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 300 | 30-04-2026 | 08:00 | 210 | 50 | 71.9568
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 300 | 24-04-2026 | 06:00 | 173 | 61 | 61.1465
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 225 | 24-04-2026 | 06:00 | 130 | 48 | 61.5904
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 225 | 03-04-2026 | 18:30 | 116 | 20 | 52.3162
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 225 | 07-04-2026 | 14:00 | 127 | 70 | 64.4506
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 300 | 08-04-2026 | 14:00 | 144 | 57 | 51.6236
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 01-04-2026 | 12:00 | 88 | 25 | 30.4941
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 25-04-2026 | 13:00 | 101 | 48 | 37.2753
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 225 | 22-04-2026 | 22:00 | 112 | 12 | 50.0627
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 225 | 22-04-2026 | 22:00 | 112 | 12 | 50.0627
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 225 | 21-04-2026 | 07:00 | 151 | 52 | 70.979
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 225 | 21-04-2026 | 07:00 | 151 | 52 | 70.979
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 300 | 20-04-2026 | 07:00 | 202 | 67 | 70.9405
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 300 | 21-04-2026 | 07:00 | 202 | 72 | 71.4827
Naogaon 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 01-04-2026 | 00:00 | 0 | 0 | 0
Naogaon 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 01-04-2026 | 00:00 | 0 | 0 | 0
Naogaon 230/132kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 01-04-2026 | 00:00 | 0 | 0 | 0
Purbasadipur 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 04-04-2026 | 08:00 | 124 | -9 | 41.4421
Purbasadipur 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 04-04-2026 | 08:00 | 124 | -9 | 41.4421
Purbasadipur 230/132kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 01-04-2026 | 00:00 | 0 | 0 | 0
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 225 | 14-04-2026 | 04:00 | 108 | 49 | 52.7093
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 225 | 14-04-2026 | 04:00 | 106 | 48 | 51.7162
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 225 | 14-04-2026 | 05:00 | 117 | 52 | 56.9045
Chowmohani 230/132 kV Grid Sub-Station | ATR-1 | 230/132 | 350 | 21-04-2026 | 10:00 | 95 | 30 | 28.4641
Chowmohani 230/132 kV Grid Sub-Station | ATR-2 | 230/132 | 350 | 23-04-2026 | 14:00 | 85 | 0 | 24.2857
Chowmohani 230/132 kV Grid Sub-Station | ATR-3 | 230/132 | 350 | 21-04-2026 | 10:00 | 95 | 30 | 28.4641
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 300 | 03-04-2026 | 20:00 | 176 | 59 | 61.8753
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 300 | 03-04-2026 | 21:00 | 197 | 72 | 69.915
Feni 230/132 kV GIS Grid Sub-Station | ATR-1 | 230/132 | 300 | 21-04-2026 | 10:00 | 56 | 29 | 21.0212
Feni 230/132 kV GIS Grid Sub-Station | ATR-2 | 230/132 | 300 | 26-04-2026 | 18:00 | 56 | 29 | 21.0212
Feni 230/132 kV GIS Grid Sub-Station | ATR-3 | 230/132 | 300 | 26-04-2026 | 18:00 | 56 | 29 | 21.0212
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 125 | 04-04-2026 | 09:00 | 86 | 0 | 68.8
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 125 | 04-04-2026 | 09:00 | 86 | 0 | 68.8
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 225 | 25-04-2026 | 12:00 | 110 | 73 | 58.6751
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 225 | 25-04-2026 | 12:00 | 120 | 71 | 61.9693
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 225 | 25-04-2026 | 12:00 | 114 | 77 | 61.1414
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 225 | 23-04-2026 | 10:00 | 118 | 61 | 59.0375
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 225 | 23-04-2026 | 10:00 | 118 | 61 | 59.0375
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 225 | 23-04-2026 | 10:00 | 118 | 61 | 59.0375
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 150 | 26-04-2026 | 10:00 | 87 | 37 | 63.0273
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 150 | 01-04-2026 | 00:00 | 0 | 0 | 0
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 150 | 26-04-2026 | 10:00 | 87 | 37 | 63.0273
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 150 | 26-04-2026 | 10:00 | 87 | 37 | 63.0273
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 225 | 22-04-2026 | 07:00 | 126 | 71 | 64.2787
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 225 | 22-04-2026 | 07:00 | 126 | 70 | 64.0617
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 225 | 01-04-2026 | 00:00 | 0 | 0 | 0
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 300 | 01-04-2026 | 19:30 | 225 | 73 | 78.8487
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 300 | 01-04-2026 | 19:30 | 225 | 73 | 78.8487
Kaliakoir 230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 300 | 18-04-2026 | 05:00 | 165 | 45 | 57.0088
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 20-04-2026 | 19:30 | 187 | 81 | 67.9297
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 20-04-2026 | 19:30 | 187 | 81 | 67.9297
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 22-04-2026 | 22:00 | 134 | 47 | 47.3345
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 225 | 27-04-2026 | 23:00 | 161 | 57 | 75.9077
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 225 | 27-04-2026 | 23:00 | 161 | 57 | 75.9077
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 300 | 27-04-2026 | 23:00 | 209 | 67 | 73.1589
Madunaghat 230/132/33kV Grid Sub-Station | ATR-1(705T) | 230/132 | 300 | 04-04-2026 | 13:00 | 123 | 25 | 41.8383
Madunaghat 230/132/33kV Grid Sub-Station | ATR-2(715T) | 230/132 | 300 | 04-04-2026 | 13:00 | 123 | 25 | 41.8383
Madunaghat 230/132/33kV Grid Sub-Station | ATR-3(725T) | 230/132 | 300 | 04-04-2026 | 13:00 | 123 | 25 | 41.8383
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 300 | 20-04-2026 | 13:00 | 181 | 80 | 65.9638
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 300 | 20-04-2026 | 13:00 | 181 | 80 | 65.9638
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 300 | 22-04-2026 | 07:00 | 110 | 26 | 37.677
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 300 | 22-04-2026 | 07:00 | 110 | 26 | 37.677
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 300 | 01-04-2026 | 00:00 | 1 | 0 | 0.33333
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 300 | 01-04-2026 | 00:00 | 0 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 230/132 | 450 | 22-04-2026 | 13:00 | 298 | 61 | 67.5954
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 230/132 | 450 | 22-04-2026 | 13:00 | 298 | 61 | 67.5954
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 230/132 | 450 | 22-04-2026 | 13:00 | 298 | 61 | 67.5954
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 26-04-2026 | 09:00 | 226 | 138 | 88.2673
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 26-04-2026 | 09:00 | 226 | 138 | 88.2673
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 300 | 10-04-2026 | 15:00 | 130 | 64 | 48.3
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 300 | 10-04-2026 | 15:00 | 130 | 64 | 48.3
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 300 | 25-04-2026 | 12:00 | 128 | 15 | 42.9586
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 300 | 25-04-2026 | 12:00 | 128 | 15 | 42.9586
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 300 | 20-04-2026 | 19:30 | 259 | 129 | 96.4492
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 300 | 20-04-2026 | 19:30 | 259 | 129 | 96.4492
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 02-04-2026 | 18:30 | 215 | 30 | 96.4813
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 02-04-2026 | 18:30 | 192 | 38 | 86.9886
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 02-04-2026 | 18:30 | 192 | 38 | 86.9886
Tongi 230/132/33kV Grid Sub-Station | T-04 | 230/132 | 450 | 22-04-2026 | 19:30 | 310 | 85 | 71.4316
Bhulta 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 25-04-2026 | 6:00 | 140 | 40 | 48.5341
Bhulta 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 27-04-2026 | 6:00 | 140 | 40 | 48.5341
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF_LDC_37
|  |  |  | POWER GRID BANGLADESH PLC. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID BANGLADESH PLC. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [12 empty] | Report on load shedding
Month: April-2026 |  |  |  | (For Evening Peak) | [10 empty] | Month: April-2026 |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur
2026-04-01 | 14218.9 | 14218.9 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-04-01 | 13353.99 | 13353.99 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-04-02 | 14865.76 | 15400.76 | 512 | 19:30 Hr. | 24 | 92 | 15 | 43 | 0 | 176 | 0 | 82 | 80 | - | 2026-04-02 | 13961.81 | 13961.81 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-04-03 | 14370.95 | 14938.95 | 544 | 21:00 Hr. | 40 | 35 | 94 | 75 | 0 | 185 | 0 | 85 | 30 | - | 2026-04-03 | 13369.18 | 13433.97 | 62 | 12:00 Hr. | 0 | 22 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | -
2026-04-04 | 14939.9 | 15699.9 | 727 | 20:00 Hr. | 40 | 17 | 70 | 160 | 60 | 160 | 30 | 90 | 100 | - | 2026-04-04 | 13335.2 | 13922.2 | 562 | 12:00 Hr. | 55 | 102 | 96 | 50 | 0 | 180 | 0 | 50 | 29 | -
2026-04-05 | 13829.22 | 14599.22 | 737 | 21:00 Hr. | 137 | 50 | 90 | 170 | 60 | 80 | 40 | 70 | 40 | - | 2026-04-05 | 13665.91 | 14083.91 | 400 | 09:00 Hr. | 100 | 87 | 113 | 100 | 0 | 0 | 0 | 0 | 0 | -
2026-04-06 | 13847.95 | 14888.95 | 996 | 21:00 Hr. | 220 | 50 | 120 | 165 | 55 | 170 | 60 | 70 | 86 | - | 2026-04-06 | 13152.29 | 13903.29 | 719 | 12:00 Hr. | 220 | 40 | 65 | 95 | 45 | 94 | 50 | 65 | 45 | -
2026-04-07 | 13305.4 | 13620.4 | 301 | 19:00 Hr. | 11 | 35 | 100 | 85 | 70 | 0 | 0 | 0 | 0 | - | 2026-04-07 | 12761.9 | 13103.9 | 327 | 12:00 Hr. | 107 | 30 | 0 | 65 | 0 | 0 | 0 | 80 | 45 | -
2026-04-08 | 13355.5 | 14098.5 | 711 | 20:00 Hr. | 194 | 120 | 80 | 120 | 72 | 35 | 18 | 34 | 38 | - | 2026-04-08 | 12430.4 | 12663.44 | 223 | 12:00 Hr. | 43 | 0 | 0 | 100 | 0 | 0 | 0 | 80 | 0 | -
2026-04-09 | 13003 | 13149 | 140 | 19:00 Hr. | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | - | 2026-04-09 | 12016.13 | 12204.13 | 180 | 12:00 Hr. | 10 | 30 | 20 | 70 | 0 | 25 | 0 | 25 | 0 | -
2026-04-10 | 12714.59 | 12751.17 | 35 | 19:30 Hr. | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | - | 2026-04-10 | 11212.51 | 11212.51 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0
2026-04-11 | 13926.3 | 14350.57 | 406 | 21:00 Hr. | 0 | 0 | 80 | 50 | 51 | 100 | 35 | 60 | 30 | - | 2026-04-11 | 12419.55 | 12652.55 | 223 | 12:00 Hr. | 58 | 30 | 65 | 45 | 0 | 0 | 0 | 0 | 25 | -
2026-04-12 | 14147.66 | 15098.66 | 910 | 21:00 Hr. | 155 | 90 | 114 | 168 | 50 | 130 | 0 | 131 | 72 | - | 2026-04-12 | 13644.57 | 14073.57 | 411 | 12:00 Hr. | 174 | 60 | 45 | 112 | 20 | 0 | 0 | 0 | 0 | -
2026-04-13 | 14196.33 | 15300.05 | 1008 | 21:00 Hr. | 190 | 80 | 110 | 130 | 55 | 155 | 72 | 110 | 106 | - | 2026-04-13 | 13536.02 | 14455.02 | 879 | 12:00 Hr. | 320 | 85 | 130 | 160 | 42 | 0 | 0 | 72 | 70 | -
2026-04-14 | 14539 | 14560 | 688 | 20:00 Hr. | 112 | 75 | 85 | 40 | 48 | 124 | 55 | 86 | 63 | - | 2026-04-14 | 13047.89 | 13653.89 | 580 | 12:00 Hr. | 155 | 35 | 55 | 15 | 40 | 160 | 15 | 30 | 75 | -
2026-04-15 | 13849.14 | 15398.14 | 1482 | 21:00 Hr. | 360 | 120 | 210 | 80 | 25 | 319 | 95 | 195 | 78 | - | 2026-04-15 | 13049.46 | 14401.46 | 1294 | 12:00 Hr. | 367 | 160 | 167 | 130 | 75 | 215 | 63 | 83 | 34 | -
2026-04-16 | 14847.2 | 15370 | 481 | 21:00 Hr. | 10 | 35 | 103 | 98 | 0 | 0 | 0 | 145 | 90 | - | 2026-04-16 | 12421.65 | 14251.65 | 1751 | 12:00 Hr. | 535 | 150 | 200 | 135 | 101 | 250 | 90 | 175 | 115 | -
2026-04-17 | 14317.04 | 15299.04 | 940 | 20:00 Hr. | 0 | 100 | 120 | 150 | 50 | 210 | 45 | 145 | 120 | - | 2026-04-17 | 13298.34 | 14162.56 | 827 | 12:00 Hr. | 261 | 128 | 96 | 138 | 63 | 0 | 0 | 51 | 90 | -
2026-04-18 | 14767.85 | 15722.12 | 643 | 20:00 Hr. | 0 | 95 | 110 | 100 | 30 | 145 | 0 | 110 | 53 | - | 2026-04-18 | 13732.59 | 14452.98 | 733 | 12:00 Hr. | 235 | 38 | 125 | 110 | 45 | 5 | 0 | 130 | 45 | -
2026-04-19 | 15049.5 | 16248.5 | 1147 | 21:00 Hr. | 276 | 92 | 123 | 156 | 85 | 167 | 48 | 124 | 76 | - | 2026-04-19 | 13777.26 | 14453.26 | 647 | 12:00 Hr. | 400 | 80 | 100 | 67 | 0 | 0 | 0 | 0 | 0 | -
2026-04-20 | 15199 | 16448.82 | 1196 | 21:00 Hr. | 113 | 50 | 206 | 213 | 76 | 257 | 77 | 86 | 118 | - | 2026-04-20 | 13919.08 | 14953.08 | 989 | 12:00 Hr. | 440 | 140 | 175 | 214 | 20 | 0 | 0 | 0 | 0 | -
2026-04-21 | 14623.58 | 16546.58 | 1840 | 21:00 Hr. | 390 | 161 | 210 | 293 | 105 | 220 | 83 | 223 | 155 | - | 2026-04-21 | 14073.9 | 15601.9 | 1462 | 12:00 Hr. | 511 | 124 | 210 | 255 | 57 | 0 | 0 | 180 | 125 | -
2026-04-22 | 14467.04 | 16647.04 | 2086 | 20:00 Hr. | 450 | 250 | 220 | 180 | 100 | 380 | 60 | 280 | 166 | - | 2026-04-22 | 13116.11 | 15648.75 | 2493 | 12:00 Hr. | 628 | 252 | 278 | 268 | 45 | 364 | 85 | 358 | 215 | -
2026-04-23 | 14726.43 | 16895.43 | 2076 | 21:00 Hr. | 220 | 210 | 270 | 265 | 101 | 405 | 47 | 333 | 225 | - | 2026-04-23 | 14194.78 | 15903.36 | 1635 | 12:00 Hr. | 341 | 184 | 165 | 146 | 105 | 270 | 35 | 260 | 129 | -
2026-04-24 | 14196.5 | 16096.5 | 1818 | 20:00 Hr. | 348 | 180 | 240 | 260 | 80 | 320 | 50 | 180 | 160 | - | 2026-04-24 | 12952.68 | 14699.68 | 1672 | 12:00 Hr. | 280 | 85 | 190 | 260 | 110 | 330 | 75 | 200 | 142 | -
2026-04-25 | 14712 | 16765 | 1965 | 21:00 Hr. | 390 | 220 | 250 | 260 | 0 | 335 | 110 | 240 | 160 | - | 2026-04-25 | 12774.33 | 15000.45 | 2217 | 12:00 Hr. | 685 | 270 | 271 | 246 | 117 | 218 | 0 | 320 | 90 | -
2026-04-26 | 11478.91 | 11478.91 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-04-26 | 13749.33 | 14283.33 | 511 | 12:00 Hr. | 194 | 82 | 180 | 55 | 0 | 0 | 0 | 0 | 0 | -
2026-04-27 | 13195.81 | 13230.64 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-04-27 | 10958.7 | 10958.7 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-04-28 | 11838.3 | 11838.3 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-04-28 | 10979.26 | 10979.26 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-04-29 | 11384 | 11384 | 0 | 19:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-04-29 | 9654.35 | 9654.35 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-04-30 | 13055.55 | 13055.55 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-04-30 | 11689.02 | 11689.02 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
[16 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: April 2026
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 15199 | 2026-04-20 | 21:00 Hr.
2 | Maximum Day Peak Genaration | MW | 14194.78 | 2026-04-23 | 12:00 Hr.
3 | Maximum Evening Peak Demand | MW | 16895.43 | 2026-04-23 | 21:00 Hr.
4 | Minimum Generation | MW | 7093.7 | 2026-04-29 | 08:00 Hr.
5 | Average of the daily evening peak Genaration | MW | 13883.6437 | - | -
6 | Average of the daily day peak Genaration | MW | 12874.9397 | - | -
7 | Maximum load shed (Evening Peak) | MW | 2086 | 2026-04-22 | 20:00 Hr.
8 | Minimum load shed | MW | 35 | 2026-04-10 | 19:30 Hr.
9 | Total nos. of load shed days | Day | 24 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 779.6333 | - | -
11 | Total Generation | MkWh | 9094.6421 | - | -
12 | Total Generation by BPDB | MkWh | 961.1528 | % of total Gen. | 10.57%
13 | Total Generation by IPP | MkWh | 2382.4425 | '' | 26.2%
14 | A) Total Generation by Generation Companies | MkWh | 4165.6817 | '' | 45.8%
| B) Total Generation by REB | MkWh | 47.8268 | " | 0.5259%
| C) Total Generation by RENTAL | MkWh | 70.7437 | " | 0.7779%
| D) Total Imported from India (BIPTC) | MkWh | 630.6553 | " | 6.934%
| E) Total Imported from Tripura, India (A.C) | MkWh | 109.177 | " | 1.2%
| F) Total Imported from Nepal | MkWh | 0 | " | 0%
| E) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 726.9624 | " | 7.993%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3680.8197 | % of total Gen. | 40.47%
| B) Oil | MkWh | 954.2453 | '' | 10.49%
| C) Hydro | MkWh | 44.552 | '' | 0.4899%
| D) Solar | MkWh | 124.9061 | '' | 1.373%
| E) Coal | MkWh | 2817.0837 | '' | 30.98%
| F) BIPTC (Import from India) | MkWh | 630.6553 | '' | 6.934%
| G) A.C (Import from Tripura, India) | MkWh | 109.177 | '' | 1.2%
| H) Total Imported from Nepal | MkWh | 0 | '' | 0%
| I) Adani (Import from India) | MkWh | 726.9624 | '' | 7.993%
| J) Wind | MkWh | 6.2407 | '' | 0.06862%
16 | Maximun of the daily total Generation . | MkWh | 333.5565 | 2026-04-20
17 | Monthly Load factor | % | 83.1071 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 59247.289 | - | -
| A) Gas | M.Taka | 12799.3071 | - | -
| B) Coal | M.Taka | 19136.3489 | - | -
| C) HFO | M.Taka | 16782.9807 | - | -
| D) HSD | M.Taka | 136.0005 | - | -
| E) Hydro | M.Taka | 4.4552 | - | -
| F) Solar | M.Taka | 1994.1573 | - | -
| G) Total Import | M.Taka | 8302.2392 | - | -
| H) Wind | M.Taka | 91.8 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2349.9389 | 2026-04-05
| A) Gas | M.Taka | 464.4567 | 2026-04-23
| B) Coal | M.Taka | 760.6941 | 2026-04-26
| C) HFO | M.Taka | 963.283 | 2026-04-05
| D) HSD | M.Taka | 38.2689 | 2026-04-23 | -
| E) Hydro | M.Taka | 0.19276 | 2026-04-07 | -
| F) Solar | M.Taka | 90.3729 | 2026-04-11 | -
| G) Total Import | M.Taka | 362.2664 | 2026-04-15
| H) Wind | M.Taka | 11.6644 | 2026-04-28
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 6.5145
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 6.6429
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 82.2 | 30/4/2026 | 06:00
b) | Actual | FT (MSL) | 77.07 | 30/04/2026 | 06:00
22 | Peak Genaration of April 2025 | MW | 16365.8 | 2025-04-24 | 19:30 Hr.
23 | Peak Demand of April 2025 | MW | 16510.8 | 2025-04-24 | 19:30 Hr.
24 | Maximum peak Generation recorded upto 30/04/2026 | MW | 16794 | 2025-07-23 | 21:00
25 | Maximum peak Demand recorded upto 30/04/2026 | MW | 16794 | 2025-07-23 | 21:00
26 | Maximum load shed recorded upto 31/03/2026 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## FGMO Weekly
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status | [62 empty] | SR at 50 Hz (MW)
SL | Plant Name | Owner | Fuel | Installed capacity (MW) | Capability Status of Last Week | 30.04.2026 | 23.04.2026 | 16.04.2026 | 09.04.2026 | 02.04.2026 | 26.03.2026 | 19.03.2026 | 12.03.2026 | 05.03.2026 | 26.02.2026 | 19.02.2026 | 12.02.2026 | 05.02.2026 | 29.01.2026 | 22.01.2026 | 15.01.2026 | 08.01.2026 | 01.01.2026 | 25.12.2025 | 18.12.2025 | 11.12.2025 | 04.12.2025 | 27.11.2025 | 20.11.2025 | 13.11.2025 | 06.11.2025 | 30.10.2025 | 23.10.2025 | 16.10.2025 | 09.10.2025 | 02.10.2025 | 25.09.2025 | 18.09.2025 | 11.09.2025 | 04.09.2025 | 28.08.2025 | 21.08.2025 | 14.08.2025 | 07.08.2025 | 31.07.2025 | 24.07.2025 | 17.07.2025 | 10.07.2025 | 03.07.2025 | 26.06.2025 | 19.06.2025 | 12.06.2025 | 05.06.2025 | 29.05.2025 | 22.05.2025 | 15.05.2025 | 08.05.2025 | 01.05.2025 | 24.04.2025 | 17.04.2025 | 10.04.2025 | 03.04.2025 | 27.03.2025 | 20.03.2025 | 13.03.2025 | 06.03.2025 | 27.02.2025 | 20.02.2025 | 13.02.2025 | 06.02.2025 | 30.01.2025 | 23.01.2025 | 16.01.2025 | 09.01.2025 | 02.01.2025 | 28.11.2024 | 21.11.2024 | 14.11.2024 | 07.11.2024 | 31.10.2024 | 24.10.2024 | 17.10.2024 | 10.10.2024 | 03.10.2024 | 26.09.2024 | 19.09.2024 | 05.09.2024 | 12.09.2024 | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 | Capable | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 | Capable | 30 |  | 30 | 30 | 30 | 30 | 30 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220 | Capable | [37 empty] | 20 | 20 | [7 empty] | 20 | [41 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220 | Capable | [18 empty] | 20 | 20 | [18 empty] | 20 | [5 empty] | 20 | 20 | 20 | 20 | [40 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305 | Capable | [28 empty] | 7 | 7 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 10 | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 15 | 30 | [7 empty] | 35 | [6 empty] | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360 | Capable | [8 empty] | 30 | 30 | 30 | 30 | 30 | [56 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 | Capable |  |  |  |  | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | [11 empty] | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410 | Capable | [38 empty] | 45 | [47 empty] | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
9 | Haripur 412 MW CCPP | EGCB | Gas | 412 | Capable |  | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97 | Capable | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [24 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163 | Capable
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210 | Capable
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225 | Capable
14 | Shikalbaha Peaking GT | BPDB | Gas | 150 | Capable
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330 | Capable | [62 empty] | 40 | [20 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360 | Capable |  |  |  |  | 20 | 20 | 20 | [52 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104 | Capable |  | 2 | 2 | 2 | [32 empty] | 2 |  |  | 2 | 2 | [18 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
18 | Bhola 225 MW CCPP | BPDB | Gas | 194 | Capable | [41 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365 | Capable
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210 | Capable | [10 empty] | 16 | 16 |  |  | 20 | 20 | 20 | 20 |  |  | 20 | 20 | 20 |  |  |  | 20 | [10 empty] | 20 | 16 | [7 empty] | 20 | 20 | [38 empty] | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335 | Capable | [47 empty] | 30 | 30 | 30 | 30 |  | 30 | 30
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400 | Capable |  |  | 30 | 30 | 30 | 30 | 30 | 35 | 35 | 35 | 35 | [11 empty] | 30 | 30 | 30 | 30 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | [14 empty] | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231 | Capable
24 | RPCL 210 MW CCPP | IPP | Gas | 210 | Capable but not tested recently
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100 | Not Capable but feasible
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50 | Not Capable but feasible
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410 | Not Capable but feasible
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400 | Capable | [67 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274 | Not Capable but feasible
16 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 | Capable |  |  |  |  | 20 | 20 | 20 | 30 | 30 | 30 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 60 | 60 | 60 | 60 | 60 |  |  |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | [7 empty] | 20 | 20
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 | Capable | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 16 | 16 | 30 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 16 | 16 | 16 | 16 | 10 | 10 | 10 | 10 | 10
32 | Bhola Nutan Bidyut | IPP | Gas | 220 | Capable
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360 | Not Capable but feasible
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450 | Not Capable but feasible
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150 | Capable | [36 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30
36 | Anwara 300 MW PP (United) | IPP | HFO | 300 | Capable
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 | Capable
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104 | Capable
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105 | Capable
40 | Gazipur 100 MW PP | IPP | HFO | 105 | Capable
41 | United Payra Power Ltd. | IPP | HFO | 150 | Capable
42 | Madhumati 100 MW PP | IPP | HFO | 100 | Capable
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105 | Capable
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 | Capable
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300 | Capable
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55 | Capable
47 | Kodda 149 MW PP Unit-1 (Summit) | IPP | HFO | 149 | Capable
48 | Feni Lanka Power | IPP | HFO | 114 | Capable
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110 | Capable
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162 | Capable
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55 | Capable
52 | Zodiac 54 MW | IPP | HFO | 54 | Capable
53 | Anlima Energy Ltd | IPP | HFO | 116 | Capable
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115 | Capable
55 | Confidence Unit-2 Bogura | IPP | HFO | 113 | Capable
56 | Confidence Unit-1 Bogura | IPP | HFO | 113 | Capable
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54 | Capable
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55 | Capable
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149 | Capable
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115 | Capable
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55 | Capable
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 | Capable | 33 | 33 |  | 40 | 20 | 20 | 40 | 66 | 66 | 66 | 66 |  | 66 | 33 | 66 | 66 | 66 | 66 | 66 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 66 | 66
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 | Capable | 20 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 66 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  | 50 | 50 | 50 | 50 | 20 | 20 | 40 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 | Capable | 30 | 30 | 25 | 25 | 25 | 25 | 50 | 50 | 50 | 50 | 25 | 40 | 25 | 25 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 50 | 50 | 50 | 50
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307 | Capable |  |  | 20 | 20 | 20 | 20 | 20 | 30 | 30 | 30 | 30 | 25 | 30 | 30 | 30 | 30 | [11 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
66 | Unique Meghnaghat Power Ltd(UMPL) | IPP | Gas | 584 | Capable | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 50 | 50 |  | 30 | [12 empty] | 24 | 24 | 24 |  |  |  |  | 50 | 24 | 24 | 50
67 | Meghnaghat CCPP Unit 2 (Summit) | IPP | Gas | 583 | Capable | [5 empty] | 25 | 25 | 50 | 50 | 50 | 50 |  |  |  | 50 | 50 | 50 | 50 | 50 | 50
68 | Jera Meghnaghat Power Ltd. | IPP | Gas | 718 | Capable | [11 empty] | 50 | 70
| Payra 1320 MW Unit-2 | BCPCL |  | 622 | Capable | [51 empty] | 20 | 20
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70 | Capable
| Shajibazar 100 MW PP | BPDB |  | 100 | Not Capable but feasible
| Khulna 225 MW CCPP | NWPGCL |  | 230 | Capable but not tested recently
Total Installed capacity | [5 empty] | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 20506 | 20506 | 20506 | 20506 | 20506 | 20506 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19739 | 19739 | 19739 | 19739 | 14388 | 14388 | 14388 | 14388 | 14388 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity | [5 empty] | 4051 | 4051 | 4246 | 4752 | 5680 | 6978 | 8164 | 7834 | 8174 | 8174 | 7698 | 7298 | 6286 | 4146 | 5722 | 6660 | 6754 | 7086 | 6756 | 5564 | 5851 | 5937 | 5232 | 5185 | 3503 | 3503 | 6403 | 6525 | 5821 | 6221 | 6871 | 7523 | 8031 | 7313 | 7523 | 6939 | 8121 | 8527 | 9061 | 8099 | 8099 | 7580 | 8537 | 6163 | 6795 | 6632 | 2862 | 3135 | 2325 | 2165 | 2165 | 2525 | 2855 | 2325 | 1595 | 1635 | 1072 | 1812 | 1432 | 1464 | 1064 | 592 | 1332 | 1282 | 1682 | 1302 | 1302 | 1685 | 1685 | 1315 | 1813 | 2027 | 1475 | 1475 | 1092 | 1124 | 744 | 712 | 712 | 1802 | 1492 | 1152 | 1492 | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve | [5 empty] | 186 | 186 | 198 | 238 | 304 | 349 | 394 | 489 | 519 | 519 | 490 | 455 | 419 | 256 | 359 | 399 | 429 | 443 | 398 | 365 | 358 | 358 | 328 | 324 | 228 | 228 | 351 | 372 | 349 | 379 | 427 | 477 | 471 | 451 | 477 | 427 | 459 | 452 | 503 | 386 | 404 | 382 | 452 | 356 | 424 | 408 | 262 | 288 | 218 | 193 | 193 | 202 | 232 | 212 | 152 | 137 | 92 | 172 | 142 | 144 | 109 | 67 | 137 | 132 | 167 | 137 | 137 | 162 | 162 | 122 | 160 | 179 | 132 | 132 | 107 | 109 | 79 | 77 | 77 | 172 | 137 | 107 | 137 | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO | [5 empty] | 8 | 8 | 9 | 10 | 14 | 15 | 15 | 14 |  |  | 15 | 14 | 12 | 10 | 11 | 12 | 12 | 11 | 10 | 10 | 9 | 9 | 9 | 9 | 7 | 7 | 9 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 12 | 14 | 13 | 15 | 12 | 12 | 12 | 13 | 11 | 14 | 13 | 11 | 12 | 9 | 9 | 9 | 10 | 11 | 9 | 7 | 7 | 5 | 7 | 6 | 7 | 6 | 3 | 5 | 5 | 6 | 5 | 5 | 6 | 6 | 5 | 6 | 8 | 5 | 5 | 4 | 5 | 4 | 3 | 3 | 6 | 5 | 4 | 5 | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list | [5 empty] | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 68 | 68 | 68 | 68 | 64 | 64 | 64 | 64 | 64 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list | [5 empty] | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 74 | 74 | 74 | 74 | 70 | 70 | 70 | 70 | 70 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable | [5 empty] | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 63 | 63 | 61 | 61 | 61 | 61 | 62 | 62 | 62 | 62 | 58 | 58 | 58 | 58 | 58 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible | [5 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant

## FGMO
Power Grid Bangladesh PLC.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: April 2026
SL | Plant Name | Owner | Fuel | Installed capacity | FGMO Status
|  |  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360 | [7 empty] | √
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410
9 | Haripur 412 MW CCPP | EGCB | Gas | 412
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225
14 | Shikalbaha Peaking GT | BPDB | Gas | 150
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360 | [7 empty] | √
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104
18 | Bhola 225 MW CCPP | BPDB | Gas | 194
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210 | [16 empty] | √ | √ | √
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  | √ | √ | √
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231
24 | RPCL 210 MW CCPP | IPP | Gas | 210
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274
30 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
32 | Bhola Nutan Bidyut | IPP | Gas | 220
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150
36 | Anwara 300 MW PP (United) | IPP | HFO | 300
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 | [5 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105
40 | Gazipur 100 MW PP | IPP | HFO | 105
41 | United Payra Power Ltd. | IPP | HFO | 150
42 | Madhumati 100 MW PP | IPP | HFO | 100
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105 | [8 empty] | √ | √ | √ | √ | √
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 | [5 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [5 empty] | √
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55
47 | Kodda 150 MW PP BRPL | IPP | HFO | 149
48 | Feni Lanka Power | IPP | HFO | 114
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110 | [12 empty] | √ | √ | √ | √ | √ | √ | √
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55
52 | Jodiac Power | IPP | HFO | 54
53 | Anlima Energy Ltd | IPP | HFO | 116 | [12 empty] | √ |  |  | √ |  |  |  | √ | [6 empty] | √ |  | √ | √
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115
55 | Confidence Unit-2 Bogura | IPP | HFO | 113
56 | Confidence Unit-1 Bogura | IPP | HFO | 113
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54 | √
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 | √ | √ | √ | √ | √ | √ | [23 empty] | √
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 |  |  | √ | [12 empty] | √
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 | √ | √ | √ | √ | √ | √ | √ | [15 empty] | √ |  |  |  |  | √ | √ | √
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307 | √ |  | √
66 | Unique Meghnaghat Power Limited (UMPL) | IPP | Gas | 584 | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ |  |  | √ | √ | [5 empty] | √ | √ | [5 empty] | √
67 | Meghnaghat CCPP(Summit)-2 | IPP | Gas/HSD | 583
| JERA Meghnaghat Power Limited | IPP | Gas | 718 | [27 empty] | √
| United Payra Power Ltd. | IPP |  | 150
| Mirsharai 150 MW | IPP | HFO/Gas | 150 | [5 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
Jangalia 52 MW PP (Lakdanavi)
| Ashuganj 420 MW CCPP(East) | APSCL |  | 400 | √
| Ashuganj 55 MW PP (Precision) | QRPP |  | 55
| Bagura 113 MW PP (Confidence)-2 | IPP |  | 113
| Energypac Power Venture Thakurgaon Ltd. | IPP |  | 115
| Chandpur 150 MW CCPP | BPDB |  | 163
| Khulna 225 MW CCPP | NWPGCL |  | 230
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70
| Shajibazar 100 MW PP | BPDB |  | 100
| Payra 1320 MW Unit-1 | BCPCL |  | 622