## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 20-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-05-2026 | during | 20-05-2026 | during | 20-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 376 | 353 | 412 | 412 | 392 | 392 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 302 | 297 | 335 | 335 | 315 | 315 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 8 | 8 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 112 | 149.36 | 149.36 | 90 | 128 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17 | 18 | 33 | 33 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 20 | 22 | 22 | 14 | 14 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 48 | 52.19 | 52.19 | 25 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 293 | 260 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 132 | 132 | 149 | 149 | 133 | 133 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 80 | 105 | 105 | 105 | 50 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 90 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 32 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 450 | 380 | 584 | 584 | 490 | 490 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 284 | 223 | 718 | 718 | 310 | 310 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 142 | 142 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2307 | 2357 | 6049.22 | 6017.22 | 2443 | 2692
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 0 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 36 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 65 | 30 | 30 | 30 | 30 | 30 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 213 | 216 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 85 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 24 | 58 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 17 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 24 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 8 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 19 | 51 | 108 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0 | 0 | 4.12 | 0 | 4.12 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 49 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 64 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 25 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 60 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 34 | 116 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1162 | 1162 | 1224 | 1224 | 1204 | 1204 | Can't Start AGC
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 13 | 0 | 5 | 1 | 5 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 910 | 1000 | 930 | 1000 | 930 | 1000 | AGC
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2482 | 3059 | 3711.98 | 3845.86 | 3013.48 | 3155.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 355 | 357 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 342 | 345 | 342.01 | 342.01 | 342.01 | 342.01 | FGMO not available
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 265 | 375 | 393 | 393 | 350 | 350 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 35 | 36 | 41.65 | 41.65 | 36 | 36 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 47 | 46 | 52.82 | 52.82 | 48 | 48 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 33 | 150 | 150 | 150 | 33 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 22 | 22 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 96 | 163 | 163 | 140 | 140 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 26 | 184 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 172 | 162 | 84 | 76 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 33 | 43 | 0 | 0 | 43 | 43 | plant availability zero
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 37 | 88 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 17 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 70 | 115 | 115 | 17 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 59 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1599 | 2061 | 2490.99 | 2412.99 | 1984.02 | 2091.02
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-05-2026 | during | 20-05-2026 | during | 20-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.2 | 0 | 2.25 | 0 | 2.25 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 67 | 87 | 90 | 90 | 90 | 90 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 28 | 9 | 10 | 10 | 10 | 10 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 47.58 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 144.78 | 125 | 381.25 | 334 | 201.75 | 129
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 133 | 163 | 163 | 147 | 147 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 153 | 152 | 155 | 155 | 155 | 155 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 27 | 20 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 52 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 102 | 101 | 102 | 102 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 320 | 296 | 250 | 250 | 250 | 250 | STG Under Maintenance
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1220 | 1158 | 1244 | 1244 | 1164 | 1164
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 898 | 904 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 36 | 32 | 32 | 32 | 32 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 54 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 152 | 136 | 410 | 410 | 165 | 165 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 85 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 62 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 815 | 1192 | 1234.2 | 1234.2 | 1194 | 1194
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1927 | 2407 | 3586.2 | 3496.2 | 2618.1 | 2528.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 693 | 926 | 800 | 1220 | 700 | 800 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 98 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 865 | 1060 | 1244 | 1244 | 1184 | 1184 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 90 | 150 | 150 | 17 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 223 | 277 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.39 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2121.39 | 2791 | 2962 | 3381 | 2649 | 2785
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 40.09 | 0 | 52 | 0 | 52 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 6 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 140 | 140 | 214 | 214 | 161 | 161 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 140 | 220 | 220 | 160 | 160 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 376 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | AGC
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 0 | 0 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 34 | 52.2 | 52.2 | 0.03 | 0.03 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 82 | 92 | 92 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.89 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1462 | 1270 | 1435.88 | 1435.88 | 1356 | 1356 | Can't Start AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 53.71 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 79 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2295.69 | 2378 | 3196.57 | 2977.87 | 2591.14 | 2457.44
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 80 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 48 | 52 | 52 | 50 | 50 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 97 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.6 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 35 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 197 | 0 | 199.29 | 0 | 199.29 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 284.6 | 340 | 535.29 | 300 | 433.29 | 278
System Total |  |  |  |  | 28823.2 | 29270.237 | 14381.46 | 16676 | 24157.5 | 24009.14 | 17097.78 | 17279.92
Forecast Scenario (20-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15500 |  | 0 |  | 15500
|  |  |  | 1:00 | 15110 |  | 0 |  | 15110
|  |  |  | 2:00 | 14450 |  | 0 |  | 14450
|  |  |  | 3:00 | 13960 |  | 0 |  | 13960
|  |  |  | 4:00 | 13550 |  | 0 |  | 13550
|  |  |  | 5:00 | 13280 |  | 0 |  | 13280
|  |  |  | 6:00 | 13030 |  | 0 |  | 13030
|  |  |  | 7:00 | 13230 |  | 0 |  | 13230
|  |  |  | 8:00 | 13320 |  | 0 |  | 13320
|  |  |  | 9:00 | 13720 |  | 0 |  | 13720
|  |  |  | 10:00 | 13970 |  | 0 |  | 13970
|  |  |  | 11:00 | 14260 |  | 0 |  | 14260
|  |  |  | 12:00 | 14600 |  | 0 |  | 14600
|  |  |  | 13:00 | 14890 |  | 0 |  | 14890
|  |  |  | 14:00 | 15200 |  | 0 |  | 15200
|  |  |  | 15:00 | 15410 |  | 0 |  | 15410
|  |  |  | 16:00 | 15550 |  | 0 |  | 15550
|  |  |  | 17:00 | 15340 |  | 0 |  | 15340
|  |  |  | 18:00 | 15040 |  | 0 |  | 15040
|  |  |  | 18:30 | 15900 |  | 0 |  | 15900
|  |  |  | 19:00 | 16710 |  | 0 |  | 16710
|  |  |  | 19:30 | 17070 |  | 0 |  | 17070
|  |  |  | 20:00 | 17200 |  | 0 |  | 17200
|  |  |  | 21:00 | 17180 |  | 0 |  | 17180
|  |  |  | 22:00 | 16300 |  | 0 |  | 16120
|  |  |  | 23:00 | 15880 |  | 0 |  | 15880
Probable Maximum Temperature: |  |  | 36.40°C
Probable Maximum Demand at Day Peak: |  |  | 14600.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 17200.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 17200.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 354.89 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:48 hrs on 20-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 19-05-2026 | [28 empty] | Date: | 19-05-2026 | [28 empty] | Date: | 19-05-2026 | [28 empty] | Date: | 19-05-2026 | [28 empty] | Date: | 19-05-2026 | [17 empty] | Date: | 19-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 305 | 0 | 0 | 115 | 45 | 45 | 30 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 306 | 0 | 0 | 0 | 142 | 16 | 21 | 0 | 475 | 0 | 0 | 27 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 20 | 925 | 0 | 0 | 6 | 0 | 0 | 218 | 0 | 0 | 0 | 1224 | 0 | 12 | 0 | 280 | 359 | 345 | 51 | 48 | 0 | 37 | 15 | 100 | 16 | 0 | 19 | 0 | 170 | 8 | 0 | 0 | 305 | 0 | 367 | 42 | 30 | 156 | 0 | 0 | 0 | 51 | 20 | 152 | 0 | 102 | 17 | 9 | 78 | 0 | 0 | 0 | 0 | 7389 | 923 | 144 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085 | 0 | 0 | 0 | 1451.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 399 | 0 | 0 | 0 | 50 | 70 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 120 | 220 | 0 | 696 | 1120 | 0 | 6874.51 | 14263.51 | 75.49
01:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 267 | 0 | 0 | 115 | 30 | 45 | 30 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 142 | 17 | 21 | 0 | 420 | 0 | 0 | 21 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 19 | 840 | 0 | 0 | 6 | 0 | 0 | 219 | 0 | 0 | 0 | 1224 | 0 | 12 | 0 | 280 | 357 | 345 | 51 | 48 | 0 | 37 | 17 | 100 | 16 | 0 | 19 | 0 | 158 | 8 | 0 | 0 | 310 | 0 | 367 | 42 | 30 | 149 | 0 | 14 | 0 | 51 | 25 | 155 | 0 | 102 | 17 | 9 | 78 | 0 | 0 | 0 | 0 | 7148 | 924 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 1445.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 51 | 70 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 120 | 220 | 0 | 685 | 1080 | 0 | 6743.71 | 13891.71 | 75.48
02:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 267 | 0 | 0 | 98 | 15 | 30 | 30 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 123 | 17 | 21 | 0 | 425 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 19 | 750 | 0 | 0 | 6 | 0 | 0 | 218 | 0 | 0 | 0 | 1224 | 0 | 12 | 0 | 280 | 359 | 345 | 51 | 47 | 0 | 37 | 16 | 100 | 16 | 0 | 19 | 0 | 154 | 0 | 0 | 0 | 305 | 0 | 367 | 42 | 30 | 138 | 0 | 14 | 0 | 51 | 25 | 153 | 0 | 102 | 17 | 9 | 78 | 0 | 0 | 0 | 0 | 6848 | 897 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 1447.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 51 | 35 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 120 | 220 | 0 | 633 | 980 | 0 | 6487.72 | 13335.72 | 75.48
03:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 248 | 0 | 0 | 98 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 86 | 17.5 | 21 | 0 | 405 | 0 | 0 | 18 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 21 | 740 | 0 | 0 | 6 | 0 | 0 | 218 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 280 | 358 | 345 | 51 | 48 | 0 | 37 | 0 | 100 | 0 | 0 | 19 | 0 | 144 | 0 | 0 | 0 | 300 | 0 | 368 | 42 | 30 | 140 | 0 | 16 | 0 | 51 | 25 | 153 | 0 | 102 | 17 | 9 | 78 | 0 | 0 | 0 | 0 | 6610.5 | 898 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 0 | 0 | 1456.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 120 | 220 | 0 | 623 | 920 | 0 | 6325.34 | 12935.84 | 75.47
04:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 220 | 0 | 0 | 98 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 86 | 17.5 | 21 | 0 | 365 | 0 | 0 | 19 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 27 | 743 | 0 | 0 | 6 | 0 | 0 | 218 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 310 | 358 | 345 | 51 | 47 | 0 | 37 | 0 | 100 | 0 | 0 | 19 | 0 | 150 | 0 | 0 | 0 | 305 | 0 | 368 | 42 | 30 | 133 | 0 | 16 | 0 | 51 | 25 | 154 | 0 | 102 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 6553.5 | 898 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1024 | 0 | 0 | 0 | 1351.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 120 | 220 | 0 | 617 | 830 | 0 | 6061.76 | 12615.26 | 75.47
05:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 249 | 0 | 0 | 98 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 86 | 17 | 21 | 0 | 400 | 0 | 0 | 18 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 30 | 743 | 0 | 0 | 6 | 0 | 0 | 218 | 0 | 0 | 0 | 1098 | 0 | 0 | 0 | 300 | 359 | 345 | 51 | 48 | 0 | 37 | 0 | 100 | 0 | 0 | 19 | 0 | 148 | 0 | 0 | 0 | 310 | 0 | 368 | 42 | 30 | 138 | 0 | 16 | 0 | 51 | 30 | 153 | 0 | 102 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 6485 | 897 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 948 | 0 | 0 | 0 | 1368.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 120 | 220 | 0 | 621 | 750 | 0 | 5954.78 | 12439.78 | 75.46
06:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 232 | 0 | 0 | 97 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 1 | 117 | 17 | 21 | 0 | 380 | 0 | 0 | 19 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 30 | 749 | 0 | 0 | 6 | 0 | 0 | 218 | 0 | 0 | 0 | 1056 | 1 | 0 | 0 | 285 | 358 | 345 | 51 | 48 | 0 | 37 | 0 | 99 | 0 | 0 | 19 | 0 | 134 | 0 | 2 | 0 | 305 | 0 | 368 | 42 | 30 | 130 | 1 | 16 | 0 | 51 | 30 | 153 | 0 | 102 | 0 | 9 | 78 | 0 | 0.13 | 2.41 | 0 | 6394.54 | 897 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.99 | 892 | 0 | 0 | 0 | 1365.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.65 | 4 | 0 | 0 | 2.13 | 140 | 0 | 140 | 0 | 0 | 0 | 346 | 0 | 0.19 | 0 | 48 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 12 | 0.04 | 0 | 177 | 124 | 220 | 0 | 614 | 720 | 0 | 5870.44 | 12264.98 | 75.46
07:00 | 0 | 45 | 25 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 295 | 0 | 0 | 100 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 8 | 142 | 17 | 21 | 0 | 460 | 0 | 0 | 18 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 30 | 760 | 0 | 0 | 6 | 0 | 0 | 218 | 0 | 0 | 0 | 1000 | 3 | 0 | 0 | 280 | 358 | 345 | 51 | 48 | 0 | 37 | 0 | 100 | 0 | 0 | 19 | 0 | 134 | 0 | 12 | 0 | 305 | 0 | 368 | 42 | 30 | 148 | 2 | 8 | 0 | 51 | 30 | 152 | 0 | 102 | 0 | 9 | 78 | 0 | 0.6 | 10.54 | 0 | 6597.14 | 897 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.18 | 822 | 0 | 0 | 0 | 1365.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.44 | 21 | 0 | 0 | 10.77 | 140 | 0 | 140 | 0 | 0 | 0 | 391 | 0 | 1 | 0 | 46 | 0 | 6 | 0 | 0 | 0 | 0 | 0.5 | 44 | 0.05 | 0 | 179 | 120 | 220 | 0 | 630 | 740 | 0 | 5959.41 | 12556.55 | 75.45
08:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 282 | 0 | 0 | 131 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 9 | 142 | 17 | 21 | 0 | 445 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 760 | 0 | 0 | 6 | 0 | 0 | 221 | 0 | 0 | 0 | 1004 | 4 | 0 | 0 | 270 | 359 | 345 | 51 | 48 | 0 | 37 | 0 | 98 | 0 | 0 | 19 | 0 | 148 | 0 | 22 | 0 | 305 | 0 | 368 | 42 | 30 | 150 | 3 | 17 | 0 | 51 | 30 | 154 | 0 | 102 | 0 | 9 | 78 | 0 | 1.03 | 20.99 | 0 | 6649.02 | 897 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.85 | 821 | 0 | 0 | 0 | 1366.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.92 | 42 | 0 | 0 | 25.5 | 140 | 0 | 140 | 0 | 0 | 0 | 381 | 0 | 1 | 0 | 49 | 0 | 8 | 0 | 0 | 0 | 0 | 1.4 | 92 | 0.04 | 0 | 179 | 120 | 220 | 0 | 638 | 750 | 0 | 6061.61 | 12710.63 | 75.45
09:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 297 | 0 | 0 | 132 | 15 | 0 | 15 | 4 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 20 | 142 | 17 | 21 | 0 | 470 | 0 | 0 | 18 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2.98 | 30 | 0 | 2 | 780 | 0 | 0 | 6 | 0 | 0 | 219 | 0 | 0 | 0 | 1162 | 6 | 0 | 0 | 265 | 357 | 345 | 51 | 48 | 0 | 37 | 0 | 97 | 0 | 0 | 19 | 0 | 158 | 0 | 50 | 0 | 305 | 0 | 356 | 42 | 30 | 153 | 8 | 17 | 0 | 51 | 30 | 154 | 0 | 102 | 0 | 9 | 78 | 0 | 1.4 | 34 | 0 | 6942.38 | 898 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 819 | 0 | 0 | 0 | 1355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.91 | 67 | 0 | 0 | 32.93 | 140 | 0 | 140 | 0 | 0 | 0 | 404 | 0 | 3.01 | 0 | 50 | 0 | 19 | 0 | 0 | 0 | 0 | 5.3 | 138 | 0.42 | 0 | 178 | 120 | 220 | 0 | 664 | 760 | 0 | 6235.57 | 13177.95 | 75.44
10:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 294 | 0 | 0 | 132 | 15 | 130 | 40 | 22 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 306 | 0 | 0 | 25 | 142 | 17 | 21 | 0 | 450 | 0 | 0 | 19 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0.73 | 30 | 0 | 2 | 780 | 1 | 0 | 6 | 0 | 0 | 219 | 0 | 0 | 0 | 1160 | 13 | 10 | 0 | 265 | 357 | 345 | 51 | 47 | 0 | 36 | 0 | 96 | 3 | 0 | 19 | 3 | 152 | 1 | 52 | 0 | 300 | 0 | 344 | 42 | 30 | 157 | 6 | 17 | 0 | 51 | 30 | 154 | 0 | 102 | 0 | 28 | 67 | 0 | 1.8 | 43.75 | 0 | 7144.28 | 897 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 779 | 0 | 0 | 0 | 1356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.12 | 86 | 0 | 0 | 47.46 | 140 | 0 | 140 | 0 | 0 | 0 | 383 | 0 | 4.2 | 0 | 48 | 0 | 26 | 0 | 0 | 0 | 0 | 6.5 | 175 | 0.21 | 0 | 177 | 120 | 220 | 0 | 687 | 800 | 0 | 6365.49 | 13509.77 | 75.44
11:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 304 | 0 | 0 | 132 | 15 | 205 | 53 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 23 | 142 | 17 | 21 | 0 | 460 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 4.38 | 30 | 0 | 2 | 920 | 15 | 0 | 6 | 0 | 0 | 214 | 0 | 0 | 0 | 1162 | 17 | 33 | 0 | 265 | 354 | 345 | 51 | 46 | 0 | 35 | 15 | 96 | 16 | 1 | 19 | 14 | 158 | 8 | 61 | 1 | 300 | 0 | 320 | 42 | 30 | 154 | 11 | 17 | 0 | 51 | 28 | 154 | 0 | 102 | 0 | 28 | 67 | 0 | 1.4 | 46.98 | 0 | 7465.76 | 897 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 774 | 0 | 0 | 0 | 1367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.4 | 95 | 0 | 0 | 53.01 | 140 | 0 | 140 | 0 | 0 | 0 | 397 | 0 | 4.77 | 0 | 48 | 0 | 30 | 0 | 0 | 0 | 0 | 7.2 | 185 | 0.3 | 0 | 189 | 120 | 220 | 0 | 669 | 800 | 0 | 6422.68 | 13888.44 | 75.44
12:00 | 0 | 80 | 25 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 284 | 17 | 0 | 132 | 30 | 293 | 55 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 31 | 142 | 17 | 21 | 0 | 450 | 0 | 0 | 19 | 0 | 13 | 17 | 24 | 0 | 0 | 0 | 0 | 65 | 0 | 2 | 910 | 34 | 0 | 6 | 0 | 0 | 213 | 0 | 0 | 0 | 1162 | 17 | 33 | 0 | 265 | 355 | 342 | 51 | 47 | 0 | 35 | 17 | 96 | 26 | 9 | 0 | 37 | 172 | 33 | 59 | 22 | 315 | 0 | 320 | 42 | 30 | 153 | 11 | 17 | 0 | 50 | 27 | 153 | 0 | 102 | 0 | 28 | 67 | 0 | 2.2 | 47.58 | 0 | 7752.78 | 898 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 815 | 0 | 0 | 0 | 1462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.09 | 79 | 0 | 0 | 53.71 | 140 | 0 | 140 | 0 | 0 | 0 | 376 | 0 | 4.89 | 0 | 48 | 0 | 32 | 0 | 0 | 0 | 0 | 7.6 | 197 | 0.39 | 0 | 223 | 120 | 220 | 0 | 693 | 865 | 0 | 6628.68 | 14381.46 | 75.43
13:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 282 | 17 | 0 | 132 | 45 | 293 | 55 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 29 | 130 | 17 | 21 | 0 | 425 | 0 | 0 | 19 | 0 | 4 | 17 | 28 | 0 | 0 | 0 | 4.1 | 53 | 0 | 7 | 880 | 100 | 0 | 6 | 0 | 0 | 213 | 0 | 0 | 0 | 1160 | 17 | 35 | 0 | 330 | 350 | 342 | 51 | 44 | 0 | 34 | 17 | 96 | 76 | 9 | 12 | 52 | 178 | 43 | 39 | 22 | 320 | 0 | 296 | 42 | 30 | 149 | 10 | 17 | 0 | 52 | 25 | 153 | 0 | 102 | 0 | 28 | 67 | 0 | 2.2 | 38.89 | 0 | 7868.19 | 897 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 916 | 0 | 0 | 0 | 1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.3 | 49 | 0 | 0 | 49.39 | 140 | 0 | 140 | 0 | 0 | 0 | 357 | 0 | 4.71 | 0 | 49 | 0 | 26 | 0 | 0 | 0 | 0 | 7.2 | 175 | 0.65 | 0 | 228 | 120 | 220 | 0 | 687 | 995 | 0 | 6770.25 | 14638.44 | 75.43
14:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 287 | 17 | 4 | 132 | 45 | 293 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 18 | 123 | 17 | 21 | 0 | 470 | 0 | 0 | 19 | 0 | 13 | 33 | 45 | 0 | 0 | 0 | 0.36 | 65 | 10 | 4 | 804 | 115 | 0 | 6 | 0 | 23 | 213 | 0 | 0 | 0 | 1162 | 17 | 36 | 0 | 365 | 347 | 340 | 51 | 44 | 0 | 35 | 17 | 93 | 148 | 8 | 19 | 66 | 188 | 43 | 49 | 21 | 320 | 0 | 296 | 42 | 30 | 145 | 8 | 17 | 0 | 52 | 25 | 154 | 0 | 101 | 0 | 28 | 68 | 0 | 1.32 | 43.09 | 0 | 8025.77 | 898 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 987 | 0 | 0 | 0 | 1455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.73 | 29 | 0 | 0 | 28.64 | 140 | 0 | 140 | 0 | 0 | 0 | 387 | 0 | 2.21 | 0 | 47 | 0 | 27 | 0 | 0 | 0 | 0 | 6.4 | 151 | 0.56 | 0 | 209 | 120 | 220 | 0 | 681 | 1100 | 0 | 6868.54 | 14894.31 | 75.42
15:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 291 | 0 | 17 | 132 | 75 | 278 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 20 | 142 | 17 | 20 | 0 | 440 | 0 | 0 | 19 | 0 | 3 | 33 | 45 | 0 | 2 | 0 | 0.66 | 30 | 17 | 2 | 890 | 116 | 0 | 5 | 0 | 35 | 212 | 0 | 0 | 0 | 1162 | 12 | 33 | 0 | 373 | 352 | 340 | 51 | 43 | 0 | 34 | 16 | 93 | 186 | 9 | 19 | 67 | 184 | 43 | 26 | 21 | 315 | 0 | 296 | 42 | 30 | 151 | 7 | 17 | 0 | 52 | 25 | 153 | 0 | 102 | 0 | 28 | 67 | 0 | 0.8 | 31.09 | 0 | 8091.55 | 897 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 1050 | 0 | 0 | 0 | 1445 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 21.73 | 49 | 0 | 0 | 33.39 | 140 | 0 | 140 | 0 | 0 | 0 | 377 | 0 | 3.01 | 0 | 47 | 0 | 23 | 29 | 0 | 0 | 0 | 5.2 | 117 | 0.47 | 0 | 257 | 120 | 220 | 0 | 690 | 1135 | 0 | 7010.8 | 15102.35 | 75.42
16:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 302 | 0 | 17 | 132 | 90 | 262 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 9 | 142 | 17 | 20 | 0 | 460 | 0 | 0 | 15 | 0 | 3 | 50 | 45 | 0 | 12 | 0 | 0.58 | 30 | 31 | 2 | 920 | 113 | 0 | 6 | 0 | 45 | 212 | 0 | 0 | 0 | 1160 | 7 | 33 | 0 | 384 | 351 | 342 | 51 | 41 | 0 | 31 | 17 | 94 | 184 | 9 | 19 | 67 | 180 | 43 | 24 | 22 | 320 | 0 | 296 | 42 | 30 | 149 | 4 | 17 | 0 | 52 | 20 | 153 | 0 | 101 | 0 | 18 | 76 | 0 | 0.77 | 20.31 | 0 | 8163.66 | 903 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 1095 | 0 | 0 | 0 | 1459 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 13.88 | 37 | 0 | 0 | 19.65 | 140 | 0 | 140 | 0 | 0 | 0 | 395 | 0 | 1.99 | 0 | 49 | 0 | 14 | 34 | 0 | 0 | 0 | 3.7 | 64 | 0.23 | 0 | 277 | 120 | 220 | 0 | 690 | 1170 | 0 | 7049.45 | 15213.11 | 75.42
17:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 258 | 0 | 17 | 132 | 92 | 260 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 302 | 0 | 0 | 5 | 142 | 17 | 20 | 0 | 420 | 5 | 0 | 18 | 0 | 0 | 50 | 52 | 0 | 12 | 12 | 0.51 | 30 | 32 | 3 | 810 | 114 | 0 | 6 | 0 | 48 | 212 | 0 | 0 | 0 | 1162 | 2 | 35 | 0 | 386 | 354 | 342 | 51 | 40 | 0 | 32 | 17 | 93 | 183 | 9 | 19 | 66 | 174 | 43 | 10 | 22 | 310 | 0 | 296 | 42 | 30 | 143 | 2 | 17 | 0 | 52 | 20 | 152 | 0 | 101 | 0 | 18 | 77 | 0 | 0.25 | 7.78 | 8 | 7974.54 | 903 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 1093 | 0 | 0 | 0 | 1401 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 6.63 | 7 | 0 | 0 | 5.46 | 140 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0.38 | 0 | 49 | 35 | 7 | 60 | 0 | 0 | 0 | 2 | 37 | 0.14 | 7 | 240 | 120 | 220 | 0 | 699 | 1170 | 0 | 6952.61 | 14927.15 | 75.42
18:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 257 | 0 | 17 | 132 | 92 | 260 | 55 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 35 | 302 | 0 | 0 | 1 | 142 | 17 | 20 | 0 | 430 | 15 | 20 | 18 | 0 | 0 | 50 | 58 | 0 | 12 | 12 | 0.07 | 30 | 31 | 4 | 740 | 85 | 0 | 6 | 1 | 47 | 214 | 0 | 0 | 0 | 1102 | 0 | 33 | 0 | 389 | 353 | 342 | 51 | 44 | 0 | 32 | 32 | 93 | 183 | 15 | 19 | 67 | 174 | 43 | 3 | 22 | 315 | 0 | 296 | 42 | 30 | 139 | 0 | 17 | 0 | 52 | 25 | 152 | 0 | 101 | 17 | 9 | 87 | 0 | 0.05 | 1.55 | 12 | 7992.67 | 904 | 135 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 15 | 3 | 1009 | 0 | 0 | 0 | 1361 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 8 | 1.94 | 5 | 0 | 0 | 1.54 | 140 | 0 | 140 | 0 | 0 | 0 | 350 | 0 | 0.06 | 0 | 48 | 35 | 1 | 69 | 0 | 0 | 0 | 0.5 | 3 | 0.03 | 16 | 210 | 120 | 180 | 0 | 729 | 1106 | 0 | 6664.07 | 14656.74 | 75.42
19:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 298 | 35 | 17 | 132 | 129 | 260 | 55 | 35 | 90 | 0 | 0 | 0 | 0 | 0 | 35 | 303 | 0 | 0 | 0 | 142 | 17 | 20 | 0 | 450 | 36 | 49 | 40 | 0 | 0 | 50 | 58 | 4 | 24 | 20 | 0 | 30 | 35 | 2 | 1000 | 104 | 0 | 14 | 7 | 45 | 214 | 0 | 0 | 0 | 1165 | 0 | 46 | 0 | 375 | 356 | 342 | 51 | 44 | 0 | 35 | 68 | 94 | 183 | 17 | 19 | 83 | 188 | 43 | 0 | 22 | 320 | 0 | 296 | 42 | 30 | 142 | 0 | 17 | 0 | 52 | 20 | 152 | 0 | 101 | 17 | 9 | 87 | 0 | 0 | 0 | 12 | 8704 | 904 | 136 | 0 | 15 | 31 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 1070 | 0 | 0 | 0 | 1359 | 0 | 0 | 0 | 50 | 71 | 0 | 50 | 0 | 34 | 0 | 0 | 27 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 47 | 110 | 0 | 96 | 0 | 165 | 0 | 0 | 0 | 0 | 38 | 244 | 120 | 220 | 0 | 891 | 1045 | 35 | 7527 | 16231 | 75.42
19:30 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 237 | 35 | 17 | 132 | 112 | 260 | 55 | 35 | 90 | 0 | 0 | 0 | 0 | 0 | 35 | 302 | 0 | 0 | 0 | 142 | 17 | 20 | 0 | 370 | 54 | 49 | 50 | 0 | 0 | 50 | 58 | 17 | 24 | 25 | 0 | 30 | 51 | 6 | 1000 | 110 | 0 | 37 | 8 | 85 | 216 | 0 | 0 | 0 | 1160 | 0 | 150 | 0 | 375 | 355 | 345 | 51 | 44 | 0 | 36 | 69 | 96 | 185 | 17 | 19 | 81 | 174 | 43 | 0 | 22 | 315 | 0 | 296 | 42 | 30 | 136 | 0 | 17 | 0 | 52 | 20 | 151 | 0 | 101 | 17 | 9 | 87 | 0 | 0 | 0 | 12 | 8739 | 903 | 136 | 0 | 30 | 40 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 1160 | 0 | 0 | 0 | 1310 | 0 | 9 | 0 | 113 | 110 | 0 | 80 | 0 | 34 | 0 | 0 | 30 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 47 | 115 | 0 | 98 | 0 | 80 | 0 | 0 | 0 | 0 | 101 | 275 | 120 | 220 | 0 | 912 | 1040 | 72 | 7819 | 16558 | 75.42
20:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 223 | 35 | 17 | 132 | 112 | 260 | 55 | 35 | 90 | 0 | 0 | 0 | 0 | 0 | 35 | 297 | 0 | 0 | 0 | 142 | 18 | 20 | 0 | 380 | 60 | 49 | 51 | 0 | 0 | 50 | 58 | 17 | 24 | 25 | 0 | 30 | 64 | 8 | 1000 | 116 | 0 | 36 | 8 | 85 | 216 | 0 | 0 | 0 | 1162 | 0 | 150 | 0 | 375 | 357 | 345 | 51 | 46 | 0 | 36 | 70 | 96 | 184 | 17 | 19 | 88 | 162 | 43 | 0 | 22 | 315 | 0 | 296 | 42 | 30 | 133 | 0 | 17 | 0 | 52 | 20 | 152 | 0 | 101 | 17 | 9 | 87 | 0 | 0 | 0 | 12 | 8760 | 904 | 136 | 0 | 36 | 54 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1192 | 0 | 0 | 0 | 1270 | 0 | 40 | 0 | 113 | 113 | 0 | 82 | 6 | 34 | 0 | 0 | 26 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 48 | 115 | 0 | 97 | 0 | 80 | 0 | 0 | 0 | 0 | 98 | 277 | 120 | 220 | 0 | 926 | 1060 | 90 | 7916 | 16676 | 75.42
21:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 250 | 35 | 17 | 132 | 112 | 260 | 55 | 35 | 90 | 0 | 0 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 142 | 18 | 20 | 0 | 390 | 58 | 65 | 50 | 0 | 0 | 48 | 58 | 17 | 24 | 25 | 0 | 30 | 68 | 14 | 1000 | 112 | 0 | 45 | 2 | 82 | 216 | 0 | 0 | 0 | 1162 | 0 | 150 | 0 | 355 | 357 | 345 | 51 | 46 | 0 | 39 | 69 | 96 | 184 | 17 | 19 | 83 | 168 | 43 | 0 | 22 | 320 | 0 | 296 | 42 | 30 | 139 | 0 | 17 | 0 | 50 | 20 | 153 | 0 | 101 | 17 | 9 | 87 | 0 | 0 | 0 | 12 | 8813 | 904 | 136 | 0 | 30 | 41 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1191 | 0 | 0 | 0 | 1218 | 0 | 40 | 0 | 113 | 113 | 0 | 91 | 0 | 34 | 0 | 0 | 26 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 47 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 278 | 120 | 220 | 0 | 930 | 1095 | 90 | 7808 | 16621 | 75.42
22:00 | 0 | 88 | 48 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 224 | 33 | 0 | 132 | 97 | 260 | 55 | 35 | 90 | 0 | 0 | 0 | 0 | 0 | 35 | 295 | 0 | 0 | 0 | 0 | 18 | 20 | 0 | 370 | 61 | 95 | 47 | 0 | 0 | 48 | 63 | 17 | 24 | 25 | 0 | 30 | 68 | 21 | 945 | 64 | 0 | 46 | 0 | 81 | 217 | 0 | 0 | 0 | 1162 | 0 | 150 | 0 | 360 | 357 | 345 | 51 | 0 | 0 | 0 | 68 | 97 | 136 | 17 | 19 | 30 | 156 | 43 | 0 | 22 | 315 | 0 | 296 | 42 | 30 | 148 | 0 | 17 | 0 | 50 | 28 | 151 | 0 | 101 | 0 | 9 | 78 | 0 | 0 | 0 | 12 | 8313 | 814 | 132 | 0 | 25 | 35 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1192 | 0 | 0 | 0 | 1254 | 0 | 40 | 0 | 113 | 113 | 0 | 91 | 0 | 16 | 0 | 0 | 26 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 47 | 115 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 260 | 120 | 220 | 0 | 924 | 1130 | 72 | 7584 | 15897 | 75.42
23:00 | 0 | 88 | 48 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 302 | 9 | 0 | 132 | 131 | 260 | 55 | 35 | 90 | 0 | 0 | 0 | 0 | 0 | 35 | 311 | 0 | 0 | 0 | 2 | 18 | 20 | 0 | 460 | 61 | 120 | 49 | 0 | 0 | 48 | 63 | 17 | 24 | 25 | 0 | 30 | 67 | 18 | 945 | 63 | 0 | 48 | 0 | 81 | 217 | 0 | 0 | 0 | 1162 | 0 | 58 | 0 | 385 | 357 | 345 | 51 | 25 | 0 | 33 | 50 | 98 | 132 | 17 | 19 | 32 | 160 | 43 | 0 | 23 | 315 | 0 | 296 | 42 | 30 | 145 | 0 | 16 | 0 | 50 | 20 | 153 | 0 | 101 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 8483 | 903 | 131 | 0 | 25 | 38 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1192 | 0 | 0 | 0 | 1273 | 0 | 40 | 0 | 113 | 113 | 0 | 91 | 0 | 16 | 0 | 0 | 26 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 49 | 115 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 268 | 120 | 220 | 0 | 928 | 1130 | 72 | 7744 | 16227 | 75.42
Total KWH | 0 | 1954560 | 695520 | 0 | 0 | 0 | 0 | 0 | 8902800 | 0 | 6979870 | 235440 | 150480 | 2988576 | 1315200 | 3835396 | 1001515 | 334859 | 792000 | 0 | 0 | 0 | 0 | 0 | 270076 | 7306058 | 0 | 0 | 198970 | 3022800 | 426000 | 496440 | 0 | 10560000 | 376364 | 479236 | 611520 | 0 | 115200 | 548810 | 613920 | 101037 | 176640 | 156480 | 16328 | 820280 | 505163 | 304320 | 20465454.55 | 1309745 | 0 | 348960 | 18761.4 | 673272 | 5023749 | 0 | 0 | 0 | 27610907 | 106920 | 898254 | 16727 | 7797000 | 8878000 | 8314000 | 1229948 | 1068000 | 0 | 827280 | 559680 | 2302809 | 2014560 | 160440 | 447920 | 852720 | 3844800 | 574402 | 422782 | 272832 | 7516000 | 0 | 8026000 | 998000 | 728160 | 3490772.73 | 74024 | 354000 | 0 | 1184640 | 595392 | 3540000 | 0 | 2442100 | 130680 | 360000 | 1819200 | 0 | 13550 | 335130 | 72240 | 184011669.68 | 21648000 | 3621024 | 0 | 136320 | 190080 | 0 | 0 | 0 | 0 | 0 | 411264 | 544320 | 24174550 | 0 | 0 | 0 | 33093452 | 0 | 177722 | 0 | 554784 | 818592 | 0 | 428240 | 5830 | 159336 | 317792 | 591460 | 143950 | 0 | 352544 | 3443727 | 0 | 3644173 | 0 | 0 | 0 | 9216727 | 0 | 31200 | 0 | 1154181 | 844566 | 206182 | 923251 | 0 | 187582 | 0 | 51558.96 | 1287360 | 3649 | 557184 | 5127000 | 2886000 | 5346250 | 0 | 17490909 | 24011636.36 | 429600 | 164211996.32 | 348223666

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 19-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14381.46 | MW | 12:00 Hr. | Energy Generated |  |  | 348.2237 |  | MKWHr.
| Day Peak Demand |  |  | 14433.71 | MW | 12:00 Hr. | Energy Unserverd |  |  | 4.126 |  | MKWHr.
| Evening Peak Generation |  |  | 16676 | MW | 20:00 Hr. | Energy Demand |  |  | 352.3497 |  | MKWHr.
| Evening Peak Demand |  |  | 16995 | MW | 20:00 Hr. | Maximum Temperature |  |  | 34.7 |  | °C
| Minimum Generation of the Day |  |  | 12264.98 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 926.01 |  | MMCFD
| Maximum Generation of the Day |  |  | 16676 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 6.5199 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.6712 | 0 | 16.5964 | 0 | 0 | 0.19897 | 0 | 0 | 51.4666 | Gas | 127.9139 | Gas | 447205163.8616
| Chattogram Zone |  |  | 5.3281 | 48.0764 | 5.9199 | 0 | 0.82028 | 0.12325 | 0 | 0.1152 | 60.3831 | Coal | 120.0346 | Coal | 786494493.3775
| Cumilla Zone |  |  | 30.8817 | 0 | 5.3329 | 0 | 0 | 0.42278 | 3.8448 | 0 | 40.4822 | HFO | 36.0121 | HFO | 613433576.628
| Mymensingh Zone |  |  | 0 | 0 | 2.3821 | 0 | 0 | 0.34868 | 0 | 0 | 2.7308 | HSD | 0.18758 | HSD | 5792532.16
| Sylhet Zone |  |  | 28.8751 | 0 | 0 | 0 | 0 | 0.074024 | 0 | 0 | 28.9491 | Hydro | 0.82028 | Hydro | 82028
| Khulna Zone |  |  | 3.621 | 24.1745 | 0.73766 | 0 | 0 | 0.54432 | 21.648 | 0 | 50.7256 | Solar | 4.5538 | Solar | 74116396.2292
| Barishal Zone |  |  | 8.2323 | 46.6295 | 0.98678 | 0 | 0 | 0.003649 | 0 | 0 | 55.8522 | Import | 58.5863 | Import | 341549803.68
| Rajshahi Zone |  |  | 16.3046 | 0 | 2.2885 | 0 | 0 | 1.293 | 33.0935 | 0 | 52.9795 | Wind | 0.1152 | Wind | 1694592
| Rangpur Zone |  |  | 0 | 1.1542 | 1.7678 | 0.18758 | 0 | 1.5451 | 0 | 0 | 4.6547
| Total |  |  | 127.9139 | 120.0346 | 36.0121 | 0.18758 | 0.82028 | 4.5538 | 58.5863 | 0.1152 | 348.2237
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 447205163.8616 |  | Hydro | 82028
|  |  |  | Coal | 786494493.3775 |  | Solar | 74116396.2292
|  |  |  | HFO | 613433576.628 |  | Import | 341549803.68
|  |  |  | HSD | 5792532.16 |  | Wind | 1694592
[5 empty] | Total: | 227,03,68,585 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.648 | Peak Hr Flow | 904.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 54570236.42 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 33.0935 | Peak Hr Flow | 1270.00 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2461 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.8448 | Peak Hr Flow | 162.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2689 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 58.5863 | Peak Hr Flow | 2336.00 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 33 |  | 6132
|  |  |  | Chattogram |  | 10 |  | 1626
|  |  |  | Cumilla |  | 16 |  | 1569
|  |  |  | Mymensingh |  | 197 |  | 1203
|  |  |  | Sylhet |  | 0 |  | 629
|  |  |  | Khulna |  | 49 |  | 2011
|  |  |  | Barishal |  | 0 |  | 520
|  |  |  | Rajshahi |  | 0 |  | 1716
|  |  |  | Rangpur |  | 0 |  | 1066
|  |  |  | Total |  | 305 |  | 16472
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:25 | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat is restored.
|  | 08:26 | Mymensingh 132/33kV S/S Bus B is restored.
|  | 08:40 | Lalmonirhat-Rangpur 132 kV Ckt-2 is restored.
|  | 08:45 | Kurigram-Lalmonirhat 132kV Ckt-1 is restored.
| 08:57 |  | Chowmuhani 230/132/33kV S/S ATR-03 HT Project Work S/D Due to AVR Replacement & testing
work.
| 08:57 |  | Chowmuhani 230/132/33kV S/S ATR-03 LT Project Work S/D Due to AVR Replacement & testing
work.
|  | 09:04 | Mymensingh-Netrokona 132kV Ckt-1 is restored.
| 09:21 | 17:29 | Gopalganj(N)-Madaripur 132kV Ckt-1 Scheduled S/D from Gopalganj 400/132kV end Due to
Tree trimming and from Madaripur 132/33kV end Due to Gopalgonj (N) 400 KV Work Purpose
| 09:22 | 17:30 | Gopalganj(N)-Madaripur 132kV Ckt-2 Scheduled S/D from Gopalganj 400/132kV end Due to
Tree Trimming and from Madaripur 132/33kV end Due to Gopalgonj (N) 400KV work purpose
| 09:28 | 19:40 | Korerhat 400/230/132kV S/S Feni -1 Project Work S/D Due to project work
| 09:31 | 20:41 | BSRM-Cumilla(N) 230 kV Ckt-1 Project Work S/D from Feni 230/132kV end Due to Witness Work
of SAS And DFDR
| 10:01 | 12:58 | Ishurdi-Pabna 132kV ckt Project Work S/D from Ishurdi 132/33kV end Due to remove
scaffolding work
|  | 10:10 | Mymensingh 132/33kV S/S Transformer-1 (404T) HT is restored.
|  | 10:10 | Mymensingh 132/33kV S/S Transformer-1 (404T) LT is restored.
| 10:12 | 14:02 | Mymensingh 132/33kV S/S Transformer-3 (424T) HT Scheduled S/D
| 10:12 | 14:03 | Mymensingh 132/33kV S/S Transformer-3 (424T) LT Scheduled S/D Due to None
|  | 10:33 | Kalurghat 132/33kV S/S TRFO-02(516T) LT is restored.
| 10:38 | 13:04 | Patuakhali-Payra 132kV Ckt-1 Project Work S/D from Patuakhali 132/33kV end Due to S/D by
ALDC and from Payra 400/132/33kV end Due to High temperature at primary junction point of
CT
| 11:02 | 13:11 | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat Scheduled S/D Due to Line clearing from 33
ke feer
| 11:04 | 13:11 | Lalmonirhat-Rangpur 132 kV Ckt-2 Forced S/D from Kurigram 132/33kV end.
| 12:00 |  | Day Peak Generation is 14378 MW.
| 12:08 |  | Aggreko-keraniganj 132kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Maintenance work at hasnabad end.
| 13:20 | 14:55 | Patuakhali-Payra 132kV Ckt-2 Project Work S/D from Patuakhali 132/33kV end Due to S/D by
ALDC and from Payra 400/132/33kV end Due to High temperature at primary junction point of
CT
| 13:25 |  | Gopalganj old 132/33kV T-3 (80/120 MVA) transformer was charged from 132kV end at 13:25
hrs. for the first time.
| 13:42 | 16:06 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT Scheduled S/D Due to Pbs redhot maintenance | [7 empty] | 15.0MW load
interrup.
| 13:43 | 16:05 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT Scheduled S/D Due to Pbs red hot maintenance | [7 empty] | 15.0MW load
interrup.
| 13:48 |  | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D Due to Increase system voltage.
| 16:31 | 17:10 | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to TR -1(A+B) side132 KV CT Red Hot
maintenance
| 16:32 | 17:08 | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to TR -1(A+B) side132 KV CT Red Hot
maintenance
| 17:12 | 18:10 | Jhenaidah 132/33kV S/S Transformer T-3 LT Forced S/D Due to 33kv T3A side DS, Y-phase nut | [7 empty] | 20.0MW load
|  |  | bolt redhot under the T3 transformer. | [7 empty] | interrup.
| 17:13 | 18:10 | Jhenaidah 132/33kV S/S Transformer T-3 HT Forced S/D Due to 33kv T3A side DS, Y-phase nut | [7 empty] | 20.0MW load
|  |  | bolt redhot under the T3 transformer. | [7 empty] | interrup.
|  | 18:16 | Aminbazar-Kallyanpur 132kV Ckt-2 is restored.
| 20:00 |  | Evening Peak Generation is 16676 MW.
| 21:47 | 21:57 | Bhaluka-Mymensingh 132 kV Ckt-1 Tripped from Bhaluka 132/33kV end showing 67 Dicectional | [7 empty] | 100.0MW load
|  |  | overcurrent relays. | [7 empty] | interrup. Bhaluka
132/33kV end
| 21:47 | 21:57 | Bhaluka-Mymensingh 132 kV Ckt-2 Tripped from Bhaluka 132/33kV end showing 67 Dicectional | [7 empty] | 100.0MW load
|  |  | overcurrent. relays. | [7 empty] | interrup. Bhaluka
132/33kV end
| 21:47 | 22:00 | Bhaluka 132/33kV S/S 01. Transformer- 01 LT Tripped showing SPS Trip. relays Due to None | [7 empty] | 75.0MW load
interrup.
| 21:47 | 22:00 | Bhaluka 132/33kV S/S 02. Transformer- 02 LT Tripped showing SPS Trip. relays. | [7 empty] | 75.0MW load
interrup.
| 22:08 | 23:47 | Feni 132/33kV S/S T-1(405T) HT Scheduled S/D Due to For PDB 33KV Doreen Ckt Red Hot | [7 empty] | 40.0MW load
|  |  | Maintenance Work. | [7 empty] | interrup.
| 22:09 | 23:47 | Feni 132/33kV S/S T-1(405T) LT Scheduled S/D Due to For PDB 33KV Doreen Ckt Red Hot | [7 empty] | 40.0MW load
|  |  | Maintenance Work. | [7 empty] | interrup.
| 22:26 | 02:38 | Lalmonirhat-Rangpur 132 kV Ckt-2 Forced S/D from Rangpur 132/33kV end Due to CT (Current
Transformer) connection strip burned at the 132kV Lalmonirhat Control & Relay Panel
requires an emergency maintenance.
| 04:43 |  | Kaliakoir 400/230/132kV S/S 230kV Bus 1 Forced S/D Due to Trip
| 06:11 |  | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to 33kv jhalokathi feeder DS maintenance | [7 empty] | 35.0MW load
interrup.
| 06:12 |  | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to 33kv jhalokathi feeder DS maintenance | [7 empty] | 35.0MW load
interrup.
| 06:27 | 06:59 | Bhaluka 132/33kV S/S 01. Transformer- 01 LT Scheduled S/D Due to High temp. maintenance . | [7 empty] | 45.0MW load
interrup.
| 06:28 | 06:58 | Bhaluka 132/33kV S/S 01. Transformer- 01 HT Scheduled S/D Due to High temp. maintenance. | [7 empty] | 45.0MW load
interrup.
| 06:49 |  | Rangpur 132/33kV S/S T-1(414T) LT Scheduled S/D Due to 33kV BUS Section-1 shutdown due to
NESCO Burihat-1 feeder raiser red hot.
| 06:49 |  | Rangpur 132/33kV S/S T-1(414T) HT Scheduled S/D Due to 33kV BUS Section-1 shutdown due to
NESCO Burihat-1 feeder raiser red hot.
| 07:00 |  | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Redhot Maintenance. | [7 empty] | 60.0MW load
interrup.
| 07:01 |  | Bhaluka 132/33kV S/S 02. Transformer- 02 LT Scheduled S/D Due to High temperature | [7 empty] | 50.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 07:02 |  | Bhaluka 132/33kV S/S 02. Transformer- 02 HT Scheduled S/D Due to High temperature | [7 empty] | 49.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 07:02 | 08:00 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Redhot Maintenance. | [7 empty] | 60.0MW load
interrup.
| 07:20 |  | Narshingdi 132/33kV S/S T-2 LT Scheduled S/D Due to 33 kv bus DS redhot | [7 empty] | 35.0MW load
interrup.
| 07:23 |  | Narshingdi 132/33kV S/S T-2 HT Scheduled S/D Due to 33 kv bus BS redhot | [7 empty] | 35.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 19-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 353 | 8902800 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1001515 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 297 | 7306058 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 235440 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 112 | 1315200 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 334859 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 270076 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 426000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 496440 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 48 | 695520 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 260 | 3835396 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 2988576 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1954560 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 792000 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 198970 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 150480 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 380 | 10560000 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 223 | 6979870 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3022800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2357 | 51466560
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 18761.4 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 106920 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 36 | 348960 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 820280 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 216 | 5023749 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 85 | 673272 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 58 | 613920 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 548810 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 176640 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 8 | 304320 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 51 | 611520 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 16328 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 49 | 479236 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 17 | 101037 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 64 | 505163 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 156480 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 60 | 376364 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 116 | 1309745 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1162 | 27610907 | Can't Start AGC
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 115200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1000 | 20465454.55 | AGC
Chattogram Area Total |  |  |  |  | 4898.863 | 3059 | 60383066.95
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 0 | 0 | Under Maintenance
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 357 | 8878000 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 345 | 8314000 | FGMO not available
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 375 | 7797000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 36 | 827280 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 46 | 1068000 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 16727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1229948 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 898254 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 22 | 272832 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 96 | 2302809 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 184 | 2014560 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 162 | 3844800 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 574402 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 447920 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 88 | 852720 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 17 | 160440 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 70 | 559680 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 422782 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 2061 | 40482154
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13550 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 1819200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 360000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 335130 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 72240 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 130680 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 125 | 2730800
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 74024 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 998000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 728160 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 133 | 3490772.73 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 152 | 3540000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 595392 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 52 | 1184640 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2442100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 354000 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7516000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 296 | 8026000 | Plant availability less
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1158 | 28949088.73
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 904 | 21648000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 36 | 136320 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 54 | 190080 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 136 | 3621024 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 85 | 411264 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 544320 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1192 | 24174550 | U-2 Under Maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2407 | 50725558
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 926 | 17490909 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 98 | 557184 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2886000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1060 | 24011636.36 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5346250 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 90 | 429600 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 277 | 5127000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3649 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2791 | 55852228.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 317792 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 177722 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 6 | 5830 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 140 | 3443727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 140 | 3644173 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9216727 | AGC
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 143950 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 34 | 159336 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 82 | 428240 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 818592 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 554784 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 31200 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1270 | 33093452 | Can't Start AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 352544 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 591460 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2378 | 52979529
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 80 | 187582 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 48 | 1154181 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 97 | 923251 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 51558.96 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 844566 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 206182 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1287360 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 340 | 4654680.96
Eastern Grid Total |  |  |  |  | 17418.042 | 8760 | 184011669.68
Western Grid Total |  |  |  |  | 11852.195 | 7916 | 164211996.32
National Grid Total |  |  |  |  | 29270.237 | 16676 | 348223666
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 19-05-2026
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10903.67 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5263.9 | MW
i) Dhaka area |  |  | 6099.17 |  | MW | i) Khulna area |  |  |  | 1962 | MW
ii) Chattogram area |  |  | 1616.5 |  | MW | ii) Barishal area |  |  |  | 519.5 | MW
iii) Cumilla area |  |  | 1553 |  | MW | iii) Rajshahi area |  |  |  | 1716.4 | MW
iv) Mymensingh area |  |  | 1006 |  | MW | iv) Rangpur area |  |  |  | 1066 | MW
v) Sylhet area |  |  | 629 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 16167.57 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 6 | 15:00 | 67 | Hasnabad | 102 | 20:00 | 133 | Natore | 171 | 22:00
2 | AKSML | 113.8 | 05:00 | 68 | Hathazari | 99 | 18:30 | 134 | Nawabganj | 70.2 | 22:00
3 | Aftabnagar | 46 | 21:00 | 69 | Hatirjheel | 58 | 13:00 | 135 | Netrakona | 112 | 00:00
4 | Agargaon | 143 | 14:00 | 70 | Ishurdi | 92 | 19:30 | 136 | New | 86 | 14:00
5 | Agrabad | 80 | 15:00 | 71 | Jaldhaka | 88 | 19:00 | 137 | Niamatpur | 87 | 22:00
6 | Amnura | 31 | 22:00 | 72 | Jamalpur | 95 | 08:00 | 138 | Noapara | 46 | 16:00
7 | Ashuganj | 99 | 19:00 | 73 | Jashore | 181 | 20:00 | 139 | PHP | 11 | 13:00
8 | BSRM | 201 | 23:00 | 74 | Jhenaidah | 143 | 19:00 | 140 | Pabna | 111 | 19:30
9 | Bagerhat | 84 | 00:00 | 75 | Joydebpur | 163 | 17:00 | 141 | Palashbari | 136 | 20:00
10 | Bajitpur | 80 | 23:00 | 76 | Joypurhat | 66 | 19:30 | 142 | Panchagarh | 66 | 19:30
11 | Bakerganj | 12.4 | 22:00 | 77 | Juldah | 16 | 11:00 | 143 | Patiya | 11.5 | 20:00
12 | Bakulia | 103 | 23:00 | 78 | KSRM | 12 | 07:00 | 144 | Patuakhali | 77.5 | 21:00
13 | Banani | 57.4 | 13:00 | 79 | Kabirpur | 249 | 15:00 | 145 | Payra | 38 | 22:00
14 | Bangabhaban | 21 | 13:00 | 80 | Kachua | 108 | 23:00 | 146 | Postogola | 60 | 23:00
15 | Barapukuria | 68 | 19:00 | 81 | Kaliganj | 9 | 10:00 | 147 | Pubail | 30 | 18:30
16 | Barguna | 26 | 23:00 | 82 | Kallyanpur | 120 | 18:30 | 148 | Purbachal | 36 | 13:00
17 | Barishal | 120 | 21:00 | 83 | Kalurghat | 64 | 19:00 | 149 | Purbasadipur | 142 | 20:00
18 | Barishal-230 | 114 | 22:00 | 84 | Kamrangirchar | 85 | 19:30 | 150 | Rahanpur | 42 | 22:00
19 | Baroaulia | 72 | 19:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 24 | 18:00
20 | Baroirhat | 76 | 23:00 | 86 | Kasba | 41 | 21:00 | 152 | Rajbari | 91 | 19:30
21 | Bashundhara | 207 | 19:00 | 87 | Kazla | 124 | 12:00 | 153 | Rajendrapur | 127 | 12:00
22 | BashundharaCement | 6 | 00:00 | 88 | Keranigonj | 94 | 19:30 | 154 | Rajshahi | 150 | 21:00
23 | Beanibazar | 78 | 19:30 | 89 | Khagrachori | 34 | 19:00 | 155 | Rajshahi-230 | 90 | 23:00
24 | Benapole | 78 | 22:00 | 90 | Khulna | 73 | 13:00 | 156 | Ramganj | 124 | 22:00
25 | Bhaluka | 187 | 20:00 | 91 | Khulshi | 204 | 12:00 | 157 | Rampur | 48 | 23:00
26 | Bhandaria | 60 | 22:00 | 92 | Kishoreganj | 105 | 13:00 | 158 | Rangamati | 20 | 19:00
27 | Bhangura | 44 | 19:00 | 93 | Kodda | 339 | 19:00 | 159 | Rangpur | 148 | 19:30
28 | Bheramara(GK) | 74 | 22:00 | 94 | Kulaura | 51 | 23:00 | 160 | Ruppur | 4.2 | 11:00
29 | Bhulta | 238 | 15:00 | 95 | Kurigram | 74 | 19:00 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 86 | 22:00 | 96 | Kushtia | 180 | 19:30 | 162 | Saidpur | 107 | 19:30
31 | Bogura | 177 | 19:00 | 97 | Laksam | 39 | 22:00 | 163 | Santhia | 40 | 20:00
32 | Borhanuddin | 95 | 01:00 | 98 | Lakshmipur | 51 | 23:00 | 164 | Satkhira | 134 | 23:00
33 | Brahmanbaria | 130 | 19:00 | 99 | Lalbag | 87 | 13:00 | 165 | Satmasjid | 111 | 20:00
34 | Cantonment | 124 | 13:00 | 100 | Lalmonirhat | 64 | 19:00 | 166 | Savar | 232 | 12:00
35 | Chandina | 39 | 21:00 | 101 | MI_Cement | 17.7 | 23:00 | 167 | SevenRings | 18.69 | 09:00
36 | Chandpur | 94 | 22:00 | 102 | Madanganj | 49 | 21:00 | 168 | ShahCement | 43 | 16:00
37 | Chandraghona | 39 | 19:30 | 103 | Madaripur | 129 | 21:00 | 169 | Shahjadpur | 96 | 20:00
38 | Chapai | 81 | 21:00 | 104 | Madartek | 89 | 23:00 | 170 | Shahjibazar | 125 | 21:00
39 | Charsaidpur | 45 | 16:00 | 105 | Madunaghat | 60 | 20:00 | 171 | Shahmirpur | 58 | 16:00
40 | Chauddagram | 84 | 19:30 | 106 | Magura | 77 | 19:00 | 172 | Shariatpur | 100 | 21:00
41 | Chhatak | 41 | 20:00 | 107 | Mahasthangarh | 87 | 19:30 | 173 | Sherpur | 104 | 02:00
42 | Chowmuhani | 168 | 22:00 | 108 | Maijdee | 52 | 21:00 | 174 | Shikalbaha | 33 | 17:00
43 | Chuadanga | 111 | 19:30 | 109 | Manikganj | 142 | 20:00 | 175 | Shitalakhya | 94.3 | 16:00
44 | Coxsbazar | 159 | 13:00 | 110 | Maniknagar | 82 | 23:00 | 176 | Sholosohor | 50 | 19:00
45 | Cumilla(N) | 133 | 19:00 | 111 | Matarbari | 56 | 23:00 | 177 | Shomvuganj | 19 | 18:30
46 | Cumilla(S) | 189 | 19:00 | 112 | Matuail | 80 | 23:00 | 178 | Shyampur | 182 | 12:00
47 | Daganbhuiyan | 43 | 23:00 | 113 | Metrorail_Motijheel | 35 | 17:00 | 179 | Siddhirganj | 136 | 19:00
48 | Daudkandi | 155 | 19:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 128 | 20:00
49 | DhakaUniversity | 98 | 13:00 | 115 | Millgate | 108 | 15:00 | 181 | Sonargaon | 145 | 23:00
50 | Dhamrai | 126 | 19:00 | 116 | Mirpur | 163 | 19:00 | 182 | Sreemongol | 87 | 23:00
51 | Dhanmondi | 111 | 14:00 | 117 | Mirsorai | 48 | 02:00 | 183 | Sreepur | 96 | 16:00
52 | Dohazari | 106 | 21:00 | 118 | Mirzapur | 43 | 12:00 | 184 | Srinagar | 54.4 | 23:00
53 | Faridpur | 180 | 19:00 | 119 | Mithapukur | 66 | 19:30 | 185 | Sunamganj | 64 | 21:00
54 | Fatullah | 100 | 15:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 74 | 21:00
55 | Fenchuganj | 45 | 20:00 | 121 | Mogbazar | 118.2 | 13:00 | 187 | Sylhet-132 | 121 | 19:00
56 | Feni | 114 | 13:00 | 122 | Mongla | 50 | 16:00 | 188 | TK | 27 | 22:00
57 | GPH | 1 | 00:00 | 123 | Motijheel | 53 | 13:00 | 189 | Tangail | 150 | 12:00
58 | Ghatail | 72 | 12:00 | 124 | Muktagacha | 30 | 17:00 | 190 | Taraganj | 28 | 19:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 119 | 23:00 | 191 | Tasnim | 32 | 11:00
60 | Ghorashal-230 | 112 | 03:00 | 126 | Muradnagar | 47 | 21:00 | 192 | Thakurgaon | 110 | 19:30
61 | Goalpara | 39 | 00:00 | 127 | Mymensingh | 177 | 21:00 | 193 | Tongi | 164 | 23:00
62 | Gollamari | 118 | 13:00 | 128 | Nabinagar | 86 | 18:00 | 194 | Ullahpara | 43 | 20:00
63 | Gopalganj | 129 | 19:30 | 129 | Naogaon | 150 | 20:00 | 195 | Ullon | 48 | 23:00
64 | Gulshan | 140 | 15:00 | 130 | Narail | 53 | 19:00 | 196 | Uttara | 108 | 13:00
65 | Halishahar | 106 | 15:00 | 131 | Narinda | 78 | 17:00 | 197 | UttaraNew | 61 | 23:00
66 | HaripurSBU | 140 | 07:00 | 132 | Narshingdi | 198 | 23:00 | 198 | Zigatola | 92 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 19-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14263.51 | 119 |  | 14387.87
1:00 | 13891.71 | 142 |  | 14039.71
2:00 | 13335.72 | 119 |  | 13459.72
3:00 | 12935.84 | 110 |  | 13050.84
4:00 | 12615.26 | 101 |  | 12721.26
5:00 | 12439.78 | 96 |  | 12539.78
6:00 | 12264.98 | 94 |  | 12362.98
7:00 | 12556.55 | 93 |  | 12653.55
8:00 | 12710.63 | 109 |  | 12824.63
9:00 | 13177.95 | 120 |  | 13302.95
10:00 | 13509.77 | 118 |  | 13632.77
11:00 | 13888.44 | 110 |  | 14003.44
12:00 | 14381.46 | 50 |  | 14433.71
13:00 | 14638.44 | 72 |  | 14713.44
14:00 | 14894.31 | 114 |  | 15013.31
15:00 | 15102.35 | 116 |  | 15223.57
16:00 | 15213.11 | 136 |  | 15355.11
17:00 | 14927.15 | 206 |  | 15142.15
18:00 | 14656.74 | 168 |  | 14832.74
19:00 | 16231 | 257 |  | 16500
19:30 | 16558 | 279 |  | 16849.56
20:00 | 16676 | 305 |  | 16995
21:00 | 16621 | 314 |  | 16949.13
22:00 | 15897 | 605 |  | 16529
23:00 | 16227 | 452 |  | 16699
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 19-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7389 | 6874.51 | 14263.51 | DAILY GENERATION CURVE
00:30 | 7268.5 | 6809.11 | 14077.61
01:00 | 7148 | 6743.71 | 13891.71 | 19-05-2026
01:30 | 6998 | 6615.715 | 13613.715
02:00 | 6848 | 6487.72 | 13335.72
02:30 | 6729.25 | 6406.53 | 13135.78
03:00 | 6610.5 | 6325.34 | 12935.84
03:30 | 6582 | 6193.55 | 12775.55
04:00 | 6553.5 | 6061.76 | 12615.26
04:30 | 6519.25 | 6008.27 | 12527.52
05:00 | 6485 | 5954.78 | 12439.78
05:30 | 6439.77 | 5912.61 | 12352.38
06:00 | 6394.54 | 5870.44 | 12264.98
06:30 | 6495.84 | 5914.925 | 12410.765
07:00 | 6597.14 | 5959.41 | 12556.55
07:30 | 6623.08 | 6010.51 | 12633.59
08:00 | 6649.02 | 6061.61 | 12710.63
08:30 | 6795.7 | 6148.59 | 12944.29
09:00 | 6942.38 | 6235.57 | 13177.95
09:30 | 7043.33 | 6300.53 | 13343.86
10:00 | 7144.28 | 6365.49 | 13509.77
10:30 | 7305.02 | 6394.085 | 13699.105
11:00 | 7465.76 | 6422.68 | 13888.44
11:30 | 7609.27 | 6525.68 | 14134.95
12:00 | 7752.78 | 6628.68 | 14381.46
12:30 | 7810.485 | 6699.465 | 14509.95
13:00 | 7868.19 | 6770.25 | 14638.44
13:30 | 7946.98 | 6819.395 | 14766.375
14:00 | 8025.77 | 6868.54 | 14894.31
14:30 | 8058.66 | 6939.67 | 14998.33
15:00 | 8091.55 | 7010.8 | 15102.35
15:30 | 8127.605 | 7030.125 | 15157.73
16:00 | 8163.66 | 7049.45 | 15213.11
16:30 | 8069.1 | 7001.03 | 15070.13
17:00 | 7974.54 | 6952.61 | 14927.15
17:30 | 7983.605 | 6808.34 | 14791.945
18:00 | 7992.67 | 6664.07 | 14656.74
18:30 | 8348.335 | 7095.535 | 15443.87
19:00 | 8704 | 7527 | 16231
19:30 | 8739 | 7819 | 16558
20:00 | 8760 | 7916 | 16676
20:30 | 8786.5 | 7862 | 16648.5 |  | Executive Engineer
21:00 | 8813 | 7808 | 16621 |  | Network Operation Division
21:30 | 8563 | 7696 | 16259
22:00 | 8313 | 7584 | 15897
22:30 | 8398 | 7664 | 16062
23:00 | 8483 | 7744 | 16227

## En-Curve
QF-LDC-12
Date | 19-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3684 | 1687 | 923 | 0 | 170 | 1451.51 | 30 | 5279 | 0 | 404 | 635 | 0 | 0 | 0 | 119 | DAILY ENERGY CURVE
00:30 | 3653 | 1646.5 | 923.5 | 0 | 164 | 1448.61 | 30 | 5218 | 0 | 361 | 633 | 0 | 0 | 0 | 130.5 | 19-05-2026
01:00 | 3622 | 1606 | 924 | 0 | 158 | 1445.71 | 30 | 5157 | 0 | 318 | 631 | 0 | 0 | 0 | 142
01:30 | 3623.5 | 1600 | 910.5 | 0 | 156 | 1446.715 | 30 | 5034.5 | 0 | 265.5 | 547 | 0 | 0 | 0 | 130.5 | Energy Generated | 348.2237 |  | MKWHr
02:00 | 3625 | 1594 | 897 | 0 | 154 | 1447.72 | 30 | 4912 | 0 | 213 | 463 | 0 | 0 | 0 | 119 | Energy not Served | 4.126 |  | MKWHr
02:30 | 3609 | 1575.75 | 897.5 | 0 | 149 | 1452.03 | 30 | 4873.5 | 0 | 190 | 352 | 0 | 0 | 7 | 114.5 | Total Energy Requirement | 352.3497 |  | MKWHr
03:00 | 3593 | 1557.5 | 898 | 0 | 144 | 1456.34 | 30 | 4835 | 0 | 167 | 241 | 0 | 0 | 14 | 110
03:30 | 3609.5 | 1525 | 898 | 0 | 147 | 1404.05 | 30 | 4750 | 0 | 167 | 233 | 0 | 0 | 12 | 105.5
04:00 | 3626 | 1492.5 | 898 | 0 | 150 | 1351.76 | 30 | 4665 | 0 | 167 | 225 | 0 | 0 | 10 | 101
04:30 | 3641.5 | 1531.25 | 897.5 | 0 | 149 | 1360.27 | 30 | 4526.5 | 0 | 159 | 224.5 | 0 | 0 | 8 | 98.5
05:00 | 3657 | 1570 | 897 | 0 | 148 | 1368.78 | 30 | 4388 | 0 | 151 | 224 | 0 | 0 | 6 | 96
05:30 | 3635.5 | 1545 | 897 | 0 | 141 | 1367.11 | 30 | 4322 | 16.27 | 166.5 | 224 | 0 | 0 | 8 | 95
06:00 | 3614 | 1520 | 897 | 0 | 134 | 1365.44 | 30 | 4256 | 32.54 | 182 | 224 | 0 | 0 | 10 | 94
06:30 | 3647.5 | 1596.5 | 897 | 0 | 134 | 1365.455 | 30 | 4216.5 | 88.31 | 204.5 | 225 | 0 | 0 | 6 | 93.5
07:00 | 3681 | 1673 | 897 | 0 | 134 | 1365.47 | 30 | 4177 | 144.08 | 227 | 226 | 0 | 0 | 2 | 93
07:30 | 3675.5 | 1652 | 897 | 0 | 141 | 1366.185 | 30 | 4189 | 200.905 | 239.5 | 241.5 | 0 | 0 | 1 | 101
08:00 | 3670 | 1631 | 897 | 0 | 148 | 1366.9 | 30 | 4201 | 257.73 | 252 | 257 | 0 | 0 | 0 | 109
08:30 | 3675 | 1651 | 897.5 | 0 | 153 | 1360.95 | 30 | 4307 | 353.84 | 252 | 263 | 0 | 0 | 1 | 114.5
09:00 | 3680 | 1671 | 898 | 0 | 158 | 1355 | 30 | 4413 | 449.95 | 252 | 269 | 0 | 0 | 2 | 120
09:30 | 3659 | 1658.5 | 897.5 | 0 | 155 | 1355.5 | 30 | 4422 | 527.86 | 252 | 382.5 | 0 | 0 | 4 | 119
10:00 | 3638 | 1646 | 897 | 0 | 152 | 1356 | 30 | 4431 | 605.77 | 252 | 496 | 0 | 0 | 6 | 118
10:30 | 3624 | 1654 | 897 | 0 | 155 | 1361.5 | 30 | 4496.5 | 640.105 | 252.5 | 580 | 0 | 0 | 8.5 | 114
11:00 | 3610 | 1662 | 897 | 0 | 158 | 1367 | 30 | 4562 | 674.44 | 253 | 664 | 0 | 0 | 11 | 110
11:30 | 3598 | 1644.5 | 897.5 | 0 | 165 | 1414.5 | 47.5 | 4639 | 659.45 | 296.5 | 761 | 0 | 0 | 12 | 80
12:00 | 3586 | 1627 | 898 | 0 | 172 | 1462 | 65 | 4716 | 644.46 | 340 | 858 | 0 | 0 | 13 | 50
12:30 | 3593.5 | 1622 | 897.5 | 0 | 175 | 1454.5 | 59 | 4815.5 | 607.45 | 347.5 | 929.5 | 0 | 0 | 8.5 | 61
13:00 | 3601 | 1617 | 897 | 0 | 178 | 1447 | 53 | 4915 | 570.44 | 355 | 1001 | 0 | 0 | 4 | 72
13:30 | 3629 | 1642 | 897.5 | 0 | 183 | 1451 | 59 | 4952.5 | 523.375 | 367.5 | 1053 | 0 | 0 | 8.5 | 93
14:00 | 3657 | 1667 | 898 | 0 | 188 | 1455 | 65 | 4990 | 476.31 | 380 | 1105 | 0 | 0 | 13 | 114
14:30 | 3653.5 | 1652.5 | 897.5 | 0 | 186 | 1450 | 47.5 | 5110.5 | 445.83 | 404.5 | 1142.5 | 0 | 0 | 8 | 115
15:00 | 3650 | 1638 | 897 | 0 | 184 | 1445 | 30 | 5231 | 415.35 | 429 | 1180 | 0 | 0 | 3 | 116
15:30 | 3661.5 | 1654 | 900 | 0 | 182 | 1452 | 30 | 5296 | 333.23 | 445.5 | 1200.5 | 0 | 0 | 3 | 126
16:00 | 3673 | 1670 | 903 | 0 | 180 | 1459 | 30 | 5361 | 251.11 | 462 | 1221 | 0 | 0 | 3 | 136
16:30 | 3678 | 1620 | 903 | 0 | 177 | 1430 | 30 | 5292 | 182.63 | 475 | 1281 | 0 | 0 | 1.5 | 171
17:00 | 3683 | 1570 | 903 | 0 | 174 | 1401 | 30 | 5223 | 114.15 | 488 | 1341 | 0 | 0 | 0 | 206
17:30 | 3651 | 1557.5 | 903.5 | 0 | 174 | 1381 | 30 | 5083.5 | 67.945 | 512 | 1431.5 | 0 | 0 | 0 | 187
18:00 | 3619 | 1545 | 904 | 0 | 174 | 1361 | 30 | 4944 | 21.74 | 536 | 1522 | 0 | 0 | 0 | 168
18:30 | 3651 | 1598.5 | 904 | 0 | 181 | 1360 | 30 | 5203 | 10.87 | 644 | 1779 | 82.5 | 0 | 0 | 212.5
19:00 | 3683 | 1652 | 904 | 0 | 188 | 1359 | 30 | 5462 | 0 | 752 | 2036 | 165 | 0 | 0 | 257
19:30 | 3665 | 1504 | 903 | 0 | 174 | 1310 | 30 | 5594 | 0 | 816 | 2482 | 80 | 0 | 0 | 279
20:00 | 3666 | 1502 | 904 | 0 | 162 | 1270 | 30 | 5665 | 0 | 866 | 2531 | 80 | 0 | 0 | 305
20:30 | 3661 | 1528 | 904 | 0 | 165 | 1244 | 30 | 5684 | 0 | 857 | 2535.5 | 40 | 0 | 0 | 309.5
21:00 | 3656 | 1554 | 904 | 0 | 168 | 1218 | 30 | 5703 | 0 | 848 | 2540 | 0 | 0 | 0 | 314
21:30 | 3599 | 1513.5 | 859 | 0 | 162 | 1236 | 30 | 5681.5 | 0 | 740.5 | 2437.5 | 0 | 0 | 0 | 459.5
22:00 | 3542 | 1473 | 814 | 0 | 156 | 1254 | 30 | 5660 | 0 | 633 | 2335 | 0 | 0 | 0 | 605
22:30 | 3593.5 | 1566 | 858.5 | 0 | 158 | 1263.5 | 30 | 5667 | 0 | 653 | 2272.5 | 0 | 0 | 0 | 528.5
23:00 | 3645 | 1659 | 903 | 0 | 160 | 1273 | 30 | 5674 | 0 | 673 | 2210 | 0 | 0 | 0 | 452
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 19-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 145 | 8 | 564 | 144 | 1904 | 650 | Ishurdi-Ghorashal Ckt-1 | Export | 3653236.42
1:00 | 160 | 10 | 562 | 130 | 1866 | 644
2:00 | 171 | 18 | 566 | 132 | 1918 | 684 |  | Import | 0
3:00 | 179 | 22 | 584 | 130 | 1916 | 692
4:00 | 177 | 11 | 596 | 114 | 1912 | 718 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 179 | 10 | 592 | 104 | 1816 | 706
6:00 | 173 | 9 | 570 | 86 | 1756 | 686 |  | Import | 0
7:00 | 156 | 2 | 560 | 86 | 1616 | 624
8:00 | 178 | 9 | 622 | 108 | 1724 | 674 | Sirajganj-Sreepur Ckt-1 | Export | 3324000
9:00 | 203 | 25 | 664 | 154 | 1822 | 748
10:00 | 201 | 22 | 636 | 144 | 1838 | 732 |  | Import | 0
11:00 | 195 | 21 | 445 | 345 | 1776 | 714
12:00 | 178 | 15 | 640 | 180 | 1826 | 692 | Sirajganj-Sreepur Ckt-2 | Export | 3333000
13:00 | 155 | 10 | 580 | 166 | 1848 | 640
14:00 | 136 | 17 | 550 | 164 | 1704 | 622 |  | Import | 0
15:00 | 150 | 25 | 530 | 150 | 1886 | 688
16:00 | 147 | 29 | 580 | 208 | 1940 | 704 | Gopalganj-Aminbazar Ckt-1 | Export | 22100000
17:00 | 141 | 25 | 560 | 192 | 1904 | 686
18:00 | 128 | 24 | 520 | 170 | 1768 | 632 |  | Import | 0
18:30 | 111 | 17 | 480 | 154 | 1794 | 608
19:00 | 92 | 9 | 460 | 160 | 1794 | 594 | Gopalganj-Aminbazar Ckt-2 | Export | 22160000
19:30 | 92 | 8 | 450 | 138 | 1860 | 574
20:00 | 95 | 9 | 450 | 144 | 1916 | 596 |  | Import | 0
21:00 | 86 | 9 | 410 | 138 | 1848 | 604
22:00 | 64 | 1 | 260 | 58 | 1834 | 550 |  | Total Export | 54570236.42
23:00 | 88 | 2 | 390 | 148 | 1860 | 588 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 19-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 377 | 07:00 | 358 | 16:00 | Madunaghat | 391 | 06:00 | 384 | 00:00
Amtali | 412 | 04:00 | 404 | 15:00 | Meghnaghat | 374 | 07:00 | 358 | 16:00
Ashuganj | 408 | 6:00 | 383 | 15:000 | Payra | 414 | 05:00 | 406 | 15:00
Bhulta | 399 | 05:00 | 373 | 16:00 | Rahanpur | 398 | 06:00 | 386 | 12:00
Bibiana | 392 | 07:00 | 381 | 16:00 | Rampal | 402 | 05:00 | 383 | 23:00
BIPTC | 404 | 06:00 | 394 | 00:00
Bogura | 385 | 06:00 | 372 | 13:00
Gopalganj | 397 | 21:00 | 376 | 23:00
Kaliakoir | 370 | 07:00 | 353 | 16:00
Korerhat | 385 | 06:00 | 376 | 16:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 06:00 | 220 | 13:00 | Jhenaidah | 231 | 03:00 | 211 | 19:00
AKSML | 230 | 22:00 | 221.8 | 00:00 | Kachua | 228 | 18:00 | 218 | 00:00
Aminbazar | 227 | 06:00 | 214 | 15:00 | Kaliakoir | 229 | 07:00 | 216 | 16:00
Ashuganj | 228 | 05:00 | 216 | 15:00 | Keranigonj | 225 | 06:00 | 209 | 16:00
Ashuganj-400 | 228 | 05:00 | 216 | 15:00 | Khulna(S) | 233 | 04:00 | 210 | 23:00
Baghabari | 231 | 06:00 | 221 | 12:00 | Korerhat | 228 | 18:00 | 221 | 00:00
Barapukuria | 217 | 05:00 | 211 | 13:00 | Madunaghat | 229 | 18:00 | 223 | 00:00
Barapukuria-230 | 217 | 05:00 | 211 | 13:00 | Madunaghat-400 | 230 | 19:00 | 224 | 00:00
Barishal | 226 | 06:00 | 216 | 16:00 | Maniknagar | 225 | 04:00 | 208 | 16:00
Bheramara | 233 | 03:00 | 222 | 12:00 | Meghnaghat | 231 | 05:00 | 221 | 16:00
Bhulta | 226 | 05:00 | 210 | 16:00 | Meghnaghat-400 | 229 | 07:00 | 213 | 16:00
Bibiana | 235 | 07:00 | 225 | 16:00 | Mirsorai | 227 | 20:00 | 218 | 00:00
BIPTC | 236 | 03:00 | 222 | 13:00 | Naogaon | 214 | 09:00 | 202 | 19:30
Bogura | 232 | 05:00 | 225 | 12:00 | Purbasadipur | 219 | 18:00 | 209 | 12:00
Bogura-400 | 231 | 05:00 | 224 | 13:00 | Rajshahi | 231 | 04:00 | 219 | 13:00
Borhanuddin | 230 | 04:00 | 224 | 13:00 | Rampal | 229 | 04:00 | 213 | 23:00
BSRM | 227 | 07:00 | 221 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 227 | 18:00 | 220 | 00:00 | Rampura | 226 | 06:00 | 207 | 16:00
Cumilla(N) | 225 | 08:00 | 215 | 16:00 | Shikalbaha | 229 | 20:00 | 221 | 00:00
Faridpur | 223 | 05:00 | 209 | 16:00 | Shyampur | 226 | 06:00 | 210 | 16:00
Fenchuganj | 235 | 07:00 | 227 | 20:00 | Siddhirganj | 227 | 05:00 | 212 | 13:00
Feni | 223 | 06:00 | 215 | 16:00 | Sirajgonj | 236 | 06:00 | 230 | 12:00
Ghorashal | 225 | 04:00 | 215 | 22:00 | Sreepur | 225 | 22:00 | 212 | 12:00
Ghorashal-230 | 223 | 06:00 | 208 | 15:00 | Tongi | 221 | 07:00 | 208 | 15:00
Gopalganj | 221 | 04:00 | 210 | 16:00
GPH | 228 | 04:00 | 222 | 12:00
Haripur | 226 | 06:00 | 210 | 16:00
Hasnabad | 225 | 05:00 | 210 | 16:00
Hathazari | 226 | 05:00 | 221 | 00:00
Ishurdi | 236 | 06:00 | 224 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 05:00 | 120 | 16:00 | Madunaghat | 132 | 06:00 | 128 | 16:00
Agargaon | 131 | 04:00 | 120 | 16:00 | Magura | 137 | 03:00 | 122 | 19:30
Agrabad | 131 | 07:00 | 125 | 15:00 | Mahasthangarh | 130 | 04:00 | 125 | 12:00
AKS | 129 | 07:00 | 124 | 00:00 | Maijdee | 128 | 18:30 | 122 | 00:00
Aminbazar | 130 | 07:00 | 119 | 16:00 | Manikganj | 130 | 07:00 | 124 | 00:00
Amnura | 134 | 06:00 | 125 | 00:00 | Maniknagar | 132 | 05:00 | 120 | 16:00
Ashuganj | ` | 06:00 | 127 | 16:00 | Matarbari | 119 | 18:00 | 106 | 19:30
Ashuganj-230 | 135 | 06:00 | 127 | 16:00 | Matuail | 130 | 07:00 | 121 | 16:00
Bagerhat | 129 | 05:00 | 112 | 23:00 | Metrorail_Motijheel | 132 | 05:00 | 120 | 16:00
Bajitpur | 130 | 06:00 | 118 | 15:00 | Metrorail_Uttara | 133 | 03:00 | 123 | 13:00
Bakerganj | 131 | 04:00 | 125 | 16:00 | Millgate | 133 | 03:00 | 122 | 15:00
Bakulia | 132 | 07:00 | 126 | 13:00 | Mirpur | 128 | 07:00 | 118 | 16:00
Banani | 133 | 04:00 | 119 | 16:00 | Mirzapur | 129 | 07:00 | 122 | 02:00
Bangabhaban | 132 | 04:00 | 120 | 13:00 | Mithapukur | 128 | 17:00 | 123 | 13:00
Barapukuria | 128 | 05:00 | 123 | 13:00 | MI_Cement | 129 | 05:00 | 119 | 18:30
Barguna | 131 | 05:00 | 126 | 16:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 04:00 | 123 | 13:00 | Mogbazar | 135 | 06:00 | 120 | 16:00
Barishal-230 | 131 | 04:00 | 124 | 13:00 | Mongla | 128 | 06:00 | 114 | 23:00
Baroaulia | 132 | 20:00 | 127 | 12:00 | Motijheel | 132 | 04:00 | 120 | 13:00
Baroirhat | 130 | 18:00 | 126 | 00:00 | Muktagacha | 125 | 07:00 | 112 | 23:00
Bashundhara | 133 | 03:00 | 120 | 15:00 | Munshiganj | 128 | 06:00 | 120 | 16:00
BashundharaCement | 129 | 04:00 | 123 | 12:00 | Muradnagar | 127 | 06:00 | 120 | 16:00
Beanibazar | 129 | 06:00 | 120 | 23:00 | Mymensingh | 126 | 22:00 | 112 | 16:00
Benapole | 132 | 05:00 | 111 | 23:00 | Nabinagar | 130 | 07:00 | 119 | 16:00
Bhaluka | 130 | 06:00 | 118 | 16:00 | Naogaon | 133 | 09:00 | 122 | 00:00
Bhandaria | 129 | 04:00 | 115 | 15:00 | Narail | 139 | 03:00 | 121 | 19:00
Bhangura | 133 | 05:00 | 125 | 12:00 | Narinda | 132 | 05:00 | 120 | 16:00
Bheramara | 136 | 03:00 | 129 | 22:00 | Narshingdi | 128 | 22:00 | 114 | 15:00
Bheramara(GK) | 136 | 01:00 | 129 | 22:00 | Natore | 133 | 06:00 | 126 | 12:00
Bhulta | 126 | 01:00 | 120 | 16:00 | Nawabganj | 132 | 06:00 | 121 | 16:00
Bog-Sherpur | 133 | 05:00 | 126 | 12:00 | Netrakona | 123 | 06:00 | 112 | 16:00
Bogura | 134 | 06:00 | 129 | 00:00 | New | 133 | 05:00 | 123 | 14:00
Bogura-230 | 134 | 05:00 | 129 | 12:00 | Niamatpur | 129 | 08:00 | 123 | 00:00
Brahmanbaria | 128 | 06:00 | 120 | 16:00 | Noapara | 134 | 04:00 | 116 | 23:00
Cantonment | 131 | 05:00 | 120 | 16:00 | Pabna | 134 | 06:00 | 124 | 12:00
Chandina | 130 | 06:00 | 124 | 16:00 | Palashbari | 128 | 04:00 | 121 | 12:00
Chandpur | 133 | 18:30 | 123 | 00:00 | Panchagarh | 133 | 01:00 | 126 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 132 | 06:00 | 128 | 15:00 | Patiya | 131 | 06:00 | 124 | 12:00
Chapai | 130 | 06:00 | 126 | 00:00 | Patuakhali | 131 | 04:00 | 126 | 00:00
Charsaidpur | 128 | 04:00 | 120 | 16:00 | Payra | 135 | 04:00 | 131 | 23:00
Chauddagram | 129 | 05:00 | 126 | 00:00 | PHP | 130 | 08:00 | 126 | 00:00
Chhatak | 129 | 07:00 | 117 | 19:00 | Postogola | 130 | 06:00 | 118 | 16:00
Chowmuhani | 127 | 08:00 | 123 | 00:00 | Pubail | 131 | 04:00 | 122 | 12:00
Chuadanga | 138 | 05:00 | 116 | 19:00 | Purbachal | 133 | 05:00 | 119 | 16:00
Coxsbazar | 119 | 09:00 | 108 | 19:30 | Purbasadipur | 129 | 18:00 | 123 | 12:00
Cumilla(N) | 130 | 06:00 | 124 | 16:00 | Rahanpur | 131 | 05:00 | 127 | 00:00
Cumilla(S) | 130 | 06:00 | 118 | 14:00 | Rahanpur-400 | 131 | 04:00 | 128 | 00:00
Daganbhuiyan | 130 | 18:00 | 125 | 00:00 | Rahim | 130 | 05:00 | 122 | 16:00
Daudkandi | 124 | 05:00 | 119 | 11:00 | Rajbari | 128 | 06:00 | 117 | 23:00
DhakaUniversity | 133 | 05:00 | 120 | 16:00 | Rajendrapur | 128 | 06:00 | 118 | 12:00
Dhamrai | 131 | 05:00 | 121 | 16:00 | Rajshahi | 132 | 06:00 | 124 | 12:00
Dhanmondi | 134 | 06:00 | 121.8 | 16:00 | Rajshahi-230 | 133 | 04:00 | 126 | 12:00
Dohazari | 128 | 06:00 | 120 | 13:00 | Ramganj | 129 | 18:00 | 120 | 00:00
Faridpur | 130 | 06:00 | 121 | 15:00 | Rampur | 131 | 04:00 | 124 | 15:00
Fatullah | 135 | 05:00 | 116 | 15:00 | Rampura | 134 | 06:00 | 120 | 16:00
Fenchuganj | 135 | 06:00 | 129 | 19:00 | Rangamati | 131 | 06:00 | 127 | 16:00
Feni | 130 | 08:00 | 126 | 00:00 | Rangpur | 127 | 05:00 | 123 | 13:00
Feni-230 | 131 | 06:00 | 127 | 00:00 | Ruppur | 135 | 02:00 | 129 | 21:00
Ghatail | 125 | 07:00 | 114 | 00:00 | Saidpur | 129 | 17:00 | 122 | 13:00
Ghorashal | 134 | 05:00 | 125 | 14:00 | Santhia | 133 | 03:00 | 127 | 12:00
Goalpara | 134 | 04:00 | 121 | 19:00 | Satkhira | 133 | 06:00 | 112 | 23:00
Gollamari | 135 | 06:00 | 121 | 23:00 | Satmasjid | 131 | 07:00 | 119 | 16:00
Gopalganj | 133 | 04:00 | 121 | 15:00 | Savar | 128 | 05:00 | 116 | 16:00
Gopalganj-400 | 132 | 04:00 | 124 | 16:00 | SevenRings | 134 | 06:00 | 123 | 16:00
Gulshan | 133 | 05:00 | 119 | 16:00 | ShahCement | 128 | 04:00 | 120 | 16:00
Halishahar | 131 | 05:00 | 125 | 12:00 | Shahjadpur | 135 | 02:00 | 130 | 11:00
Haripur | 130 | 04:00 | 122 | 16:00 | Shahjibazar | 127 | 06:00 | 119 | 16:00
HaripurSBU | 136 | 21:00 | 124 | 15:00 | Shahmirpur | 132 | 03:00 | 126 | 15:00
Hasnabad | 130 | 04:00 | 118 | 15:00 | Shariatpur | 132 | 05:00 | 120 | 15:00
Hathazari | 132 | 04:00 | 128 | 15:00 | Sherpur | 122 | 10:00 | 109 | 01:00
Hatirjheel | 133 | 05:00 | 120 | 16:00 | Shikalbaha | 123 | 04:00 | 117 | 15:00
Ishurdi | 137 | 03:00 | 130 | 23:00 | Shikalbaha-230 | 134 | 06:00 | 126 | 15:00
Jaldhaka | 126 | 19:00 | 119 | 23:00 | Shitalakhya | 129.2 | 06:00 | 114 | 16:00
Jamalpur | 125 | 10:00 | 113 | 02:00 | Sholosohor | 131 | 05:00 | 126 | 12:00
Jashore | 133 | 05:00 | 112 | 23:00 | Shomvuganj | 124 | 04:00 | 118 | 12:00
Jhenaidah | 139 | 03:00 | 118 | 21:00 | Shyampur | 134 | 06:00 | 125 | 12:00
Jhenaidah-230 | 139 | 03:00 | 122 | 19:00 | Shyampur-230 | 135 | 06:00 | 125 | 16:00
Joydebpur | 129 | 05:00 | 116 | 16:00 | Siddhirganj | 130 | 05:00 | 122 | 16:00
Joypurhat | 130 | 04:00 | 124 | 00:00 | Sirajganj | 132 | 04:00 | 122 | 12:00
Juldah | 132 | 03:00 | 126 | 12:00 | Sonargaon | 127 | 04:00 | 119 | 16:00
Kabirpur | 133 | 07:00 | 118 | 15:00 | Sreemongol | 129 | 06:00 | 121 | 16:00
Kachua | 130 | 18:00 | 123 | 00:00 | Sreepur | 131 | 06:00 | 122 | 12:00
Kaliakoir | 135 | 07:00 | 126 | 16:00 | Srinagar | 132 | 05:00 | 123 | 13:00
Kaliganj | 137 | 05:00 | 124 | 13:00 | SSM | 134 | 18:00 | 130 | 12:00
Kallyanpur | 129 | 07:00 | 120 | 14:00 | Sunamganj | 127 | 01:00 | 114 | 20:00
Kalurghat | 132 | 06:00 | 129 | 00:00 | Sylhet | 130 | 06:00 | 122 | 21:00
Kamrangirchar | 132 | 06:00 | 117 | 16:00 | Sylhet-132 | 129 | 07:00 | 123 | 19:00
Kaptai | N/A | N/A | N/A | N/A | Tangail | 125 | 07:00 | 116 | 12:00
Kasba | 126 | 06:00 | 119 | 16:00 | Taraganj | 128 | 09:00 | 121 | 07:00
Kazla | 132 | 07:00 | 120 | 16:00 | Tasnim | 128 | 05:00 | 120 | 15:00
Keranigonj | 133 | 06:00 | 122 | 16:00 | Thakurgaon | 132 | 19:00 | 123 | 13:00
Khagrachori | 131 | 08:00 | 127 | 00:00 | TK | 132 | 06:00 | 128 | 13:00
Khulna | 134 | 05:00 | 118 | 23:00 | Tongi | 135 | 07:00 | 126 | 15:00
Khulna(S) | 136 | 06:00 | 120 | 23:00 | Ullahpara | 133 | 04:00 | 124 | 12:00
Khulshi | 130 | 06:00 | 124 | 12:00 | Ullon | 136 | 06:00 | 120 | 16:00
Kishoreganj | 129 | 06:00 | 116 | 14:00 | Uttara | 134 | 06:00 | 120 | 15:00
Kodda | 132 | 18:00 | 125 | 01:00 | UttaraNew | 133 | 03:00 | 121 | 16:00
Korerhat | 131 | 06:00 | 127 | 16:00 | Zigatola | 133 | 06:00 | 121 | 16:00
KSRM | 132 | 01:00 | 126 | 12:00
Kulaura | 134 | 06:00 | 127 | 21:00
Kurigram | 131 | 18:00 | 116 | 23:00
Kushtia | 137 | 04:00 | 123 | 23:00
Laksam | 129 | 18:00 | 123 | 00:00
Lakshmipur | 127 | 18:00 | 121 | 00:00
Lalbag | 132 | 06:00 | 121 | 16:00
Lalmonirhat | 124 | 11:00 | 116 | 23:00
Madanganj | 129 | 04:00 | 123 | 12:00
Madaripur | 132 | 04:00 | 124 | 13:00
Madartek | 133 | 04:00 | 120 | 16:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division