## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 21-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-05-2026 | during | 21-05-2026 | during | 21-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 401 | 406 | 412 | 412 | 392 | 392 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 313 | 317 | 335 | 335 | 315 | 315 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 110 | 127 | 149.36 | 149.36 | 90 | 128 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17 | 18 | 33 | 33 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 21 | 21 | 21 | 14 | 14 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 48 | 24 | 52.19 | 52.19 | 25 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 260 | 145 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 131 | 132 | 149 | 149 | 133 | 133 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 52 | 105 | 105 | 50 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 54 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 14 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 470 | 375 | 584 | 584 | 490 | 490 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 297 | 186 | 718 | 718 | 310 | 310 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 142 | 142 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2509 | 2193 | 6048.22 | 6016.22 | 2437 | 2684
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 21 | 25.5 | 25.5 | 0 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 38 | 45 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 107 | 30 | 30 | 30 | 30 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 210 | 215 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 89 | 95 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 36 | 60 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 49 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 74 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 5 | 5 | 25 | 5 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 19 | 50 | 108 | 108 | 18 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.04 | 0 | 0 | 0 | 0 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 33 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 33 | 106 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 24 | 50 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 92 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 147 | 140 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1204 | 1204 | Can't Start AGC
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 12 | 3 | 12 | 12 | 12 | 12 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 930 | 1000 | 930 | 1000 | 930 | 1000 | AGC
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2826.04 | 3423.36 | 3713.86 | 3857.86 | 3033.36 | 3205.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 0 | 0 | 221.25 | 221.24 | 200 | 200 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 353 | 357 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 250 | 300 | 342.01 | 342.01 | 240 | 240 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 388 | 393 | 393 | 393 | 245 | 245 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 38 | 36 | 41.65 | 41.65 | 36 | 36 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 43 | 46 | 52.82 | 52.82 | 48 | 48 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 8 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 0 | 35 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 56 | 150 | 150 | 33 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 22 | 20 | 40 | 40 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 92 | 96 | 163 | 163 | 140 | 140 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 186 | 69 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 158 | 168 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 25 | 34 | 52.2 | 52.2 | 43 | 43 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 19 | 17.75 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 103 | 104 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 12 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 29 | 69 | 115 | 115 | 17 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 57 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1766 | 1822 | 2765.69 | 2696.43 | 1977.01 | 2084.01
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-05-2026 | during | 21-05-2026 | during | 21-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.5 | 0 | 2.25 | 0 | 2.25 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 92 | 115 | 90 | 90 | 90 | 90 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 12 | 10 | 10 | 10 | 10 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 48.34 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 16 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 167.84 | 139 | 381.25 | 334 | 164.25 | 129
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 0 | 0 | 30 | 30 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 147 | 142 | 163 | 163 | 147 | 147 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 152 | 154 | 155 | 155 | 155 | 155 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 22 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 84 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 100 | 102 | 102 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 16 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 230 | 308 | 250 | 250 | 250 | 250 | Plant availability less
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1052 | 1221 | 1214 | 1214 | 1164 | 1164
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 903 | 781 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 33 | 32 | 32 | 32 | 32 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 42 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 150 | 152 | 410 | 410 | 165 | 165 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 105 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 98.53 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 876 | 1100 | 617.1 | 617.1 | 550 | 550 | U-2 S/D
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2027.53 | 2213 | 2969.1 | 2879.1 | 1974.1 | 1884.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 793 | 1003 | 1244 | 1244 | 1245 | 1245 | RRT
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 110 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1108 | 1230 | 1244 | 1244 | 1184 | 1184 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 17 | 35 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 237 | 307 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.66 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2478.66 | 3044 | 3406 | 3405 | 3194 | 3211
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 36.49 | 0 | 52 | 0 | 52 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 19 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 150 | 140 | 214 | 214 | 161 | 161 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 150 | 140 | 220 | 220 | 160 | 160 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 380 | 360 | 413.79 | 413.79 | 372.41 | 372.41 | AGC
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 30 | 30 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 92 | 92 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.01 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1422 | 1448.43 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 50.61 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 91 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2285.11 | 2550.43 | 3226.57 | 3007.87 | 2728.19 | 2594.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 45 | 46 | 52 | 52 | 50 | 50 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 171 | 0 | 0 | 152 | 152 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 20 | 98 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.6 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 35 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 201 | 0 | 160.26 | 0 | 160.26 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 306.6 | 595 | 496.26 | 300 | 546.26 | 430
System Total |  |  |  |  | 28823.2 | 29270.237 | 15418.78 | 17200.79 | 24220.95 | 23710.48 | 17218.17 | 17385.96
Forecast Scenario (21-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15911 |  | 1389 |  | 17300
|  |  |  | 1:00 | 15643 |  | 1167 |  | 16810
|  |  |  | 2:00 | 15548 | 15548 | 592 |  | 16140
|  |  |  | 3:00 | 15430 | 15430 | 340 |  | 15770
|  |  |  | 4:00 | 15400 |  | 550 |  | 15950
|  |  |  | 5:00 | 14807 | 14807 | 83 |  | 14890
|  |  |  | 6:00 | 14330 | 14330 | 170 |  | 14500
|  |  |  | 7:00 | 13972 | 13972 | 408 |  | 14380
|  |  |  | 8:00 | 13894 |  | 406 |  | 14300
|  |  |  | 9:00 | 14132 |  | 478 |  | 14610
|  |  |  | 10:00 | 14577 |  | 363 |  | 14940
|  |  |  | 11:00 | 15022 |  | 388 |  | 15410
|  |  |  | 12:00 | 15415 |  | 485 |  | 15900
|  |  |  | 13:00 | 15349 |  | 721 |  | 16070
|  |  |  | 14:00 | 15491 |  | 659 |  | 16150
|  |  |  | 15:00 | 15610 |  | 760 |  | 16370
|  |  |  | 16:00 | 15143 |  | 857 |  | 16000
|  |  |  | 17:00 | 15182 |  | 948 |  | 16130
|  |  |  | 18:00 | 14932 |  | 918 |  | 15850
|  |  |  | 18:30 | 16216 |  | 134 |  | 16350
|  |  |  | 19:00 | 16850 |  | 280 |  | 17130
|  |  |  | 19:30 | 16900 |  | 830 |  | 17730
|  |  |  | 20:00 | 17150 |  | 590 |  | 17740
|  |  |  | 21:00 | 17200 |  | 600 |  | 17800
|  |  |  | 22:00 | 16698 |  | 1152 |  | 17850
|  |  |  | 23:00 | 15800 |  | 1400 |  | 17200
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 15900.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 600
Probable Maximum Demand at Evening Peak: |  |  | 17800.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 17200.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 361.34762 MKWHr. |  | 130 | 70 | 50 | 150 | 30 | 70 | 10 | 50 | 40 | 600
*** This report is generated digitally from Operation Information System (OIS) at 08:40 hrs on 21-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 20-05-2026 | [28 empty] | Date: | 20-05-2026 | [28 empty] | Date: | 20-05-2026 | [28 empty] | Date: | 20-05-2026 | [28 empty] | Date: | 20-05-2026 | [17 empty] | Date: | 20-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 93 | 24 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 284 | 35 | 0 | 132 | 131 | 260 | 55 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 94 | 18 | 20 | 0 | 420 | 77 | 120 | 35 | 0 | 0 | 48 | 63 | 23 | 24 | 37 | 0 | 30 | 68 | 20 | 890 | 108 | 0 | 50 | 0 | 89 | 218 | 0 | 0 | 0 | 1160 | 0 | 26 | 0 | 393 | 357 | 345 | 51 | 46 | 0 | 36 | 38 | 98 | 135 | 0 | 19 | 98 | 160 | 43 | 0 | 23 | 305 | 0 | 296 | 42 | 30 | 152 | 0 | 16 | 0 | 50 | 20 | 153 | 0 | 102 | 0 | 9 | 77 | 0 | 0 | 0 | 0 | 8490 | 762 | 136 | 0 | 27 | 38 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1191 | 0 | 0 | 0 | 1433 | 0 | 40 | 0 | 113 | 113 | 0 | 91 | 0 | 45 | 0 | 0 | 26 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 49 | 115 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 275 | 120 | 220 | 0 | 875 | 1175 | 72 | 7905 | 16395 | 75.42
01:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 242 | 0 | 0 | 132 | 131 | 260 | 55 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 142 | 18 | 20 | 0 | 370 | 110 | 16 | 19 | 0 | 0 | 16 | 63 | 37 | 24 | 37 | 0 | 30 | 71 | 21 | 840 | 148 | 0 | 50 | 0 | 90 | 218 | 0 | 0 | 0 | 1160 | 0 | 26 | 0 | 393 | 358 | 345 | 51 | 47 | 0 | 39 | 35 | 97 | 132 | 0 | 19 | 100 | 162 | 43 | 0 | 23 | 310 | 0 | 296 | 42 | 30 | 142 | 0 | 16 | 0 | 50 | 20 | 152 | 0 | 101 | 0 | 9 | 77 | 0 | 0 | 0 | 0 | 8254 | 904 | 136 | 0 | 25 | 36 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1191 | 0 | 0 | 0 | 1440 | 0 | 40 | 0 | 113 | 113 | 0 | 0 | 0 | 52 | 0 | 0 | 26 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 47 | 115 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 274 | 120 | 220 | 0 | 733 | 1120 | 17 | 7714 | 15968 | 75.42
02:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 209 | 0 | 0 | 132 | 78 | 260 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 0 | 0 | 142 | 18 | 20 | 0 | 345 | 110 | 16 | 18 | 0 | 0 | 0 | 63 | 54.36 | 24 | 25 | 0 | 30 | 92 | 18 | 835 | 142 | 0 | 50 | 0 | 88 | 218 | 0 | 0 | 0 | 1100 | 0 | 26 | 0 | 393 | 358 | 345 | 51 | 47 | 0 | 36 | 0 | 97 | 130 | 0 | 19 | 67 | 160 | 43 | 0 | 23 | 315 | 0 | 296 | 42 | 30 | 129 | 0 | 0 | 0 | 50 | 20 | 0 | 0 | 101 | 0 | 9 | 77 | 0 | 0 | 0 | 0 | 7762.36 | 904 | 135 | 0 | 25 | 36 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1190 | 0 | 0 | 0 | 1439 | 0 | 40 | 0 | 113 | 113 | 0 | 0 | 0 | 52 | 0 | 0 | 26 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 48 | 115 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 268 | 120 | 220 | 0 | 704 | 1060 | 17 | 7618 | 15380.36 | 75.42
03:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 283 | 0 | 0 | 132 | 45 | 260 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 18 | 20 | 0 | 440 | 110 | 16 | 19 | 0 | 14 | 0 | 63 | 54.36 | 24 | 25 | 0 | 30 | 98 | 20 | 865 | 0 | 0 | 50 | 0 | 89 | 218 | 0 | 0 | 0 | 1160 | 0 | 26 | 0 | 393 | 358 | 345 | 51 | 47 | 0 | 36 | 0 | 97 | 85 | 0 | 19 | 0 | 154 | 34 | 0 | 23 | 305 | 0 | 296 | 42 | 30 | 139 | 0 | 0 | 0 | 50 | 20 | 151 | 0 | 101 | 0 | 9 | 77 | 0 | 0 | 0 | 0 | 7922.36 | 904 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 1191 | 0 | 0 | 0 | 1448 | 0 | 0 | 0 | 50 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 49 | 115 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 276 | 120 | 180 | 0 | 704 | 990 | 17 | 7144 | 15066.36 | 75.42
04:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 280 | 0 | 0 | 132 | 0 | 260 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 142 | 18 | 20 | 0 | 435 | 109 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 25 | 0 | 30 | 95 | 20 | 860 | 0 | 0 | 50 | 0 | 90 | 218 | 0 | 0 | 0 | 1158 | 0 | 26 | 0 | 393 | 359 | 345 | 51 | 48 | 0 | 36 | 0 | 97 | 0 | 0 | 19 | 0 | 154 | 16 | 0 | 23 | 305 | 0 | 296 | 42 | 30 | 145 | 0 | 0 | 0 | 50 | 20 | 152 | 0 | 101 | 0 | 9 | 77 | 0 | 0 | 0 | 0 | 7602 | 904 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1192 | 0 | 0 | 0 | 1450 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 47 | 90 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 275 | 100 | 180 | 0 | 704 | 980 | 17 | 7011 | 14613 | 75.42
05:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 286 | 0 | 0 | 120 | 0 | 145 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 19 | 20 | 0 | 415 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 25 | 0 | 30 | 34 | 22 | 903 | 0 | 0 | 50 | 0 | 88 | 218 | 0 | 0 | 0 | 1158 | 0 | 26 | 0 | 393 | 358 | 345 | 51 | 47 | 0 | 36 | 0 | 97 | 0 | 0 | 19 | 0 | 152 | 0 | 0 | 0 | 315 | 0 | 296 | 42 | 30 | 151 | 0 | 0 | 0 | 50 | 20 | 152 | 0 | 102 | 0 | 9 | 77 | 0 | 0 | 0 | 0 | 7328 | 904 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1194 | 0 | 0 | 0 | 1450 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 48 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 274 | 120 | 220 | 0 | 703 | 1045 | 17 | 6971 | 14299 | 75.42
06:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 221 | 0 | 0 | 119 | 0 | 45 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 2 | 142 | 18 | 20 | 0 | 365 | 15 | 16 | 0 | 0 | 5 | 0 | 0 | 0 | 24 | 25 | 0.26 | 30 | 33 | 22 | 830 | 0 | 0 | 0 | 0 | 90 | 218 | 0 | 0 | 0 | 1158 | 0 | 26 | 0 | 393 | 358 | 345 | 51 | 47 | 0 | 36 | 0 | 97 | 0 | 0 | 19 | 0 | 134 | 0 | 5 | 0 | 300 | 0 | 296 | 42 | 30 | 127 | 0 | 5 | 0 | 50 | 20 | 152 | 0 | 102 | 0 | 9 | 77 | 0 | 0.04 | 0.15 | 0 | 6909.45 | 904 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.73 | 1190 | 0 | 0 | 0 | 1438 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 3.08 | 5 | 0 | 0 | 1.86 | 140 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0.2 | 0 | 47 | 50 | 1 | 49 | 0 | 0 | 0 | 0 | 3 | 0.04 | 14 | 274 | 120 | 220 | 0 | 703 | 1150 | 17 | 7076.91 | 13986.36 | 75.42
07:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 211 | 0 | 0 | 115 | 45 | 45 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 1 | 142 | 18 | 20 | 0 | 350 | 13 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 25 | 0.97 | 30 | 34 | 22 | 833 | 0 | 0 | 0 | 0 | 90 | 217 | 0 | 0 | 0 | 1140 | 2 | 26 | 0 | 393 | 358 | 345 | 51 | 45 | 0 | 36 | 0 | 97 | 14 | 0 | 19 | 0 | 136 | 1 | 15 | 0 | 300 | 0 | 296 | 42 | 30 | 128 | 0 | 5 | 0 | 50 | 30 | 154 | 0 | 102 | 0 | 9 | 77 | 0 | 0.17 | 1.05 | 0 | 6936.19 | 904 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1195 | 0 | 0 | 0 | 1433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.62 | 16 | 0 | 0 | 9.08 | 140 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 1.02 | 0 | 46 | 0 | 6 | 0 | 0 | 0 | 0 | 1.4 | 27 | 0.14 | 0 | 269 | 120 | 220 | 0 | 703 | 1158 | 0 | 6979.26 | 13915.45 | 75.42
08:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 228 | 0 | 0 | 131 | 45 | 45 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 9 | 142 | 18 | 21 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 25 | 1.94 | 30 | 33 | 7 | 835 | 0 | 0 | 0 | 0 | 89 | 216 | 0 | 0 | 0 | 1160 | 0 | 28 | 0 | 393 | 358 | 300 | 51 | 45 | 0 | 38 | 0 | 97 | 47 | 0 | 19 | 0 | 142 | 8 | 34 | 0 | 295 | 0 | 296 | 42 | 30 | 123 | 1 | 0 | 0 | 50 | 30 | 153 | 0 | 103 | 0 | 9 | 76 | 0 | 0.06 | 5.31 | 0 | 7017.31 | 904 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 1092 | 0 | 0 | 0 | 1466.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.17 | 25 | 0 | 0 | 14.81 | 140 | 0 | 140 | 0 | 0 | 0 | 350 | 0 | 2.01 | 0 | 46 | 0 | 9 | 0 | 0 | 0 | 0 | 2.7 | 45 | 0.31 | 0 | 247 | 120 | 220 | 0 | 702 | 1143 | 0 | 6880.64 | 13897.95 | 75.42
09:00 | 0 | 75 | 18 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 218 | 0 | 0 | 131 | 45 | 150 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 306 | 0 | 0 | 20 | 142 | 17 | 21 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 25 | 2.84 | 30 | 34 | 0 | 930 | 4 | 0 | 0 | 0 | 90 | 213 | 0 | 0 | 0 | 1160 | 11 | 6 | 0 | 350 | 358 | 270 | 5 | 45 | 0 | 39 | 2 | 96 | 52 | 0 | 19 | 15 | 152 | 8 | 44 | 0 | 305 | 0 | 334 | 42 | 30 | 141 | 4 | 8 | 0 | 50 | 25 | 153 | 0 | 101 | 0 | 9 | 77 | 0 | 0.4 | 3.08 | 0 | 7220.32 | 903 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 997 | 0 | 0 | 0 | 1459.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6 | 39 | 0 | 0 | 18.02 | 140 | 0 | 140 | 0 | 0 | 0 | 350 | 0 | 4.12 | 0 | 45 | 0 | 7 | 0 | 0 | 0 | 0 | 2.9 | 180 | 0.18 | 0 | 224 | 120 | 220 | 0 | 729 | 1100 | 0 | 6914.99 | 14135.31 | 75.42
10:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 283 | 0 | 0 | 131 | 45 | 260 | 55 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 15 | 142 | 17 | 20 | 0 | 440 | 0 | 0 | 0 | 0 | 3 | 0 | 14 | 0 | 24 | 24 | 3.25 | 30 | 33 | 0 | 882 | 34 | 0 | 0 | 2 | 88 | 212 | 0 | 0 | 0 | 1160 | 17 | 0 | 0 | 350 | 359 | 270 | 0 | 44 | 0 | 35 | 17 | 94 | 105 | 0 | 15 | 32 | 152 | 25 | 63 | 17 | 305 | 0 | 320 | 42 | 30 | 145 | 7 | 8 | 0 | 50 | 25 | 154 | 0 | 102 | 6 | 9 | 82 | 0 | 1 | 19.51 | 0 | 7703.76 | 904 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 954 | 0 | 0 | 0 | 1440.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.03 | 92 | 0 | 0 | 41.32 | 130 | 0 | 130 | 0 | 0 | 0 | 393 | 0 | 0 | 0 | 48 | 0 | 29 | 0 | 0 | 0 | 0 | 4.4 | 74 | 0.51 | 0 | 234 | 120 | 220 | 0 | 756 | 1070 | 0 | 6875.47 | 14579.23 | 75.42
11:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 284 | 0 | 0 | 131 | 45 | 260 | 55 | 35 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 14 | 142 | 17 | 20 | 0 | 440 | 0 | 0 | 16 | 0 | 7 | 0 | 14 | 0 | 24 | 24 | 2.55 | 30 | 34 | 0 | 887 | 114 | 0 | 0 | 8 | 90 | 211 | 0 | 0 | 0 | 1224 | 17 | 0 | 0 | 370 | 352 | 270 | 0 | 44 | 0 | 32 | 18 | 92 | 169 | 2 | 11 | 50 | 170 | 25 | 28 | 22 | 310 | 0 | 308 | 42 | 30 | 150 | 6 | 8 | 0 | 50 | 25 | 152 | 0 | 101 | 17 | 9 | 82 | 0 | 1.2 | 37.81 | 0 | 8030.56 | 903 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.56 | 947 | 0 | 0 | 0 | 1427.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.97 | 82 | 0 | 0 | 30.06 | 130 | 0 | 130 | 0 | 0 | 0 | 391 | 0 | 5.39 | 0 | 49 | 0 | 9 | 0 | 0 | 0 | 0 | 5.2 | 167 | 0.15 | 0 | 251 | 120 | 180 | 0 | 778 | 1105 | 0 | 6995.57 | 15026.13 | 75.42
12:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 297 | 17 | 0 | 131 | 110 | 260 | 55 | 35 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 34 | 142 | 17 | 20 | 0 | 470 | 0 | 0 | 19 | 0 | 12 | 0 | 36 | 0 | 24 | 24 | 2.04 | 30 | 33 | 0 | 930 | 147 | 0 | 38 | 8 | 89 | 210 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 388 | 353 | 250 | 0 | 43 | 0 | 38 | 29 | 92 | 186 | 9 | 13 | 103 | 158 | 25 | 57 | 22 | 310 | 0 | 230 | 42 | 30 | 147 | 10 | 8 | 0 | 0 | 22 | 152 | 0 | 101 | 16 | 9 | 92 | 0 | 2.5 | 48.34 | 0 | 8320.88 | 903 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.53 | 876 | 0 | 0 | 0 | 1422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.49 | 91 | 0 | 0 | 50.61 | 150 | 0 | 150 | 0 | 0 | 0 | 380 | 0 | 5.01 | 0 | 45 | 0 | 34 | 20 | 0 | 0 | 0 | 6.6 | 201 | 0.66 | 0 | 237 | 120 | 220 | 0 | 793 | 1108 | 0 | 7097.9 | 15418.78 | 75.42
13:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 255 | 17 | 0 | 131 | 126 | 260 | 55 | 35 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 30 | 142 | 17 | 20 | 0 | 380 | 0 | 0 | 18 | 0 | 19 | 0 | 36 | 0 | 24 | 24 | 3.86 | 30 | 34 | 0 | 930 | 145 | 0 | 45 | 8 | 89 | 211 | 0 | 0 | 0 | 1224 | 16 | 0 | 0 | 389 | 354 | 280 | 0 | 41 | 0 | 37 | 17 | 92 | 187 | 9 | 13 | 109 | 170 | 25 | 60 | 21 | 305 | 0 | 232 | 42 | 30 | 146 | 11 | 0 | 0 | 0 | 20 | 154 | 0 | 101 | 17 | 9 | 90 | 0 | 2.1 | 41.69 | 0 | 8250.65 | 904 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.58 | 871 | 0 | 0 | 0 | 1409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.62 | 103 | 0 | 0 | 39.99 | 169 | 0 | 190 | 0 | 0 | 0 | 350 | 0 | 4.93 | 0 | 48 | 30 | 31 | 34 | 0 | 0 | 0 | 2.8 | 140 | 0.22 | 0 | 240 | 120 | 220 | 0 | 774 | 1145 | 0 | 7104.14 | 15354.79 | 75.42
14:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 283 | 17 | 4 | 130 | 127 | 260 | 55 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 25 | 142 | 17 | 20 | 0 | 450 | 6 | 0 | 18 | 0 | 23 | 0 | 36 | 0 | 24 | 24 | 3.4 | 30 | 33 | 0 | 930 | 145 | 0 | 45 | 0 | 91 | 210 | 0 | 0 | 0 | 1224 | 14 | 0 | 0 | 380 | 342 | 280 | 0 | 41 | 0 | 37 | 17 | 92 | 186 | 8 | 13 | 107 | 176 | 28 | 63 | 21 | 310 | 0 | 226 | 42 | 30 | 143 | 9 | 0 | 0 | 0 | 20 | 152 | 0 | 102 | 17 | 9 | 93 | 0 | 1.8 | 27.28 | 0 | 8279.48 | 903 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 75.4 | 974 | 0 | 0 | 0 | 1407 | 0 | 0 | 0 | 0 | 7 | 0 | 8 | 0 | 0 | 43.08 | 93 | 0 | 0 | 47.85 | 140 | 0 | 140 | 0 | 0 | 0 | 388 | 0 | 4.31 | 0 | 49 | 50 | 27 | 50 | 0 | 0 | 0 | 1.9 | 166 | 0.54 | 0 | 224 | 120 | 220 | 0 | 758 | 1123 | 0 | 7216.08 | 15495.56 | 75.42
15:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 287 | 0 | 17 | 130 | 126 | 260 | 55 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 8 | 142 | 17 | 20 | 0 | 470 | 15 | 0 | 18 | 0 | 21 | 0 | 36 | 0 | 24 | 24 | 2.87 | 30 | 34 | 0 | 933 | 148 | 0 | 44 | 3 | 89 | 210 | 0 | 0 | 0 | 1224 | 12 | 0 | 0 | 380 | 345 | 280 | 0 | 43 | 0 | 37 | 17 | 92 | 182 | 8 | 19 | 106 | 176 | 25 | 43 | 20 | 300 | 0 | 266 | 42 | 30 | 149 | 3 | 0 | 0 | 0 | 20 | 152 | 0 | 100 | 17 | 9 | 82 | 0 | 1.3 | 28.25 | 0 | 8289.42 | 904 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 49.49 | 1000 | 0 | 0 | 0 | 1448 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 29.77 | 65 | 0 | 0 | 23.43 | 140 | 0 | 140 | 0 | 0 | 0 | 391 | 0 | 3.14 | 0 | 47 | 70 | 21 | 54 | 0 | 0 | 0 | 2.4 | 118 | 0.24 | 0 | 248 | 120 | 220 | 0 | 802 | 1130 | 0 | 7324.47 | 15613.89 | 75.42
16:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 256 | 0 | 17 | 80 | 125 | 145 | 55 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 12 | 142 | 17 | 19 | 0 | 390 | 15 | 0 | 18 | 0 | 18 | 0 | 40 | 0 | 24 | 24 | 1.96 | 30 | 33 | 0 | 930 | 150 | 0 | 44 | 8 | 87 | 212 | 0 | 0 | 0 | 1224 | 6 | 0 | 0 | 385 | 350 | 280 | 0 | 42 | 0 | 37 | 16 | 94 | 60 | 8 | 19 | 107 | 168 | 34 | 30 | 20 | 310 | 0 | 312 | 42 | 30 | 147 | 4 | 0 | 0 | 0 | 20 | 153 | 0 | 100 | 17 | 9 | 85 | 0 | 0.85 | 22.59 | 0 | 7940.4 | 903 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 6.01 | 1008 | 0 | 0 | 0 | 1425 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 16.97 | 38 | 0 | 0 | 17.91 | 140 | 0 | 140 | 0 | 0 | 0 | 346 | 0 | 0.64 | 0 | 46 | 70 | 14 | 70 | 0 | 0 | 0 | 3.5 | 88 | 0.23 | 0 | 255 | 120 | 220 | 0 | 793 | 1170 | 0 | 7208.26 | 15148.66 | 75.42
17:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 293 | 0 | 17 | 60 | 125 | 95 | 52 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 310 | 0 | 0 | 6 | 142 | 19 | 19 | 0 | 460 | 15 | 0 | 18 | 0 | 10 | 0 | 57 | 0 | 24 | 24 | 0.84 | 30 | 33 | 3 | 930 | 153 | 0 | 45 | 8 | 97 | 213 | 0 | 0 | 0 | 1224 | 3 | 0 | 0 | 380 | 343 | 280 | 0 | 42 | 0 | 34 | 17 | 93 | 52 | 8 | 19 | 106 | 158 | 34 | 12 | 20 | 315 | 0 | 312 | 42 | 30 | 142 | 2 | 8 | 0 | 86 | 25 | 150 | 0 | 100 | 17 | 9 | 85 | 0 | 0.43 | 10.28 | 8 | 8049.55 | 904 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 18.78 | 1004 | 0 | 0 | 0 | 1382 | 0 | 40 | 0 | 0 | 70 | 0 | 51 | 3 | 0 | 9.68 | 19 | 3 | 0 | 9.2 | 140 | 0 | 140 | 0 | 0 | 0 | 389 | 0 | 0.89 | 0 | 46 | 70 | 7 | 70 | 0 | 0 | 0 | 0.4 | 48 | 0.15 | 0 | 236 | 120 | 220 | 0 | 769 | 1120 | 0 | 7137.1 | 15186.65 | 75.42
18:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 209 | 0 | 17 | 60 | 125 | 97 | 41 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 313 | 0 | 0 | 0 | 142 | 19 | 19 | 0 | 350 | 15 | 15 | 26 | 0 | 4 | 0 | 60 | 0 | 32 | 30 | 0.08 | 30 | 36 | 8 | 1000 | 148 | 0 | 45 | 9 | 96 | 214 | 0 | 0 | 0 | 1224 | 1 | 0 | 0 | 393 | 355 | 280 | 0 | 43 | 0 | 38 | 17 | 94 | 50 | 14 | 19 | 108 | 158 | 34 | 3 | 20 | 310 | 0 | 306 | 42 | 30 | 140 | 0 | 8 | 0 | 86 | 30 | 150 | 0 | 100 | 17 | 9 | 85 | 0 | 0.03 | 2.16 | 12 | 7908.27 | 903 | 145 | 0 | 16 | 20 | 0 | 0 | 0 | 0 | 0 | 105 | 3.73 | 1001 | 0 | 0 | 0 | 1306.06 | 0 | 40 | 0 | 20 | 70 | 0 | 100 | 10 | 8 | 0.4 | 7 | 15 | 0 | 0.32 | 140 | 0 | 140 | 0 | 0 | 0 | 321 | 0 | 0.04 | 18 | 45 | 80 | 1 | 80 | 0 | 0 | 0 | 0.1 | 9 | 0.02 | 1 | 192 | 120 | 220 | 0 | 778 | 1108 | 2 | 7025.67 | 14933.94 | 75.42
19:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 290 | 35 | 17 | 78 | 125 | 97 | 45 | 55 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 142 | 19 | 19 | 0 | 410 | 30 | 20 | 48 | 0 | 0 | 32 | 60 | 16 | 36 | 36 | 0 | 30 | 71 | 9 | 1000 | 145 | 0 | 45 | 21 | 95 | 214 | 0 | 0 | 0 | 1224 | 0 | 12 | 0 | 390 | 356 | 280 | 4 | 45 | 0 | 39 | 54 | 96 | 51 | 17 | 19 | 107 | 180 | 34 | 0 | 20 | 310 | 0 | 313 | 42 | 30 | 138 | 0 | 8 | 0 | 86 | 25 | 151 | 0 | 100 | 0 | 9 | 85 | 0 | 0 | 0 | 12 | 8347 | 877 | 145 | 0 | 32 | 36 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1063 | 0 | 0 | 0 | 1471.36 | 0 | 40 | 0 | 100 | 90 | 0 | 100 | 17 | 48 | 0 | 0 | 24 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 379 | 0 | 0 | 113 | 47 | 115 | 0 | 94 | 0 | 70 | 0 | 0 | 0 | 0 | 52 | 239 | 120 | 220 | 0 | 899 | 1040 | 54 | 7870.36 | 16217.36 | 75.42
19:30 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 263 | 35 | 17 | 131 | 127 | 130 | 55 | 55 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 317 | 0 | 0 | 0 | 142 | 19 | 19 | 0 | 400 | 92 | 23 | 50 | 0 | 0 | 49 | 60 | 54.3 | 36 | 36 | 0 | 30 | 97 | 3 | 1000 | 150 | 0 | 45 | 25.5 | 96 | 214 | 0 | 0 | 0 | 1224 | 0 | 12 | 0 | 393 | 359 | 280 | 10 | 45 | 0 | 39 | 70 | 96 | 51 | 17 | 19 | 106 | 174 | 34 | 0 | 21 | 315 | 0 | 309 | 42 | 30 | 142 | 0 | 8 | 0 | 86 | 25 | 153 | 0 | 100 | 0 | 9 | 86 | 0 | 0 | 0 | 12 | 8603.8 | 876 | 145 | 0 | 37 | 52 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1156 | 0 | 0 | 0 | 1449.89 | 0 | 40 | 0 | 113 | 113 | 0 | 100 | 17 | 52 | 0 | 0 | 25 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 358 | 0 | 0 | 86 | 45 | 115 | 0 | 98 | 0 | 165 | 0 | 0 | 0 | 0 | 110 | 307 | 120 | 220 | 0 | 899 | 1180 | 54 | 8317.89 | 16921.69
20:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 235 | 35 | 17 | 132 | 125 | 130 | 55 | 55 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 318 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 380 | 91 | 20 | 51 | 0 | 0 | 49 | 60 | 54.36 | 36 | 36 | 0 | 30 | 107 | 8 | 1000 | 150 | 0 | 45 | 20 | 96 | 214 | 0 | 0 | 0 | 1224 | 0 | 12 | 8 | 393 | 359 | 280 | 20 | 45 | 0 | 39 | 69 | 96 | 51 | 16 | 19 | 104 | 166 | 34 | 0 | 21 | 315 | 0 | 308 | 42 | 30 | 136 | 0 | 16 | 0 | 85 | 26 | 150 | 0 | 100 | 0 | 9 | 87 | 0 | 0 | 0 | 12 | 8572.36 | 781 | 150 | 0 | 33 | 45 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1190 | 0 | 0 | 0 | 1456.82 | 0 | 40 | 0 | 113 | 113 | 0 | 100 | 19 | 52 | 0 | 0 | 25 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 338 | 0 | 0 | 104 | 47 | 115 | 0 | 99 | 0 | 165 | 0 | 0 | 0 | 0 | 110 | 307 | 120 | 220 | 0 | 926 | 1180 | 54 | 8287.82 | 16860.18 | 75.42
21:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 186 | 35 | 14 | 132 | 127 | 145 | 55 | 55 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 317 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 375 | 92 | 33 | 50 | 0 | 3 | 49 | 60 | 54.36 | 74 | 50 | 0 | 107 | 106 | 5 | 1000 | 140 | 0 | 45 | 21 | 95 | 215 | 0 | 0 | 0 | 1224 | 0 | 56 | 8 | 393 | 357 | 300 | 35 | 46 | 0 | 36 | 69 | 96 | 69 | 12 | 19 | 104 | 168 | 34 | 0 | 20 | 315 | 0 | 308 | 42 | 30 | 142 | 0 | 16 | 0 | 84 | 30 | 154 | 0 | 100 | 0 | 12 | 115 | 0 | 0 | 0 | 12 | 8798.36 | 781 | 152 | 0 | 33 | 42 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1100 | 0 | 0 | 0 | 1448.43 | 0 | 40 | 0 | 113 | 113 | 0 | 100 | 19 | 52 | 0 | 0 | 25 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 360 | 0 | 0 | 171 | 46 | 115 | 0 | 98 | 0 | 165 | 0 | 0 | 0 | 0 | 110 | 307 | 120 | 220 | 0 | 1003 | 1230 | 54 | 8402.43 | 17200.79 | 75.42
22:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 296 | 35 | 14 | 132 | 127 | 145 | 55 | 55 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 305 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 460 | 89 | 23 | 50 | 0 | 2 | 32 | 62 | 54.36 | 74 | 60 | 0 | 30 | 105 | 13 | 1000 | 141 | 0 | 44 | 8 | 93 | 215 | 0 | 0 | 0 | 1224 | 0 | 30 | 8 | 350 | 355 | 260 | 51 | 47 | 0 | 36 | 65 | 96 | 171 | 16 | 19 | 107 | 154 | 34 | 0 | 21 | 305 | 0 | 308 | 42 | 30 | 145 | 0 | 16 | 0 | 85 | 30 | 152 | 0 | 102 | 0 | 37 | 115 | 0 | 0 | 0 | 0 | 8879.36 | 781 | 150 | 0 | 33 | 39 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 617 | 0 | 0 | 0 | 1440.82 | 0 | 40 | 0 | 113 | 113 | 0 | 100 | 17 | 25 | 0 | 0 | 25 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 403 | 0 | 0 | 169 | 48 | 115 | 0 | 98 | 0 | 165 | 0 | 0 | 0 | 0 | 110 | 307 | 120 | 220 | 0 | 1164 | 1244 | 54 | 8095.82 | 16975.18 | 75.42
23:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 320 | 35 | 0 | 82 | 127 | 145 | 55 | 55 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 295 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 440 | 97 | 23 | 50 | 0 | 0 | 49 | 62 | 54.36 | 74 | 60 | 0 | 30 | 106 | 18 | 930 | 148 | 0 | 44 | 8 | 100 | 215 | 0 | 0 | 0 | 1224 | 0 | 30 | 8 | 350 | 352 | 260 | 51 | 46 | 0 | 39 | 51 | 96 | 187 | 17 | 8 | 105 | 144 | 34 | 0 | 22 | 310 | 0 | 308 | 42 | 30 | 152 | 0 | 8 | 0 | 85 | 25 | 152 | 0 | 100 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 8698.36 | 781 | 145 | 0 | 30 | 39 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 503 | 0 | 0 | 0 | 1446.61 | 0 | 40 | 0 | 113 | 113 | 0 | 100 | 17 | 25 | 0 | 0 | 25 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 400 | 0 | 0 | 192 | 47 | 115 | 0 | 98 | 0 | 165 | 0 | 0 | 0 | 0 | 110 | 295 | 120 | 220 | 0 | 1180 | 1242 | 54 | 8000.61 | 16698.97 | 75.42
Total KWH | 0 | 2054400 | 711360 | 0 | 0 | 0 | 0 | 0 | 9237600 | 0 | 6691750 | 259560 | 154080 | 2749680 | 2092800 | 4169607 | 1297336 | 443118 | 804960 | 0 | 0 | 0 | 0 | 0 | 269961 | 7344740 | 0 | 0 | 199676 | 3480000 | 433800 | 480960 | 0 | 10080000 | 1087691 | 303600 | 522240 | 0 | 131040 | 273528 | 843120 | 479525 | 760320 | 712320 | 28402 | 744200 | 1533884 | 240960 | 21992727.27 | 2463927 | 0 | 858240 | 143530.2 | 2245635 | 5034298 | 0 | 0 | 0 | 28696361 | 112725 | 501818 | 33455 | 9184500 | 8853300 | 7276000 | 693644 | 1073760 | 0 | 887400 | 563520 | 2276521 | 2425440 | 153720 | 435280 | 1689480 | 3797760 | 611582 | 412327 | 408368 | 7476000 | 0 | 7221000 | 999000 | 723720 | 3398563.64 | 61859 | 147792 | 0 | 1237440 | 554112 | 3524000 | 0 | 2422900 | 151920 | 261600 | 2016000 | 0 | 11700 | 231470 | 59520 | 193940133.11 | 21261091 | 3641184 | 0 | 232800 | 303488 | 0 | 0 | 0 | 0 | 0 | 1359648 | 519840 | 24254543 | 0 | 0 | 0 | 34473869 | 0 | 372621 | 0 | 986784 | 1517184 | 0 | 721440 | 100916 | 315946 | 310392 | 677080 | 204010 | 0 | 328176 | 3460455 | 0 | 3693200 | 0 | 0 | 0 | 9166545 | 0 | 28800 | 833000 | 1093963 | 1631237 | 195264 | 1449619 | 0 | 854280 | 0 | 38781.96 | 1241280 | 3933 | 1087488 | 6328000 | 2686000 | 5238350 | 0 | 19665454 | 27585454.55 | 435600 | 178297716.51 | 372237849.62

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 20-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 15418.78 | MW | 12:00 Hr. | Energy Generated |  |  | 372.2378 |  | MKWHr.
| Day Peak Demand |  |  | 15733.78 | MW | 12:00 Hr. | Energy Unserverd |  |  | 8.876 |  | MKWHr.
| Evening Peak Generation |  |  | 17200.79 | MW | 21:00 Hr. | Energy Demand |  |  | 381.1138 |  | MKWHr.
| Evening Peak Demand |  |  | 17610.79 | MW | 21:00 Hr. | Maximum Temperature |  |  | 36.2 |  | °C
| Minimum Generation of the Day |  |  | 13897.95 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 904.94 |  | MMCFD
| Maximum Generation of the Day |  |  | 17200.79 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.9871 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.2689 | 0 | 18.4869 | 0 | 0 | 0.19968 | 0 | 0 | 52.9554 | Gas | 125.8482 | Gas | 440204728.1988
| Chattogram Zone |  |  | 5.2753 | 50.6891 | 12.2276 | 0 | 0.7442 | 0.14113 | 0 | 0.13104 | 69.2083 | Coal | 130.4495 | Coal | 853304762.3856
| Cumilla Zone |  |  | 30.7139 | 0 | 6.3539 | 0 | 0 | 0.41233 | 3.7978 | 0 | 41.2779 | HFO | 50.2762 | HFO | 858771515.064
| Mymensingh Zone |  |  | 0 | 0 | 2.489 | 0 | 0 | 0.24317 | 0 | 0 | 2.7322 | HSD | 0.85428 | HSD | 26380166.4
| Sylhet Zone |  |  | 27.7045 | 0 | 0 | 0 | 0 | 0.061859 | 0 | 0 | 27.7664 | Hydro | 0.7442 | Hydro | 74420
| Khulna Zone |  |  | 3.6412 | 24.2545 | 1.8959 | 0 | 0 | 0.51984 | 21.2611 | 0 | 51.5726 | Solar | 4.4017 | Solar | 71067598.5392
| Barishal Zone |  |  | 7.9243 | 53.5789 | 1.5231 | 0 | 0 | 0.003933 | 0 | 0 | 63.0303 | Import | 59.5327 | Import | 349133381.24
| Rajshahi Zone |  |  | 16.3202 | 0 | 4.2189 | 0 | 0 | 1.3444 | 34.4739 | 0 | 56.3574 | Wind | 0.13104 | Wind | 1927598.4
| Rangpur Zone |  |  | 0 | 1.927 | 3.0809 | 0.85428 | 0 | 1.4753 | 0 | 0 | 7.3374
| Total |  |  | 125.8482 | 130.4495 | 50.2762 | 0.85428 | 0.7442 | 4.4017 | 59.5327 | 0.13104 | 372.2378
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 440204728.1988 |  | Hydro | 74420
|  |  |  | Coal | 853304762.3856 |  | Solar | 71067598.5392
|  |  |  | HFO | 858771515.064 |  | Import | 349133381.24
|  |  |  | HSD | 26380166.4 |  | Wind | 1927598.4
[5 empty] | Total: | 260,08,64,170 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.2611 | Peak Hr Flow | 781.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 53617309.09 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 34.4739 | Peak Hr Flow | 1448.43 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2496 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.7978 | Peak Hr Flow | 168.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2661 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 59.5327 | Peak Hr Flow | 2397.43 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 70 |  | 6283
|  |  |  | Chattogram |  | 0 |  | 1682
|  |  |  | Cumilla |  | 40 |  | 1661
|  |  |  | Mymensingh |  | 220 |  | 1214
|  |  |  | Sylhet |  | 0 |  | 678
|  |  |  | Khulna |  | 62 |  | 2120
|  |  |  | Barishal |  | 0 |  | 533
|  |  |  | Rajshahi |  | 0 |  | 1821
|  |  |  | Rangpur |  | 0 |  | 1137
|  |  |  | Total |  | 392 |  | 17129
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:00 | Shahjibazar 132/33kV S/S TR-04 HT is restored.
|  | 08:02 | Shahjibazar 132/33kV S/S TR-04 LT is restored.
|  | 08:14 | Bhaluka 132/33kV S/S 02. Transformer- 02 HT is restored.
|  | 08:15 | Bhaluka 132/33kV S/S 02. Transformer- 02 LT is restored.
|  | 08:20 | Rangpur 132/33kV S/S T-1(414T) HT is restored.
| 08:21 | 08:55 | Bhaluka 132/33kV S/S 03. Transformer-03 LT Scheduled S/D Due to High temp. maientence. | [7 empty] | 23.0MW load
interrup.
|  | 08:21 | Rangpur 132/33kV S/S T-1(414T) LT is restored.
| 08:22 | 08:54 | Bhaluka 132/33kV S/S 03. Transformer-03 HT Scheduled S/D Due to High temperature
maintenance.
| 08:35 | 09:47 | Faridpur 132/33kV S/S ATR-1 LT Scheduled S/D
| 08:36 | 09:46 | Faridpur 132/33kV S/S ATR-1 HT Scheduled S/D
| 08:44 | 16:56 | Gopalganj(N)-Madaripur 132kV Ckt-1 Scheduled S/D from Gopalganj 400/132kV end Due to
None
| 08:44 | 16:56 | Gopalganj(N)-Madaripur 132kV Ckt-2 Scheduled S/D from Gopalganj 400/132kV end.
|  | 08:49 | Barishal 230/132kV S/S T-5 HT is restored.
|  | 08:50 | Barishal 230/132kV S/S T-5 LT is restored.
|  | 09:01 | Narshingdi 132/33kV S/S T-2 HT is restored.
|  | 09:03 | Narshingdi 132/33kV S/S T-2 LT is restored.
| 09:57 | 12:28 | Ishwardi-Rooppur 132kV Ckt-2 Project Work S/D from Ishurdi 132/33kV end.
| 10:21 | 16:45 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-1 Project Work S/D Due to Project
work
| 10:21 | 16:45 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Project Work S/D Due to Project
work
| 10:35 |  | 230kV Bhola - Char Fasson- ckt 1 and 2 tripped.
| 10:41 | 12:47 | Chandraghona-Kaptai 132 kV Ckt-2 Forced S/D from Chandraghona 132/33kV end Due to
Emergency ROW
| 10:44 | 20:20 | BSRM-Cumilla(N) 230 kV Ckt-1 Project Work S/D from Feni 230/132kV end Due to Witness of
SAS and DFDR work
| 10:45 | 20:10 | Korerhat 400/230/132kV S/S Feni -1 Project Work S/D Due to For project work
| 11:58 | 12:59 | BIPTC S/S 10CF11 Forced S/D
| 12:00 |  | Day Peak Generation is 15415 MW.
| 12:30 | 16:31 | Ishwardi-Rooppur 132kV Ckt-1 Project Work S/D from Ishurdi 132/33kV end. and from Ruppur
132/11kV end Due to Project Work
| 13:13 | 18:43 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to
Mainenance work at Munshiganj
| 14:30 | 15:24 | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D
| 14:30 | 15:26 | Shahjibazar 132/33kV S/S TR-02 LT Scheduled S/D | [7 empty] | 30.0MW load
interrup.
| 14:52 | 16:20 | Chapainawabganj-Rahanpur 132kV Ckt-1 Tripped from Chapai 132/33kV end showing Protection
relay relays Due to General trip
| 15:55 | 16:10 | Aminbazar-Kallyanpur 132kV Ckt-1 Tripped from Kallyanpur 132/33kV end showing Ph A
fault 87L optd 87L com.fail relays.
| 16:00 | 17:39 | Chowmuhani-Feni 132 kV Ckt-2 Forced S/D from Daganbhuiyan 132/33kV end Due to Chowmuhani
S/S project Work. and from Chowmuhani 230/132/33kV end Due to PT R Phase Secondary
Ground.
| 16:22 | 16:31 | Barishal 132/33kV S/S T-2 (415T) LT Tripped showing O/C relays Due to 33 kv Dopdopia 1& | [7 empty] | 47.0MW load
|  |  | Nolcity 33 feeder fault. | [7 empty] | interrup.
| 16:40 | 17:55 | Nabinagar 132/33kV S/S T-2 HT Project Work S/D Due to CT, PT sealing and metering
| 16:40 |  | Nabinagar 132/33kV S/S T-2 LT Project Work S/D Due to CT, PT sealing and metering
|  | 16:42 | Sreepur 230/132/33kV S/S 132/33 kV T-1 HT is restored.
|  | 16:43 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT is restored.
|  | 18:07 | Chowmuhani 230/132/33kV S/S ATR-03 LT is restored.
|  | 18:07 | Chowmuhani 230/132/33kV S/S ATR-03 HT is restored.
| 21:00 |  | Evening Peak Generation is 17200 MW.
| 21:35 |  | Rampal 1320 MW (BIFPCL) Shutdown with remarks:- U2
| 21:36 |  | Rampal 1320 MW (BIFPCL) Synchronized
| 21:36 |  | Rampal 1320 MW (BIFPCL) Synchronized
| 21:41 | 00:03 | Noapara 132/33kV S/S T-2 LT Scheduled S/D Due to Due to REB-1 Feeder Red Hot Maintenance | [7 empty] | 20.0MW load
|  |  | by PBS | [7 empty] | interrup.
| 21:42 | 00:02 | Noapara 132/33kV S/S T-2 HT Scheduled S/D Due to Due to REB-1 Feeder Red Hot Maintenance | [7 empty] | 20.0MW load
|  |  | by PBS | [7 empty] | interrup.
| 21:47 | 23:56 | Noapara 132/33kV S/S Bus Section-2 Scheduled S/D Due to Due to REB-1 Feeder Red Hot | [7 empty] | 20.0MW load
|  |  | Maintenance by PBS | [7 empty] | interrup.
| 00:14 |  | Ashuganj 225 MW CCPP GT was sync.
| 00:14 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- GT
| 03:57 |  | Ashuganj 225 MW CCPP ST was sync.
| 03:57 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- ST
| 06:08 |  | Hasnabad 230/132kV S/S Bus-1 Scheduled S/D Due to High temperature maintenance at DS-801,
DS-803
| 06:18 | 07:26 | Ghatail 132/33kV S/S T-2 LT Tripped showing REC650 relays Due to Birds flying | [7 empty] | 28.0MW load
interrup.
| 06:18 |  | Ghatail 132/33kV S/S T-1 LT Tripped showing REC650 relays Due to Birds flying | [7 empty] | 56.0MW load
interrup.
| 07:00 |  | Minimum Generation: 13972 MW.
| 07:30 |  | Ishurdi 132/33kV S/S 132/33 kV T-3 LT Scheduled S/D Due to 33kv busber maintenance work. | [7 empty] | 34.0MW load
interrup.
| 07:31 |  | Ishurdi 132/33kV S/S 132/33 kV T-3 HT Scheduled S/D Due to 33kv busber red hot | [7 empty] | 34.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 20-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 406 | 9237600 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1297336 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 317 | 7344740 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 259560 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 127 | 2092800 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 443118 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 269961 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 433800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 480960 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 711360 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 4169607 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 2749680 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 2054400 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 804960 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 199676 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 14 | 154080 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 375 | 10080000 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 186 | 6691750 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3480000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2193 | 52955388
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 21 | 143530.2 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 112725 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 45 | 858240 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 107 | 744200 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 215 | 5034298 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 95 | 2245635 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 60 | 843120 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 49 | 273528 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 74 | 760320 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 5 | 240960 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 522240 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 28402 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 33 | 303600 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 479525 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 106 | 1533884 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 712320 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 92 | 1087691 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 140 | 2463927 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28696361 | Can't Start AGC
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 3 | 131040 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1000 | 21992727.27 | AGC
Chattogram Area Total |  |  |  |  | 4898.863 | 3423.36 | 69208273.47
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 0 | 0 | Under Maintenance
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 357 | 8853300 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 300 | 7276000 | FGMO not available
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 9184500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 36 | 887400 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 46 | 1073760 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 33455 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 35 | 693644 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 56 | 501818 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 20 | 408368 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 96 | 2276521 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 69 | 2425440 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 168 | 3797760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 34 | 611582 | plant availability zero
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 435280 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 104 | 1689480 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 12 | 153720 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 69 | 563520 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 412327 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1822 | 41277875
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 115 | 2016000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 12 | 261600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 231470 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 59520 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 151920 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 139 | 2732210
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 61859 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 999000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 723720 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 142 | 3398563.64 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 154 | 3524000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 554112 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1237440 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2422900 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 147792 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7476000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 308 | 7221000 | Plant availability less
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1221 | 27766386.64
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 781 | 21261091 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 33 | 232800 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 42 | 303488 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 152 | 3641184 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 1359648 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 519840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1100 | 24254543 | U-2 Under Maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2213 | 51572594
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 1003 | 19665454 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 1087488 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2686000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1230 | 27585454.55 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5238350 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 435600 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6328000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3933 | -
Barishal Area Total |  |  |  |  | 3481.04 | 3044 | 63030279.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 310392 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 372621 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 19 | 100916 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 140 | 3460455 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 140 | 3693200 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 360 | 9166545 | AGC
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 204010 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52 | 315946 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 721440 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1517184 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 986784 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28800 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1448.43 | 34473869 | Can't Start AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 328176 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 677080 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2550.43 | 56357418
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 165 | 854280 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 46 | 1093963 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 171 | 833000 | Under Maintenance
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1449619 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 38781.96 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1631237 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 195264 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1241280 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 595 | 7337424.96
Eastern Grid Total |  |  |  |  | 17418.042 | 8798.36 | 193940133.11
Western Grid Total |  |  |  |  | 11852.195 | 8402.43 | 178297716.51
National Grid Total |  |  |  |  | 29270.237 | 17200.79 | 372237849.62
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 20-05-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 11187.43 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5549.3 | MW
i) Dhaka area |  |  | 6212.63 |  | MW | i) Khulna area |  |  |  | 2058.5 | MW
ii) Chattogram area |  |  | 1681.8 |  | MW | ii) Barishal area |  |  |  | 533 | MW
iii) Cumilla area |  |  | 1621 |  | MW | iii) Rajshahi area |  |  |  | 1820.8 | MW
iv) Mymensingh area |  |  | 994 |  | MW | iv) Rangpur area |  |  |  | 1137 | MW
v) Sylhet area |  |  | 678 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 16736.73 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 8 | 17:00 | 67 | Hasnabad | 105 | 19:30 | 133 | Natore | 182 | 23:00
2 | AKSML | 128 | 09:00 | 68 | Hathazari | 100 | 23:00 | 134 | Nawabganj | 77.4 | 21:00
3 | Aftabnagar | 50 | 23:00 | 69 | Hatirjheel | 63 | 15:00 | 135 | Netrakona | 119 | 11:00
4 | Agargaon | 142 | 13:00 | 70 | Ishurdi | 95 | 19:30 | 136 | New | 84 | 09:00
5 | Agrabad | 82 | 13:00 | 71 | Jaldhaka | 91 | 19:30 | 137 | Niamatpur | 90 | 22:00
6 | Amnura | 35 | 23:00 | 72 | Jamalpur | 114 | 08:00 | 138 | Noapara | 54 | 14:00
7 | Ashuganj | 93 | 03:00 | 73 | Jashore | 185 | 19:30 | 139 | PHP | 12 | 10:00
8 | BSRM | 200 | 21:00 | 74 | Jhenaidah | 143 | 19:30 | 140 | Pabna | 118 | 19:00
9 | Bagerhat | 84 | 07:00 | 75 | Joydebpur | 177 | 16:00 | 141 | Palashbari | 142 | 19:30
10 | Bajitpur | 86 | 00:00 | 76 | Joypurhat | 68 | 20:00 | 142 | Panchagarh | 68 | 19:30
11 | Bakerganj | 12.6 | 19:00 | 77 | Juldah | 19 | 12:00 | 143 | Patiya | 12 | 23:00
12 | Bakulia | 117 | 20:00 | 78 | KSRM | 11 | 09:00 | 144 | Patuakhali | 79 | 23:00
13 | Banani | 62.6 | 13:00 | 79 | Kabirpur | 265 | 09:00 | 145 | Payra | 38 | 22:00
14 | Bangabhaban | 22 | 11:00 | 80 | Kachua | 107 | 22:00 | 146 | Postogola | 63 | 23:00
15 | Barapukuria | 72 | 20:00 | 81 | Kaliganj | 9 | 00:00 | 147 | Pubail | 31 | 00:00
16 | Barguna | 24 | 00:00 | 82 | Kallyanpur | 138 | 23:00 | 148 | Purbachal | 38 | 11:00
17 | Barishal | 119 | 21:00 | 83 | Kalurghat | 46 | 16:00 | 149 | Purbasadipur | 156 | 19:30
18 | Barishal-230 | 122 | 21:00 | 84 | Kamrangirchar | 89 | 20:00 | 150 | Rahanpur | 45 | 22:00
19 | Baroaulia | 78 | 12:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 24 | 10:00
20 | Baroirhat | 75 | 21:00 | 86 | Kasba | 42 | 20:00 | 152 | Rajbari | 97 | 19:00
21 | Bashundhara | 223 | 19:00 | 87 | Kazla | 126 | 12:00 | 153 | Rajendrapur | 130 | 07:00
22 | BashundharaCement | 8 | 16:00 | 88 | Keranigonj | 94 | 20:00 | 154 | Rajshahi | 147 | 23:00
23 | Beanibazar | 86 | 21:00 | 89 | Khagrachori | 36 | 19:00 | 155 | Rajshahi-230 | 104 | 21:00
24 | Benapole | 78 | 00:00 | 90 | Khulna | 70 | 13:00 | 156 | Ramganj | 126 | 21:00
25 | Bhaluka | 182 | 01:00 | 91 | Khulshi | 204 | 19:00 | 157 | Rampur | 50 | 23:00
26 | Bhandaria | 64 | 01:00 | 92 | Kishoreganj | 128 | 08:00 | 158 | Rangamati | 20 | 19:00
27 | Bhangura | 47 | 19:30 | 93 | Kodda | 323 | 11:00 | 159 | Rangpur | 162 | 20:00
28 | Bheramara(GK) | 79 | 23:00 | 94 | Kulaura | 62 | 19:00 | 160 | Ruppur | 4.6 | 09:00
29 | Bhulta | 218 | 00:00 | 95 | Kurigram | 76 | 19:30 | 161 | SSM | 8 | 23:00
30 | Bog-Sherpur | 90 | 21:00 | 96 | Kushtia | 181 | 19:00 | 162 | Saidpur | 118 | 19:30
31 | Bogura | 191 | 21:00 | 97 | Laksam | 39 | 01:00 | 163 | Santhia | 38 | 19:00
32 | Borhanuddin | 96 | 00:00 | 98 | Lakshmipur | 56 | 00:00 | 164 | Satkhira | 146 | 21:00
33 | Brahmanbaria | 134 | 20:00 | 99 | Lalbag | 85 | 17:00 | 165 | Satmasjid | 118 | 19:00
34 | Cantonment | 134 | 14:00 | 100 | Lalmonirhat | 70 | 19:30 | 166 | Savar | 231 | 20:00
35 | Chandina | 42 | 22:00 | 101 | MI_Cement | 17.5 | 01:00 | 167 | SevenRings | 22.39 | 12:00
36 | Chandpur | 96 | 21:00 | 102 | Madanganj | 48 | 21:00 | 168 | ShahCement | 43 | 21:00
37 | Chandraghona | 41 | 20:00 | 103 | Madaripur | 134 | 21:00 | 169 | Shahjadpur | 104 | 20:00
38 | Chapai | 82 | 22:00 | 104 | Madartek | 95 | 22:00 | 170 | Shahjibazar | 130 | 18:30
39 | Charsaidpur | 44 | 18:00 | 105 | Madunaghat | 68 | 19:30 | 171 | Shahmirpur | 64 | 00:00
40 | Chauddagram | 88 | 19:30 | 106 | Magura | 78 | 22:00 | 172 | Shariatpur | 104 | 21:00
41 | Chhatak | 36 | 01:00 | 107 | Mahasthangarh | 92 | 20:00 | 173 | Sherpur | 120 | 21:00
42 | Chowmuhani | 200 | 22:00 | 108 | Maijdee | 24 | 00:00 | 174 | Shikalbaha | 33 | 00:00
43 | Chuadanga | 132 | 22:00 | 109 | Manikganj | 143 | 19:30 | 175 | Shitalakhya | 97.2 | 15:00
44 | Coxsbazar | 148 | 13:00 | 110 | Maniknagar | 86 | 15:00 | 176 | Sholosohor | 50 | 16:00
45 | Cumilla(N) | 131 | 19:00 | 111 | Matarbari | 57 | 21:00 | 177 | Shomvuganj | 16 | 19:00
46 | Cumilla(S) | 182 | 19:00 | 112 | Matuail | 85 | 16:00 | 178 | Shyampur | 196 | 11:00
47 | Daganbhuiyan | 47 | 17:00 | 113 | Metrorail_Motijheel | 28 | 10:00 | 179 | Siddhirganj | 138 | 18:30
48 | Daudkandi | 156 | 20:00 | 114 | Metrorail_Uttara | 3 | 03:00 | 180 | Sirajganj | 142 | 20:00
49 | DhakaUniversity | 106 | 13:00 | 115 | Millgate | 110 | 15:00 | 181 | Sonargaon | 154 | 23:00
50 | Dhamrai | 128 | 19:30 | 116 | Mirpur | 177 | 19:00 | 182 | Sreemongol | 97 | 22:00
51 | Dhanmondi | 120.4 | 13:00 | 117 | Mirsorai | 46 | 02:00 | 183 | Sreepur | 130 | 21:00
52 | Dohazari | 108 | 00:00 | 118 | Mirzapur | 44 | 10:00 | 184 | Srinagar | 59 | 19:30
53 | Faridpur | 198 | 19:30 | 119 | Mithapukur | 68 | 20:00 | 185 | Sunamganj | 66 | 20:00
54 | Fatullah | 100 | 12:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 77 | 19:00
55 | Fenchuganj | 48 | 22:00 | 121 | Mogbazar | 129.4 | 15:00 | 187 | Sylhet-132 | 135 | 23:00
56 | Feni | 126 | 21:00 | 122 | Mongla | 44 | 15:00 | 188 | TK | 28.5 | 20:00
57 | GPH | 1 | 00:00 | 123 | Motijheel | 57 | 16:00 | 189 | Tangail | 182 | 22:00
58 | Ghatail | 66 | 10:00 | 124 | Muktagacha | 35 | 08:00 | 190 | Taraganj | 29 | 19:30
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 131 | 21:00 | 191 | Tasnim | 28 | 03:00
60 | Ghorashal-230 | 116 | 12:00 | 126 | Muradnagar | 55 | 20:00 | 192 | Thakurgaon | 122 | 19:30
61 | Goalpara | 42 | 23:00 | 127 | Mymensingh | 171 | 19:30 | 193 | Tongi | 177 | 11:00
62 | Gollamari | 124 | 00:00 | 128 | Nabinagar | 92 | 08:00 | 194 | Ullahpara | 47 | 19:00
63 | Gopalganj | 133 | 20:00 | 129 | Naogaon | 146 | 00:00 | 195 | Ullon | 54 | 21:00
64 | Gulshan | 152 | 16:00 | 130 | Narail | 58.5 | 21:00 | 196 | Uttara | 112 | 19:00
65 | Halishahar | 113 | 16:00 | 131 | Narinda | 83 | 13:00 | 197 | UttaraNew | 65 | 23:00
66 | HaripurSBU | 140 | 01:00 | 132 | Narshingdi | 196 | 21:00 | 198 | Zigatola | 110 | 16:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 20-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 16395 | 322 |  | 16731.49
1:00 | 15968 | 288 |  | 16269
2:00 | 15380.36 | 239 |  | 15630.36
3:00 | 15066.36 | 223 |  | 15299.36
4:00 | 14613 | 217 |  | 14840
5:00 | 14299 | 173 |  | 14480
6:00 | 13986.36 | 139 |  | 14131.36
7:00 | 13915.45 | 121 |  | 14041.9
8:00 | 13897.95 | 92 |  | 13993.95
9:00 | 14135.31 | 194 |  | 14338.31
10:00 | 14579.23 | 113 |  | 14697.32
11:00 | 15026.13 | 175 |  | 15209.13
12:00 | 15418.78 | 301 |  | 15733.78
13:00 | 15354.79 | 507 |  | 15884.79
14:00 | 15495.56 | 438 |  | 15953.56
15:00 | 15613.89 | 525 |  | 16162.89
16:00 | 15148.66 | 608 |  | 15783.66
17:00 | 15186.65 | 676 |  | 15892.65
18:00 | 14933.94 | 647 |  | 15609.94
19:00 | 16217.36 | 625 |  | 16870.36
19:30 | 16921.69 | 535 |  | 17480.69
20:00 | 16860.18 | 593 |  | 17480.18
21:00 | 17200.79 | 392 |  | 17610.79
22:00 | 16975.18 | 445 |  | 17440.18
23:00 | 16698.97 | 823 |  | 17558.97
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 20-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 145 | 8 | 460 | 140 | 1866 | 588 | Ishurdi-Ghorashal Ckt-1 | Export | 3029309.09
1:00 | 107 | 3 | 484 | 130 | 1842 | 586
2:00 | 111 | 1 | 496 | 192 | 1804 | 592 |  | Import | 0
3:00 | 94 | 0 | 450 | 132 | 1666 | 558
4:00 | 102 | 3 | 460 | 128 | 1682 | 566 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 116 | 6 | 500 | 120 | 1834 | 556
6:00 | 134 | 11 | 520 | 132 | 1976 | 598 |  | Import | 0
7:00 | 119 | 5 | 470 | 116 | 1874 | 554
8:00 | 138 | 15 | 500 | 144 | 1892 | 704 | Sirajganj-Sreepur Ckt-1 | Export | 3021000
9:00 | 172 | 27 | 580 | 140 | 1886 | 720
10:00 | 173 | 35 | 590 | 180 | 1876 | 728 |  | Import | 0
11:00 | 169 | 33 | 600 | 200 | 1892 | 750
12:00 | 156 | 28 | 580 | 190 | 1764 | 736 | Sirajganj-Sreepur Ckt-2 | Export | 3027000
13:00 | 128 | 22 | 510 | 160 | 1672 | 666
14:00 | 146 | 30 | 550 | 182 | 1826 | 778 |  | Import | 0
15:00 | 149 | 35 | 570 | 202 | 1868 | 810
16:00 | 138 | 32 | 550 | 200 | 1828 | 738 | Gopalganj-Aminbazar Ckt-1 | Export | 22250000
17:00 | 150 | 39 | 560 | 188 | 1856 | 814
18:00 | 143 | 39 | 500 | 168 | 1826 | 832 |  | Import | 0
18:30 | 149 | 40 | 530 | 176 | 1872 | 846
19:00 | 114 | 23 | 500 | 170 | 1912 | 698 | Gopalganj-Aminbazar Ckt-2 | Export | 22290000
19:30 | 106 | 16 | 480 | 172 | 2000 | 720
20:00 | 98 | 24 | 480 | 156 | 2040 | 714 |  | Import | 0
21:00 | 90 | 20 | 440 | 120 | 1966 | 684
22:00 | 85 | 18 | 470 | 160 | 1704 | 538 |  | Total Export | 53617309.09
23:00 | 101 | 25 | 510 | 164 | 1816 | 580 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 20-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8490 | 7905 | 16395 | DAILY GENERATION CURVE
00:30 | 8372 | 7809.5 | 16181.5
01:00 | 8254 | 7714 | 15968 | 20-05-2026
01:30 | 8008.18 | 7666 | 15674.18
02:00 | 7762.36 | 7618 | 15380.36
02:30 | 7842.36 | 7381 | 15223.36
03:00 | 7922.36 | 7144 | 15066.36
03:30 | 7762.18 | 7077.5 | 14839.68
04:00 | 7602 | 7011 | 14613
04:30 | 7465 | 6991 | 14456
05:00 | 7328 | 6971 | 14299
05:30 | 7118.725 | 7023.955 | 14142.68
06:00 | 6909.45 | 7076.91 | 13986.36
06:30 | 6922.82 | 7028.085 | 13950.905
07:00 | 6936.19 | 6979.26 | 13915.45
07:30 | 6976.75 | 6929.95 | 13906.7
08:00 | 7017.31 | 6880.64 | 13897.95
08:30 | 7118.815 | 6897.815 | 14016.63
09:00 | 7220.32 | 6914.99 | 14135.31
09:30 | 7462.04 | 6895.23 | 14357.27
10:00 | 7703.76 | 6875.47 | 14579.23
10:30 | 7867.16 | 6935.52 | 14802.68
11:00 | 8030.56 | 6995.57 | 15026.13
11:30 | 8175.72 | 7046.735 | 15222.455
12:00 | 8320.88 | 7097.9 | 15418.78
12:30 | 8285.765 | 7101.02 | 15386.785
13:00 | 8250.65 | 7104.14 | 15354.79
13:30 | 8265.065 | 7160.11 | 15425.175
14:00 | 8279.48 | 7216.08 | 15495.56
14:30 | 8284.45 | 7270.275 | 15554.725
15:00 | 8289.42 | 7324.47 | 15613.89
15:30 | 8114.91 | 7266.365 | 15381.275
16:00 | 7940.4 | 7208.26 | 15148.66
16:30 | 7994.975 | 7172.68 | 15167.655
17:00 | 8049.55 | 7137.1 | 15186.65
17:30 | 7978.91 | 7081.385 | 15060.295
18:00 | 7908.27 | 7025.67 | 14933.94
18:30 | 8127.635 | 7448.015 | 15575.65
19:00 | 8347 | 7870.36 | 16217.36
19:30 | 8603.8 | 8317.89 | 16921.69
20:00 | 8572.36 | 8287.82 | 16860.18
20:30 | 8685.36 | 8345.125 | 17030.485 |  | Executive Engineer
21:00 | 8798.36 | 8402.43 | 17200.79 |  | Network Operation Division
21:30 | 8838.86 | 8249.125 | 17087.985
22:00 | 8879.36 | 8095.82 | 16975.18
22:30 | 8788.86 | 8048.215 | 16837.075
23:00 | 8698.36 | 8000.61 | 16698.97

## En-Curve
QF-LDC-12
Date | 20-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3714 | 1621 | 762 | 0 | 160 | 1433 | 30 | 5615 | 0 | 803 | 2257 | 0 | 0 | 0 | 322 | DAILY ENERGY CURVE
00:30 | 3705 | 1573.5 | 833 | 0 | 161 | 1436.5 | 30 | 5490 | 0 | 769.5 | 2183 | 0 | 0 | 0 | 305 | 20-05-2026
01:00 | 3696 | 1526 | 904 | 0 | 162 | 1440 | 30 | 5365 | 0 | 736 | 2109 | 0 | 0 | 0 | 288
01:30 | 3604 | 1483.5 | 904 | 0 | 161 | 1439.5 | 30 | 5285 | 0 | 701.5 | 2065.68 | 0 | 0 | 0 | 263.5 | Energy Generated | 372.2378 |  | MKWHr
02:00 | 3512 | 1441 | 904 | 0 | 160 | 1439 | 30 | 5205 | 0 | 667 | 2022.36 | 0 | 0 | 0 | 239 | Energy not Served | 8.876 |  | MKWHr
02:30 | 3567.5 | 1506.5 | 904 | 0 | 157 | 1443.5 | 30 | 5220 | 0 | 552 | 1835.86 | 0 | 0 | 7 | 231 | Total Energy Requirement | 381.1138 |  | MKWHr
03:00 | 3623 | 1572 | 904 | 0 | 154 | 1448 | 30 | 5235 | 0 | 437 | 1649.36 | 0 | 0 | 14 | 223
03:30 | 3623 | 1571.5 | 904 | 0 | 154 | 1449 | 30 | 5225.5 | 0 | 353 | 1522.68 | 0 | 0 | 7 | 220
04:00 | 3623 | 1571 | 904 | 0 | 154 | 1450 | 30 | 5216 | 0 | 269 | 1396 | 0 | 0 | 0 | 217
04:30 | 3674.5 | 1593 | 904 | 0 | 153 | 1450 | 30 | 5270.5 | 0 | 257.5 | 1123.5 | 0 | 0 | 0 | 195
05:00 | 3726 | 1615 | 904 | 0 | 152 | 1450 | 30 | 5325 | 0 | 246 | 851 | 0 | 0 | 0 | 173
05:30 | 3706 | 1540 | 904 | 0 | 143 | 1444 | 30 | 5338.5 | 13.68 | 246 | 775 | 0 | 0 | 2.5 | 156
06:00 | 3686 | 1465 | 904 | 0 | 134 | 1438 | 30 | 5352 | 27.36 | 246 | 699 | 0 | 0 | 5 | 139
06:30 | 3687.5 | 1452 | 904 | 0 | 135 | 1435.5 | 30 | 5348 | 66.405 | 268.5 | 621.5 | 0 | 0 | 2.5 | 130
07:00 | 3689 | 1439 | 904 | 0 | 136 | 1433 | 30 | 5344 | 105.45 | 291 | 544 | 0 | 0 | 0 | 121
07:30 | 3652.5 | 1450.5 | 904 | 0 | 139 | 1449.82 | 30 | 5284.5 | 157.38 | 282 | 557 | 0 | 0 | 0 | 106.5
08:00 | 3616 | 1462 | 904 | 0 | 142 | 1466.64 | 30 | 5225 | 209.31 | 273 | 570 | 0 | 0 | 0 | 92
08:30 | 3596.5 | 1445.5 | 903.5 | 0 | 147 | 1462.905 | 30 | 5205 | 315.225 | 276.5 | 634.5 | 0 | 0 | 0 | 143
09:00 | 3577 | 1429 | 903 | 0 | 152 | 1459.17 | 30 | 5185 | 421.14 | 280 | 699 | 0 | 0 | 0 | 194
09:30 | 3578.5 | 1488 | 903.5 | 0 | 152 | 1449.69 | 30 | 5144.5 | 435.58 | 325.5 | 848.5 | 0 | 0 | 1.5 | 153.5
10:00 | 3580 | 1547 | 904 | 0 | 152 | 1440.21 | 30 | 5104 | 450.02 | 371 | 998 | 0 | 0 | 3 | 113
10:30 | 3590 | 1530.5 | 903.5 | 0 | 161 | 1433.725 | 30 | 5172.5 | 495.455 | 373.5 | 1107.5 | 0 | 0 | 5 | 144
11:00 | 3600 | 1514 | 903 | 0 | 170 | 1427.24 | 30 | 5241 | 540.89 | 376 | 1217 | 0 | 0 | 7 | 175
11:30 | 3586 | 1529.5 | 903 | 0 | 164 | 1424.62 | 30 | 5227 | 609.335 | 419.5 | 1320 | 0 | 0 | 9.5 | 238
12:00 | 3572 | 1545 | 903 | 0 | 158 | 1422 | 30 | 5213 | 677.78 | 463 | 1423 | 0 | 0 | 12 | 301
12:30 | 3603 | 1471 | 903.5 | 0 | 164 | 1415.5 | 30 | 5222.5 | 646.785 | 470.5 | 1444.5 | 0 | 0 | 15.5 | 404
13:00 | 3634 | 1397 | 904 | 0 | 170 | 1409 | 30 | 5232 | 615.79 | 478 | 1466 | 0 | 0 | 19 | 507
13:30 | 3597 | 1447 | 903.5 | 0 | 173 | 1408 | 30 | 5257 | 609.175 | 507.5 | 1472 | 0 | 0 | 21 | 472.5
14:00 | 3560 | 1497 | 903 | 0 | 176 | 1407 | 30 | 5282 | 602.56 | 537 | 1478 | 0 | 0 | 23 | 438
14:30 | 3580 | 1511 | 903.5 | 0 | 176 | 1427.5 | 30 | 5333 | 506.725 | 559.5 | 1505.5 | 0 | 0 | 22 | 481.5
15:00 | 3600 | 1525 | 904 | 0 | 176 | 1448 | 30 | 5384 | 410.89 | 582 | 1533 | 0 | 0 | 21 | 525
15:30 | 3605.5 | 1472.5 | 903.5 | 0 | 172 | 1436.5 | 30 | 5405 | 336.775 | 583.5 | 1416.5 | 0 | 0 | 19.5 | 566.5
16:00 | 3611 | 1420 | 903 | 0 | 168 | 1425 | 30 | 5426 | 262.66 | 585 | 1300 | 0 | 0 | 18 | 608
16:30 | 3627 | 1523 | 903.5 | 0 | 163 | 1403.5 | 30 | 5377.5 | 205.155 | 642 | 1279 | 0 | 0 | 14 | 642
17:00 | 3643 | 1626 | 904 | 0 | 158 | 1382 | 30 | 5329 | 147.65 | 699 | 1258 | 0 | 0 | 10 | 676
17:30 | 3629.5 | 1528.5 | 903.5 | 0 | 158 | 1344.03 | 30 | 5347.5 | 87.765 | 714 | 1310.5 | 0 | 0 | 7 | 661.5
18:00 | 3616 | 1431 | 903 | 0 | 158 | 1306.06 | 30 | 5366 | 27.88 | 729 | 1363 | 0 | 0 | 4 | 647
18:30 | 3640.5 | 1504 | 890 | 0 | 169 | 1388.71 | 30 | 5495.5 | 13.94 | 769 | 1638 | 35 | 0 | 2 | 636
19:00 | 3665 | 1577 | 877 | 0 | 180 | 1471.36 | 30 | 5625 | 0 | 809 | 1913 | 70 | 0 | 0 | 625
19:30 | 3661 | 1549 | 876 | 0 | 174 | 1449.89 | 30 | 5897 | 0 | 851 | 2268.8 | 165 | 0 | 0 | 535
20:00 | 3648 | 1526 | 781 | 0 | 166 | 1456.82 | 30 | 5978 | 0 | 840 | 2269.36 | 165 | 0 | 0 | 593
20:30 | 3672 | 1508 | 781 | 0 | 167 | 1452.625 | 68.5 | 6029.5 | 0 | 839 | 2346.36 | 165 | 0 | 1.5 | 492.5
21:00 | 3696 | 1490 | 781 | 0 | 168 | 1448.43 | 107 | 6081 | 0 | 838 | 2423.36 | 165 | 0 | 3 | 392
21:30 | 3666.5 | 1597 | 781 | 0 | 161 | 1444.625 | 68.5 | 5927 | 0 | 828.5 | 2446.36 | 165 | 0 | 2.5 | 418.5
22:00 | 3637 | 1704 | 781 | 0 | 154 | 1440.82 | 30 | 5773 | 0 | 819 | 2469.36 | 165 | 0 | 2 | 445
22:30 | 3626.5 | 1704.5 | 781 | 0 | 149 | 1443.715 | 30 | 5693 | 0 | 826.5 | 2416.86 | 165 | 0 | 1 | 634
23:00 | 3616 | 1705 | 781 | 0 | 144 | 1446.61 | 30 | 5613 | 0 | 834 | 2364.36 | 165 | 0 | 0 | 823
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 20-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 367 | 04:00 | 353 | 19:30 | Madunaghat | 392 | 02:00 | 386 | 10:00
Amtali | 408 | 02:00 | 399 | 22:00 | Meghnaghat | 368 | 02:00 | 357 | 11:00
Ashuganj | 404 | 20:00 | 392 | 16:00 | Payra | 410 | 02:00 | 402 | 22:00
Bhulta | 390 | 03:00 | 373 | 12:00 | Rahanpur | 407 | 18:30 | 391 | 11:00
Bibiana | 386 | 02:00 | 379 | 19:30 | Rampal | 392 | 03:00 | 370 | 22:00
BIPTC | 404 | 20:00 | 392 | 16:00
Bogura | 393 | 18:30 | 375 | 11:00
Gopalganj | 385 | 02:00 | 369 | 22:00
Kaliakoir | 365 | 03:00 | 348 | 22:00
Korerhat | 387 | 09:00 | 377 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 221 | 03:00 | 213 | 11:00 | Jhenaidah | 225 | 18:00 | 211 | 19:30
AKSML | 238 | 03:00 | 223 | 09:00 | Kachua | 225 | 00:00 | 219 | 19:30
Aminbazar | 221 | 04:00 | 213 | 11:00 | Kaliakoir | 226 | 03:00 | 215 | 19:30
Ashuganj | 223 | 04:00 | 214 | 12:00 | Keranigonj | 220 | 03:00 | 210 | 11:00
Ashuganj-400 | 223 | 04:00 | 214 | 12:00 | Khulna(S) | 221 | 09:00 | 209 | 22:00
Baghabari | 230 | 18:00 | 223 | 11:00 | Korerhat | 226 | 02:00 | 222 | 09:00
Barapukuria | 224 | 18:30 | 209 | 07:00 | Madunaghat | 231 | 02:00 | 224 | 09:00
Barapukuria-230 | 224 | 18:30 | 209 | 07:00 | Madunaghat-400 | 231 | 01:00 | 226 | 09:00
Barishal | 222 | 03:00 | 215 | 15:00 | Maniknagar | 220 | 03:00 | 209 | 11:00
Bheramara | 232 | 18:00 | 222 | 19:30 | Meghnaghat | 229 | 03:00 | 219 | 11:00
Bhulta | 221 | 03:00 | 209 | 12:00 | Meghnaghat-400 | 224 | 02:00 | 213 | 11:00
Bibiana | 229 | 07:00 | 223 | 21:00 | Mirsorai | 227 | 01:00 | 220 | 05:00
BIPTC | 235 | 18:00 | 222 | 19:30 | Naogaon | 218 | 18:30 | 204 | 00:00
Bogura | 236 | 18:30 | 225 | 11:00 | Purbasadipur | 223 | 18:30 | 206 | 07:00
Bogura-400 | 236 | 18:30 | 224 | 11:00 | Rajshahi | 231 | 18:00 | 219 | 12:00
Borhanuddin | 227 | 02:00 | 223 | 22:00 | Rampal | 222 | 18:00 | 207 | 22:00
BSRM | 227 | 02:00 | 221 | 10:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 225 | 00:00 | 220 | 15:00 | Rampura | 220 | 03:00 | 207 | 11:00
Cumilla(N) | 222 | 02:00 | 215 | 19:30 | Shikalbaha | 230 | 00:00 | 223 | 08:00
Faridpur | 214 | 02:00 | 205 | 22:00 | Shyampur | 221 | 03:00 | 25 | 18:30
Fenchuganj | 230 | 06:00 | 225 | 19:00 | Siddhirganj | 221 | 07:00 | 211 | 10:00
Feni | 223 | 02:00 | 215 | 19:30 | Sirajgonj | 236 | 18:00 | 230 | 11:00
Ghorashal | 225 | 04:00 | 210 | 14:00 | Sreepur | 221 | 06:00 | 211 | 11:00
Ghorashal-230 | 219 | 03:00 | 206 | 11:00 | Tongi | 220 | 04:00 | 205 | 15:00
Gopalganj | 215 | 02:00 | 207 | 22:00
GPH | 229 | 02:00 | 222 | 10:00
Haripur | 222 | 05:00 | 211 | 11:00
Hasnabad | 217 | 00:00 | 210 | 11:00
Hathazari | 227 | 18:00 | 222 | 11:00
Ishurdi | 233 | 18:00 | 223 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 131 | 06:00 | 123 | 12:00 | Madunaghat | 134 | 23:00 | 129 | 10:00
Agargaon | 128 | 01:00 | 121 | 11:00 | Magura | 131 | 09:00 | 120 | 19:00
Agrabad | 133 | 23:00 | 125 | 15:00 | Mahasthangarh | 132 | 18:00 | 126 | 07:00
AKS | 130 | 23:00 | 125 | 09:00 | Maijdee | 126 | 02:00 | 122 | 20:00
Aminbazar | 125 | 03:00 | 120 | 09:00 | Manikganj | 129 | 13:00 | 120 | 06:00
Amnura | 136 | 18:00 | 125 | 12:00 | Maniknagar | 129 | 02:00 | 119 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 135 | 23:00 | 109 | 00:00
Ashuganj-230 | 131 | 01:00 | 127 | 12:00 | Matuail | 127 | 02:00 | 121 | 11:00
Bagerhat | 120 | 18:00 | 108 | 22:00 | Metrorail_Motijheel | 129 | 02:00 | 119 | 12:00
Bajitpur | 125 | 00:00 | 117 | 16:00 | Metrorail_Uttara | 128 | 01:00 | 120 | 11:00
Bakerganj | 131 | 18:30 | 125 | 15:00 | Millgate | 132 | 03:00 | 120 | 11:00
Bakulia | 132 | 03:00 | 127 | 11:00 | Mirpur | 124 | 02:00 | 119 | 11:00
Banani | 130 | 04:00 | 123 | 15:00 | Mirzapur | 125 | 00:00 | 119 | 23:00
Bangabhaban | 129 | 02:00 | 119 | 11:00 | Mithapukur | 130 | 18:30 | 122 | 11:00
Barapukuria | 131 | 18:00 | 122 | 07:00 | MI_Cement | 127 | 05:00 | 119 | 19:00
Barguna | 130 | 18:30 | 124 | 15:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 129 | 18:00 | 123 | 12:00 | Mogbazar | 130 | 03:00 | 125 | 09:00
Barishal-230 | 129 | 03:00 | 123 | 14:00 | Mongla | 121 | 18:00 | 111 | 22:00
Baroaulia | 132 | 00:00 | 127 | 15:00 | Motijheel | 129 | 02:00 | 119 | 11:00
Baroirhat | 130 | 02:00 | 126 | 10:00 | Muktagacha | 120 | 09:00 | 111 | 23:00
Bashundhara | 132 | 03:00 | 120 | 12:00 | Munshiganj | 125 | 02:00 | 120 | 12:00
BashundharaCement | 127 | 01:00 | 122 | 11:00 | Muradnagar | 124 | 07:00 | 119 | 19:30
Beanibazar | 126 | 07:00 | 120 | 19:00 | Mymensingh | 121 | 10:00 | 110 | 11:00
Benapole | 128 | 09:00 | 111 | 13:00 | Nabinagar | 126 | 03:00 | 12 | 16:00
Bhaluka | 125 | 09:00 | 119 | 11:00 | Naogaon | 133 | 18:00 | 123 | 00:00
Bhandaria | 123 | 08:00 | 113 | 15:00 | Narail | 132 | 09:00 | 118 | 22:00
Bhangura | 130 | 02:00 | 127 | 07:00 | Narinda | 129 | 02:00 | 119 | 12:00
Bheramara | 133 | 18:00 | 127 | 19:30 | Narshingdi | 124 | 09:00 | 116 | 22:00
Bheramara(GK) | 133 | 18:00 | 127 | 19:30 | Natore | 133 | 18:30 | 126 | 12:00
Bhulta | 123 | 07:00 | 118 | 22:00 | Nawabganj | 128 | 03:00 | 122 | 15:00
Bog-Sherpur | 133 | 18:00 | 127 | 07:00 | Netrakona | 122 | 05:00 | 109 | 11:00
Bogura | 136 | 18:00 | 129 | 10:00 | New | 130 | 03:00 | 121 | 12:00
Bogura-230 | 136 | 18:00 | 129 | 11:00 | Niamatpur | 132 | 18:00 | 125 | 00:00
Brahmanbaria | 125 | 02:00 | 118 | 12:00 | Noapara | 125 | 18:00 | 114 | 22:00
Cantonment | 128 | 03:00 | 120 | 10:00 | Pabna | 131 | 18:00 | 126 | 20:00
Chandina | 128 | 02:00 | 124 | 11:00 | Palashbari | 128 | 18:00 | 121 | 00:00
Chandpur | 131 | 13:00 | 124 | 04:00 | Panchagarh | 137 | 18:30 | 124 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 133 | 21:00 | 129 | 09:00 | Patiya | 134 | 23:00 | 125 | 09:00
Chapai | 133 | 18:00 | 127 | 00:00 | Patuakhali | 129 | 18:00 | 125 | 13:00
Charsaidpur | 127 | 06:00 | 121 | 11:00 | Payra | 133 | 02:00 | 129 | 23:00
Chauddagram | 128 | 00:00 | 125 | 19:30 | PHP | 129 | 00:00 | 127 | 05:00
Chhatak | 124 | 06:00 | 115 | 19:00 | Postogola | 127 | 05:00 | 119 | 11:00
Chowmuhani | 126 | 02:00 | 123 | 05:00 | Pubail | 130 | 00:00 | 122 | 10:00
Chuadanga | 129 | 18:00 | 116 | 22:00 | Purbachal | 132 | 02:00 | 120 | 12:00
Coxsbazar | 119 | 23:00 | 109 | 21:00 | Purbasadipur | 132 | 18:30 | 121 | 07:00
Cumilla(N) | 128 | 02:00 | 124 | 19:30 | Rahanpur | 134 | 18:00 | 129 | 00:00
Cumilla(S) | 130 | 03:00 | 123 | 14:00 | Rahanpur-400 | 134 | 18:00 | 129 | 00:00
Daganbhuiyan | 129 | 01:00 | 125 | 19:30 | Rahim | 128 | 04:00 | 122 | 11:00
Daudkandi | 122 | 03:00 | 116 | 19:30 | Rajbari | 131 | 18:30 | 115 | 19:00
DhakaUniversity | 130 | 03:00 | 124 | 11:00 | Rajendrapur | 132 | 03:00 | 119 | 11:00
Dhamrai | 128 | 13:00 | 120 | 19:30 | Rajshahi | 130 | 18:30 | 123 | 12:00
Dhanmondi | 130 | 03:00 | 122 | 11:00 | Rajshahi-230 | 133 | 18:00 | 125 | 12:00
Dohazari | 130 | 23:00 | 121 | 11:00 | Ramganj | 127 | 13:00 | 122 | 05:00
Faridpur | 124 | 02:00 | 120 | 13:00 | Rampur | 132 | 23:00 | 126 | 09:00
Fatullah | 131 | 02:00 | 116 | 12:00 | Rampura | 130 | 03:00 | 124 | 09:00
Fenchuganj | 132 | 06:00 | 128 | 18:30 | Rangamati | 132 | 02:00 | 127 | 11:00
Feni | 130 | 00:00 | 126 | 15:00 | Rangpur | 129 | 16:00 | 122 | 07:00
Feni-230 | 131 | 02:00 | 127 | 19:30 | Ruppur | 134 | 18:00 | 129 | 19:30
Ghatail | 121 | 09:00 | 112 | 23:00 | Saidpur | 131 | 18:30 | 121 | 11:00
Ghorashal | 131 | 00:00 | 124 | 11:00 | Santhia | 133 | 05:00 | 127 | 12:00
Goalpara | 129 | 18:00 | 119 | 12:00 | Satkhira | 122 | 09:00 | 109 | 22:00
Gollamari | 129 | 18:00 | 118 | 22:00 | Satmasjid | 127 | 03:00 | 119 | 11:00
Gopalganj | 130 | 18:00 | 120 | 13:00 | Savar | 124 | 16:00 | 117 | 09:00
Gopalganj-400 | 128 | 18:00 | 122 | 22:00 | SevenRings | 130 | 00:00 | 123 | 11:00
Gulshan | 129 | 04:00 | 124 | 12:00 | ShahCement | 127 | 06:00 | 121 | 11:00
Halishahar | 135 | 23:00 | 126 | 10:00 | Shahjadpur | 134 | 18:00 | 130 | 12:00
Haripur | 128 | 07:00 | 122 | 11:00 | Shahjibazar | 128 | 18:00 | 118 | 12:00
HaripurSBU | 128 | 06:00 | 122 | 11:00 | Shahmirpur | 132 | 00:00 | 127 | 10:00
Hasnabad | 127 | 06:00 | 119 | 16:00 | Shariatpur | 126 | 18:00 | 118 | 22:00
Hathazari | 133 | 03:00 | 129 | 15:00 | Sherpur | 119 | 13:00 | 109 | 02:00
Hatirjheel | 130 | 02:00 | 124 | 11:00 | Shikalbaha | 123 | 21:00 | 117 | 15:00
Ishurdi | 135 | 18:00 | 129 | 19:30 | Shikalbaha-230 | 134 | 23:00 | 128 | 08:00
Jaldhaka | 129 | 18:30 | 118 | 07:00 | Shitalakhya | 127 | 05:00 | 115 | 15:00
Jamalpur | 122 | 13:00 | 112 | 17:00 | Sholosohor | 133 | 02:00 | 127 | 15:00
Jashore | 130 | 09:00 | 113 | 13:00 | Shomvuganj | 124 | 06:00 | 114 | 15:00
Jhenaidah | 134 | 09:00 | 113 | 19:30 | Shyampur | 130 | 01:00 | 122 | 11:00
Jhenaidah-230 | 134 | 10:00 | 124 | 19:30 | Shyampur-230 | 132 | 03:00 | 125 | 11:00
Joydebpur | 128 | 00:00 | 118 | 10:00 | Siddhirganj | 128 | 04:00 | 122 | 11:00
Joypurhat | 130 | 18:00 | 124 | 12:00 | Sirajganj | 130 | 05:00 | 124 | 07:00
Juldah | 134 | 23:00 | 128 | 08:00 | Sonargaon | 124 | 02:00 | 120 | 10:00
Kabirpur | 132 | 13:00 | 116 | 12:00 | Sreemongol | 127 | 07:00 | 121 | 00:00
Kachua | 128 | 00:00 | 125 | 05:00 | Sreepur | 127 | 04:00 | 122 | 11:00
Kaliakoir | 133 | 03:00 | 125 | 19:30 | Srinagar | 128 | 00:00 | 122 | 15:00
Kaliganj | 133 | 09:00 | 121 | 19:00 | SSM | 136 | 00:00 | 132 | 07:00
Kallyanpur | 124 | 05:00 | 118 | 15:00 | Sunamganj | 124 | 07:00 | 113 | 19:00
Kalurghat | 134 | 02:00 | 128 | 15:00 | Sylhet | 128 | 08:00 | 121 | 19:00
Kamrangirchar | 129 | 04:00 | 117 | 11:00 | Sylhet-132 | 127 | 06:00 | 122 | 19:00
Kaptai | N/A | N/A | N/A | N/A | Tangail | 122 | 09:00 | 115 | 22:00
Kasba | 124 | 07:00 | 118 | 19:30 | Taraganj | 130 | 18:30 | 120 | 07:00
Kazla | 129 | 04:00 | 119 | 11:00 | Tasnim | 125 | 02:00 | 120 | 10:00
Keranigonj | 129 | 02:00 | 123 | 11:00 | Thakurgaon | 137 | 18:30 | 121 | 07:00
Khagrachori | 131 | 02:00 | 126 | 11:00 | TK | 133 | 23:00 | 128 | 15:00
Khulna | 126 | 18:00 | 115 | 22:00 | Tongi | 134 | 04:00 | 123 | 11:00
Khulna(S) | 129 | 18:30 | 121 | 13:00 | Ullahpara | 131 | 18:00 | 126 | 07:00
Khulshi | 133 | 23:00 | 125 | 15:00 | Ullon | 129 | 04:00 | 124 | 12:00
Kishoreganj | 126 | 21:00 | 116 | 15:00 | Uttara | 131 | 04:00 | 119 | 12:00
Kodda | 132 | 13:00 | 122 | 23:00 | UttaraNew | 130 | 02:00 | 120 | 11:00
Korerhat | 131 | 02:00 | 128 | 09:00 | Zigatola | 129 | 04:00 | 122 | 11:00
KSRM | 133 | 18:00 | 128 | 09:00
Kulaura | 131 | 07:00 | 126 | 19:00
Kurigram | 126 | 03:00 | 116 | 00:00
Kushtia | 129 | 18:00 | 120 | 19:30
Laksam | 128 | 02:00 | 124 | 20:00
Lakshmipur | 125 | 02:00 | 122 | 06:00
Lalbag | 128 | 06:00 | 122 | 15:00
Lalmonirhat | 127 | 06:00 | 117 | 00:00
Madanganj | 127 | 00:00 | 122 | 11:00
Madaripur | 127 | 08:00 | 121 | 14:00
Madartek | 129 | 02:00 | 123 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division