## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 23-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-05-2026 | during | 23-05-2026 | during | 23-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 343 | 383 | 412 | 412 | 392 | 392 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 297 | 304 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 145 | 60 | 149.36 | 149.36 | 90 | 128 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19 | 0 | 33 | 33 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 22 | 0 | 0 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 50 | 52.19 | 52.19 | 25 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 32 | 32 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 51 | 149 | 149 | 133 | 133 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 88 | 105 | 105 | 50 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 17 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 9 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 400 | 440 | 584 | 584 | 490 | 490 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 262 | 259 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 105 | 142 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1755 | 1992 | 6027.22 | 5995.22 | 2155 | 2402
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 0 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 9 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 39 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 30 | 30 | 30 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 214 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 99 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 44 | 46 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 24 | 100 | 100 | 24 | 24 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 13 | 20 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 24 | 50 | 108 | 108 | 18 | 38 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.27 | 0 | 4.45 | 0 | 4.45 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 15 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 34 | 104 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 24 | 24 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 76 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 14 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1212 | 1224 | 1224 | 1224 | 1204 | 1204
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 8 | 21 | 24 | 28 | 24 | 28 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 625 | 1000 | 655 | 1000 | 600 | 600 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2364.27 | 3067 | 3455.31 | 3863.86 | 2768.81 | 2860.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 200 | 199 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 357 | 357 | 350.01 | 350.01 | 350.01 | 350.01
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 240 | 345 | 342.01 | 342.01 | 342.01 | 342.01
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 393 | 393 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 20 | 37 | 41.65 | 41.65 | 0 | 0 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 1 | 47 | 52.82 | 52.82 | 0 | 0 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 11 | 58 | 150 | 150 | 33 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 31 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 95 | 98 | 163 | 163 | 100 | 100 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 120 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 138 | 144 | 84 | 80 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 34 | 43 | 52.2 | 52.2 | 43 | 43 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 17 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 51 | 115 | 115 | 17 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 42 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1325 | 1634 | 2764.44 | 2690.44 | 2108.27 | 2215.27
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-05-2026 | during | 23-05-2026 | during | 23-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.01 | 0 | 2.3 | 0 | 2.3 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 78 | 117 | 90 | 90 | 90 | 90 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 37 | 10 | 10 | 10 | 10 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 14.08 | 0 | 22 | 0 | 22 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 101.09 | 171 | 358.3 | 334 | 141.3 | 129
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 42 | 42 | 42 | 42 | Partial Shutdown due to maintenance
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 136 | 147 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 152 | 152 | 155 | 155 | 155 | 155 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 25 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 101 | 102 | 102 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 22 | 22 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 308 | 344 | 250 | 250 | 320 | 320 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1210 | 1259 | 1244 | 1244 | 1234 | 1234
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 465 | 889 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 33 | 35 | 35 | 35 | 35 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 45 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 177 | 182 | 410 | 410 | 180 | 180 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 16 | 105 | 105 | 0.1 | 0.1 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 64 | 0 | 95 | 0 | 95 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 400 | 499 | 500 | 500 | 617.1 | 1200
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1123 | 1664 | 2860 | 2765 | 2054.2 | 2542.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 1249 | 1251 | 1244 | 1244 | 655 | 655
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 64 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 83 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1206 | 1070 | 1244 | 1244 | 1184 | 1184 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 0 | 35 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 274 | 307 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.45 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 3069.45 | 3049 | 3406 | 3405 | 2577 | 2611
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 22.36 | 0 | 51 | 0 | 51 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 140 | 140 | 214 | 214 | 180 | 180 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 140 | 220 | 220 | 190 | 190 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 366 | 379 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 32 | 32 | 26 | 26 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 91 | 100 | 100 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.07 | 0 | 3.3 | 0 | 3.3 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1174 | 1445 | 1435.88 | 1435.88 | 1355.88 | 1355.88 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 33.27 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 36 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1913.7 | 2486 | 3233.17 | 3017.87 | 2689.79 | 2559.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 48 | 50 | 50 | 50 | 50 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 158 | 179 | 170 | 170 | 190 | 190 | Machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 104 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 0 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 8 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 3 | 0 | 68 | 0 | 68 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 217 | 446 | 570 | 468 | 570 | 468
System Total |  |  |  |  | 28823.2 | 29270.237 | 13078.51 | 15768 | 23918.44 | 23783.39 | 16298.37 | 17021.22
Forecast Scenario (23-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15800 |  | 0 |  | 15800
|  |  |  | 1:00 | 15550 |  | 0 |  | 15550
|  |  |  | 2:00 | 15480 |  | 0 |  | 15480
|  |  |  | 3:00 | 15260 |  | 0 |  | 15260
|  |  |  | 4:00 | 14900 |  | 0 |  | 14900
|  |  |  | 5:00 | 14260 |  | 0 |  | 14260
|  |  |  | 6:00 | 13810 |  | 0 |  | 13810
|  |  |  | 7:00 | 13530 |  | 0 |  | 13530
|  |  |  | 8:00 | 13260 |  | 0 |  | 13260
|  |  |  | 9:00 | 13510 |  | 0 |  | 13510
|  |  |  | 10:00 | 13600 |  | 0 |  | 13600
|  |  |  | 11:00 | 13770 |  | 0 |  | 13770
|  |  |  | 12:00 | 14300 |  | 0 |  | 14300
|  |  |  | 13:00 | 14490 |  | 0 |  | 14490
|  |  |  | 14:00 | 14680 |  | 0 |  | 14680
|  |  |  | 15:00 | 15150 |  | 0 |  | 15150
|  |  |  | 16:00 | 15420 |  | 0 |  | 15420
|  |  |  | 17:00 | 15180 |  | 0 |  | 15180
|  |  |  | 18:00 | 14840 |  | 0 |  | 14840
|  |  |  | 18:30 | 15500 |  | 0 |  | 15500
|  |  |  | 19:00 | 16270 |  | 0 |  | 16270
|  |  |  | 19:30 | 16840 |  | 0 |  | 16840
|  |  |  | 20:00 | 16730 |  | 0 |  | 16730
|  |  |  | 21:00 | 16800 |  | 0 |  | 16800
|  |  |  | 22:00 | 16340 |  | 0 |  | 16340
|  |  |  | 23:00 | 16370 |  | 0 |  | 16370
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 14300.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16840.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16840.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 358.01313 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:03 hrs on 23-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 22-05-2026 | [28 empty] | Date: | 22-05-2026 | [28 empty] | Date: | 22-05-2026 | [28 empty] | Date: | 22-05-2026 | [28 empty] | Date: | 22-05-2026 | [17 empty] | Date: | 22-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [17 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 299 | 35 | 0 | 52 | 148 | 32 | 55 | 35 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 125 | 17 | 21 | 0 | 450 | 101 | 16 | 46 | 0 | 7 | 49 | 51 | 54.36 | 24 | 24 | 0 | 30 | 108 | 27 | 935 | 35 | 0 | 50 | 0 | 104 | 216 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 270 | 356 | 220 | 51 | 0 | 203 | 0 | 37 | 98 | 192 | 0 | 19 | 108 | 154 | 43 | 0 | 23 | 315 | 0 | 308 | 42 | 30 | 153 | 0 | 24 | 0 | 86 | 30 | 154 | 0 | 100 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 8385.36 | 794 | 152 | 0 | 30 | 40 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 372 | 0 | 0 | 0 | 1411.45 | 0 | 40 | 0 | 113 | 113 | 0 | 100 | 27 | 0 | 0 | 0 | 30 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 391 | 0 | 0 | 161 | 50 | 115 | 0 | 105 | 0 | 80 | 0 | 0 | 0 | 0 | 108 | 307 | 120 | 220 | 0 | 1250 | 1232 | 54 | 7710.45 | 16095.81 | 75.25
01:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 235 | 0 | 0 | 34 | 147 | 32 | 55 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 125 | 18 | 21 | 0 | 360 | 90 | 16 | 24 | 0 | 8 | 34 | 51 | 54.36 | 24 | 24 | 0 | 30 | 105 | 27 | 935 | 17 | 0 | 50 | 0 | 95 | 217 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 20 | 356 | 220 | 51 | 0 | 201 | 0 | 17 | 97 | 181 | 0 | 19 | 108 | 160 | 43 | 0 | 23 | 305 | 0 | 308 | 42 | 30 | 137 | 0 | 22 | 0 | 86 | 30 | 152 | 0 | 100 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 7709.36 | 888 | 154 | 0 | 27 | 40 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 383 | 0 | 0 | 0 | 1306.42 | 0 | 40 | 0 | 113 | 113 | 0 | 0 | 27 | 0 | 0 | 0 | 30 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 341 | 0 | 0 | 156 | 49 | 115 | 0 | 106 | 0 | 80 | 0 | 0 | 0 | 0 | 70 | 307 | 120 | 220 | 0 | 1245 | 1225 | 17 | 7467.42 | 15176.78 | 75.25
02:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 272 | 0 | 0 | 34 | 147 | 32 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 125 | 18 | 21 | 0 | 440 | 90 | 16 | 21 | 0 | 11 | 0 | 44 | 54.36 | 24 | 24 | 0 | 30 | 104 | 27 | 830 | 16 | 0 | 50 | 0 | 94 | 217 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 0 | 355 | 220 | 51 | 0 | 202 | 0 | 0 | 98 | 182 | 0 | 19 | 107 | 158 | 43 | 0 | 23 | 295 | 0 | 308 | 42 | 30 | 142 | 0 | 22 | 0 | 86 | 30 | 152 | 0 | 100 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 7606.36 | 888 | 156 | 0 | 27 | 40 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 400 | 0 | 0 | 0 | 1296.23 | 0 | 40 | 0 | 113 | 113 | 0 | 0 | 27 | 0 | 0 | 0 | 30 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 375 | 0 | 0 | 163 | 50 | 115 | 0 | 99 | 0 | 80 | 0 | 0 | 0 | 0 | 21 | 307 | 120 | 220 | 0 | 1244 | 1232 | 17 | 7468.23 | 15074.59 | 75.25
03:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 248 | 0 | 0 | 34 | 147 | 32 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 125 | 18 | 21 | 0 | 410 | 91 | 16 | 18 | 0 | 15 | 0 | 44 | 54.36 | 24 | 24 | 0 | 30 | 99 | 29 | 730 | 17 | 0 | 50 | 0 | 92 | 218 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 0 | 356 | 220 | 51 | 0 | 200 | 0 | 0 | 98 | 180 | 0 | 19 | 108 | 154 | 43 | 0 | 23 | 295 | 0 | 308 | 42 | 30 | 144 | 0 | 22 | 0 | 86 | 30 | 154 | 0 | 100 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 7450.36 | 888 | 160 | 0 | 27 | 40 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 402 | 0 | 0 | 0 | 1266.71 | 0 | 40 | 0 | 113 | 113 | 0 | 0 | 27 | 0 | 0 | 0 | 30 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 360 | 0 | 0 | 166 | 50 | 115 | 0 | 98 | 0 | 80 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 1253 | 1234 | 17 | 7437.71 | 14888.07 | 75.25
04:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 297 | 0 | 0 | 19 | 147 | 32 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 125 | 18 | 21 | 0 | 430 | 90 | 16 | 19 | 0 | 11 | 0 | 44 | 54.36 | 24 | 24 | 0 | 30 | 105 | 29 | 670 | 16 | 0 | 50 | 0 | 90 | 218 | 0 | 0 | 0 | 1224 | 0 | 147 | 0 | 0 | 357 | 220 | 51 | 0 | 202 | 0 | 0 | 98 | 181 | 0 | 19 | 107 | 148 | 43 | 0 | 23 | 300 | 0 | 308 | 42 | 30 | 145 | 0 | 22 | 0 | 86 | 30 | 147 | 0 | 100 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 7420.36 | 888 | 161 | 0 | 27 | 35 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 402 | 0 | 0 | 0 | 1239.8 | 0 | 40 | 0 | 113 | 113 | 0 | 0 | 27 | 0 | 0 | 0 | 30 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 397 | 0 | 0 | 168 | 49 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 1250 | 1235 | 17 | 7363.8 | 14784.16 | 75.25
05:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 253 | 0 | 0 | 17 | 130 | 32 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 125 | 18 | 21 | 0 | 370 | 91 | 16 | 19 | 0 | 19 | 0 | 44 | 54.36 | 24 | 24 | 0 | 30 | 104 | 31 | 625 | 18 | 0 | 50 | 0 | 89 | 219 | 0 | 0 | 0 | 1224 | 0 | 117 | 0 | 0 | 355 | 220 | 51 | 0 | 200 | 0 | 0 | 98 | 180 | 0 | 19 | 107 | 144 | 43 | 0 | 23 | 295 | 0 | 308 | 42 | 30 | 146 | 0 | 14 | 0 | 86 | 30 | 152 | 0 | 100 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 7215.36 | 888 | 164 | 0 | 27 | 35 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 402 | 0 | 0 | 0 | 1201.97 | 0 | 40 | 0 | 113 | 113 | 0 | 0 | 27 | 8 | 0 | 0 | 30 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 343 | 0 | 0 | 163 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 1248 | 1240 | 17 | 7279.97 | 14495.33 | 75.25
06:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 248 | 0 | 0 | 17 | 130 | 32 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 1 | 125 | 18 | 21 | 0 | 410 | 89 | 16 | 22 | 0 | 7 | 0 | 44 | 54.36 | 24 | 24 | 0.28 | 30 | 98 | 31 | 625 | 17 | 0 | 50 | 0 | 90 | 219 | 0 | 0 | 0 | 1224 | 1 | 45 | 0 | 0 | 356 | 220 | 51 | 0 | 203 | 0 | 0 | 96 | 179 | 0 | 19 | 100 | 144 | 43 | 3 | 23 | 310 | 0 | 308 | 42 | 30 | 134 | 1 | 22 | 0 | 86 | 30 | 152 | 0 | 100 | 0 | 9 | 78 | 0 | 0.08 | 1.78 | 0 | 7169.5 | 490 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 3.53 | 403 | 0 | 0 | 0 | 1133.05 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 8 | 1.52 | 2 | 28 | 0 | 1.18 | 140 | 0 | 140 | 0 | 0 | 0 | 364 | 0 | 0.13 | 168 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 1 | 0.04 | 16 | 307 | 120 | 220 | 0 | 1248 | 1240 | 17 | 6718.45 | 13887.95 | 75.25
07:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 232 | 0 | 0 | 17 | 123 | 32 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 3 | 125 | 18 | 21 | 0 | 380 | 17 | 16 | 24 | 0 | 6 | 0 | 44 | 17 | 24 | 24 | 1.12 | 30 | 85 | 26 | 625 | 16 | 0 | 50 | 0 | 51 | 218 | 0 | 0 | 0 | 1224 | 5 | 13 | 0 | 0 | 354 | 270 | 51 | 0 | 200 | 0 | 0 | 97 | 178 | 0 | 19 | 107 | 132 | 43 | 10 | 23 | 300 | 0 | 309 | 42 | 30 | 133 | 3 | 22 | 0 | 86 | 30 | 153 | 0 | 100 | 0 | 9 | 78 | 0 | 0.12 | 3.58 | 0 | 6957.82 | 465 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19.06 | 403 | 8 | 0 | 0 | 1063.14 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 0 | 16 | 7.56 | 8 | 0 | 0 | 6.51 | 140 | 0 | 140 | 0 | 0 | 0 | 344 | 0 | 0.81 | 164 | 49 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 9 | 0.14 | 16 | 307 | 120 | 220 | 0 | 1253 | 1242 | 17 | 6439.22 | 13397.04 | 75.25
08:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 224 | 0 | 0 | 17 | 147 | 32 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 9 | 86 | 18 | 21 | 0 | 390 | 17 | 16 | 25 | 0 | 8 | 0 | 44 | 17 | 24 | 24 | 2.26 | 30 | 34 | 13 | 625 | 0 | 0 | 50 | 0 | 51 | 215 | 0 | 0 | 0 | 1224 | 9 | 13 | 0 | 0 | 356 | 270 | 51 | 0 | 195 | 0 | 0 | 96 | 100 | 0 | 19 | 17 | 140 | 34 | 32 | 0 | 295 | 0 | 308 | 42 | 30 | 140 | 5 | 22 | 0 | 86 | 30 | 152 | 0 | 100 | 0 | 9 | 78 | 0 | 0.28 | 12.4 | 0 | 6735.94 | 465 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.79 | 405 | 14 | 0 | 0 | 1168.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.59 | 30 | 0 | 0 | 11.18 | 140 | 0 | 140 | 0 | 0 | 0 | 332 | 0 | 0.91 | 153 | 48 | 0 | 3 | 49 | 0 | 0 | 0 | 0 | 4 | 0.3 | 0 | 307 | 120 | 220 | 0 | 1247 | 1216 | 0 | 6291.42 | 13027.36 | 75.25
09:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 262 | 0 | 0 | 17 | 145 | 32 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 9 | 105 | 19 | 21 | 0 | 400 | 0 | 16 | 24 | 0 | 8 | 0 | 44 | 0 | 24 | 24 | 3.27 | 30 | 34 | 13 | 625 | 0 | 0 | 50 | 0 | 34 | 214 | 0 | 0 | 0 | 1212 | 9 | 11 | 0 | 0 | 357 | 240 | 51 | 1 | 200 | 20 | 0 | 95 | 100 | 0 | 19 | 17 | 138 | 34 | 42 | 0 | 300 | 0 | 308 | 42 | 30 | 136 | 7 | 22 | 0 | 83 | 30 | 152 | 0 | 100 | 0 | 9 | 78 | 0 | 0.01 | 14.08 | 0 | 6755.36 | 465 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 400 | 17 | 0 | 0 | 1174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.36 | 36 | 0 | 0 | 33.27 | 140 | 0 | 140 | 0 | 0 | 0 | 366 | 0 | 2.07 | 158 | 48 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 3 | 0.45 | 0 | 274 | 120 | 220 | 0 | 1249 | 1206 | 0 | 6323.15 | 13078.51 | 75.25
10:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 344 | 0 | 0 | 32 | 129 | 32 | 55 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 296 | 0 | 0 | 21 | 105 | 11.5 | 20 | 0 | 385 | 0 | 0 | 24 | 0 | 15 | 0 | 44 | 0 | 24 | 24 | 4.11 | 30 | 0 | 6 | 625 | 0 | 0 | 50 | 0 | 17 | 213 | 0 | 0 | 0 | 1160 | 10 | 13 | 0 | 0 | 356 | 240 | 51 | 10 | 198 | 33 | 0 | 95 | 68 | 0 | 19 | 17 | 134 | 34 | 9 | 0 | 300 | 0 | 295 | 42 | 30 | 130 | 1 | 22 | 0 | 80 | 30 | 152 | 0 | 100 | 0 | 9 | 87 | 0 | 0 | 11.69 | 0 | 6636.3 | 888 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 400 | 17 | 0 | 0 | 1076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.07 | 56 | 0 | 0 | 0.17 | 140 | 0 | 140 | 0 | 0 | 0 | 337 | 0 | 0 | 150 | 50 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 2 | 0.45 | 0 | 219 | 100 | 180 | 0 | 1249 | 1070 | 0 | 6383.69 | 13019.99 | 75.25
11:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 384 | 0 | 0 | 34 | 128 | 32 | 55 | 25 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 299 | 0 | 0 | 12 | 105 | 11.5 | 20 | 0 | 400 | 0 | 0 | 25 | 0 | 16 | 0 | 44 | 0 | 24 | 24 | 4.65 | 30 | 0 | 6 | 625 | 0 | 0 | 50 | 0 | 15 | 212 | 0 | 0 | 0 | 1057 | 14 | 13 | 0 | 0 | 349 | 240 | 51 | 23 | 200 | 40 | 0 | 94 | 67 | 0 | 17 | 17 | 146 | 43 | 47 | 0 | 310 | 0 | 295 | 42 | 30 | 134 | 1 | 22 | 0 | 81 | 30 | 152 | 0 | 100 | 0 | 9 | 65 | 0 | 0.05 | 2.42 | 0 | 6657.62 | 888 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 442 | 17 | 0 | 0 | 1015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.3 | 83 | 0 | 0 | 8.34 | 140 | 0 | 140 | 0 | 0 | 0 | 352 | 0 | 0 | 157 | 50 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 19 | 0.35 | 0 | 186 | 100 | 180 | 0 | 1248 | 1000 | 0 | 6314.99 | 12972.61 | 75.25
12:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 232 | 0 | 0 | 34 | 144 | 32 | 55 | 32 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 299 | 0 | 0 | 7 | 68 | 20 | 20 | 0 | 415 | 0 | 0 | 24 | 0 | 15 | 0 | 23 | 0 | 24 | 24 | 0.9 | 30 | 0 | 9 | 625 | 0 | 0 | 50 | 0 | 17 | 212 | 0 | 0 | 0 | 1054 | 16 | 0 | 0 | 0 | 300 | 240 | 20 | 25 | 200 | 38 | 0 | 92 | 34 | 0 | 19 | 0 | 158 | 25 | 63 | 22 | 305 | 0 | 320 | 42 | 30 | 130 | 0 | 22 | 0 | 52 | 30 | 154 | 0 | 100 | 0 | 9 | 65 | 0 | 0.62 | 0 | 0 | 6354.52 | 888 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 448 | 17 | 0 | 0 | 1041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.72 | 100 | 0 | 0 | 55.49 | 140 | 0 | 140 | 0 | 0 | 0 | 358 | 0 | 5.44 | 163 | 47 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 100 | 0.42 | 0 | 194 | 100 | 180 | 0 | 1250 | 900 | 0 | 6450.07 | 12804.59 | 75.25
13:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 312 | 0 | 0 | 34 | 128 | 32 | 55 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 12 | 61 | 20 | 0 | 0 | 450 | 0 | 0 | 24 | 0 | 26 | 0 | 0 | 0 | 24 | 24 | 0.84 | 30 | 0 | 14 | 605 | 0 | 0 | 50 | 0 | 17 | 212 | 0 | 0 | 0 | 1171 | 16 | 0 | 0 | 0 | 355 | 345 | 32 | 27 | 206 | 38 | 0 | 93 | 0 | 0 | 19 | 0 | 154 | 0 | 59 | 7 | 310 | 0 | 320 | 42 | 30 | 154 | 3 | 22 | 0 | 61 | 30 | 153 | 0 | 100 | 0 | 9 | 79 | 0 | 1.78 | 11.11 | 0 | 6712.73 | 888 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 462 | 3 | 0 | 0 | 1259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.23 | 93 | 0 | 0 | 52.17 | 140 | 0 | 140 | 0 | 0 | 0 | 407 | 0 | 4.33 | 163 | 46 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 141 | 0.64 | 0 | 251 | 120 | 220 | 0 | 1244 | 960 | 0 | 6854.37 | 13567.1 | 75.25
14:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 216 | 0 | 4 | 34 | 130 | 32 | 30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 27 | 68 | 23 | 14 | 0 | 470 | 0 | 0 | 20 | 0 | 15 | 0 | 0 | 0 | 12 | 24 | 3.74 | 30 | 0 | 14 | 500 | 0 | 0 | 40 | 0 | 17 | 211 | 0 | 0 | 0 | 1116 | 7 | 0 | 0 | 0 | 354 | 345 | 51 | 43 | 205 | 39 | 0 | 97 | 0 | 0 | 19 | 0 | 156 | 0 | 38 | 0 | 305 | 0 | 320 | 42 | 30 | 145 | 4 | 22 | 0 | 61 | 30 | 154 | 0 | 100 | 0 | 9 | 87 | 0 | 1.72 | 15.71 | 0 | 6429.17 | 888 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 462 | 0 | 0 | 0 | 1305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.33 | 79 | 0 | 0 | 44.48 | 140 | 0 | 140 | 0 | 0 | 0 | 400 | 0 | 4.09 | 162 | 47 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 125 | 0.37 | 0 | 244 | 120 | 220 | 0 | 1254 | 1050 | 0 | 6960.27 | 13389.44 | 75.25
15:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 312 | 0 | 17 | 38 | 130 | 32 | 30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 16 | 51 | 19 | 14 | 0 | 460 | 0 | 0 | 6 | 0 | 17 | 0 | 0 | 0 | 12 | 24 | 2.94 | 30 | 0 | 9 | 500 | 0 | 0 | 32 | 0 | 15 | 212 | 0 | 0 | 0 | 1173 | 13 | 0 | 0 | 0 | 356 | 345 | 51 | 47 | 206 | 39 | 0 | 99 | 0 | 0 | 19 | 0 | 150 | 0 | 44 | 0 | 315 | 0 | 344 | 42 | 30 | 155 | 2 | 22 | 0 | 61 | 30 | 153 | 0 | 100 | 0 | 9 | 87 | 0 | 1.32 | 17.81 | 0 | 6616.07 | 888 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 474 | 2 | 0 | 0 | 1310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.29 | 68 | 0 | 0 | 32.29 | 140 | 0 | 140 | 0 | 0 | 0 | 402 | 0 | 3.03 | 177 | 47 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 113 | 0.14 | 0 | 278 | 120 | 220 | 0 | 1253 | 1050 | 0 | 6993.75 | 13609.82 | 75.25
16:00 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 305 | 0 | 17 | 42 | 130 | 32 | 30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 13 | 51 | 19 | 14 | 0 | 450 | 0 | 0 | 6 | 0 | 16 | 33 | 0 | 0 | 12 | 24 | 2.02 | 30 | 0 | 3 | 500 | 0 | 0 | 32 | 0 | 16 | 212 | 0 | 0 | 0 | 1162 | 8 | 0 | 0 | 0 | 357 | 345 | 51 | 47 | 200 | 39 | 0 | 99 | 0 | 0 | 19 | 0 | 150 | 0 | 8 | 0 | 315 | 0 | 344 | 42 | 30 | 154 | 1 | 22 | 0 | 83 | 30 | 153 | 0 | 101 | 0 | 19 | 97 | 0 | 0.72 | 22.38 | 0 | 6633.12 | 888 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 471 | 16 | 0 | 0 | 1301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.31 | 43 | 0 | 0 | 7.35 | 140 | 0 | 140 | 0 | 0 | 0 | 389 | 0 | 0.96 | 172 | 47 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 75 | 0.24 | 0 | 278 | 0 | 220 | 0 | 1251 | 1120 | 0 | 6794.86 | 13427.98 | 75.25
17:00 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 265 | 17 | 17 | 36 | 130 | 32 | 30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 297 | 0 | 0 | 5 | 51 | 18.5 | 18 | 0 | 440 | 0 | 0 | 6 | 0 | 13 | 48 | 0 | 0 | 12 | 24 | 0.56 | 30 | 0 | 16 | 500 | 0 | 0 | 32 | 1 | 15 | 212 | 0 | 0 | 0 | 1160 | 3 | 0 | 0 | 0 | 356 | 345 | 51 | 46 | 200 | 35 | 0 | 99 | 0 | 0 | 19 | 0 | 144 | 0 | 1 | 0 | 310 | 0 | 344 | 42 | 30 | 150 | 2 | 22 | 0 | 86 | 30 | 153 | 0 | 101 | 0 | 19 | 97 | 0 | 0.37 | 8.68 | 8 | 6601.11 | 888 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 489 | 16 | 0 | 0 | 1323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6 | 12 | 0 | 0 | 9.88 | 140 | 0 | 140 | 0 | 0 | 0 | 390 | 0 | 0.91 | 166 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0.16 | 0 | 275 | 0 | 220 | 0 | 1250 | 1130 | 0 | 6707.55 | 13308.66 | 75.25
18:00 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 208 | 17 | 17 | 51 | 130 | 32 | 30 | 14 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 295 | 0 | 0 | 2 | 51 | 18.5 | 18 | 0 | 420 | 0 | 0 | 6 | 0 | 7 | 48 | 22 | 0 | 12 | 24 | 0.04 | 30 | 0 | 4 | 500 | 0 | 0 | 32 | 13 | 17 | 212 | 0 | 0 | 0 | 1160 | 1 | 1 | 0 | 0 | 357 | 345 | 51 | 45 | 197 | 39 | 6 | 99 | 0 | 0 | 19 | 0 | 142 | 1 | 0 | 0 | 310 | 0 | 320 | 42 | 30 | 145 | 0 | 16 | 0 | 86 | 30 | 151 | 0 | 101 | 0 | 19 | 97 | 0 | 0 | 2.82 | 12 | 6514.36 | 888 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 509 | 16 | 0 | 0 | 1322 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 0 | 2.64 | 4 | 15 | 0 | 2.47 | 140 | 0 | 140 | 0 | 0 | 0 | 363 | 0 | 0.18 | 175 | 50 | 35 | 2 | 34 | 0 | 0 | 0 | 0.5 | 9 | 0.05 | 0.28 | 259 | 0 | 220 | 0 | 1253 | 1110 | 0 | 6766.12 | 13280.48 | 75.25
19:00 | 0 | 60 | 50 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 331 | 17 | 17 | 51 | 131 | 32 | 32 | 54 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 317 | 0 | 0 | 0 | 92 | 22 | 18 | 0 | 480 | 13 | 15 | 22 | 0 | 1 | 48 | 46 | 0 | 24 | 24 | 0 | 30 | 24 | 18 | 720 | 15 | 0 | 35 | 17 | 56 | 212 | 0 | 0 | 0 | 1205 | 0 | 70 | 0 | 0 | 357 | 345 | 51 | 47 | 213 | 40 | 34 | 98 | 37 | 0 | 19 | 17 | 152 | 10 | 0 | 31 | 305 | 0 | 354 | 42 | 30 | 138 | 0 | 16 | 0 | 86 | 30 | 152 | 0 | 101 | 17 | 19 | 98 | 0 | 0 | 0 | 12 | 7568 | 888 | 179 | 0 | 27 | 29 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 509 | 16 | 0 | 0 | 1444 | 0 | 40 | 0 | 50 | 25 | 0 | 93 | 21 | 0 | 0 | 0 | 34 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 408 | 0 | 0 | 176 | 49 | 108 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 261 | 0 | 220 | 0 | 1252 | 1040 | 17 | 7287 | 14855 | 75.25
19:30 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 282 | 17 | 17 | 52 | 130 | 32 | 55 | 55 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 298 | 0 | 0 | 0 | 142 | 22 | 21 | 0 | 440 | 72 | 15 | 45 | 0 | 5 | 48 | 46 | 0 | 24 | 24 | 0 | 30 | 51 | 18 | 860 | 14 | 0 | 45 | 17 | 88 | 212 | 0 | 0 | 0 | 1224 | 0 | 70 | 0 | 0 | 357 | 345 | 51 | 47 | 197 | 40 | 51 | 98 | 145 | 18 | 19 | 17 | 158 | 43 | 0 | 31 | 310 | 0 | 342 | 42 | 30 | 150 | 0 | 22 | 0 | 86 | 30 | 152 | 0 | 101 | 17 | 19 | 98 | 0 | 0 | 0 | 12 | 8058 | 888 | 179 | 0 | 37 | 41 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 504 | 16 | 0 | 0 | 1437 | 0 | 40 | 0 | 70 | 70 | 0 | 93 | 21 | 11 | 0 | 0 | 33 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 391 | 0 | 0 | 180 | 49 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 0 | 220 | 0 | 1248 | 1130 | 54 | 7591 | 15649
20:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 210 | 17 | 17 | 51 | 132 | 32 | 55 | 55 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 131 | 5 | 22 | 0 | 370 | 61 | 15 | 48 | 0 | 7 | 50 | 46 | 0 | 24 | 24 | 0 | 30 | 86 | 20 | 920 | 15 | 0 | 45 | 17 | 95 | 214 | 0 | 0 | 0 | 1224 | 0 | 70 | 0 | 0 | 357 | 345 | 51 | 48 | 198 | 37 | 51 | 98 | 133 | 15 | 19 | 16 | 156 | 43 | 0 | 31 | 310 | 0 | 344 | 42 | 30 | 142 | 0 | 22 | 0 | 86 | 30 | 152 | 0 | 101 | 17 | 19 | 98 | 0 | 0 | 0 | 12 | 7966 | 889 | 179 | 0 | 33 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 499 | 17 | 0 | 0 | 1445 | 0 | 40 | 0 | 70 | 90 | 0 | 91 | 28 | 25 | 0 | 0 | 32 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 344 | 0 | 0 | 180 | 48 | 115 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 307 | 15 | 220 | 0 | 1250 | 1112 | 54 | 7573 | 15539 | 75.25
21:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 259 | 17 | 17 | 51 | 60 | 32 | 55 | 55 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 142 | 0 | 22 | 0 | 440 | 76 | 15 | 50 | 0 | 21 | 50 | 46 | 0 | 24 | 24 | 0 | 30 | 104 | 20 | 1000 | 14 | 0 | 39 | 17 | 99 | 214 | 0 | 0 | 0 | 1224 | 0 | 58 | 0 | 0 | 357 | 345 | 51 | 47 | 199 | 37 | 51 | 98 | 120 | 17 | 19 | 17 | 144 | 43 | 0 | 31 | 310 | 0 | 344 | 42 | 30 | 147 | 0 | 22 | 0 | 86 | 25 | 152 | 0 | 101 | 17 | 37 | 117 | 0 | 0 | 0 | 0 | 8123 | 889 | 182 | 0 | 33 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 499 | 16 | 0 | 0 | 1445 | 0 | 40 | 0 | 70 | 113 | 0 | 91 | 28 | 8 | 0 | 0 | 32 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 379 | 0 | 0 | 179 | 48 | 115 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 83 | 220 | 0 | 1251 | 1070 | 54 | 7645 | 15768 | 75.25
22:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 228 | 17 | 17 | 42 | 60 | 32 | 55 | 55 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 142 | 0 | 22 | 0 | 450 | 75 | 15 | 49 | 0 | 13 | 49 | 46 | 0 | 24 | 24 | 0 | 30 | 105 | 16 | 1000 | 16 | 0 | 39 | 17 | 96 | 215 | 0 | 0 | 0 | 1224 | 0 | 20 | 0 | 0 | 356 | 345 | 51 | 48 | 200 | 37 | 48 | 98 | 115 | 18 | 19 | 17 | 156 | 43 | 0 | 31 | 310 | 0 | 344 | 42 | 30 | 147 | 0 | 22 | 0 | 86 | 25 | 152 | 0 | 101 | 17 | 37 | 117 | 0 | 0 | 0 | 0 | 8043 | 888 | 185 | 0 | 33 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 486 | 16 | 0 | 0 | 1439 | 0 | 40 | 0 | 70 | 113 | 0 | 92 | 28 | 8 | 0 | 0 | 32 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 397 | 0 | 0 | 180 | 48 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 123 | 220 | 0 | 1252 | 1090 | 54 | 7704 | 15747 | 75.25
23:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 301 | 17 | 0 | 25 | 114 | 32 | 55 | 55 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 142 | 22 | 22 | 0 | 460 | 79 | 16 | 50 | 0 | 27 | 49 | 45 | 1 | 24 | 24 | 0 | 30 | 106 | 16 | 930 | 45 | 0 | 44 | 17 | 101 | 216 | 0 | 0 | 0 | 1224 | 0 | 20 | 2 | 0 | 357 | 345 | 51 | 48 | 200 | 33 | 34 | 31 | 123 | 17 | 19 | 28 | 166 | 43 | 0 | 31 | 310 | 0 | 331 | 42 | 30 | 154 | 0 | 24 | 0 | 86 | 30 | 154 | 0 | 101 | 17 | 9 | 78 | 0 | 0 | 0 | 0 | 8047 | 888 | 183 | 0 | 33 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 486 | 16 | 0 | 0 | 1440 | 0 | 40 | 0 | 100 | 113 | 0 | 83 | 28 | 8 | 0 | 0 | 32 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 398 | 0 | 0 | 175 | 48 | 115 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 123 | 220 | 0 | 1248 | 1130 | 54 | 7731 | 15778 | 75.25
Total KWH | 0 | 478080 | 624000 | 0 | 0 | 0 | 0 | 0 | 8690400 | 0 | 6636480 | 129600 | 153000 | 812448 | 3066240 | 774556 | 1210116 | 439149 | 424800 | 0 | 0 | 0 | 0 | 0 | 137910 | 7271767 | 0 | 0 | 146844 | 2586000 | 423000 | 462260 | 0 | 10131818.18 | 1019945 | 225818 | 617280 | 0 | 304320 | 442063 | 835248 | 445966 | 528000 | 582720 | 25664 | 718260 | 1374975 | 441120 | 16625454.55 | 354618 | 0 | 1088160 | 96669 | 1472836 | 5011264 | 0 | 0 | 0 | 28532724 | 106380 | 1119054 | 16727.27 | 150000 | 8849800 | 7002000 | 1188868 | 597120 | 4955000 | 547776 | 288960 | 2222880 | 2420640 | 70560 | 472000 | 1067040 | 3553920 | 713304 | 344791 | 366416 | 7427000 | 0 | 7857000 | 994000 | 729120 | 3438081.82 | 0 | 532752 | 0 | 1916160 | 708576 | 3534000 | 0 | 2411470 | 92520 | 339600 | 2068800 | 0 | 7400 | 134690 | 55680 | 173641658.82 | 19750545 | 4351968 | 0 | 307680 | 394627 | 0 | 0 | 0 | 0 | 0 | 145728 | 503280 | 10734545 | 220320 | 0 | 0 | 30473242 | 0 | 446872 | 0 | 1204704 | 1401216 | 0 | 527872 | 266643 | 113803 | 289112 | 581858 | 377800 | 0 | 259568 | 3447909 | 0 | 3654355 | 0 | 0 | 0 | 9017673 | 0 | 23520 | 4119000 | 1144145 | 1445879 | 158148 | 1292448 | 0 | 0 | 0 | 472.08 | 600480 | 3925 | 541632 | 6698000 | 2370000 | 5334900 | 0 | 30021818 | 27594181.82 | 415200 | 170235068.9 | 343876727.72

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 22-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13078.51 | MW | 09:00 Hr. | Energy Generated |  |  | 343.8767 |  | MKWHr.
| Day Peak Demand |  |  | 13140.51 | MW | 09:00 Hr. | Energy Unserverd |  |  | 8.284 |  | MKWHr.
| Evening Peak Generation |  |  | 15768 | MW | 21:00 Hr. | Energy Demand |  |  | 352.1607 |  | MKWHr.
| Evening Peak Demand |  |  | 16080 | MW | 21:00 Hr. | Maximum Temperature |  |  | 29 |  | °C
| Minimum Generation of the Day |  |  | 12804.59 | MW | 12:00 Hr. | Total Gas Supplied |  |  | 938.65 |  | MMCFD
| Maximum Generation of the Day |  |  | 16095.81 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.5685 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.6157 | 0 | 10.8359 | 0 | 0 | 0.14684 | 0 | 0 | 44.5985 | Gas | 122.7952 | Gas | 430804817.5636
| Chattogram Zone |  |  | 5.4524 | 45.1582 | 9.0843 | 0 | 0.71826 | 0.13204 | 0 | 0.30432 | 60.8495 | Coal | 125.4699 | Coal | 807846074.0085
| Cumilla Zone |  |  | 26.0022 | 0 | 6.046 | 0 | 0 | 0.34479 | 3.5539 | 0 | 35.9469 | HFO | 37.6252 | HFO | 651361825.79
| Mymensingh Zone |  |  | 0 | 0 | 2.5566 | 0 | 0 | 0.14209 | 0 | 0 | 2.6987 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 29.5482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.5482 | Hydro | 0.71826 | Hydro | 71826
| Khulna Zone |  |  | 4.352 | 10.7345 | 1.0684 | 0 | 0 | 0.50328 | 19.7505 | 0 | 36.4087 | Solar | 3.1861 | Solar | 50225673.5316
| Barishal Zone |  |  | 7.7049 | 64.314 | 0.95683 | 0 | 0 | 0.003925 | 0 | 0 | 72.9797 | Import | 53.7777 | Import | 313957201.68
| Rajshahi Zone |  |  | 16.1199 | 0 | 4.3389 | 0 | 0 | 1.1541 | 30.4732 | 0 | 52.0861 | Wind | 0.30432 | Wind | 4476547.2
| Rangpur Zone |  |  | 0 | 5.2631 | 2.7383 | 0 | 0 | 0.7591 | 0 | 0 | 8.7606
| Total |  |  | 122.7952 | 125.4699 | 37.6252 | 0 | 0.71826 | 3.1861 | 53.7777 | 0.30432 | 343.8767
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 430804817.5636 |  | Hydro | 71826
|  |  |  | Coal | 807846074.0085 |  | Solar | 50225673.5316
|  |  |  | HFO | 651361825.79 |  | Import | 313957201.68
|  |  |  | HSD | 0 |  | Wind | 4476547.2
[5 empty] | Total: | 225,87,43,965 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.7505 | Peak Hr Flow | 889.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 56466545.45 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.4732 | Peak Hr Flow | 1445.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2413 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.5539 | Peak Hr Flow | 144.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2792 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.7777 | Peak Hr Flow | 2478.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 53 |  | 5344
|  |  |  | Chattogram |  | 13 |  | 1630
|  |  |  | Cumilla |  | 29 |  | 1616
|  |  |  | Mymensingh |  | 167 |  | 1262
|  |  |  | Sylhet |  | 0 |  | 618
|  |  |  | Khulna |  | 37 |  | 2051
|  |  |  | Barishal |  | 0 |  | 487
|  |  |  | Rajshahi |  | 0 |  | 1545
|  |  |  | Rangpur |  | 0 |  | 963
|  |  |  | Total |  | 299 |  | 15516
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Baghabari 100 MW GTPP |  |  | 100
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 700 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 09:07 | Barishal 132/33kV S/S T-1 (405T) HT is restored.
|  | 09:08 | Barishal 132/33kV S/S T-1 (405T) LT is restored.
| 09:12 | 09:49 | Ishurdi 132/33kV S/S 132/33 kV T-1 LT Scheduled S/D Due to maintenance work on station | [7 empty] | 30.0MW load
|  |  | auxiliary x-former | [7 empty] | interrup.
| 09:13 | 09:49 | Ishurdi 132/33kV S/S 132/33 kV T-1 HT Scheduled S/D Due to maintenance work on station | [7 empty] | 30.0MW load
|  |  | auxiliary x-former | [7 empty] | interrup.
|  | 09:15 | Baroaulia 132/33kV S/S T-1(405T) HT is restored.
| 09:28 | 12:22 | Panchagarh 132/33kV S/S T-3(A+B)(427T) HT Forced S/D Due to Red hot Maintenance work
| 09:28 | 12:23 | Panchagarh 132/33kV S/S T-3(A+B)(427T) LT Forced S/D Due to Red hot Maintenance work
| 09:37 | 20:09 | BIPTC S/S Baharampur-3 Scheduled S/D
| 09:41 | 11:39 | Rangpur 132/33kV S/S T-1(414T) HT Forced S/D Due to Red hot
| 09:41 | 11:40 | Rangpur 132/33kV S/S T-1(414T) LT Forced S/D Due to Red hot
| 10:00 | 10:35 | Halishahar-Julda 132kV Ckt-1 Forced S/D from Juldah 132/33kV end Due to Order of NLDC
|  | 10:00 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) HT is restored.
|  | 10:01 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT is restored.
| 10:32 | 15:53 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-1 Scheduled S/D Due to As per ALDC 's
instruction
| 10:32 | 15:53 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Scheduled S/D Due to As per ALDC 's
instruction
| 10:37 | 12:20 | Patuakhali-Payra 132kV Ckt-1 Scheduled S/D from Payra 400/132/33kV end Due to High
temperature at primary junction point of CT
|  | 10:44 | Bhandaria 132/33kV S/S Transformer-1 HT is restored.
|  | 10:47 | Bhandaria 132/33kV S/S Transformer-2 HT is restored.
|  | 10:47 | Bhandaria 132/33kV S/S Transformer-1 LT is restored.
|  | 10:48 | Bhandaria 132/33kV S/S Transformer-2 LT is restored.
| 10:58 | 10:58 | Brahmanbaria 132/33kV S/S 401T HT Forced S/D Due to redhot maintenance at 33kv kasba | [7 empty] | 15.0MW load
|  |  | feeder bus DS | [7 empty] | interrup.
| 10:58 | 11:40 | Brahmanbaria 132/33kV S/S 401T LT Forced S/D Due to redhot at 33 kv kasba feeder bus DS | [7 empty] | 15.0MW load
interrup.
| 11:18 | 22:52 | Bhulta-Ghorasal 230 kV Ckt-2 Scheduled S/D from Bhulta 400/230kV end.
|  | 11:37 | Meghnaghat-Shyampur 230kV Ckt-2 is restored.
| 11:57 | 13:01 | Maniknagar-Narinda 132kV Ckt-1 Scheduled S/D from Maniknagar 132/33kV end Due to Dc
supply replacement work with new charger /distribution panel for main and backup
protection relay.
|  | 12:16 | Jamalpur 132/33kV S/S T-2 LT is restored.
|  | 12:16 | Jamalpur 132/33kV S/S T-2 HT is restored.
| 12:22 |  | Jamalpur 132/33kV S/S T-3 LT Scheduled S/D Due to Auxiliary T-2 Shifting work
| 12:58 |  | BIPTC S/S 20DF43 Tripped showing 186, 286 Lockout Relay relays.
| 13:42 |  | Matarbari 2*600 MW (CPGCBL) Shutdown
| 13:55 |  | Matarbari 2*600 MW (CPGCBL) Synchronized
| 13:55 |  | Matarbari 2*600 MW (CPGCBL) Synchronized
| 15:03 | 16:03 | Maniknagar-Narinda 132kV Ckt-2 Scheduled S/D from Maniknagar 132/33kV end Due to New DC
connection with new DC distribution panel
| 15:44 | 15:59 | Purbasadipur 230/132/33kV S/S TR-4 LT Tripped showing Siprotec,siemens relays Due to | [7 empty] | 35.0MW load
|  |  | Bochaganj 33kv feeder fault | [7 empty] | interrup.
| 16:10 | 17:10 | Dohazari 132/33kV S/S Power Transformer -T-1 LT Scheduled S/D Due to Due to Banshkhali 33 | [7 empty] | 25.0MW load
|  |  | KV BUS DS redhot maintenance | [7 empty] | interrup.
| 16:10 | 17:10 | Dohazari 132/33kV S/S Power Transformer -T-1 HT Scheduled S/D Due to Due to Banshkhali 33 | [7 empty] | 25.0MW load
|  |  | KV BUS DS redhot maintenance | [7 empty] | interrup.
| 16:21 | 17:34 | Maniknagar 132/33kV S/S Motijheel Ckt-1 Scheduled S/D Due to New DC connection with new
DC distribution panel
| 17:44 |  | Maniknagar 132/33kV S/S Motijheel Ckt-2 Scheduled S/D Due to Connect new DC from new DC
distribution panel.
| 18:03 |  | Matarbari 2*600 MW (CPGCBL) Synchronized with remarks:- U2
| 19:16 |  | Joypurhat-Potnitola 132 KV -II syn.( Bay charge Joypurhat S/S).
| 19:17 |  | Joypurhat-Potnitola 132 KV -I syn.( Bay charge Joypurhat S/S).
| 21:00 |  | Evening Peak Generation is 15768 MW.
| 21:15 | 22:37 | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Banaripara 33kv feeder DS problem | [7 empty] | 52.0MW load
interrup.
| 21:15 | 22:35 | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Banaripara DS problem | [7 empty] | 52.0MW load
interrup.
|  | 21:54 | Rangpur 132/33kV S/S Rangpur-Teesta Solar-2 is restored.
|  | 23:28 | Siddhirganj 132/33kV S/S T-2 HT is restored.
| 23:55 |  | JERA Meghnaghat Power Limited 718 MW CCPP tripped.
| 00:15 |  | Ashuganj 420 MW CCPP (East) GT was sync.
| 00:32 | 00:53 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing 33kc OC/EF Relay relays Due to
Chunarughat and Shaitaganj Feeder Trip.
| 05:46 |  | Khulshi-Madunaghat 132kV Ckt-2 Scheduled S/D from Khulshi 132/33kV end Due to Red hot
maintenance Work
| 05:52 |  | Sholosohor 132/33kV S/S Sholoshahar-Khulshi Ckt-2 Scheduled S/D Due to Maintenance
regarding red hot on overhead line
| 06:03 |  | Khulna (C) S/S TR-1 425T HT Scheduled S/D Due to project work | [7 empty] | 22.0MW load
interrup.
| 06:03 |  | Khulna (C) S/S TR-1 425T LT Scheduled S/D Due to project work | [7 empty] | 22.0MW load
interrup.
| 06:55 |  | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT Scheduled S/D Due to Cleaning & | [7 empty] | 10.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 06:55 |  | Rajshahi 132/33kV S/S Transformer T-2(415T) LT Scheduled S/D Due to Cleaning &
maintenance work.
| 06:56 |  | Rajshahi 132/33kV S/S Transformer T-2(415T) HT Scheduled S/D Due to Cleaning &
maintenance work.
| 06:56 |  | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT Scheduled S/D Due to Cleaning & | [7 empty] | 10.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 07:33 |  | Goalpara 132/33kV S/S T-6 LT Scheduled S/D Due to Heat removal work
| 07:34 |  | Goalpara 132/33kV S/S T-6 HT Scheduled S/D Due to Heat removal work
| 07:34 |  | Keranigonj 230/132/33kV S/S TR-1 HT Scheduled S/D Due to High temperature maintenance | [7 empty] | 15.0MW load
|  |  | work. | [7 empty] | interrup.
| 07:34 |  | Keranigonj 230/132/33kV S/S TR-1 LT Scheduled S/D Due to High temperature maintenance | [7 empty] | 15.0MW load
|  |  | work. | [7 empty] | interrup.
| 07:40 |  | Candpur- Kachua 132kV Ckt-2 Scheduled S/D from Kachua 230/132/33kV end Due to 132 kv
Chandpur -2 has been S/D By Backup NLDC and from Chandpur 132/33kV end Due to Maintenance
work
| 07:58 |  | Korerhat 400/230/132kV S/S Feni -2 Project Work S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 22-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 383 | 8690400 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1210116 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 304 | 7271767 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 129600 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 60 | 3066240 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 439149 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 137910 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 0 | 423000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 462260 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 624000 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 32 | 774556 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 51 | 812448 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 478080 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 424800 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 146844 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 153000 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 440 | 10131818.18 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 259 | 6636480 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 2586000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1992 | 44598468.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 96669 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 106380 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 39 | 1088160 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 718260 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 214 | 5011264 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 99 | 1472836 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 46 | 835248 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 442063 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 528000 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 441120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 617280 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 25664 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 225818 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 445966 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 104 | 1374975 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 582720 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 76 | 1019945 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 14 | 354618 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28532724 | Can't Start AGC
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 21 | 304320 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1000 | 16625454.55 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 3067 | 60849484.55
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 199 | 4955000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 357 | 8849800 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 345 | 7002000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 150000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 37 | 547776 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 47 | 597120 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 16727.27 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1188868 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 58 | 1119054 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 31 | 366416 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 98 | 2222880 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 2420640 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 144 | 3553920 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 713304 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 472000 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 1067040 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 17 | 70560 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 51 | 288960 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 344791 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1634 | 35946856.27
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 117 | 2068800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 37 | 339600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 134690 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 55680 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 92520 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 171 | 2698690
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 994000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 729120 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 147 | 3438081.82 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 152 | 3534000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 25 | 708576 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1916160 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2411470 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 532752 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7427000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 344 | 7857000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1259 | 29548159.82
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 889 | 19750545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 33 | 307680 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 45 | 394627 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 182 | 4351968 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 16 | 220320 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 145728 | FGMO
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 503280 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 499 | 10734545 | U-2 Under Maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1664 | 36408693
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 1251 | 30021818 | RRT
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 64 | 541632 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 83 | 2370000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1070 | 27594181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5334900 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 415200 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6698000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3925 | -
Barishal Area Total |  |  |  |  | 3481.04 | 3049 | 72979656.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 289112 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 446872 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 266643 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 140 | 3447909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 140 | 3654355 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 379 | 9017673 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 377800 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 113803 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 91 | 527872 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1401216 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 70 | 1204704 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 23520 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1445 | 30473242 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 259568 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 581858 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2486 | 52086147
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 48 | 1144145 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 179 | 4119000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 104 | 1292448 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 472.08 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1445879 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 158148 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 600480 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 446 | 8760572.08
Eastern Grid Total |  |  |  |  | 17418.042 | 8123 | 173641658.82
Western Grid Total |  |  |  |  | 11852.195 | 7645 | 170235068.9
National Grid Total |  |  |  |  | 29270.237 | 15768 | 343876727.72
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 22-05-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10208.16 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5009.5 | MW
i) Dhaka area |  |  | 5291.26 |  | MW | i) Khulna area |  |  |  | 2013.9 | MW
ii) Chattogram area |  |  | 1616.9 |  | MW | ii) Barishal area |  |  |  | 487.2 | MW
iii) Cumilla area |  |  | 1587 |  | MW | iii) Rajshahi area |  |  |  | 1545.4 | MW
iv) Mymensingh area |  |  | 1095 |  | MW | iv) Rangpur area |  |  |  | 963 | MW
v) Sylhet area |  |  | 618 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15217.66 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 7 | 19:00 | 67 | Hasnabad | 101 | 00:00 | 133 | Natore | 164 | 21:00
2 | AKSML | 102.9 | 00:00 | 68 | Hathazari | 101 | 19:30 | 134 | Nawabganj | 65.4 | 00:00
3 | Aftabnagar | 46 | 00:00 | 69 | Hatirjheel | 46 | 12:00 | 135 | Netrakona | 138 | 18:30
4 | Agargaon | 124 | 00:00 | 70 | Ishurdi | 88 | 19:30 | 136 | New | 76.8 | 00:00
5 | Agrabad | 70 | 15:00 | 71 | Jaldhaka | 86 | 20:00 | 137 | Niamatpur | 84 | 23:00
6 | Amnura | 32 | 22:00 | 72 | Jamalpur | 111 | 21:00 | 138 | Noapara | 51 | 22:00
7 | Ashuganj | 106 | 21:00 | 73 | Jashore | 178 | 13:00 | 139 | PHP | 6 | 00:00
8 | BSRM | 205 | 23:00 | 74 | Jhenaidah | 144 | 19:00 | 140 | Pabna | 109 | 20:00
9 | Bagerhat | 92 | 22:00 | 75 | Joydebpur | 141 | 11:00 | 141 | Palashbari | 130 | 20:00
10 | Bajitpur | 94 | 20:00 | 76 | Joypurhat | 62 | 15:00 | 142 | Panchagarh | 63 | 19:30
11 | Bakerganj | 12.4 | 22:00 | 77 | Juldah | 17.5 | 00:00 | 143 | Patiya | 12 | 19:00
12 | Bakulia | 106 | 00:00 | 78 | KSRM | 11 | 06:00 | 144 | Patuakhali | 78.5 | 00:00
13 | Banani | 38.6 | 11:00 | 79 | Kabirpur | 231 | 10:00 | 145 | Payra | 40 | 23:00
14 | Bangabhaban | 5 | 11:00 | 80 | Kachua | 105 | 22:00 | 146 | Postogola | 60 | 00:00
15 | Barapukuria | 67 | 19:30 | 81 | Kaliganj | 12 | 05:00 | 147 | Pubail | 29 | 08:00
16 | Barguna | 28 | 22:00 | 82 | Kallyanpur | 129 | 00:00 | 148 | Purbachal | 34 | 00:00
17 | Barishal | 117 | 22:00 | 83 | Kalurghat | 40 | 00:00 | 149 | Purbasadipur | 138 | 19:30
18 | Barishal-230 | 186 | 07:00 | 84 | Kamrangirchar | 85 | 00:00 | 150 | Rahanpur | 46 | 22:00
19 | Baroaulia | 75 | 00:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 23 | 01:00
20 | Baroirhat | 74 | 22:00 | 86 | Kasba | 41 | 22:00 | 152 | Rajbari | 95 | 00:00
21 | Bashundhara | 197 | 11:00 | 87 | Kazla | 109 | 00:00 | 153 | Rajendrapur | 118 | 05:00
22 | BashundharaCement | 8 | 00:00 | 88 | Keranigonj | 86 | 00:00 | 154 | Rajshahi | 128 | 20:00
23 | Beanibazar | 78 | 23:00 | 89 | Khagrachori | 34 | 19:00 | 155 | Rajshahi-230 | 94 | 20:00
24 | Benapole | 79 | 21:00 | 90 | Khulna | 67 | 19:00 | 156 | Ramganj | 120 | 18:30
25 | Bhaluka | 149 | 20:00 | 91 | Khulshi | 195 | 20:00 | 157 | Rampur | 52 | 00:00
26 | Bhandaria | 65.1 | 22:00 | 92 | Kishoreganj | 148 | 19:00 | 158 | Rangamati | 19 | 20:00
27 | Bhangura | 44 | 19:00 | 93 | Kodda | 291 | 20:00 | 159 | Rangpur | 134 | 13:00
28 | Bheramara(GK) | 75 | 19:00 | 94 | Kulaura | 50 | 00:00 | 160 | Ruppur | 4 | 15:00
29 | Bhulta | 218 | 20:00 | 95 | Kurigram | 52 | 19:30 | 161 | SSM | 4 | 05:00
30 | Bog-Sherpur | 80 | 22:00 | 96 | Kushtia | 173 | 20:00 | 162 | Saidpur | 90 | 19:30
31 | Bogura | 171 | 01:00 | 97 | Laksam | 37 | 03:00 | 163 | Santhia | 38 | 19:00
32 | Borhanuddin | 97 | 06:00 | 98 | Lakshmipur | 49 | 00:00 | 164 | Satkhira | 145 | 19:30
33 | Brahmanbaria | 140 | 22:00 | 99 | Lalbag | 85 | 12:00 | 165 | Satmasjid | 117 | 10:00
34 | Cantonment | 114 | 11:00 | 100 | Lalmonirhat | 59 | 19:30 | 166 | Savar | 190 | 01:00
35 | Chandina | 39 | 19:00 | 101 | MI_Cement | 16.4 | 00:00 | 167 | SevenRings | 16.91 | 03:00
36 | Chandpur | 90 | 04:00 | 102 | Madanganj | 45 | 12:00 | 168 | ShahCement | 24 | 00:00
37 | Chandraghona | 38 | 19:30 | 103 | Madaripur | 134 | 23:00 | 169 | Shahjadpur | 87 | 19:30
38 | Chapai | 77 | 19:00 | 104 | Madartek | 88 | 00:00 | 170 | Shahjibazar | 124 | 02:00
39 | Charsaidpur | 41 | 12:00 | 105 | Madunaghat | 59 | 23:00 | 171 | Shahmirpur | 54.5 | 01:00
40 | Chauddagram | 87 | 23:00 | 106 | Magura | 76 | 19:30 | 172 | Shariatpur | 102 | 00:00
41 | Chhatak | 38 | 20:00 | 107 | Mahasthangarh | 78 | 23:00 | 173 | Sherpur | 120 | 18:30
42 | Chowmuhani | 191 | 22:00 | 108 | Maijdee | 23 | 00:00 | 174 | Shikalbaha | 36 | 21:00
43 | Chuadanga | 127 | 13:00 | 109 | Manikganj | 145 | 21:00 | 175 | Shitalakhya | 78.8 | 12:00
44 | Coxsbazar | 152 | 13:00 | 110 | Maniknagar | 77 | 00:00 | 176 | Sholosohor | 47 | 22:00
45 | Cumilla(N) | 132 | 19:00 | 111 | Matarbari | 58 | 21:00 | 177 | Shomvuganj | 18 | 00:00
46 | Cumilla(S) | 167 | 23:00 | 112 | Matuail | 78 | 12:00 | 178 | Shyampur | 180 | 00:00
47 | Daganbhuiyan | 41 | 23:00 | 113 | Metrorail_Motijheel | 24 | 17:00 | 179 | Siddhirganj | 112 | 11:00
48 | Daudkandi | 145 | 12:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 112 | 19:30
49 | DhakaUniversity | 64 | 12:00 | 115 | Millgate | 86 | 00:00 | 181 | Sonargaon | 149 | 00:00
50 | Dhamrai | 116 | 20:00 | 116 | Mirpur | 153 | 11:00 | 182 | Sreemongol | 85 | 00:00
51 | Dhanmondi | 87.8 | 12:00 | 117 | Mirsorai | 47 | 02:00 | 183 | Sreepur | 115 | 00:00
52 | Dohazari | 114 | 23:00 | 118 | Mirzapur | 49 | 10:00 | 184 | Srinagar | 52.6 | 00:00
53 | Faridpur | 182 | 22:00 | 119 | Mithapukur | 59 | 00:00 | 185 | Sunamganj | 58 | 19:00
54 | Fatullah | 92 | 00:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 52 | 00:00
55 | Fenchuganj | 40 | 04:00 | 121 | Mogbazar | 87.6 | 01:00 | 187 | Sylhet-132 | 125 | 19:30
56 | Feni | 119 | 22:00 | 122 | Mongla | 40 | 00:00 | 188 | TK | 28 | 00:00
57 | GPH | 1 | 00:00 | 123 | Motijheel | 44 | 00:00 | 189 | Tangail | 172 | 08:00
58 | Ghatail | 86 | 09:00 | 124 | Muktagacha | 33 | 10:00 | 190 | Taraganj | 21 | 17:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 118 | 00:00 | 191 | Tasnim | 26 | 18:30
60 | Ghorashal-230 | 109 | 19:30 | 126 | Muradnagar | 54 | 22:00 | 192 | Thakurgaon | 114 | 19:30
61 | Goalpara | 42 | 01:00 | 127 | Mymensingh | 175 | 21:00 | 193 | Tongi | 158 | 11:00
62 | Gollamari | 126 | 23:00 | 128 | Nabinagar | 92 | 11:00 | 194 | Ullahpara | 40 | 19:00
63 | Gopalganj | 129.2 | 22:00 | 129 | Naogaon | 146 | 21:00 | 195 | Ullon | 56 | 00:00
64 | Gulshan | 98 | 11:00 | 130 | Narail | 67.5 | 20:00 | 196 | Uttara | 92 | 11:00
65 | Halishahar | 87 | 23:00 | 131 | Narinda | 61 | 00:00 | 197 | UttaraNew | 61 | 00:00
66 | HaripurSBU | 140 | 00:00 | 132 | Narshingdi | 183 | 00:00 | 198 | Zigatola | 96 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 22-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 16095.81 | 1053 |  | 17195.81
1:00 | 15176.78 | 1388 |  | 16626.78
2:00 | 15074.59 | 1285 |  | 16417.59
3:00 | 14888.07 | 1250 |  | 16194.07
4:00 | 14784.16 | 728 |  | 15545.16
5:00 | 14495.33 | 388 |  | 14900.33
6:00 | 13887.95 | 319 |  | 14220.95
7:00 | 13397.04 | 370 |  | 13784.04
8:00 | 13027.36 | 106 |  | 13138.36
9:00 | 13078.51 | 59 |  | 13140.51
10:00 | 13019.99 | 40 |  | 13061.99
11:00 | 12972.61 | 0 |  | 12972.61
12:00 | 12804.59 | 43 |  | 12849.59
13:00 | 13567.1 | 22 |  | 13590.1
14:00 | 13389.44 | 25 |  | 13415.44
15:00 | 13609.82 | 99 |  | 13712.82
16:00 | 13427.98 | 0 |  | 13427.98
17:00 | 13308.66 | 10 |  | 13318.66
18:00 | 13280.48 | 20 |  | 13301.48
19:00 | 14855 | 175 |  | 15038
19:30 | 15649 | 203 |  | 15861
20:00 | 15539 | 171 |  | 15718
21:00 | 15768 | 299 |  | 16080
22:00 | 15747 | 157 |  | 15911
23:00 | 15778 | 277 |  | 16067
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 22-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8385.36 | 7710.45 | 16095.81 | DAILY GENERATION CURVE
00:30 | 8047.36 | 7588.935 | 15636.295
01:00 | 7709.36 | 7467.42 | 15176.78 | 22-05-2026
01:30 | 7657.86 | 7467.825 | 15125.685
02:00 | 7606.36 | 7468.23 | 15074.59
02:30 | 7528.36 | 7452.97 | 14981.33
03:00 | 7450.36 | 7437.71 | 14888.07
03:30 | 7435.36 | 7400.755 | 14836.115
04:00 | 7420.36 | 7363.8 | 14784.16
04:30 | 7317.86 | 7321.885 | 14639.745
05:00 | 7215.36 | 7279.97 | 14495.33
05:30 | 7192.43 | 6999.21 | 14191.64
06:00 | 7169.5 | 6718.45 | 13887.95
06:30 | 7063.66 | 6578.835 | 13642.495
07:00 | 6957.82 | 6439.22 | 13397.04
07:30 | 6846.88 | 6365.32 | 13212.2
08:00 | 6735.94 | 6291.42 | 13027.36
08:30 | 6745.65 | 6307.285 | 13052.935
09:00 | 6755.36 | 6323.15 | 13078.51
09:30 | 6695.83 | 6353.42 | 13049.25
10:00 | 6636.3 | 6383.69 | 13019.99
10:30 | 6646.96 | 6349.34 | 12996.3
11:00 | 6657.62 | 6314.99 | 12972.61
11:30 | 6506.07 | 6382.53 | 12888.6
12:00 | 6354.52 | 6450.07 | 12804.59
12:30 | 6533.625 | 6652.22 | 13185.845
13:00 | 6712.73 | 6854.37 | 13567.1
13:30 | 6570.95 | 6907.32 | 13478.27
14:00 | 6429.17 | 6960.27 | 13389.44
14:30 | 6522.62 | 6977.01 | 13499.63
15:00 | 6616.07 | 6993.75 | 13609.82
15:30 | 6624.595 | 6894.305 | 13518.9
16:00 | 6633.12 | 6794.86 | 13427.98
16:30 | 6617.115 | 6751.205 | 13368.32
17:00 | 6601.11 | 6707.55 | 13308.66
17:30 | 6557.735 | 6736.835 | 13294.57
18:00 | 6514.36 | 6766.12 | 13280.48
18:30 | 7041.18 | 7026.56 | 14067.74
19:00 | 7568 | 7287 | 14855
19:30 | 8058 | 7591 | 15649
20:00 | 7966 | 7573 | 15539
20:30 | 8044.5 | 7609 | 15653.5 |  | Executive Engineer
21:00 | 8123 | 7645 | 15768 |  | Network Operation Division
21:30 | 8083 | 7674.5 | 15757.5
22:00 | 8043 | 7704 | 15747
22:30 | 8045 | 7717.5 | 15762.5
23:00 | 8047 | 7731 | 15778

## En-Curve
QF-LDC-12
Date | 22-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3662 | 1682 | 794 | 0 | 154 | 1411.45 | 30 | 5531 | 0 | 694 | 2050.36 | 80 | 0 | 7 | 1053 | DAILY ENERGY CURVE
00:30 | 3487 | 1591.5 | 841 | 0 | 157 | 1358.935 | 30 | 5527.5 | 0 | 634.5 | 1921.36 | 80 | 0 | 7.5 | 1220.5 | 22-05-2026
01:00 | 3312 | 1501 | 888 | 0 | 160 | 1306.42 | 30 | 5524 | 0 | 575 | 1792.36 | 80 | 0 | 8 | 1388
01:30 | 3324 | 1557 | 888 | 0 | 159 | 1301.325 | 30 | 5487 | 0 | 554.5 | 1735.36 | 80 | 0 | 9.5 | 1336.5 | Energy Generated | 343.8767 |  | MKWHr
02:00 | 3336 | 1613 | 888 | 0 | 158 | 1296.23 | 30 | 5450 | 0 | 534 | 1678.36 | 80 | 0 | 11 | 1285 | Energy not Served | 8.284 |  | MKWHr
02:30 | 3332 | 1588 | 888 | 0 | 156 | 1281.47 | 30 | 5408 | 0 | 534 | 1670.86 | 80 | 0 | 13 | 1267.5 | Total Energy Requirement | 352.1607 |  | MKWHr
03:00 | 3328 | 1563 | 888 | 0 | 154 | 1266.71 | 30 | 5366 | 0 | 534 | 1663.36 | 80 | 0 | 15 | 1250
03:30 | 3337 | 1600.5 | 888 | 0 | 151 | 1253.255 | 30 | 5335.5 | 0 | 531.5 | 1656.36 | 40 | 0 | 13 | 989
04:00 | 3346 | 1638 | 888 | 0 | 148 | 1239.8 | 30 | 5305 | 0 | 529 | 1649.36 | 0 | 0 | 11 | 728
04:30 | 3320 | 1581 | 888 | 0 | 146 | 1220.885 | 30 | 5281.5 | 0 | 520.5 | 1636.86 | 0 | 0 | 15 | 558
05:00 | 3294 | 1524 | 888 | 0 | 144 | 1201.97 | 30 | 5258 | 0 | 512 | 1624.36 | 0 | 0 | 19 | 388
05:30 | 3303 | 1547 | 689 | 0 | 144 | 1167.51 | 30 | 5261 | 8.77 | 446.5 | 1581.86 | 0 | 0 | 13 | 353.5
06:00 | 3312 | 1570 | 490 | 0 | 144 | 1133.05 | 30 | 5264 | 17.54 | 381 | 1539.36 | 0 | 0 | 7 | 319
06:30 | 3326.5 | 1539 | 477.5 | 0 | 138 | 1098.095 | 30 | 5265.5 | 47.22 | 363.5 | 1350.68 | 0 | 0 | 6.5 | 344.5
07:00 | 3341 | 1508 | 465 | 0 | 132 | 1063.14 | 30 | 5267 | 76.9 | 346 | 1162 | 0 | 0 | 6 | 370
07:30 | 3335 | 1503.5 | 465 | 0 | 136 | 1115.895 | 30 | 5246 | 118.305 | 328 | 927.5 | 0 | 0 | 7 | 238
08:00 | 3329 | 1499 | 465 | 0 | 140 | 1168.65 | 30 | 5225 | 159.71 | 310 | 693 | 0 | 0 | 8 | 106
08:30 | 3350 | 1523 | 465 | 0 | 139 | 1171.325 | 30 | 5198.5 | 206.61 | 318.5 | 643 | 0 | 0 | 8 | 82.5
09:00 | 3371 | 1547 | 465 | 0 | 138 | 1174 | 30 | 5172 | 253.51 | 327 | 593 | 0 | 0 | 8 | 59
09:30 | 3335.5 | 1552.75 | 676.5 | 0 | 136 | 1125 | 30 | 5047.5 | 250.5 | 319 | 565 | 0 | 0 | 11.5 | 49.5
10:00 | 3300 | 1558.5 | 888 | 0 | 134 | 1076 | 30 | 4923 | 247.49 | 311 | 537 | 0 | 0 | 15 | 40
10:30 | 3313.5 | 1599 | 888 | 0 | 140 | 1045.5 | 30 | 4844 | 275.8 | 302 | 543 | 0 | 0 | 15.5 | 20
11:00 | 3327 | 1639.5 | 888 | 0 | 146 | 1015 | 30 | 4765 | 304.11 | 293 | 549 | 0 | 0 | 16 | 0
11:30 | 3313 | 1544.25 | 888 | 0 | 152 | 1028 | 30 | 4723 | 399.35 | 283 | 512.5 | 0 | 0 | 15.5 | 21.5
12:00 | 3299 | 1449 | 888 | 0 | 158 | 1041 | 30 | 4681 | 494.59 | 273 | 476 | 0 | 0 | 15 | 43
12:30 | 3446 | 1545 | 888 | 0 | 156 | 1150 | 30 | 4791.5 | 485.845 | 242.5 | 430.5 | 0 | 0 | 20.5 | 32.5
13:00 | 3593 | 1641 | 888 | 0 | 154 | 1259 | 30 | 4902 | 477.1 | 212 | 385 | 0 | 0 | 26 | 22
13:30 | 3581.5 | 1622 | 888 | 0 | 155 | 1282 | 30 | 4868.5 | 462.27 | 213 | 355.5 | 0 | 0 | 20.5 | 23.5
14:00 | 3570 | 1603 | 888 | 0 | 156 | 1305 | 30 | 4835 | 447.44 | 214 | 326 | 0 | 0 | 15 | 25
14:30 | 3599.5 | 1653.5 | 888 | 0 | 153 | 1307.5 | 30 | 4893.5 | 429.63 | 205.5 | 323.5 | 0 | 0 | 16 | 62
15:00 | 3629 | 1704 | 888 | 0 | 150 | 1310 | 30 | 4952 | 411.82 | 197 | 321 | 0 | 0 | 17 | 99
15:30 | 3558.5 | 1703 | 888 | 0 | 150 | 1305.5 | 30 | 4976.5 | 325.4 | 216.5 | 349 | 0 | 0 | 16.5 | 49.5
16:00 | 3488 | 1702 | 888 | 0 | 150 | 1301 | 30 | 5001 | 238.98 | 236 | 377 | 0 | 0 | 16 | 0
16:30 | 3476 | 1681.75 | 888 | 0 | 147 | 1312 | 30 | 5010.5 | 156.07 | 266 | 386.5 | 0 | 0 | 14.5 | 5
17:00 | 3464 | 1661.5 | 888 | 0 | 144 | 1323 | 30 | 5020 | 73.16 | 296 | 396 | 0 | 0 | 13 | 10
17:30 | 3431.5 | 1611 | 888 | 0 | 143 | 1322.5 | 30 | 5018 | 52.43 | 330 | 458.14 | 0 | 0 | 10 | 15
18:00 | 3399 | 1560.5 | 888 | 0 | 142 | 1322 | 30 | 5016 | 31.7 | 364 | 520.28 | 0 | 0 | 7 | 20
18:30 | 3470.5 | 1655.75 | 888 | 0 | 147 | 1383 | 30 | 5114 | 15.85 | 540.5 | 819.14 | 0 | 0 | 4 | 97.5
19:00 | 3542 | 1751 | 888 | 0 | 152 | 1444 | 30 | 5212 | 0 | 717 | 1118 | 0 | 0 | 1 | 175
19:30 | 3481 | 1688 | 888 | 0 | 158 | 1437 | 30 | 5502 | 0 | 815 | 1645 | 0 | 0 | 5 | 203
20:00 | 3449 | 1525 | 889 | 0 | 156 | 1445 | 30 | 5540 | 0 | 809 | 1689 | 0 | 0 | 7 | 171
20:30 | 3502 | 1584 | 889 | 0 | 150 | 1445 | 30 | 5559 | 0 | 772.5 | 1708 | 0 | 0 | 14 | 235
21:00 | 3555 | 1643 | 889 | 0 | 144 | 1445 | 30 | 5578 | 0 | 736 | 1727 | 0 | 0 | 21 | 299
21:30 | 3584 | 1631 | 888.5 | 0 | 150 | 1442 | 30 | 5582.5 | 0 | 732.5 | 1700 | 0 | 0 | 17 | 228
22:00 | 3613 | 1619 | 888 | 0 | 156 | 1439 | 30 | 5587 | 0 | 729 | 1673 | 0 | 0 | 13 | 157
22:30 | 3578 | 1677 | 888 | 0 | 161 | 1439.5 | 30 | 5567.5 | 0 | 751.5 | 1650 | 0 | 0 | 20 | 217
23:00 | 3543 | 1735 | 888 | 0 | 166 | 1440 | 30 | 5548 | 0 | 774 | 1627 | 0 | 0 | 27 | 277
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 22-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 155 | 24 | 636 | 182 | 1840 | 554 | Ishurdi-Ghorashal Ckt-1 | Export | 3462545.45
1:00 | 170 | 25 | 614 | 172 | 1874 | 582
2:00 | 174 | 24 | 668 | 190 | 1878 | 588 |  | Import | 0
3:00 | 172 | 19 | 674 | 178 | 1886 | 556
4:00 | 172 | 19 | 676 | 174 | 1880 | 534 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 182 | 21 | 700 | 180 | 1910 | 530
6:00 | 118 | 19 | 600 | 154 | 1696 | 498 |  | Import | 0
7:00 | 98 | 15 | 520 | 140 | 1694 | 460
8:00 | 107 | 20 | 540 | 160 | 1792 | 486 | Sirajganj-Sreepur Ckt-1 | Export | 4170000
9:00 | 141 | 33 | 612 | 192 | 1900 | 546
10:00 | 202 | 15 | 660 | 176 | 1902 | 582 |  | Import | 0
11:00 | 181 | 8 | 596 | 116 | 1888 | 572
12:00 | 141 | -20 | 482 | 40 | 1650 | 468 | Sirajganj-Sreepur Ckt-2 | Export | 4184000
13:00 | 127 | -3 | 542 | 104 | 1780 | 468
14:00 | 147 | 3 | 560 | 92 | 1984 | 538 |  | Import | 0
15:00 | 147 | 11 | 600 | 140 | 1980 | 514
16:00 | 143 | 11 | 582 | 140 | 1952 | 498 | Gopalganj-Aminbazar Ckt-1 | Export | 22300000
17:00 | 136 | 10 | 540 | 130 | 1930 | 490
18:00 | 143 | 13 | 580 | 134 | 1968 | 496 |  | Import | 0
18:30 | 160 | 17 | 622 | 144 | 1954 | 498
19:00 | 129 | 2 | 590 | 166 | 1730 | 394 | Gopalganj-Aminbazar Ckt-2 | Export | 22350000
19:30 | 109 | 1 | 518 | 138 | 1706 | 374
20:00 | 113 | 3 | 532 | 160 | 1692 | 416 |  | Import | 0
21:00 | 125 | 10 | 558 | 180 | 1730 | 448
22:00 | 128 | 8 | 554 | 172 | 1768 | 426 |  | Total Export | 56466545.45
23:00 | 118 | 3 | 540 | 160 | 1722 | 412 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 22-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 05:00 | 356 | 00:00 | Madunaghat | 397 | 01:00 | 386 | 15:00
Amtali | 408 | 11:00 | 398 | 19:00 | Meghnaghat | 369 | 18:00 | 360 | 00:00
Ashuganj | 405 | 18:00 | 393 | 10:00 | Payra | 410 | 12:00 | 400 | 19:00
Bhulta | 401 | 18:00 | 388 | 10:00 | Rahanpur | 412 | 06:00 | 400 | 19:30
Bibiana | 388 | 12:00 | 381 | 01:00 | Rampal | 389 | 10:00 | 373 | 21:00
BIPTC | 407 | 06:00 | 387 | 15:00
Bogura | 399 | 06:00 | 385 | 19:30
Gopalganj | 381 | 18:00 | 369 | 23:00
Kaliakoir | 364 | 12:00 | 351 | 00:00
Korerhat | 386 | 07:00 | 377 | 21:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 18:00 | 216 | 00:00 | Jhenaidah | 224 | 18:30 | 210 | 19:00
AKSML | 234 | 06:00 | 223 | 15:00 | Kachua | 228 | 07:00 | 220 | 21:00
Aminbazar | 226 | 18:00 | 217 | 00:00 | Kaliakoir | 227 | 12:00 | 218 | 00:00
Ashuganj | 228 | 12:00 | 220 | 00:00 | Keranigonj | 224 | 18:00 | 214 | 00:00
Ashuganj-400 | 228 | 12:00 | 220 | 00:00 | Khulna(S) | 219 | 18:00 | 206 | 23:00
Baghabari | 232 | 05:00 | 225 | 23:00 | Korerhat | 229 | 18:30 | 221 | 21:00
Barapukuria | 231 | 04:00 | 219 | 13:00 | Madunaghat | 234 | 06:00 | 224 | 13:00
Barapukuria-230 | 231 | 04:00 | 219 | 13:00 | Madunaghat-400 | 235 | 07:00 | 225 | 15:00
Barishal | 222 | 18:00 | 214 | 23:00 | Maniknagar | 224 | 18:00 | 213 | 00:00
Bheramara | 233 | 06:00 | 221 | 12:00 | Meghnaghat | 232 | 16:00 | 223 | 00:00
Bhulta | 224 | 18:00 | 216 | 10:00 | Meghnaghat-400 | 227 | 18:00 | 219 | 00:00
Bibiana | 231 | 12:00 | 226 | 01:00 | Mirsorai | 224 | 06:00 | 219 | 21:00
BIPTC | 236 | 18:30 | 222 | 12:00 | Naogaon | 219 | 07:00 | 205 | 21:00
Bogura | 240 | 05:00 | 231 | 13:00 | Purbasadipur | 230 | 06:00 | 214 | 13:00
Bogura-400 | 240 | 05:00 | 231 | 13:00 | Rajshahi | 233 | 18:00 | 220 | 12:00
Borhanuddin | 228 | 02:00 | 219 | 22:00 | Rampal | 220 | 18:30 | 208 | 21:00
BSRM | 228 | 06:00 | 221 | 21:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 230 | 15:00 | 220 | 13:00 | Rampura | 223 | 18:00 | 214 | 10:00
Cumilla(N) | 223 | 12:00 | 218 | 21:00 | Shikalbaha | 232 | 06:00 | 223 | 14:00
Faridpur | 215 | 11:00 | 207 | 23:00 | Shyampur | 225 | 18:00 | 215 | 00:00
Fenchuganj | 234 | 12:00 | 228 | 00:00 | Siddhirganj | 224 | 13:00 | 216 | 00:00
Feni | 224 | 06:00 | 217 | 22:00 | Sirajgonj | 237 | 04:00 | 233 | 21:00
Ghorashal | 230 | 04:00 | 210 | 00:00 | Sreepur | 226 | 12:00 | 216 | 00:00
Ghorashal-230 | 221 | 12:00 | 212 | 10:00 | Tongi | 220 | 13:00 | 210 | 00:00
Gopalganj | 216 | 18:00 | 208 | 23:00
GPH | 231 | 16:00 | 224 | 03:00
Haripur | 224 | 18:00 | 215 | 00:00
Hasnabad | 225 | 17:00 | 215 | 00:00
Hathazari | 231 | 05:00 | 222 | 14:00
Ishurdi | 235 | 18:30 | 224 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 04:00 | 131 | 10:00 | Madunaghat | 136 | 06:00 | 129 | 15:00
Agargaon | 131 | 18:00 | 124 | 00:00 | Magura | 131 | 18:30 | 119 | 23:00
Agrabad | 135 | 06:00 | 127 | 10:00 | Mahasthangarh | 138 | 05:00 | 129 | 23:00
AKS | 129 | 01:00 | 125 | 13:00 | Maijdee | 128 | 07:00 | 122 | 23:00
Aminbazar | 129 | 18:00 | 122 | 00:00 | Manikganj | 128 | 12:00 | 120 | 05:00
Amnura | 136 | 18:30 | 127 | 12:00 | Maniknagar | 131 | 18:00 | 122 | 09:00
Ashuganj | 136 | 11:00 | 130 | 00:00 | Matarbari | 125 | 06:00 | 108 | 22:00
Ashuganj-230 | 136 | 11:00 | 130 | 00:00 | Matuail | 130 | 18:00 | 123 | 00:00
Bagerhat | 124 | 10:00 | 109 | 22:00 | Metrorail_Motijheel | 131 | 18:00 | 122 | 09:00
Bajitpur | 131 | 12:00 | 121 | 00:00 | Metrorail_Uttara | 132 | 12:00 | 124 | 10:00
Bakerganj | 130 | 10:00 | 125 | 01:00 | Millgate | 132 | 12:00 | 126 | 00:00
Bakulia | 136 | 05:00 | 127 | 14:00 | Mirpur | 128 | 18:00 | 122 | 00:00
Banani | 139 | 18:00 | 131 | 00:00 | Mirzapur | 128 | 11:00 | 119 | 09:00
Bangabhaban | 131 | 18:00 | 122 | 09:00 | Mithapukur | 136 | 06:00 | 124 | 13:00
Barapukuria | 137 | 04:00 | 127 | 13:00 | MI_Cement | 130.2 | 13:00 | 122 | 10:00
Barguna | 130 | 10:00 | 123 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 129 | 08:00 | 123 | 23:00 | Mogbazar | 137 | 18:00 | 131 | 10:00
Barishal-230 | 128 | 07:00 | 123 | 23:00 | Mongla | 123 | 09:00 | 110 | 23:00
Baroaulia | 134 | 05:00 | 127 | 14:00 | Motijheel | 131 | 18:30 | 122 | 09:00
Baroirhat | 131 | 06:00 | 126 | 13:00 | Muktagacha | 132 | 10:00 | 112 | 00:00
Bashundhara | 136 | 06:00 | 125 | 09:00 | Munshiganj | 129 | 18:00 | 122 | 00:00
BashundharaCement | 131 | 13:00 | 123 | 00:00 | Muradnagar | 127 | 13:00 | 122 | 00:00
Beanibazar | 129 | 10:00 | 122 | 22:00 | Mymensingh | 133 | 10:00 | 110 | 01:00
Benapole | 127 | 09:00 | 108 | 23:00 | Nabinagar | 134 | 12:00 | 122 | 00:00
Bhaluka | 131 | 12:00 | 120 | 19:00 | Naogaon | 138 | 05:00 | 123 | 21:00
Bhandaria | 130 | 08:00 | 114 | 23:00 | Narail | 131 | 04:00 | 118 | 22:00
Bhangura | 132 | 18:00 | 127 | 02:00 | Narinda | 131 | 18:00 | 122 | 09:00
Bheramara | 135 | 06:00 | 130 | 13:00 | Narshingdi | 130 | 11:00 | 118 | 00:00
Bheramara(GK) | 135 | 18:30 | 130 | 12:00 | Natore | 134 | 18:30 | 127 | 13:00
Bhulta | 127 | 18:00 | 120 | 00:00 | Nawabganj | 131 | 13:00 | 123 | 00:00
Bog-Sherpur | 136 | 03:00 | 131 | 21:00 | Netrakona | 123 | 11:00 | 103 | 20:00
Bogura | 140 | 04:00 | 132 | 15:00 | New | 134 | 12:00 | 126 | 10:00
Bogura-230 | 140 | 04:00 | 133 | 13:00 | Niamatpur | 132 | 06:00 | 126 | 21:00
Brahmanbaria | 132 | 11:00 | 123 | 21:00 | Noapara | 126 | 18:30 | 114 | 22:00
Cantonment | 131 | 18:00 | 124 | 00:00 | Pabna | 133 | 18:30 | 128 | 13:00
Chandina | 129 | 18:00 | 125 | 22:00 | Palashbari | 135 | 05:00 | 124 | 23:00
Chandpur | 131 | 06:00 | 123 | 13:00 | Panchagarh | 138 | 05:00 | 124 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 134 | 06:00 | 129 | 14:00 | Patiya | 134 | 07:00 | 126 | 13:00
Chapai | 133 | 07:00 | 127 | 21:00 | Patuakhali | 128 | 08:00 | 124 | 23:00
Charsaidpur | 131 | 13:00 | 123 | 00:00 | Payra | 134 | 11:00 | 129 | 23:00
Chauddagram | 130 | 06:00 | 125 | 22:00 | PHP | 131 | 05:00 | 126 | 22:00
Chhatak | 126 | 09:00 | 119 | 00:00 | Postogola | 130 | 18:00 | 122 | 00:00
Chowmuhani | 128 | 07:00 | 123 | 15:00 | Pubail | 136 | 12:00 | 127 | 00:00
Chuadanga | 128 | 18:00 | 116 | 22:00 | Purbachal | 136 | 07:00 | 125 | 00:00
Coxsbazar | 128 | 06:00 | 110 | 22:00 | Purbasadipur | 136 | 05:00 | 125 | 13:00
Cumilla(N) | 129 | 07:00 | 126 | 01:00 | Rahanpur | 135 | 05:00 | 131 | 19:30
Cumilla(S) | 130 | 06:00 | 125 | 09:00 | Rahanpur-400 | 136 | 06:00 | 131 | 21:00
Daganbhuiyan | 130 | 06:00 | 125 | 22:00 | Rahim | 130 | 13:00 | 124 | 00:00
Daudkandi | 126 | 13:00 | 120 | 00:00 | Rajbari | 122 | 14:00 | 116 | 23:00
DhakaUniversity | 137 | 18:00 | 132 | 00:00 | Rajendrapur | 135 | 12:00 | 121 | 00:00
Dhamrai | 132 | 13:00 | 123 | 00:00 | Rajshahi | 132 | 04:00 | 124 | 13:00
Dhanmondi | 136 | 06:00 | 131 | 10:00 | Rajshahi-230 | 133 | 05:00 | 127 | 12:00
Dohazari | 133 | 06:00 | 120 | 14:00 | Ramganj | 127 | 05:00 | 120 | 13:00
Faridpur | 125 | 07:00 | 121 | 23:00 | Rampur | 135 | 05:00 | 126 | 15:00
Fatullah | 135 | 14:00 | 121 | 00:00 | Rampura | 136 | 06:00 | 131 | 10:00
Fenchuganj | 135 | 12:00 | 129 | 00:00 | Rangamati | 133 | 07:00 | 127 | 13:00
Feni | 131 | 05:00 | 126 | 22:00 | Rangpur | 136 | 05:00 | 125 | 12:00
Feni-230 | 132 | 06:00 | 127 | 22:00 | Ruppur | 135 | 04:00 | 131 | 19:30
Ghatail | 128 | 10:00 | 113 | 13:00 | Saidpur | 134 | 00:00 | 126 | 12:00
Ghorashal | 134 | 18:00 | 128 | 00:00 | Santhia | 134 | 04:00 | 129 | 23:00
Goalpara | 129 | 10:00 | 119 | 21:00 | Satkhira | 122 | 18:00 | 108 | 23:00
Gollamari | 129 | 18:00 | 118 | 23:00 | Satmasjid | 131 | 18:30 | 123 | 00:00
Gopalganj | 128 | 18:30 | 119 | 23:00 | Savar | 128 | 20:00 | 120 | 00:00
Gopalganj-400 | 132 | 19:00 | 125 | 22:00 | SevenRings | 135 | 12:00 | 128 | 00:00
Gulshan | 136 | 06:00 | 131 | 10:00 | ShahCement | 131 | 13:00 | 123 | 00:00
Halishahar | 135 | 06:00 | 127 | 09:00 | Shahjadpur | 135 | 04:00 | 132 | 19:30
Haripur | 130 | 13:00 | 124 | 00:00 | Shahjibazar | 131 | 11:00 | 123 | 00:00
HaripurSBU | 130 | 14:00 | 124 | 00:00 | Shahmirpur | 136 | 07:00 | 128 | 15:00
Hasnabad | 130 | 18:00 | 122 | 00:00 | Shariatpur | 130 | 14:00 | 120 | 23:00
Hathazari | 136 | 06:00 | 130 | 14:00 | Sherpur | 133 | 10:00 | 110 | 13:00
Hatirjheel | 137 | 18:00 | 131 | 10:00 | Shikalbaha | 126 | 07:00 | 117 | 14:00
Ishurdi | 136 | 09:00 | 131 | 23:00 | Shikalbaha-230 | 135 | 07:00 | 129 | 14:00
Jaldhaka | 133 | 05:00 | 123 | 13:00 | Shitalakhya | 130 | 18:00 | 120 | 00:00
Jamalpur | 130 | 10:00 | 112 | 03:00 | Sholosohor | 134 | 03:00 | 129 | 13:00
Jashore | 129 | 09:00 | 111 | 19:00 | Shomvuganj | 124 | 12:00 | 114 | 21:00
Jhenaidah | 133 | 09:00 | 118 | 19:00 | Shyampur | 134 | 14:00 | 126 | 00:00
Jhenaidah-230 | 134 | 09:00 | 122 | 21:00 | Shyampur-230 | 134 | 14:00 | 128 | 00:00
Joydebpur | 135 | 12:00 | 124 | 21:00 | Siddhirganj | 131 | 18:00 | 125 | 00:00
Joypurhat | 135 | 08:00 | 127 | 23:00 | Sirajganj | 134 | 10:00 | 128 | 15:00
Juldah | 134 | 08:00 | 128 | 15:00 | Sonargaon | 129 | 13:00 | 122 | 00:00
Kabirpur | 132 | 12:00 | 121 | 10:00 | Sreemongol | 131 | 11:00 | 122 | 00:00
Kachua | 130 | 07:00 | 125 | 13:00 | Sreepur | 133 | 12:00 | 123 | 21:00
Kaliakoir | 136 | 12:00 | 126 | 00:00 | Srinagar | 132 | 18:00 | 125 | 00:00
Kaliganj | 133 | 09:00 | 120 | 19:00 | SSM | 140 | 05:00 | 131 | 15:00
Kallyanpur | 127 | 14:00 | 124 | 07:00 | Sunamganj | 124 | 08:00 | 117 | 00:00
Kalurghat | 135 | 06:00 | 129 | 13:00 | Sylhet | 129 | 08:00 | 123 | 00:00
Kamrangirchar | 131 | 17:00 | 120 | 00:00 | Sylhet-132 | 128 | 09:00 | 123 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Tangail | 125 | 11:00 | 112 | 08:00
Kasba | 126 | 13:00 | 120 | 21:00 | Taraganj | 135 | 05:00 | 125 | 13:00
Kazla | 130 | 14:00 | 122 | 09:00 | Tasnim | 129 | 13:00 | 122 | 00:00
Keranigonj | 132 | 18:00 | 122 | 13:00 | Thakurgaon | 140 | 05:00 | 123 | 13:00
Khagrachori | 133 | 06:00 | 127 | 15:00 | TK | 136 | 06:00 | 129 | 14:00
Khulna | 127 | 18:00 | 115 | 22:00 | Tongi | 134 | 13:00 | 128 | 00:00
Khulna(S) | 129 | 18:00 | 118 | 23:00 | Ullahpara | 134 | 04:00 | 128 | 23:00
Khulshi | 134 | 06:00 | 125 | 15:00 | Ullon | 136 | 06:00 | 130 | 10:00
Kishoreganj | 130 | 12:00 | 117 | 21:00 | Uttara | 132 | 12:00 | 124 | 00:00
Kodda | 130 | 12:00 | 122 | 04:00 | UttaraNew | 132 | 12:00 | 124 | 10:00
Korerhat | 132 | 06:00 | 126 | 21:00 | Zigatola | 132 | 18:00 | 125 | 00:00
KSRM | 134 | 05:00 | 128 | 14:00
Kulaura | 134 | 12:00 | 129 | 00:00
Kurigram | 133 | 06:00 | 120 | 13:00
Kushtia | 130 | 04:00 | 124 | 19:00
Laksam | 129 | 06:00 | 124 | 13:00
Lakshmipur | 127 | 07:00 | 122 | 21:00
Lalbag | 132 | 18:00 | 124 | 00:00
Lalmonirhat | 132 | 05:00 | 119 | 23:00
Madanganj | 131 | 13:00 | 123 | 00:00
Madaripur | 129 | 14:00 | 122 | 23:00
Madartek | 136 | 06:00 | 130 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division