## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 24-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-05-2026 | during | 24-05-2026 | during | 24-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 394 | 317 | 412 | 412 | 392 | 392 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 36 | 92 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 312 | 290 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 141 | 146 | 149.36 | 149.36 | 149 | 149 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 18 | 18 | 33 | 33 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 48 | 52.19 | 52.19 | 16 | 50 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 32 | 32 | 300 | 300 | 32 | 32 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 33 | 52 | 149 | 149 | 34 | 51 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 105 | 105 | 0 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 90 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 0 | 0 | 0 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 405 | 315 | 584 | 584 | 490 | 490 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 219 | 718 | 718 | 300 | 300 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 142 | 142 | 0 | 0 | 140 | 140 | plant availability zero
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1710 | 2024 | 5857.22 | 5857.22 | 2056 | 2371
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 4 | 23 | 25.5 | 25.5 | 0 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 43 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 30 | 30 | 30 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 208 | 215 | 212 | 212 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 86 | 87 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 7 | 52 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 49 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 24 | 100 | 100 | 24 | 24 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 11 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 28 | 58 | 108 | 108 | 18 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.35 | 0 | 4.72 | 0 | 4.72 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 48 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 5 | 54.36 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 97 | 95 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 24 | 24 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 71 | 89 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 108 | 136 | 163 | 163 | 35 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1130 | 1224 | 1224 | 612 | 612 | Unit-2 under maint
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 18 | 12 | 7 | 12 | 7 | 12 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 655 | 1000 | 930 | 1000 | 600 | 600 | Coal shortage
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2704.35 | 3155.36 | 3710.58 | 3844.86 | 2048.08 | 2264.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 191 | 188 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 300 | 355 | 350.01 | 350.01 | 350.01 | 350.01
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 240 | 230 | 342.01 | 342.01 | 342.01 | 342.01
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 300 | 350 | 393 | 393 | 393 | 393
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 10 | 0 | 41.65 | 41.65 | 0 | 0 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 150 | 150 | 150 | 33 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 22 | 36 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 96 | 163 | 163 | 100 | 100 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 172 | 176 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 158 | 110 | 84 | 80 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 43 | 52.2 | 52.2 | 52.2 | 43 | 43 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 110 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 17 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 68 | 115 | 115 | 17 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 71 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1779 | 2008.2 | 2764.44 | 2690.44 | 2108.27 | 2215.27
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-05-2026 | during | 24-05-2026 | during | 24-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 6 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.98 | 0 | 2.3 | 0 | 2.3 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 96 | 87 | 90 | 90 | 90 | 98 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 56 | 68 | 10 | 10 | 68 | 68 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 44.08 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 203.06 | 172 | 381.3 | 334 | 222.3 | 195
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 0 | 0 | 42 | 42 | machine problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 0 | 0 | 30 | 30 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 141 | 138 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 90 | 151 | 155 | 155 | 155 | 155 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 101 | 102 | 102 | 100 | 100 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 6 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 333 | 344 | 250 | 250 | 320 | 320 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1156 | 1233 | 1152 | 1152 | 1234 | 1234
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 889 | 888 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 30 | 37 | 37 | 37 | 37 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 52 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 229 | 254 | 410 | 410 | 180 | 180 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 16 | 21 | 105 | 105 | 16 | 16 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 39.5 | 0 | 72 | 0 | 72 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 600 | 922 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1773.5 | 2167 | 3573.2 | 3501.2 | 2666.2 | 2594.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 1249 | 1249 | 1244 | 1244 | 1244 | 1244 | RRT
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 100 | 125 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 900 | 1040 | 1244 | 1244 | 1184 | 1184 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 0 | 35 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 168 | 237 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.74 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2597.74 | 2941 | 3406 | 3405 | 3166 | 3200
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 40.06 | 0 | 51 | 0 | 51 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 140 | 185 | 214 | 214 | 180 | 180 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 150 | 199 | 220 | 220 | 190 | 190 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 338 | 0 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 41 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 97 | 100 | 100 | 0 | 85 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 13 | 90 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 90 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.09 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1320.22 | 1443.85 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 55.97 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 94 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2191.34 | 2243.85 | 3235.57 | 3017.87 | 2778.19 | 2645.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 100 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 45 | 48 | 48 | 50 | 50 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 169 | 177 | 170 | 170 | 190 | 190 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 65 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.7 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 25 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 16 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 61 | 0 | 70.84 | 0 | 70.84 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 327.7 | 502 | 584.84 | 480 | 572.84 | 468
System Total |  |  |  |  | 28823.2 | 29270.237 | 14442.69 | 16446.41 | 24665.15 | 24282.59 | 16851.88 | 17187.32
Forecast Scenario (24-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15800 |  | 0 |  | 15800
|  |  |  | 1:00 | 15290 |  | 0 |  | 15290
|  |  |  | 2:00 | 14660 |  | 0 |  | 14660
|  |  |  | 3:00 | 14420 |  | 0 |  | 14420
|  |  |  | 4:00 | 14010 |  | 0 |  | 14010
|  |  |  | 5:00 | 13880 |  | 0 |  | 13880
|  |  |  | 6:00 | 13250 |  | 0 |  | 13250
|  |  |  | 7:00 | 13210 |  | 0 |  | 13210
|  |  |  | 8:00 | 13410 |  | 0 |  | 13410
|  |  |  | 9:00 | 13490 |  | 0 |  | 13490
|  |  |  | 10:00 | 13890 |  | 0 |  | 13890
|  |  |  | 11:00 | 14310 |  | 0 |  | 14310
|  |  |  | 12:00 | 15000 |  | 0 |  | 15000
|  |  |  | 13:00 | 15170 |  | 0 |  | 15170
|  |  |  | 14:00 | 15370 |  | 0 |  | 15370
|  |  |  | 15:00 | 15400 |  | 0 |  | 15400
|  |  |  | 16:00 | 15420 |  | 0 |  | 15420
|  |  |  | 17:00 | 15110 |  | 0 |  | 15110
|  |  |  | 18:00 | 14780 |  | 0 |  | 14780
|  |  |  | 18:30 | 15550 |  | 0 |  | 15550
|  |  |  | 19:00 | 16450 |  | 0 |  | 16450
|  |  |  | 19:30 | 16800 |  | 0 |  | 16800
|  |  |  | 20:00 | 16350 |  | 0 |  | 16350
|  |  |  | 21:00 | 16400 |  | 0 |  | 16400
|  |  |  | 22:00 | 15700 |  | 0 |  | 15700
|  |  |  | 23:00 | 15420 |  | 0 |  | 15420
Probable Maximum Temperature: |  |  | 28.00°C
Probable Maximum Demand at Day Peak: |  |  | 15000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16800.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16800.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 355.61 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:33 hrs on 24-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 23-05-2026 | [28 empty] | Date: | 23-05-2026 | [28 empty] | Date: | 23-05-2026 | [28 empty] | Date: | 23-05-2026 | [28 empty] | Date: | 23-05-2026 | [17 empty] | Date: | 23-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 17 | 146 | 32 | 55 | 55 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 23 | 21 | 0 | 390 | 90 | 16 | 49 | 0 | 13 | 49 | 44 | 39.8 | 24 | 24 | 0 | 30 | 105 | 16 | 865 | 151 | 0 | 44 | 0 | 96 | 215 | 0 | 0 | 0 | 1224 | 0 | 22 | 25 | 0 | 356 | 345 | 51 | 48 | 203 | 34 | 28 | 30 | 180 | 0 | 19 | 104 | 156 | 43 | 0 | 31 | 305 | 0 | 332 | 42 | 30 | 143 | 0 | 24 | 0 | 86 | 30 | 159 | 0 | 103 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 7681.8 | 888 | 184 | 0 | 33 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 487 | 16 | 0 | 0 | 1447 | 0 | 40 | 0 | 113 | 113 | 0 | 33 | 28 | 52.2 | 0 | 0 | 32 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 369 | 0 | 0 | 172 | 48 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 307 | 120 | 220 | 0 | 1252 | 1160 | 54 | 7733.2 | 15415 | 75.25
01:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 17 | 146 | 32 | 15 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 23 | 22 | 0 | 370 | 90 | 16 | 22 | 0 | 19 | 17 | 43 | 54.36 | 24 | 24 | 0 | 30 | 104 | 28 | 735 | 145 | 0 | 44 | 0 | 98 | 217 | 0 | 0 | 0 | 1224 | 0 | 33 | 45 | 5 | 356 | 345 | 51 | 48 | 195 | 34 | 16 | 31 | 184 | 0 | 19 | 102 | 158 | 43 | 0 | 31 | 300 | 0 | 332 | 42 | 30 | 143 | 0 | 0 | 0 | 86 | 30 | 152 | 0 | 103 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 7386.36 | 888 | 184 | 0 | 33 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 491 | 16 | 0 | 0 | 1444 | 0 | 40 | 0 | 113 | 113 | 0 | 0 | 28 | 52.2 | 0 | 0 | 32 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 331 | 0 | 0 | 170 | 48 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 307 | 120 | 220 | 0 | 1254 | 1075 | 17 | 7544.2 | 14930.56 | 75.25
02:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 17 | 146 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 142 | 23 | 0 | 0 | 370 | 87 | 16 | 19 | 0 | 10 | 0 | 43 | 54.36 | 24 | 24 | 0 | 30 | 105 | 31 | 655 | 123 | 0 | 44 | 0 | 95 | 217 | 0 | 0 | 0 | 1224 | 0 | 33 | 45 | 35 | 356 | 345 | 51 | 48 | 198 | 34 | 17 | 31 | 167 | 0 | 19 | 78 | 154 | 39 | 0 | 31 | 295 | 0 | 332 | 42 | 30 | 135 | 0 | 16 | 0 | 86 | 30 | 152 | 0 | 102 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 7178.36 | 888 | 188 | 0 | 23 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 491 | 16 | 0 | 0 | 1338 | 0 | 40 | 0 | 113 | 113 | 0 | 0 | 28 | 52.2 | 0 | 0 | 32 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 331 | 0 | 0 | 167 | 48 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 307 | 120 | 220 | 0 | 1251 | 995 | 17 | 7307.2 | 14485.56 | 75.25
03:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 17 | 146 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 108 | 23.5 | 22 | 0 | 470 | 91 | 16 | 19 | 0 | 12 | 0 | 8 | 54.36 | 24 | 24 | 0 | 30 | 106 | 31 | 655 | 0 | 0 | 44 | 0 | 98 | 217 | 0 | 0 | 0 | 1160 | 0 | 33 | 8 | 109 | 357 | 300 | 51 | 37 | 210 | 30 | 0 | 31 | 100 | 0 | 19 | 0 | 148 | 34 | 0 | 24 | 300 | 0 | 332 | 42 | 30 | 146 | 0 | 16 | 0 | 86 | 30 | 152 | 0 | 102 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 6907.86 | 888 | 193 | 0 | 23 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 495 | 16 | 0 | 0 | 1420 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 394 | 0 | 0 | 167 | 48 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 277 | 120 | 220 | 0 | 1250 | 1030 | 17 | 7315 | 14222.86 | 75.25
04:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 17 | 146 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 301 | 0 | 0 | 0 | 108 | 23.5 | 22 | 0 | 470 | 91 | 16 | 19 | 0 | 5 | 0 | 0 | 17 | 24 | 24 | 0 | 30 | 105 | 31 | 655 | 0 | 0 | 44 | 0 | 97 | 218 | 0 | 0 | 0 | 1160 | 0 | 33 | 0 | 152 | 356 | 300 | 51 | 0 | 220 | 0 | 0 | 31 | 0 | 0 | 19 | 0 | 142 | 0 | 0 | 31 | 295 | 0 | 332 | 42 | 30 | 150 | 0 | 16 | 0 | 86 | 30 | 152 | 0 | 103 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 6718.5 | 836 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 497 | 16 | 0 | 0 | 1419 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 385 | 0 | 0 | 168 | 47 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 277 | 120 | 220 | 0 | 1253 | 1070 | 17 | 7086 | 13804.5 | 75.25
05:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 17 | 146 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 108 | 24.5 | 22 | 0 | 400 | 91 | 16 | 18 | 0 | 15 | 0 | 0 | 17 | 24 | 24 | 0 | 30 | 104 | 32 | 655 | 0 | 0 | 44 | 0 | 96 | 219 | 0 | 0 | 0 | 1160 | 0 | 33 | 0 | 250 | 360 | 300 | 51 | 0 | 203 | 0 | 0 | 21 | 0 | 0 | 19 | 0 | 140 | 0 | 0 | 31 | 295 | 0 | 332 | 42 | 30 | 144 | 0 | 16 | 0 | 86 | 30 | 151 | 0 | 101 | 0 | 9 | 78 | 0 | 0 | 0 | 0 | 6675.5 | 888 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 494 | 16 | 0 | 0 | 1374 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 361 | 0 | 0 | 168 | 47 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 277 | 120 | 220 | 0 | 1251 | 1092 | 17 | 7005 | 13680.5 | 75.25
06:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 10 | 0 | 0 | 17 | 146 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 1 | 108 | 24.5 | 22 | 0 | 370 | 15 | 0 | 18 | 0 | 33 | 0 | 0 | 0 | 24 | 24 | 0.37 | 30 | 66 | 32 | 655 | 0 | 0 | 44 | 0 | 97 | 218 | 0 | 0 | 0 | 1160 | 1 | 0 | 0 | 230 | 356 | 300 | 51 | 0 | 209 | 0 | 0 | 26 | 0 | 0 | 19 | 0 | 132 | 0 | 4 | 0 | 300 | 0 | 332 | 42 | 30 | 133 | 0 | 0 | 0 | 86 | 30 | 152 | 0 | 101 | 0 | 9 | 78 | 0 | 0.1 | 3 | 0 | 6421.97 | 888 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.57 | 495 | 16 | 0 | 0 | 1275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.73 | 2 | 0 | 0 | 0.69 | 140 | 0 | 140 | 0 | 0 | 0 | 340 | 0 | 0.08 | 169 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0.04 | 0 | 277 | 120 | 220 | 0 | 1255 | 1000 | 0 | 6602.11 | 13024.08 | 75.25
07:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 17 | 145 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 7 | 108 | 24 | 21 | 0 | 440 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 12 | 24 | 0.87 | 30 | 0 | 9 | 655 | 0 | 0 | 44 | 0 | 34 | 218 | 0 | 0 | 0 | 1160 | 5 | 0 | 0 | 230 | 357 | 300 | 51 | 0 | 189 | 0 | 0 | 60 | 0 | 0 | 19 | 0 | 136 | 0 | 16 | 0 | 295 | 0 | 356 | 42 | 30 | 135 | 0 | 16 | 0 | 86 | 30 | 153 | 0 | 101 | 0 | 9 | 78 | 18 | 0.3 | 4.27 | 0 | 6354.44 | 888 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 494 | 16 | 0 | 0 | 1322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.45 | 14 | 0 | 0 | 11.54 | 140 | 0 | 140 | 0 | 0 | 0 | 373 | 0 | 1.02 | 169 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0.15 | 0 | 166 | 120 | 220 | 0 | 1246 | 1020 | 0 | 6633.86 | 12988.3 | 75.25
08:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 0 | 17 | 144 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 8 | 121 | 23 | 21 | 0 | 470 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 12 | 24 | 1.54 | 30 | 0 | 2 | 655 | 0 | 0 | 44 | 0 | 31 | 217 | 0 | 0 | 0 | 1165 | 8 | 0 | 0 | 230 | 356 | 300 | 51 | 0 | 195 | 0 | 0 | 86 | 0 | 0 | 19 | 0 | 128 | 0 | 24 | 0 | 295 | 0 | 344 | 42 | 30 | 135 | 2 | 16 | 0 | 86 | 30 | 152 | 0 | 101 | 0 | 18 | 78 | 10 | 0.11 | 14.5 | 0 | 6498.15 | 888 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 498 | 16 | 0 | 0 | 1297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.43 | 38 | 0 | 0 | 18.96 | 140 | 0 | 140 | 0 | 0 | 0 | 385 | 0 | 2.09 | 170 | 49 | 0 | 6 | 0 | 0 | 0 | 0 | 3.2 | 20 | 0.37 | 0 | 170 | 120 | 220 | 0 | 1251 | 1030 | 0 | 6724.05 | 13222.2 | 75.25
09:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 0 | 19 | 142 | 32 | 15 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 9 | 133 | 20 | 21 | 0 | 420 | 32 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 24 | 24 | 3.04 | 30 | 17 | 2 | 655 | 23 | 0 | 44 | 0 | 32 | 215 | 0 | 0 | 0 | 1224 | 12 | 15 | 0 | 250 | 320 | 260 | 51 | 0 | 190 | 5 | 0 | 86 | 27 | 0 | 8 | 34 | 124 | 16 | 29 | 0 | 300 | 0 | 345 | 42 | 30 | 134 | 6 | 16 | 0 | 85 | 30 | 153 | 0 | 101 | 0 | 18 | 78 | 9 | 1.31 | 6.71 | 0 | 6728.06 | 888 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.86 | 465 | 16 | 0 | 0 | 1282.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.52 | 20 | 0 | 0 | 4.7 | 140 | 0 | 150 | 0 | 0 | 0 | 368 | 0 | 0.44 | 172 | 48 | 0 | 3 | 0 | 0 | 0 | 0 | 3.4 | 10 | 0.39 | 0 | 171 | 120 | 220 | 0 | 1249 | 1010 | 0 | 6594.89 | 13322.95 | 75.25
10:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 33 | 141 | 32 | 15 | 55 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 25 | 142 | 19 | 21 | 0 | 405 | 30 | 0 | 15 | 0 | 31 | 0 | 0 | 0 | 24 | 24 | 3.23 | 30 | 34 | 2 | 655 | 33 | 0 | 43 | 0 | 50 | 216 | 0 | 0 | 0 | 1224 | 8 | 20 | 0 | 320 | 320 | 240 | 51 | 0 | 195 | 20 | 12 | 113 | 69 | 0 | 8 | 40 | 128 | 34 | 39 | 0 | 305 | 0 | 345 | 42 | 30 | 136 | 6 | 16 | 0 | 85 | 30 | 153 | 0 | 102 | 0 | 18 | 78 | 7 | 1.23 | 38.08 | 0 | 7080.54 | 888 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.58 | 439 | 16 | 0 | 0 | 1282.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.27 | 56 | 0 | 0 | 37.98 | 140 | 0 | 150 | 0 | 0 | 0 | 350 | 0 | 3.48 | 164 | 50 | 0 | 8 | 0 | 0 | 0 | 0 | 5.9 | 16 | 0.6 | 0 | 172 | 120 | 180 | 0 | 1247 | 990 | 0 | 6612.39 | 13692.93 | 75.25
11:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 0 | 33 | 125 | 32 | 15 | 42 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 13 | 142 | 0 | 21 | 0 | 495 | 31 | 20 | 23 | 0 | 19 | 0 | 0 | 0 | 24 | 24 | 3.9 | 30 | 64 | 2 | 655 | 70 | 0 | 43 | 0 | 68 | 212 | 0 | 0 | 0 | 1224 | 9 | 20 | 0 | 300 | 300 | 240 | 51 | 0 | 195 | 10 | 17 | 112 | 71 | 5 | 8 | 50 | 146 | 43 | 48 | 0 | 305 | 0 | 334 | 42 | 30 | 138 | 8 | 16 | 0 | 84 | 30 | 154 | 0 | 101 | 0 | 47 | 95 | 6 | 1.63 | 14.93 | 0 | 7213.46 | 888 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.66 | 418 | 16 | 0 | 0 | 1305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.29 | 96 | 0 | 0 | 41.97 | 140 | 0 | 150 | 0 | 0 | 0 | 380 | 0 | 4.33 | 167 | 51 | 0 | 15 | 0 | 0 | 0 | 0 | 4.2 | 96 | 0.26 | 0 | 170 | 120 | 180 | 0 | 1250 | 980 | 0 | 6780.71 | 13994.17 | 75.25
12:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 17 | 0 | 33 | 141 | 32 | 15 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 17 | 312 | 36 | 0 | 31 | 142 | 18 | 14 | 0 | 405 | 71 | 48 | 28 | 0 | 18 | 0 | 7 | 5 | 24 | 24 | 4.35 | 30 | 97 | 2 | 655 | 108 | 0 | 43 | 4 | 86 | 208 | 0 | 0 | 0 | 1224 | 18 | 20 | 0 | 300 | 300 | 240 | 51 | 0 | 191 | 10 | 17 | 70 | 172 | 8 | 8 | 98 | 158 | 43 | 71 | 22 | 305 | 0 | 333 | 42 | 30 | 141 | 0 | 0 | 0 | 84 | 30 | 90 | 0 | 101 | 0 | 56 | 96 | 6 | 0.98 | 44.08 | 0 | 7552.41 | 889 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.5 | 600 | 16 | 0 | 0 | 1320.22 | 0 | 0 | 0 | 35 | 13 | 0 | 0 | 0 | 0 | 40.06 | 94 | 0 | 0 | 55.97 | 140 | 0 | 150 | 0 | 0 | 0 | 338 | 0 | 5.09 | 169 | 50 | 25 | 16 | 0 | 0 | 0 | 0 | 6.7 | 61 | 0.74 | 0 | 168 | 100 | 180 | 0 | 1249 | 900 | 0 | 6890.28 | 14442.69 | 75.25
13:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 2 | 17 | 0 | 34 | 139 | 32 | 15 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 130 | 0 | 28 | 142 | 18 | 20 | 0 | 420 | 94 | 50 | 31 | 0 | 48 | 0 | 30 | 17 | 24 | 24 | 1.13 | 30 | 107 | 2 | 655 | 45 | 0 | 44 | 8 | 104 | 211 | 0 | 0 | 0 | 1224 | 15 | 20 | 0 | 300 | 300 | 240 | 51 | 0 | 195 | 10 | 17 | 92 | 184 | 8 | 8 | 104 | 174 | 43 | 57 | 22 | 300 | 0 | 354 | 42 | 20 | 144 | 2 | 0 | 0 | 84 | 30 | 25 | 0 | 103 | 0 | 56 | 96 | 0 | 0.88 | 45.91 | 0 | 7663.92 | 889 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.19 | 782 | 16 | 0 | 0 | 1324.59 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 49.49 | 60 | 0 | 0 | 13.29 | 163 | 0 | 199 | 0 | 0 | 0 | 207 | 0 | 1.4 | 167 | 50 | 35 | 4 | 0 | 0 | 0 | 0 | 3.5 | 171 | 0.34 | 0 | 170 | 120 | 180 | 0 | 1249 | 860 | 0 | 7116.8 | 14780.72 | 75.25
14:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 35 | 17 | 5 | 36 | 135 | 32 | 15 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 185 | 0 | 25 | 142 | 19 | 0 | 0 | 465 | 95 | 50 | 30 | 0 | 23 | 0 | 29 | 19 | 24 | 24 | 3.99 | 30 | 107 | 2 | 655 | 35 | 0 | 50 | 8 | 98 | 211 | 0 | 0 | 0 | 1224 | 16 | 20 | 0 | 320 | 300 | 240 | 51 | 0 | 202 | 10 | 17 | 93 | 184 | 8 | 8 | 104 | 132 | 52.2 | 48 | 29 | 300 | 0 | 368 | 42 | 20 | 156 | 5 | 16 | 0 | 86 | 30 | 81 | 0 | 103 | 0 | 56 | 96 | 0 | 0.66 | 1.96 | 0 | 7785.81 | 888 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.79 | 900 | 0 | 0 | 0 | 1375.96 | 0 | 0 | 0 | 35 | 57 | 0 | 0 | 0 | 0 | 44.46 | 70 | 0 | 0 | 45 | 181 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 3.81 | 170 | 48 | 70 | 8 | 32 | 0 | 0 | 0 | 2.2 | 148 | 0.57 | 0 | 202 | 120 | 220 | 0 | 1248 | 878 | 0 | 7221.79 | 15007.6 | 75.25
15:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 35 | 0 | 17 | 34 | 122 | 32 | 15 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 187 | 0 | 21 | 142 | 19 | 21 | 0 | 455 | 95 | 52 | 29 | 0 | 30 | 0 | 29 | 53 | 24 | 24 | 2 | 30 | 109 | 2 | 715 | 28 | 0 | 50 | 8 | 100 | 212 | 0 | 0 | 0 | 1224 | 10 | 18 | 0 | 320 | 300 | 230 | 51 | 0 | 197 | 0 | 16 | 92 | 187 | 8 | 8 | 104 | 116 | 52.2 | 26 | 13 | 305 | 0 | 356 | 42 | 20 | 153 | 5 | 16 | 0 | 86 | 30 | 150 | 0 | 101 | 0 | 56 | 96 | 0 | 1.35 | 6.13 | 0 | 7845.68 | 888 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.71 | 935 | 0 | 0 | 0 | 1422.19 | 0 | 0 | 0 | 70 | 70 | 0 | 0 | 0 | 0 | 35.35 | 44 | 0 | 0 | 34.25 | 181 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 3.28 | 180 | 46 | 84 | 15 | 32 | 0 | 0 | 0 | 1.2 | 120 | 0.43 | 0 | 216 | 120 | 220 | 0 | 1250 | 950 | 0 | 7397.41 | 15243.09 | 75.25
16:00 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 35 | 0 | 17 | 34 | 125 | 32 | 15 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 135 | 0 | 7 | 142 | 19 | 21 | 0 | 415 | 90 | 52 | 30 | 0 | 26 | 0 | 37 | 54.36 | 24 | 24 | 1.8 | 30 | 106 | 2 | 865 | 16 | 0 | 50 | 8 | 93 | 213 | 0 | 0 | 0 | 1100 | 8 | 20 | 0 | 300 | 280 | 230 | 51 | 0 | 181 | 0 | 17 | 93 | 176 | 8 | 8 | 102 | 114 | 52.2 | 32 | 28 | 305 | 0 | 356 | 42 | 20 | 130 | 3 | 16 | 0 | 86 | 30 | 152 | 0 | 101 | 0 | 58 | 86 | 0 | 0.93 | 12.51 | 0 | 7642.8 | 888 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.81 | 985 | 2 | 0 | 0 | 1448.13 | 0 | 0 | 0 | 90 | 80 | 0 | 0 | 0 | 16 | 18.47 | 31 | 0 | 0 | 19.96 | 181 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 1.9 | 165 | 46 | 113 | 8 | 35 | 0 | 0 | 0 | 2.1 | 72 | 0.3 | 0 | 168 | 120 | 180 | 0 | 1248 | 925 | 0 | 7307.67 | 14950.47 | 75.25
17:00 | 0 | 17 | 48 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 35 | 0 | 17 | 39 | 138 | 32 | 15 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 17 | 316 | 131 | 0 | 6 | 142 | 18.5 | 21 | 0 | 400 | 89 | 16 | 30 | 0 | 24 | 0 | 37 | 54.36 | 24 | 24 | 1.23 | 30 | 105 | 2 | 1000 | 17 | 0 | 50 | 9 | 94 | 214 | 0 | 0 | 0 | 1160 | 2 | 20 | 0 | 250 | 320 | 230 | 51 | 0 | 192 | 0 | 16 | 93 | 179 | 8 | 8 | 103 | 106 | 52.2 | 11 | 28 | 305 | 0 | 356 | 42 | 30 | 133 | 1 | 16 | 0 | 86 | 30 | 152 | 0 | 101 | 0 | 68 | 87 | 0 | 0.46 | 3.12 | 8 | 7864.87 | 889 | 230 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 17.62 | 990 | 16 | 0 | 0 | 1320.23 | 0 | 0 | 0 | 90 | 90 | 0 | 0 | 0 | 52.2 | 9.69 | 17 | 0 | 0 | 10.06 | 181 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0.95 | 160 | 46 | 115 | 4 | 37 | 0 | 0 | 0 | 1.5 | 31 | 0.13 | 0 | 179 | 120 | 180 | 0 | 1248 | 820 | 0 | 7015.38 | 14880.25 | 75.25
18:00 | 0 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 101 | 0 | 17 | 52 | 142 | 32 | 15 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 50 | 318 | 91 | 0 | 1 | 142 | 18.5 | 21 | 0 | 425 | 89 | 16 | 50 | 0 | 32 | 0 | 37 | 54.36 | 24 | 24 | 0.1 | 30 | 104 | 6 | 1000 | 16 | 0 | 50 | 19 | 92 | 214 | 0 | 0 | 0 | 1100 | 1 | 45 | 0 | 300 | 320 | 230 | 51 | 0 | 194 | 0 | 0 | 94 | 176 | 12 | 8 | 102 | 112 | 52.2 | 2 | 36 | 300 | 0 | 356 | 42 | 30 | 127 | 0 | 16 | 0 | 86 | 30 | 152 | 0 | 101 | 2 | 68 | 86 | 0 | 0.08 | 3.36 | 12 | 8034.6 | 888 | 240 | 0 | 15 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 4.88 | 888 | 16 | 0 | 0 | 1207.5 | 0 | 0 | 0 | 90 | 90 | 0 | 25 | 6 | 52.2 | 0.9 | 0 | 10 | 0 | 1.4 | 140 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0.15 | 167 | 44 | 115 | 0 | 43 | 0 | 0 | 0 | 0.1 | 7 | 0.03 | 0 | 177 | 120 | 180 | 0 | 1249 | 730 | 0 | 6688.16 | 14722.76 | 75.25
19:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 295 | 35 | 17 | 52 | 148 | 32 | 15 | 35 | 90 | 0 | 0 | 0 | 0 | 0 | 35 | 304 | 90 | 0 | 0 | 142 | 18 | 21 | 0 | 500 | 89 | 16 | 58 | 0 | 14 | 47 | 52 | 54.36 | 24 | 24 | 0 | 30 | 106 | 8 | 1000 | 112 | 0 | 50 | 23 | 96 | 214 | 0 | 0 | 0 | 1160 | 0 | 127 | 0 | 350 | 320 | 230 | 51 | 0 | 195 | 0 | 15 | 94 | 179 | 16 | 8 | 107 | 116 | 52.2 | 0 | 36 | 305 | 0 | 308 | 42 | 30 | 135 | 0 | 6 | 0 | 86 | 30 | 152 | 0 | 101 | 17 | 68 | 86 | 0 | 0 | 0 | 11 | 8767.56 | 888 | 250 | 0 | 30 | 36 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 824 | 20 | 0 | 0 | 1416.59 | 0 | 40 | 0 | 90 | 90 | 0 | 97 | 26 | 41 | 0 | 0 | 32 | 0 | 0 | 154 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 45 | 115 | 0 | 49 | 0 | 60 | 0 | 0 | 0 | 0 | 16 | 221 | 125 | 220 | 0 | 1248 | 850 | 22 | 7476.59 | 16244.15 | 75.25
19:30 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 219 | 35 | 17 | 52 | 146 | 32 | 15 | 35 | 90 | 0 | 0 | 0 | 0 | 0 | 35 | 290 | 92 | 0 | 0 | 142 | 18 | 21 | 0 | 315 | 89 | 16 | 58 | 0 | 12 | 49 | 52 | 54.36 | 24 | 24 | 0 | 30 | 95 | 11 | 1000 | 136 | 0 | 50 | 23 | 87 | 215 | 0 | 0 | 0 | 1130 | 0 | 150 | 0 | 350 | 355 | 230 | 51 | 0 | 188 | 0 | 68 | 96 | 176 | 17 | 19 | 110 | 110 | 52.2 | 0 | 36 | 305 | 0 | 344 | 42 | 30 | 138 | 0 | 6 | 0 | 86 | 30 | 151 | 0 | 101 | 17 | 68 | 87 | 0 | 0 | 0 | 0 | 8592.56 | 888 | 254 | 0 | 30 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 922 | 21 | 0 | 0 | 1443.85 | 0 | 40 | 0 | 90 | 90 | 0 | 97 | 26 | 41 | 0 | 0 | 32 | 0 | 0 | 185 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 45 | 115 | 0 | 65 | 0 | 100 | 0 | 0 | 0 | 0 | 16 | 237 | 125 | 220 | 0 | 1249 | 1040 | 54 | 7853.85 | 16446.41
20:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 249 | 35 | 17 | 52 | 144 | 32 | 15 | 35 | 90 | 0 | 0 | 0 | 0 | 0 | 35 | 297 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 395 | 84 | 16 | 60 | 0 | 17 | 49 | 52 | 54.36 | 24 | 24 | 0 | 30 | 96 | 15 | 1000 | 140 | 0 | 50 | 23 | 91 | 215 | 0 | 0 | 0 | 1155 | 0 | 150 | 0 | 350 | 355 | 230 | 51 | 0 | 196 | 0 | 59 | 96 | 174 | 16 | 19 | 70 | 104 | 52.2 | 0 | 35 | 300 | 0 | 344 | 42 | 30 | 128 | 0 | 6 | 0 | 86 | 28 | 152 | 0 | 101 | 17 | 69 | 87 | 0 | 0 | 0 | 0 | 8598.56 | 888 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 975 | 23 | 0 | 0 | 1446.42 | 0 | 40 | 0 | 35 | 35 | 0 | 97 | 28 | 41 | 0 | 0 | 32 | 0 | 0 | 185 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 48 | 115 | 0 | 70 | 0 | 30 | 0 | 0 | 0 | 0 | 16 | 238 | 125 | 220 | 0 | 1248 | 1072 | 17 | 7650.42 | 16248.98 | 75.25
21:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 269 | 35 | 17 | 37 | 144 | 32 | 15 | 35 | 90 | 0 | 0 | 0 | 0 | 0 | 35 | 319 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 425 | 94 | 16 | 60 | 0 | 22 | 49 | 60 | 54.36 | 24 | 24 | 0 | 30 | 94 | 20 | 1000 | 148 | 0 | 50 | 23 | 97 | 215 | 0 | 0 | 0 | 1160 | 0 | 150 | 0 | 300 | 355 | 230 | 51 | 0 | 193 | 0 | 70 | 96 | 183 | 16 | 19 | 66 | 108 | 52.2 | 0 | 36 | 310 | 0 | 368 | 42 | 30 | 144 | 0 | 20 | 0 | 86 | 25 | 152 | 0 | 101 | 17 | 69 | 115 | 0 | 0 | 0 | 0 | 8838.56 | 794 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 992 | 27 | 0 | 0 | 1447.66 | 0 | 31 | 0 | 35 | 35 | 0 | 97 | 28 | 8 | 0 | 0 | 32 | 0 | 0 | 185 | 0 | 207 | 0 | 0 | 0 | 8 | 0 | 0 | 159 | 49 | 50 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 238 | 125 | 220 | 0 | 1248 | 1100 | 17 | 7500.66 | 16339.22 | 75.25
22:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 233 | 35 | 0 | 36 | 145 | 32 | 15 | 17 | 90 | 0 | 0 | 0 | 0 | 0 | 35 | 320 | 0 | 0 | 0 | 142 | 0 | 21 | 0 | 350 | 87 | 16 | 61 | 0 | 14 | 50 | 60 | 54 | 24 | 24 | 0 | 30 | 93 | 21 | 1000 | 140 | 0 | 50 | 23 | 93 | 216 | 0 | 0 | 0 | 1160 | 0 | 40 | 0 | 260 | 354 | 230 | 51 | 0 | 199 | 0 | 70 | 96 | 174 | 16 | 19 | 65 | 124 | 52 | 0 | 36 | 305 | 0 | 356 | 42 | 30 | 127 | 0 | 22 | 0 | 86 | 25 | 152 | 0 | 101 | 17 | 69 | 117 | 0 | 0 | 0 | 0 | 8479 | 794 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 34 | 0 | 0 | 1400 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 208 | 0 | 0 | 0 | 110 | 0 | 0 | 161 | 49 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 217 | 125 | 220 | 0 | 1247 | 1100 | 0 | 7187 | 15666 | 75.25
23:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 260 | 35 | 0 | 36 | 144 | 32 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 320 | 0 | 0 | 0 | 142 | 17.5 | 21 | 0 | 430 | 92 | 16 | 63 | 0 | 24 | 50 | 60 | 54.36 | 24 | 24 | 0 | 30 | 103 | 22 | 1000 | 108 | 0 | 50 | 17 | 97 | 216 | 0 | 0 | 0 | 1160 | 0 | 20 | 0 | 260 | 355 | 230 | 51 | 0 | 195 | 0 | 70 | 96 | 180 | 16 | 19 | 67 | 126 | 52.2 | 0 | 37 | 310 | 0 | 356 | 42 | 30 | 142 | 0 | 22 | 0 | 86 | 25 | 152 | 0 | 101 | 0 | 9 | 58 | 0 | 0 | 0 | 0 | 8426.06 | 795 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 34 | 0 | 0 | 1318.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 209 | 0 | 0 | 0 | 377 | 0 | 0 | 160 | 50 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 210 | 125 | 220 | 0 | 1249 | 1085 | 0 | 7331.03 | 15757.09 | 75.25
Total KWH | 0 | 686400 | 619680 | 0 | 0 | 0 | 0 | 0 | 8827200 | 0 | 1840850 | 255600 | 145800 | 736992 | 3373440 | 704302 | 391466 | 538640 | 799200 | 0 | 0 | 0 | 0 | 0 | 270759 | 7383003 | 1087000 | 0 | 167258 | 3272400 | 480600 | 449280 | 0 | 10572727.27 | 1768909 | 459164 | 759360 | 0 | 481440 | 285735 | 673968 | 845417 | 573120 | 578880 | 23879 | 720180 | 2116827 | 334560 | 18785454.55 | 1425163 | 0 | 1133280 | 175446 | 2093418 | 4961200 | 0 | 0 | 0 | 28363634 | 102600 | 914981 | 117091 | 5927000 | 8402700 | 6472000 | 1190868 | 137760 | 4882000 | 188136 | 533760 | 1713320 | 2991840 | 153720 | 337740 | 1503660 | 3167040 | 860414 | 349600 | 532704 | 7284000 | 0 | 8432000 | 993000 | 675840 | 3351518.18 | 38395 | 456960 | 0 | 2058240 | 697728 | 3278000 | 0 | 2430190 | 77400 | 873600 | 2071200 | 46080 | 11200 | 188910 | 32400 | 182637227 | 21075636 | 5608512 | 0 | 147360 | 210176 | 0 | 0 | 0 | 43407.27 | 0 | 0 | 580320 | 17090907 | 402820 | 0 | 0 | 31903273 | 0 | 193448 | 0 | 1061568 | 1250208 | 0 | 364448 | 127267 | 305981 | 291432 | 539423 | 188785 | 0 | 266304 | 3870273 | 0 | 4271673 | 0 | 0 | 0 | 5538400 | 0 | 24840 | 4044000 | 1124072 | 1290607 | 88794 | 526060 | 0 | 391230 | 0 | 32802.84 | 740160 | 4248 | 625344 | 5324000 | 2851000 | 5232480 | 0 | 30029091 | 23963636.36 | 208800 | 171832786.47 | 354470013.47

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 23-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14442.69 | MW | 12:00 Hr. | Energy Generated |  |  | 354.47 |  | MKWHr.
| Day Peak Demand |  |  | 14911.69 | MW | 12:00 Hr. | Energy Unserverd |  |  | 7.052 |  | MKWHr.
| Evening Peak Generation |  |  | 16446.41 | MW | 19:30 Hr. | Energy Demand |  |  | 361.522 |  | MKWHr.
| Evening Peak Demand |  |  | 16957.41 | MW | 19:30 Hr. | Maximum Temperature |  |  | 36.3 |  | °C
| Minimum Generation of the Day |  |  | 12988.3 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 917.43 |  | MMCFD
| Maximum Generation of the Day |  |  | 16446.41 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.767 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 30.6407 | 0 | 11.7947 | 0 | 0 | 0.16726 | 0 | 0 | 42.6026 | Gas | 122.3809 | Gas | 431394815.0515
| Chattogram Zone |  |  | 5.2958 | 47.1491 | 12.8887 | 0 | 0.72018 | 0.12648 | 0 | 0.48144 | 66.6616 | Coal | 128.7248 | Coal | 835532583.8775
| Cumilla Zone |  |  | 29.3686 | 0 | 7.4911 | 0 | 0 | 0.3496 | 3.167 | 0 | 40.3763 | HFO | 42.1319 | HFO | 731783737.24
| Mymensingh Zone |  |  | 0.04608 | 0 | 3.0546 | 0 | 0 | 0.20011 | 0 | 0 | 3.3008 | HSD | 0.43464 | HSD | 12958009.254
| Sylhet Zone |  |  | 29.6575 | 0 | 0 | 0 | 0 | 0.038395 | 0 | 0 | 29.6959 | Hydro | 0.72018 | Hydro | 72018
| Khulna Zone |  |  | 5.6085 | 17.0909 | 0.76036 | 0.043407 | 0 | 0.58032 | 21.0756 | 0 | 45.1591 | Solar | 3.4502 | Solar | 54841893.8968
| Barishal Zone |  |  | 8.0835 | 59.3167 | 0.83414 | 0 | 0 | 0.004248 | 0 | 0 | 68.2386 | Import | 56.1459 | Import | 325040177.4
| Rajshahi Zone |  |  | 13.6803 | 0 | 3.4917 | 0 | 0 | 1.122 | 31.9033 | 0 | 50.1973 | Wind | 0.48144 | Wind | 7081982.4
| Rangpur Zone |  |  | 0 | 5.1681 | 1.8167 | 0.39123 | 0 | 0.86176 | 0 | 0 | 8.2377
| Total |  |  | 122.3809 | 128.7248 | 42.1319 | 0.43464 | 0.72018 | 3.4502 | 56.1459 | 0.48144 | 354.47
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 431394815.0515 |  | Hydro | 72018
|  |  |  | Coal | 835532583.8775 |  | Solar | 54841893.8968
|  |  |  | HFO | 731783737.24 |  | Import | 325040177.4
|  |  |  | HSD | 12958009.254 |  | Wind | 7081982.4
[5 empty] | Total: | 239,87,05,217 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.0756 | Peak Hr Flow | 888.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 10213363.63 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.9033 | Peak Hr Flow | 1443.85 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2687 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.167 | Peak Hr Flow | 110.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2863 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 56.1459 | Peak Hr Flow | 2441.85 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 213 |  | 6319
|  |  |  | Chattogram |  | 37 |  | 1632
|  |  |  | Cumilla |  | 27 |  | 1612
|  |  |  | Mymensingh |  | 200 |  | 1263
|  |  |  | Sylhet |  | 0 |  | 531
|  |  |  | Khulna |  | 6 |  | 1780
|  |  |  | Barishal |  | 6 |  | 535
|  |  |  | Rajshahi |  | 0 |  | 1682
|  |  |  | Rangpur |  | 0 |  | 990
|  |  |  | Total |  | 489 |  | 16344
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:15 | Khulna (C) S/S TR-1 425T HT is restored.
|  | 08:16 | Khulna (C) S/S TR-1 425T LT is restored.
| 08:22 | 12:50 | Sonargaon 132/33kV S/S Tr-2 LT Scheduled S/D Due to 33kv bushing To Jack bus loop change | [7 empty] | 50.0MW load
|  |  | due To excessive temperature. | [7 empty] | interrup.
| 08:22 | 08:56 | Sherpur 132/33kV S/S Transformer- 01 LT Tripped showing IDMT E/F. relays Due to | [7 empty] | 8.0MW load
|  |  | Nalitabari 33 kv fedder fault & bad weather . | [7 empty] | interrup.
| 08:22 | 08:56 | Sherpur 132/33kV S/S Transformer- 02 LT Tripped showing IDMT E/F relays Due to Nalitabari | [7 empty] | 8.0MW load
|  |  | 33 Kv feeder fault & bad weaher. | [7 empty] | interrup.
| 08:23 | 12:49 | Sonargaon 132/33kV S/S Tr-2 HT Scheduled S/D Due to 33kv bushing To Jack bus loop change | [7 empty] | 50.0MW load
|  |  | due To excessive temperature. | [7 empty] | interrup.
| 08:39 | 11:31 | Khulna (C) S/S Tr-2 415 T LT Project Work S/D Due to project work
| 08:39 | 11:30 | Khulna (C) S/S Tr-2 415 T HT Project Work S/D Due to project work
|  | 08:45 | Chandpur 132/33kV S/S 422T(T-5) HT is restored.
| 08:48 | 17:48 | Chandpur 132/33kV S/S Bus A Forced S/D Due to Maintenance
| 09:00 | 16:55 | BSRM-Cumilla(N) 230 kV Ckt-2 Project Work S/D from Feni 230/132kV end Due to SAS AND DFDR
work witnessing
| 09:04 | 12:05 | Agrabad 132/33kV S/S MTR-01 (406T) LT Scheduled S/D Due to Oil leakage problem in the
Vacuum Valve.
|  | 09:04 | Keranigonj 230/132/33kV S/S TR-1 HT is restored.
|  | 09:05 | Keranigonj 230/132/33kV S/S TR-1 LT is restored.
|  | 09:05 | Keranigonj 230/132/33kV S/S TR-1 LT is restored.
| 09:05 | 12:04 | Agrabad 132/33kV S/S MTR-01 (406T) HT Scheduled S/D Due to Oil leakage problem in the
Vacuum Valve.
| 09:17 | 18:31 | Feni 132/33kV S/S T-2(415T) HT Scheduled S/D Due to T-2 Breaker Pre Commission
| 09:18 | 18:32 | Feni 132/33kV S/S T-2(415T) LT Scheduled S/D Due to T-2 Breaker Pre Commission
| 09:19 | 11:45 | Agrabad 132/33kV S/S Auxiliary Transformer-01 HT Scheduled S/D Due to Oil leakage problem
in the Vacuum Valve.
| 09:22 | 18:35 | Savar 132/33kV S/S T-2 LT Scheduled S/D Due to Relay change work.
| 09:23 | 18:35 | Savar 132/33kV S/S T-2 HT Scheduled S/D Due to Relay change work.
| 09:24 | 14:02 | Goalpara 132/33kV S/S Goalpara-NWPGCL Scheduled S/D Due to High Temperature Removing Work
| 09:45 | 16:40 | Baghabari-Roppur 230kV Ckt-2 Project Work S/D from Baghabari 230/132kV end Due to
টেলিকমিউনিকেশন সিস্টেম টেস্টিং এন্ড কমিশনিং
|  | 09:45 | Rajshahi 132/33kV S/S Transformer T-2(415T) HT is restored.
|  | 09:46 | Rajshahi 132/33kV S/S Transformer T-2(415T) LT is restored.
|  | 09:48 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT is restored.
|  | 09:48 | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT is restored.
|  | 10:15 | Khulshi-Madunaghat 132kV Ckt-2 is restored.
| 10:27 | 11:47 | Rajshahi 132/33kV S/S Transformer T-1(405T) HT Scheduled S/D Due to Maintenance Work
| 10:28 | 11:47 | Rajshahi 132/33kV S/S Transformer T-1(405T) LT Scheduled S/D Due to Maintenance Work
|  | 10:34 | Sholosohor 132/33kV S/S Sholoshahar-Khulshi Ckt-2 is restored.
| 11:00 |  | Mirsorai 230/33kV S/S TR-1, 718T HT Forced S/D Due to Flashing has been noticed in the
secondary side of the transformer. Therefore, it needs to be checked and maintenance
| 11:08 | 16:13 | BIPTC S/S 20DF43 Scheduled S/D Due to Tripped for zero sequence over current
|  | 11:22 | Goalpara 132/33kV S/S T-6 HT is restored.
|  | 11:23 | Goalpara 132/33kV S/S T-6 LT is restored.
| 11:28 | 18:51 | BIPTC S/S Baharampur-4 Scheduled S/D
| 11:41 | 13:12 | Goalpara 132/33kV S/S Bus 1 Scheduled S/D Due to NWPGCL Line High Tempareture Removing
Work.
| 12:00 |  | Day Peak Generation: 14438 MW.
| 12:18 | 15:12 | Bhulta-Ghorasal 230 kV Ckt-1 Forced S/D from Bhulta 400/230kV end.
| 12:49 | 13:40 | Kasba 132/33kV S/S Muradnagar-Kasba Ckt-2 Scheduled S/D Due to Shutdown has been taken
from Muranagar Substation for removing kite.
| 12:53 | 13:40 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Kosba Ckt-02 Forced S/D Due to for kite remove
| 13:46 |  | Sirajgonj 400 MW CCPP Unit-4 Shutdown with remarks:- ST
| 13:56 |  | Sirajgonj 400 MW CCPP Unit-4 Shutdown with remarks:- GT
| 14:09 |  | 120/140 MVA,230/33 KV New Txr. TR-2 Charge at 230/33 KV Charfession S/S.
| 14:19 | 15:58 | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 Forced S/D Due to Due to LA grounding
replacement
|  | 14:41 | Candpur- Kachua 132kV Ckt-2 is restored.
| 14:53 | 17:57 | Shyampur 230/132kV S/S Auto TR-1 LT Scheduled S/D Due to Connect with 132kV Bus 1 for
commissioning of 132kV Shyampur 01 Bay-E07
| 14:53 | 17:57 | Shyampur 230/132kV S/S Auto TR-1 HT Scheduled S/D Due to Connect with 132kV Bus 1 for
commissioning of 132kV Shyampur 01 Bay-E07
| 15:09 | 17:17 | Candpur- Kachua 132kV Ckt-1 Scheduled S/D from Kachua 230/132/33kV end Due to 132 kv
Chandpur -1 has been S/D By Backup NLDC
| 15:13 | 17:10 | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D | [7 empty] | 80.0MW load
interrup.
| 15:13 | 17:10 | Kabirpur 132/33kV S/S XFR, T-2 LT Scheduled S/D Due to Red Hot Maintanence of Kashimpur | [7 empty] | 80.0MW load
|  |  | -2 Bus DS. | [7 empty] | interrup.
| 15:33 | 16:57 | Barishal 230/132kV S/S ATR-1 LT Scheduled S/D
| 15:35 | 17:30 | Candpur- Kachua 132kV Ckt-1 Scheduled S/D from Chandpur 132/33kV end Due to Maintenance
work
| 16:22 | 18:37 | Khulna (C) S/S TR-1 425T LT Project Work S/D Due to 33 kv loop connector clamp
upgradation by using bymetal.
| 16:23 | 18:36 | Khulna (C) S/S TR-1 425T HT Project Work S/D Due to 33 loop connector 3 clamp upgradation
by using by metal.
|  | 16:57 | Korerhat 400/230/132kV S/S Feni -2 is restored.
|  | 17:04 | Cumilla(N)-Meghnaghat 230 kV Ckt-1 is restored.
|  | 17:04 | Cumilla(N)-Meghnaghat 230 kV Ckt-1 is restored.
|  | 17:04 | Cumilla(N)-Meghnaghat 230 kV Ckt-1 is restored.
| 17:09 | 18:17 | Noapara 132/33kV S/S T-2 HT Scheduled S/D Due to None | [7 empty] | 13.0MW load
interrup.
| 17:09 | 18:18 | Noapara 132/33kV S/S T-2 LT Scheduled S/D Due to Due to Reb-1 Red hot Maintenance. | [7 empty] | 13.0MW load
interrup.
| 17:14 | 01:07 | Bhulta-Ghorasal 230 kV Ckt-2 Forced S/D from Bhulta 400/230kV end.
| 17:48 |  | Chandpur 132/33kV S/S 422T(T-5) HT Forced S/D
| 20:46 | 21:06 | Panchagar-Thakurgaon 132kV Ckt-1 Tripped from Panchagarh 132/33kV end showing Micom p442
relays Due to Heavy Thundering
| 21:00 |  | Sirajgonj 400 MW CCPP Unit-4 Synchronized with remarks:- GT
| 21:52 | 05:50 | Bhulta 132/33kV S/S GT1 LT Forced S/D Due to 33 KV LT Bushing Red Hot | [7 empty] | 50.0MW load
interrup.
| 21:52 | 05:50 | Bhulta 132/33kV S/S GT1 LT Forced S/D Due to 33 KV LT Bushing Red Hot | [7 empty] | 50.0MW load
interrup.
| 22:00 |  | Sirajgonj 400 MW CCPP Unit-4 Synchronized with remarks:- ST
| 22:02 | 05:48 | Bhulta 132/33kV S/S GT1 HT Forced S/D Due to 33 KV LT Bushing Red Hot | [7 empty] | 50.0MW load
interrup.
| 22:18 |  | Sirajgonj 400 MW CCPP Unit-4 Synchronized with remarks:- ST
| 02:56 |  | SS Power Shutdown with remarks:- U-2
| 02:57 |  | SS Power Synchronized with remarks:- U-1 running
| 04:17 | 06:17 | Kulaura 132/33kV S/S TR-1 AB LT Tripped showing Differential Protection Relay, Over
current protection Relay relays Due to Over current fault
| 04:17 | 06:01 | Kulaura 132/33kV S/S TR-1 AB HT Tripped showing Differential Protection Relay, Over
current protection Relay relays Due to Over current fault
| 05:02 | 05:30 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Tripped from Brahmanbaria 132/33kV end showing
Distance relays Due to Fault and from Shahjibazar 132/33kV end showing Distance Ralay.
relays Due to Stormy Weather.
| 05:55 |  | Khulshi 132/33kV S/S 405T (T1) LT Scheduled S/D Due to Red hot maintenance
| 05:56 |  | Khulshi 132/33kV S/S 405T (T1) HT Scheduled S/D Due to Red hot maintenance
| 06:00 |  | Minimum Generation: 12623 MW.
| 06:04 |  | Bogura 230/132kV S/S T-02 LT Scheduled S/D Due to Red-hot Maintenance
| 06:04 |  | Bogura 230/132kV S/S T-02 HT Scheduled S/D Due to Red Hot Maintenance
| 06:14 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Scheduled S/D Due to Due | [7 empty] | 30.0MW load
|  |  | to Temperature rise at 33 kV side. | [7 empty] | interrup.
| 06:15 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D Due to Due | [7 empty] | 30.0MW load
|  |  | to Temperature rise at 33 kV side. | [7 empty] | interrup.
| 06:37 |  | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to Red Hot Repair | [7 empty] | 12.5MW load
interrup.
| 06:38 |  | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to Red Hot Repair | [7 empty] | 12.5MW load
interrup.
| 07:06 |  | Niamatpur 132/33kV S/S Transformer-2 (417T) LT Forced S/D Due to 33 kV Bus -2 PBS | [7 empty] | 23.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 07:07 |  | Niamatpur 132/33kV S/S Transformer-2 (417T) HT Forced S/D Due to 33 kV Bus -2 PBS | [7 empty] | 23.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 07:11 |  | Korerhat 400/230/132kV S/S ATR-3(7103T) LT Project Work S/D Due to Shutdown taken by
CNTIC due to project work.
| 07:13 |  | Korerhat 400/230/132kV S/S ATR-3(7103T) HT Project Work S/D Due to Shutdown taken by
CNTIC due to project work.
| 07:20 |  | Naogaon 132/33kV S/S T-2 33kV BUS Project Work S/D Due to T-2 33kV CB loop connection | [7 empty] | 10.0MW load
interrup.
| 07:27 |  | Pabna 132/33kV S/S T-3 LT Scheduled S/D Due to Redhot maintenance work | [7 empty] | 15.0MW load
interrup.
| 07:27 |  | Pabna 132/33kV S/S T-3 HT Scheduled S/D | [7 empty] | 15.0MW load
interrup.
| 07:33 |  | Ishurdi 230/132kV S/S 230 kV Bus 2 Scheduled S/D
| 07:39 |  | Baghabari-Ishurdi 230 kV Ckt-1 Scheduled S/D from Baghabari 230/132kV end.
| 07:53 |  | Jamalpur 132/33kV S/S T-4 HT Scheduled S/D Due to High temperature | [7 empty] | 15.0MW load
interrup.
| 07:53 |  | Jamalpur 132/33kV S/S T-4 LT Scheduled S/D Due to High temperature | [7 empty] | 15.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 23-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 317 | 8827200 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 391466 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 92 | 1087000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 290 | 7383003 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 255600 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 146 | 3373440 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 538640 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 270759 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 480600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 449280 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 48 | 619680 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 32 | 704302 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 52 | 736992 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 686400 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 799200 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 167258 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 145800 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 315 | 10572727.27 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 219 | 1840850 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3272400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2024 | 42602597.27
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 23 | 175446 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 102600 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1133280 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 720180 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 215 | 4961200 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 87 | 2093418 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 52 | 673968 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 49 | 285735 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 573120 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 11 | 334560 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 58 | 759360 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23879 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 459164 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 845417 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 95 | 2116827 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 578880 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 89 | 1768909 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 136 | 1425163 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1130 | 28363634 | Can't Start AGC
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 12 | 481440 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1000 | 18785454.55 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 3155.36 | 66661634.55
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 188 | 4882000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 355 | 8402700 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 230 | 6472000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 350 | 5927000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 188136 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 137760 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 117091 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1190868 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 914981 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 532704 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 96 | 1713320 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 176 | 2991840 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 110 | 3167040 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 860414 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 337740 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 110 | 1503660 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 17 | 153720 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 68 | 533760 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 349600 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 2008.2 | 40376334
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 46080 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 2071200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 873600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 188910 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 32400 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 77400 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 172 | 3300790
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 38395 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 993000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 675840 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 138 | 3351518.18 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 151 | 3278000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 697728 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2058240 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2430190 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 6 | 456960 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7284000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 344 | 8432000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1233 | 29695871.18
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 888 | 21075636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 30 | 147360 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 52 | 210176 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 254 | 5608512 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 21 | 402820 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | FGMO
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 580320 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 43407.27 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 922 | 17090907 | None
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2167 | 45159138.27
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 1249 | 30029091 | Machine Problem
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 625344 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 125 | 2851000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1040 | 23963636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5232480 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 208800 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 237 | 5324000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4248 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2941 | 68238599.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 291432 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 193448 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 127267 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 185 | 3870273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 199 | 4271673 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 0 | 5538400 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 188785 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 41 | 305981 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 364448 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 90 | 1250208 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 90 | 1061568 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24840 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1443.85 | 31903273 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 266304 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 539423 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2243.85 | 50197323
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 100 | 391230 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 45 | 1124072 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 177 | 4044000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 65 | 526060 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 32802.84 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1290607 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 88794 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 740160 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 502 | 8237725.84
Eastern Grid Total |  |  |  |  | 17418.042 | 8592.56 | 182637227
Western Grid Total |  |  |  |  | 11852.195 | 7853.85 | 171832786.47
National Grid Total |  |  |  |  | 29270.237 | 16446.41 | 354470013.47
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 23-05-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10879.56 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4975 | MW
i) Dhaka area |  |  | 6105.56 |  | MW | i) Khulna area |  |  |  | 1774 | MW
ii) Chattogram area |  |  | 1595 |  | MW | ii) Barishal area |  |  |  | 528.8 | MW
iii) Cumilla area |  |  | 1585 |  | MW | iii) Rajshahi area |  |  |  | 1682.2 | MW
iv) Mymensingh area |  |  | 1063 |  | MW | iv) Rangpur area |  |  |  | 990 | MW
v) Sylhet area |  |  | 531 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15854.56 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 7 | 02:00 | 67 | Hasnabad | 102 | 20:00 | 133 | Natore | 165 | 23:00
2 | AKSML | 124 | 08:00 | 68 | Hathazari | 99 | 23:00 | 134 | Nawabganj | 72 | 19:00
3 | Aftabnagar | 46 | 19:00 | 69 | Hatirjheel | 64 | 13:00 | 135 | Netrakona | 134 | 19:30
4 | Agargaon | 142 | 14:00 | 70 | Ishurdi | 95 | 19:00 | 136 | New | 92.2 | 15:00
5 | Agrabad | 88 | 15:00 | 71 | Jaldhaka | 80 | 19:30 | 137 | Niamatpur | 83 | 19:30
6 | Amnura | 48 | 15:00 | 72 | Jamalpur | 102 | 18:30 | 138 | Noapara | 55 | 19:30
7 | Ashuganj | 96 | 02:00 | 73 | Jashore | 181 | 19:00 | 139 | PHP | 6 | 05:00
8 | BSRM | 189 | 15:00 | 74 | Jhenaidah | 137 | 00:00 | 140 | Pabna | 121 | 19:00
9 | Bagerhat | 94 | 20:00 | 75 | Joydebpur | 152 | 19:00 | 141 | Palashbari | 118 | 00:00
10 | Bajitpur | 86 | 13:00 | 76 | Joypurhat | 64 | 19:00 | 142 | Panchagarh | 65 | 00:00
11 | Bakerganj | 12.6 | 22:00 | 77 | Juldah | 19 | 15:00 | 143 | Patiya | 12 | 00:00
12 | Bakulia | 110 | 15:00 | 78 | KSRM | 12 | 09:00 | 144 | Patuakhali | 79.5 | 22:00
13 | Banani | 61.2 | 15:00 | 79 | Kabirpur | 247 | 09:00 | 145 | Payra | 40 | 00:00
14 | Bangabhaban | 23 | 11:00 | 80 | Kachua | 108 | 20:00 | 146 | Postogola | 60 | 00:00
15 | Barapukuria | 68 | 19:30 | 81 | Kaliganj | 12 | 00:00 | 147 | Pubail | 31 | 22:00
16 | Barguna | 26 | 00:00 | 82 | Kallyanpur | 135 | 18:30 | 148 | Purbachal | 41 | 13:00
17 | Barishal | 123 | 19:00 | 83 | Kalurghat | 46 | 16:00 | 149 | Purbasadipur | 140 | 19:30
18 | Barishal-230 | 120 | 21:00 | 84 | Kamrangirchar | 88 | 13:00 | 150 | Rahanpur | 42 | 00:00
19 | Baroaulia | 78 | 09:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 27 | 16:00
20 | Baroirhat | 81 | 19:00 | 86 | Kasba | 41 | 21:00 | 152 | Rajbari | 95 | 19:00
21 | Bashundhara | 211 | 15:00 | 87 | Kazla | 125 | 13:00 | 153 | Rajendrapur | 112 | 07:00
22 | BashundharaCement | 6 | 00:00 | 88 | Keranigonj | 89 | 21:00 | 154 | Rajshahi | 126 | 19:30
23 | Beanibazar | 76 | 00:00 | 89 | Khagrachori | 36 | 19:00 | 155 | Rajshahi-230 | 116 | 14:00
24 | Benapole | 81 | 19:00 | 90 | Khulna | 68 | 13:00 | 156 | Ramganj | 120 | 18:30
25 | Bhaluka | 157 | 19:00 | 91 | Khulshi | 216 | 16:00 | 157 | Rampur | 50 | 00:00
26 | Bhandaria | 61 | 22:00 | 92 | Kishoreganj | 124 | 21:00 | 158 | Rangamati | 19 | 19:00
27 | Bhangura | 48 | 19:00 | 93 | Kodda | 334 | 21:00 | 159 | Rangpur | 142 | 19:30
28 | Bheramara(GK) | 71 | 00:00 | 94 | Kulaura | 44 | 00:00 | 160 | Ruppur | 3.2 | 14:00
29 | Bhulta | 219 | 10:00 | 95 | Kurigram | 70 | 19:30 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 80 | 00:00 | 96 | Kushtia | 166 | 12:00 | 162 | Saidpur | 96 | 19:30
31 | Bogura | 189 | 20:00 | 97 | Laksam | 38 | 01:00 | 163 | Santhia | 40 | 21:00
32 | Borhanuddin | 98 | 23:00 | 98 | Lakshmipur | 49 | 19:30 | 164 | Satkhira | 150 | 19:00
33 | Brahmanbaria | 135 | 20:00 | 99 | Lalbag | 84 | 13:00 | 165 | Satmasjid | 116 | 16:00
34 | Cantonment | 132 | 13:00 | 100 | Lalmonirhat | 60 | 19:00 | 166 | Savar | 231 | 09:00
35 | Chandina | 44 | 22:00 | 101 | MI_Cement | 11.8 | 02:00 | 167 | SevenRings | 15.66 | 02:00
36 | Chandpur | 100 | 19:30 | 102 | Madanganj | 46 | 19:00 | 168 | ShahCement | 23 | 17:00
37 | Chandraghona | 39 | 19:30 | 103 | Madaripur | 140 | 22:00 | 169 | Shahjadpur | 102 | 19:00
38 | Chapai | 80 | 23:00 | 104 | Madartek | 94 | 23:00 | 170 | Shahjibazar | 126 | 21:00
39 | Charsaidpur | 43 | 12:00 | 105 | Madunaghat | 70 | 19:00 | 171 | Shahmirpur | 59 | 23:00
40 | Chauddagram | 100 | 22:00 | 106 | Magura | 80 | 19:00 | 172 | Shariatpur | 108 | 22:00
41 | Chhatak | 39 | 00:00 | 107 | Mahasthangarh | 81 | 00:00 | 173 | Sherpur | 122 | 18:30
42 | Chowmuhani | 187 | 23:00 | 108 | Maijdee | 56 | 22:00 | 174 | Shikalbaha | 36 | 00:00
43 | Chuadanga | 131 | 01:00 | 109 | Manikganj | 152 | 19:00 | 175 | Shitalakhya | 98.7 | 15:00
44 | Coxsbazar | 149 | 12:00 | 110 | Maniknagar | 87 | 13:00 | 176 | Sholosohor | 51 | 15:00
45 | Cumilla(N) | 132 | 23:00 | 111 | Matarbari | 59 | 21:00 | 177 | Shomvuganj | 16 | 18:30
46 | Cumilla(S) | 176 | 13:00 | 112 | Matuail | 88 | 15:00 | 178 | Shyampur | 186 | 13:00
47 | Daganbhuiyan | 49 | 14:00 | 113 | Metrorail_Motijheel | 30 | 19:00 | 179 | Siddhirganj | 135 | 19:00
48 | Daudkandi | 148 | 19:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 136 | 21:00
49 | DhakaUniversity | 104 | 13:00 | 115 | Millgate | 103 | 12:00 | 181 | Sonargaon | 155 | 20:00
50 | Dhamrai | 108 | 23:00 | 116 | Mirpur | 173 | 19:00 | 182 | Sreemongol | 83 | 00:00
51 | Dhanmondi | 123 | 13:00 | 117 | Mirsorai | 48 | 09:00 | 183 | Sreepur | 121 | 21:00
52 | Dohazari | 114 | 22:00 | 118 | Mirzapur | 49 | 17:00 | 184 | Srinagar | 58.4 | 19:00
53 | Faridpur | 193 | 19:30 | 119 | Mithapukur | 62 | 19:00 | 185 | Sunamganj | 60 | 02:00
54 | Fatullah | 97 | 23:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 49 | 00:00
55 | Fenchuganj | 35 | 00:00 | 121 | Mogbazar | 109.1 | 13:00 | 187 | Sylhet-132 | 114 | 00:00
56 | Feni | 118 | 19:00 | 122 | Mongla | 51 | 16:00 | 188 | TK | 28 | 19:00
57 | GPH | 1 | 00:00 | 123 | Motijheel | 58 | 13:00 | 189 | Tangail | 174 | 18:00
58 | Ghatail | 82 | 17:00 | 124 | Muktagacha | 30 | 09:00 | 190 | Taraganj | 23 | 19:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 133 | 23:00 | 191 | Tasnim | 28 | 21:00
60 | Ghorashal-230 | 115 | 19:00 | 126 | Muradnagar | 56 | 22:00 | 192 | Thakurgaon | 109 | 19:30
61 | Goalpara | 48 | 19:00 | 127 | Mymensingh | 168 | 13:00 | 193 | Tongi | 169 | 11:00
62 | Gollamari | 130 | 13:00 | 128 | Nabinagar | 86 | 17:00 | 194 | Ullahpara | 46 | 19:00
63 | Gopalganj | 131 | 19:30 | 129 | Naogaon | 159 | 19:30 | 195 | Ullon | 56 | 23:00
64 | Gulshan | 150 | 13:00 | 130 | Narail | 72 | 19:30 | 196 | Uttara | 110 | 16:00
65 | Halishahar | 110.5 | 15:00 | 131 | Narinda | 83 | 13:00 | 197 | UttaraNew | 62 | 23:00
66 | HaripurSBU | 140 | 07:00 | 132 | Narshingdi | 194 | 23:00 | 198 | Zigatola | 104 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 23-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15415 | 465 |  | 15900.93
1:00 | 14930.56 | 420 |  | 15369.56
2:00 | 14485.56 | 233 |  | 14728.56
3:00 | 14222.86 | 233 |  | 14465.86
4:00 | 13804.5 | 233 |  | 14047.5
5:00 | 13680.5 | 210 |  | 13899.5
6:00 | 13024.08 | 215 |  | 13249.08
7:00 | 12988.3 | 198 |  | 13195.3
8:00 | 13222.2 | 155 |  | 13384.2
9:00 | 13322.95 | 120 |  | 13447.95
10:00 | 13692.93 | 133 |  | 13831.93
11:00 | 13994.17 | 229 |  | 14233.17
12:00 | 14442.69 | 449 |  | 14911.69
13:00 | 14780.72 | 316 |  | 15110.94
14:00 | 15007.6 | 319 |  | 15340.6
15:00 | 15243.09 | 883 |  | 16166.09
16:00 | 14950.47 | 477 |  | 15448.47
17:00 | 14880.25 | 275 |  | 15167.25
18:00 | 14722.76 | 146 |  | 14875.76
19:00 | 16244.15 | 316 |  | 16574.15
19:30 | 16446.41 | 489 |  | 16957.41
20:00 | 16248.98 | 274 |  | 16534.98
21:00 | 16339.22 | 343 |  | 16697.22
22:00 | 15666 | 220 |  | 15896
23:00 | 15757.09 | 190 |  | 15956.09
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 23-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7681.8 | 7733.2 | 15415 | DAILY GENERATION CURVE
00:30 | 7534.08 | 7638.7 | 15172.78
01:00 | 7386.36 | 7544.2 | 14930.56 | 23-05-2026
01:30 | 7282.36 | 7425.7 | 14708.06
02:00 | 7178.36 | 7307.2 | 14485.56
02:30 | 7043.11 | 7311.1 | 14354.21
03:00 | 6907.86 | 7315 | 14222.86
03:30 | 6813.18 | 7200.5 | 14013.68
04:00 | 6718.5 | 7086 | 13804.5
04:30 | 6697 | 7045.5 | 13742.5
05:00 | 6675.5 | 7005 | 13680.5
05:30 | 6548.735 | 6803.555 | 13352.29
06:00 | 6421.97 | 6602.11 | 13024.08
06:30 | 6388.205 | 6617.985 | 13006.19
07:00 | 6354.44 | 6633.86 | 12988.3
07:30 | 6426.295 | 6678.955 | 13105.25
08:00 | 6498.15 | 6724.05 | 13222.2
08:30 | 6613.105 | 6659.47 | 13272.575
09:00 | 6728.06 | 6594.89 | 13322.95
09:30 | 6904.3 | 6603.64 | 13507.94
10:00 | 7080.54 | 6612.39 | 13692.93
10:30 | 7147 | 6696.55 | 13843.55
11:00 | 7213.46 | 6780.71 | 13994.17
11:30 | 7382.935 | 6835.495 | 14218.43
12:00 | 7552.41 | 6890.28 | 14442.69
12:30 | 7608.165 | 7003.54 | 14611.705
13:00 | 7663.92 | 7116.8 | 14780.72
13:30 | 7724.865 | 7169.295 | 14894.16
14:00 | 7785.81 | 7221.79 | 15007.6
14:30 | 7815.745 | 7309.6 | 15125.345
15:00 | 7845.68 | 7397.41 | 15243.09
15:30 | 7744.24 | 7352.54 | 15096.78
16:00 | 7642.8 | 7307.67 | 14950.47
16:30 | 7753.835 | 7161.525 | 14915.36
17:00 | 7864.87 | 7015.38 | 14880.25
17:30 | 7949.735 | 6851.77 | 14801.505
18:00 | 8034.6 | 6688.16 | 14722.76
18:30 | 8401.08 | 7082.375 | 15483.455
19:00 | 8767.56 | 7476.59 | 16244.15
19:30 | 8592.56 | 7853.85 | 16446.41
20:00 | 8598.56 | 7650.42 | 16248.98
20:30 | 8718.56 | 7575.54 | 16294.1 |  | Executive Engineer
21:00 | 8838.56 | 7500.66 | 16339.22 |  | Network Operation Division
21:30 | 8658.78 | 7343.83 | 16002.61
22:00 | 8479 | 7187 | 15666
22:30 | 8452.53 | 7259.015 | 15711.545
23:00 | 8426.06 | 7331.03 | 15757.09

## En-Curve
QF-LDC-12
Date | 23-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3489 | 1371 | 888 | 0 | 156 | 1447 | 30 | 5515 | 0 | 630 | 1876 | 0 | 0 | 13 | 465 | DAILY ENERGY CURVE
00:30 | 3463.5 | 1363 | 888 | 0 | 157 | 1445.5 | 30 | 5409.5 | 0 | 597 | 1803.28 | 0 | 0 | 16 | 442.5 | 23-05-2026
01:00 | 3438 | 1355 | 888 | 0 | 158 | 1444 | 30 | 5304 | 0 | 564 | 1730.56 | 0 | 0 | 19 | 420
01:30 | 3444.5 | 1347 | 888 | 0 | 156 | 1391 | 30 | 5221 | 0 | 550.5 | 1665.56 | 0 | 0 | 14.5 | 326.5 | Energy Generated | 354.47 |  | MKWHr
02:00 | 3451 | 1339 | 888 | 0 | 154 | 1338 | 30 | 5138 | 0 | 537 | 1600.56 | 0 | 0 | 10 | 233 | Energy not Served | 7.052 |  | MKWHr
02:30 | 3517.5 | 1384.25 | 888 | 0 | 151 | 1379 | 30 | 5110 | 0 | 449 | 1434.46 | 0 | 0 | 11 | 233 | Total Energy Requirement | 361.522 |  | MKWHr
03:00 | 3584 | 1429.5 | 888 | 0 | 148 | 1420 | 30 | 5082 | 0 | 361 | 1268.36 | 0 | 0 | 12 | 233
03:30 | 3595.5 | 1406.5 | 862 | 0 | 145 | 1419.5 | 30 | 5104.5 | 0 | 331 | 1111.18 | 0 | 0 | 8.5 | 233
04:00 | 3607 | 1383.5 | 836 | 0 | 142 | 1419 | 30 | 5127 | 0 | 301 | 954 | 0 | 0 | 5 | 233
04:30 | 3619 | 1346.5 | 862 | 0 | 141 | 1396.5 | 30 | 5135.5 | 0 | 301 | 901 | 0 | 0 | 10 | 221.5
05:00 | 3631 | 1309.5 | 888 | 0 | 140 | 1374 | 30 | 5144 | 0 | 301 | 848 | 0 | 0 | 15 | 210
05:30 | 3610 | 1288.5 | 888 | 0 | 136 | 1324.5 | 30 | 5101 | 13.29 | 285.5 | 651.5 | 0 | 0 | 24 | 212.5
06:00 | 3589 | 1267.5 | 888 | 0 | 132 | 1275 | 30 | 5058 | 26.58 | 270 | 455 | 0 | 0 | 33 | 215
06:30 | 3653.5 | 1291.75 | 888 | 0 | 134 | 1298.5 | 30 | 5008 | 59.94 | 269.5 | 352 | 0 | 0 | 21 | 206.5
07:00 | 3718 | 1316 | 888 | 0 | 136 | 1322 | 30 | 4958 | 93.3 | 269 | 249 | 0 | 0 | 9 | 198
07:30 | 3759 | 1327 | 888 | 0 | 132 | 1309.5 | 30 | 4973 | 142.25 | 283.5 | 252 | 0 | 0 | 9 | 176.5
08:00 | 3800 | 1338 | 888 | 0 | 128 | 1297 | 30 | 4988 | 191.2 | 298 | 255 | 0 | 0 | 9 | 155
08:30 | 3781 | 1307.5 | 888 | 0 | 126 | 1289.79 | 30 | 4991 | 164.785 | 303 | 378 | 0 | 0 | 13.5 | 137.5
09:00 | 3762 | 1277 | 888 | 0 | 124 | 1282.58 | 30 | 4994 | 138.37 | 308 | 501 | 0 | 0 | 18 | 120
09:30 | 3801.5 | 1252.5 | 888 | 0 | 126 | 1282.58 | 30 | 4967.5 | 226.86 | 312 | 596.5 | 0 | 0 | 24.5 | 126.5
10:00 | 3841 | 1228 | 888 | 0 | 128 | 1282.58 | 30 | 4941 | 315.35 | 316 | 692 | 0 | 0 | 31 | 133
10:30 | 3807 | 1264 | 888 | 0 | 137 | 1293.79 | 30 | 4928 | 372.76 | 308 | 790 | 0 | 0 | 25 | 181
11:00 | 3773 | 1300 | 888 | 0 | 146 | 1305 | 30 | 4915 | 430.17 | 300 | 888 | 0 | 0 | 19 | 229
11:30 | 3711.5 | 1254 | 888.5 | 0 | 152 | 1312.61 | 30 | 4965 | 459.32 | 322.5 | 1104.5 | 0 | 0 | 18.5 | 339
12:00 | 3650 | 1208 | 889 | 0 | 158 | 1320.22 | 30 | 5015 | 488.47 | 345 | 1321 | 0 | 0 | 18 | 449
12:30 | 3652.5 | 1218.5 | 889 | 0 | 166 | 1322.405 | 30 | 5086 | 516.8 | 347 | 1350.5 | 0 | 0 | 33 | 382.5
13:00 | 3655 | 1229 | 889 | 0 | 174 | 1324.59 | 30 | 5157 | 545.13 | 349 | 1380 | 0 | 0 | 48 | 316
13:30 | 3630 | 1293.5 | 888.5 | 0 | 153 | 1350.275 | 30 | 5241 | 509.285 | 350 | 1413.1 | 0 | 0 | 35.5 | 317.5
14:00 | 3605 | 1358 | 888 | 0 | 132 | 1375.96 | 30 | 5325 | 473.44 | 351 | 1446.2 | 0 | 0 | 23 | 319
14:30 | 3619 | 1364.5 | 888 | 0 | 124 | 1399.075 | 30 | 5420.5 | 427.57 | 336.5 | 1489.7 | 0 | 0 | 26.5 | 601
15:00 | 3633 | 1371 | 888 | 0 | 116 | 1422.19 | 30 | 5516 | 381.7 | 322 | 1533.2 | 0 | 0 | 30 | 883
15:30 | 3550.5 | 1319.5 | 888 | 0 | 115 | 1435.16 | 30 | 5509 | 317.24 | 352.5 | 1551.88 | 0 | 0 | 28 | 680
16:00 | 3468 | 1268 | 888 | 0 | 114 | 1448.13 | 30 | 5502 | 252.78 | 383 | 1570.56 | 0 | 0 | 26 | 477
16:30 | 3470 | 1261.75 | 888.5 | 0 | 110 | 1384.18 | 30 | 5552.5 | 184.77 | 401.5 | 1607.16 | 0 | 0 | 25 | 376
17:00 | 3472 | 1255.5 | 889 | 0 | 106 | 1320.23 | 30 | 5603 | 116.76 | 420 | 1643.76 | 0 | 0 | 24 | 275
17:30 | 3458 | 1297.5 | 888.5 | 0 | 109 | 1263.865 | 30 | 5479 | 69.38 | 481 | 1697.26 | 0 | 0 | 28 | 210.5
18:00 | 3444 | 1339.5 | 888 | 0 | 112 | 1207.5 | 30 | 5355 | 22 | 542 | 1750.76 | 0 | 0 | 32 | 146
18:30 | 3481 | 1496.25 | 888 | 0 | 114 | 1312.045 | 30 | 5440 | 11 | 690.5 | 1917.66 | 80 | 0 | 23 | 231
19:00 | 3518 | 1653 | 888 | 0 | 116 | 1416.59 | 30 | 5525 | 0 | 839 | 2084.56 | 160 | 0 | 14 | 316
19:30 | 3594 | 1409 | 888 | 0 | 110 | 1443.85 | 30 | 5800 | 0 | 855 | 2204.56 | 100 | 0 | 12 | 489
20:00 | 3530 | 1508 | 888 | 0 | 104 | 1446.42 | 30 | 5903 | 0 | 773 | 2019.56 | 30 | 0 | 17 | 274
20:30 | 3576 | 1555.5 | 841 | 0 | 106 | 1447.04 | 30 | 5924.5 | 0 | 773 | 2006.56 | 15 | 0 | 19.5 | 308.5
21:00 | 3622 | 1603 | 794 | 0 | 108 | 1447.66 | 30 | 5946 | 0 | 773 | 1993.56 | 0 | 0 | 22 | 343
21:30 | 3649.5 | 1529 | 794 | 0 | 116 | 1423.83 | 30 | 5930 | 0 | 695.5 | 1816.78 | 0 | 0 | 18 | 281.5
22:00 | 3677 | 1455 | 794 | 0 | 124 | 1400 | 30 | 5914 | 0 | 618 | 1640 | 0 | 0 | 14 | 220
22:30 | 3804.5 | 1527.75 | 794.5 | 0 | 125 | 1359.015 | 30 | 5915 | 0 | 602.5 | 1534.28 | 0 | 0 | 19 | 205
23:00 | 3932 | 1600.5 | 795 | 0 | 126 | 1318.03 | 30 | 5916 | 0 | 587 | 1428.56 | 0 | 0 | 24 | 190
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 23-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 118 | 6 | 508 | 116 | 1796 | 452 | Ishurdi-Ghorashal Ckt-1 | Export | 3596363.63
1:00 | 129 | 3 | 540 | 100 | 1838 | 438
2:00 | 143 | 9 | 602 | 144 | 1858 | 456 |  | Import | 0
3:00 | 146 | 8 | 638 | 154 | 1936 | 462
4:00 | 127 | 13 | 596 | 146 | 1866 | 438 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 147 | 8 | 604 | 128 | 1904 | 452
6:00 | 157 | 14 | 666 | 170 | 1922 | 476 |  | Import | 0
7:00 | 166 | 17 | 656 | 158 | 1874 | 486
8:00 | 185 | 27 | 666 | 170 | 2012 | 578 | Sirajganj-Sreepur Ckt-1 | Export | 3305000
9:00 | 188 | 41 | 658 | 178 | 1948 | 616
10:00 | 189 | 42 | 604 | 150 | 1906 | 642 |  | Import | 0
11:00 | 196 | 48 | 610 | 172 | 1928 | 794
12:00 | 162 | 39 | 560 | 174 | 1826 | 776 | Sirajganj-Sreepur Ckt-2 | Export | 3312000
13:00 | 151 | 34 | 526 | 164 | 1806 | 702
14:00 | 144 | 29 | 494 | 146 | 1916 | 706 |  | Import | 0
15:00 | 140 | 23 | 466 | 112 | 1940 | 696
16:00 | 140 | 23 | 450 | 104 | 1878 | 688 | Gopalganj-Aminbazar Ckt-1 | Export | 0
17:00 | 131 | 29 | 394 | 108 | 1720 | 714
18:00 | 122 | 36 | 354 | 118 | 1604 | 618 |  | Import | 0
18:30 | 150 | 42 | 426 | 130 | 1728 | 600
19:00 | 152 | 40 | 458 | 160 | 1870 | 568 | Gopalganj-Aminbazar Ckt-2 | Export | 0
19:30 | 175 | 44 | 520 | 178 | 1992 | 604
20:00 | 158 | 45 | 456 | 160 | 1870 | 562 |  | Import | 0
21:00 | 125 | 32 | 470 | 170 | 1824 | 578
22:00 | 135 | 25 | 576 | 182 | 1850 | 496 |  | Total Export | 10213363.63
23:00 | 134 | 23 | 614 | 196 | 1804 | 562 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 23-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 364 | 17:00 | 346 | 15:00 | Madunaghat | 395 | 19:00 | 387 | 15:00
Amtali | 407 | 18:30 | 400 | 00:00 | Meghnaghat | 371 | 18:30 | 351 | 15:00
Ashuganj | 406 | 6:00 | 388 | 13:00 | Payra | 408 | 18:00 | 402 | 00:00
Bhulta | 400 | 05:00 | 378 | 14:00 | Rahanpur | 409 | 18:30 | 396 | 15:00
Bibiana | 385 | 01:00 | 378 | 14:00 | Rampal | 388 | 18:00 | 373 | 00:00
BIPTC | 401 | 04:00 | 385 | 15:00
Bogura | 396 | 18:30 | 381 | 15:00
Gopalganj | 382 | 18:00 | 367 | 23:00
Kaliakoir | 360 | 05:00 | 345 | 15:00
Korerhat | 388 | 18:30 | 375 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 223 | 04:00 | 209 | 15:00 | Jhenaidah | 227 | 18:30 | 208 | 15:00
AKSML | 231 | 01:00 | 223 | 17:00 | Kachua | 228 | 01:00 | 219 | 23:00
Aminbazar | 224 | 04:00 | 210 | 15:00 | Kaliakoir | 225 | 05:00 | 212 | 14:00
Ashuganj | 227 | 01:00 | 217 | 23:00 | Keranigonj | 222 | 05:00 | 208 | 15:00
Ashuganj-400 | 227 | 01:00 | 217 | 23:00 | Khulna(S) | 222 | 18:30 | 206 | 23:00
Baghabari | 231 | 18:00 | 224 | 14:00 | Korerhat | 227 | 02:00 | 221 | 20:00
Barapukuria | 229 | 06:00 | 220 | 13:00 | Madunaghat | 229 | 00:00 | 224 | 17:00
Barapukuria-230 | 229 | 06:00 | 220 | 13:00 | Madunaghat-400 | 231 | 01:00 | 227 | 08:00
Barishal | 227 | 18:00 | 216 | 00:00 | Maniknagar | 222 | 05:00 | 206 | 14:00
Bheramara | 233 | 18:30 | 219 | 15:00 | Meghnaghat | 230 | 07:00 | 216 | 19:30
Bhulta | 222 | 04:00 | 208 | 14:00 | Meghnaghat-400 | 224 | 04:00 | 212 | 15:00
Bibiana | 232 | 05:00 | 225 | 14:00 | Mirsorai | 229 | 18:30 | 218 | 15:00
BIPTC | 236 | 18:30 | 220 | 15:00 | Naogaon | 219 | 09:00 | 200 | 19:30
Bogura | 238 | 02:00 | 229 | 15:00 | Purbasadipur | 230 | 02:00 | 218 | 12:00
Bogura-400 | 238 | 18:30 | 229 | 15:00 | Rajshahi | 232 | 18:30 | 216 | 15:00
Borhanuddin | 229 | 18:00 | 220 | 00:00 | Rampal | 221 | 11:00 | 208 | 23:00
BSRM | 227 | 18:30 | 221 | 17:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 227 | 01:00 | 218 | 23:00 | Rampura | 222 | 05:00 | 206 | 15:00
Cumilla(N) | 222 | 00:00 | 214 | 20:00 | Shikalbaha | 230 | 18:00 | 224 | 10:00
Faridpur | 223 | 18:00 | 209 | 00:00 | Shyampur | 222 | 04:00 | 208 | 15:00
Fenchuganj | 232 | 02:00 | 227 | 22:00 | Siddhirganj | 222 | 02:00 | 208 | 20:00
Feni | 223 | 01:00 | 216 | 15:00 | Sirajgonj | 237 | 18:00 | 231 | 14:00
Ghorashal | 225 | 01:00 | 210 | 14:00 | Sreepur | 229 | 03:00 | 213 | 23:00
Ghorashal-230 | 219 | 05:00 | 205 | 15:00 | Tongi | 231 | 01:00 | 204 | 23:00
Gopalganj | 225 | 18:00 | 209 | 00:00
GPH | 229 | 01:00 | 223 | 17:00
Haripur | 222 | 04:00 | 209 | 15:00
Hasnabad | 222 | 03:00 | 209 | 14:00
Hathazari | 227 | 00:00 | 223 | 17:00
Ishurdi | 235 | 18:30 | 222 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 04:00 | 123 | 14:00 | Madunaghat | 133 | 01:00 | 129 | 17:00
Agargaon | 130 | 04:00 | 118 | 15:00 | Magura | 134 | 18:30 | 119 | 15:00
Agrabad | 131 | 00:00 | 128 | 10:00 | Mahasthangarh | 135 | 02:00 | 129 | 13:00
AKS | 130 | 01:00 | 126 | 10:00 | Maijdee | 127 | 01:00 | 122 | 04:00
Aminbazar | 127 | 02:00 | 119 | 11:00 | Manikganj | 125 | 18:00 | 117 | 13:00
Amnura | 135 | 18:00 | 124 | 15:00 | Maniknagar | 130 | 03:00 | 119 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 119 | 18:00 | 111 | 00:00
Ashuganj-230 | 137 | 17:00 | 130 | 20:00 | Matuail | 128 | 04:00 | 121 | 14:00
Bagerhat | 127 | 11:00 | 108 | 23:00 | Metrorail_Motijheel | 130 | 03:00 | 119 | 12:00
Bajitpur | 129 | 01:00 | 120 | 21:00 | Metrorail_Uttara | 130 | 03:00 | 118 | 15:00
Bakerganj | 129 | 18:00 | 122 | 23:00 | Millgate | 130 | 01:00 | 118 | 15:00
Bakulia | 133 | 18:00 | 128 | 08:00 | Mirpur | 126 | 04:00 | 117 | 15:00
Banani | 136 | 04:00 | 122 | 15:00 | Mirzapur | 125 | 07:00 | 118 | 15:00
Bangabhaban | 130 | 03:00 | 118 | 13:00 | Mithapukur | 136 | 07:00 | 126 | 13:00
Barapukuria | 137 | 06:00 | 127 | 13:00 | MI_Cement | 127.1 | 05:00 | 120 | 14:00
Barguna | 129 | 18:00 | 121 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 129 | 18:00 | 123 | 22:00 | Mogbazar | 135 | 05:00 | 125 | 13:00
Barishal-230 | 130 | 18:00 | 123 | 22:00 | Mongla | 126 | 11:00 | 110 | 23:00
Baroaulia | 132 | 00:00 | 128 | 10:00 | Motijheel | 130 | 03:00 | 118 | 13:00
Baroirhat | 132 | 18:30 | 126 | 15:00 | Muktagacha | 129 | 09:00 | 113 | 04:00
Bashundhara | 137 | 04:00 | 118 | 12:00 | Munshiganj | 126 | 00:00 | 120 | 12:00
BashundharaCement | 127 | 00:00 | 122 | 12:00 | Muradnagar | 125 | 00:00 | 118 | 19:00
Beanibazar | 130 | 05:00 | 123 | 00:00 | Mymensingh | 130 | 09:00 | 111 | 20:00
Benapole | 128 | 18:30 | 109 | 23:00 | Nabinagar | 128 | 03:00 | 119 | 15:00
Bhaluka | 128 | 16:00 | 119 | 19:30 | Naogaon | 136 | 02:00 | 120 | 19:30
Bhandaria | 127 | 06:00 | 112 | 23:00 | Narail | 135 | 18:30 | 118 | 15:00
Bhangura | 132 | 06:00 | 127 | 21:00 | Narinda | 130 | 03:00 | 119 | 12:00
Bheramara | 135 | 18:30 | 129 | 15:00 | Narshingdi | 133 | 17:00 | 113 | 20:00
Bheramara(GK) | 135 | 04:00 | 129 | 15:00 | Natore | 135 | 18:30 | 126 | 15:00
Bhulta | 125 | 01:00 | 117 | 20:00 | Nawabganj | 129 | 04:00 | 120 | 15:00
Bog-Sherpur | 135 | 02:00 | 129 | 15:00 | Netrakona | 123 | 10:00 | 108 | 19:30
Bogura | 138 | 02:00 | 131 | 21:00 | New | 132 | 01:00 | 121 | 14:00
Bogura-230 | 138 | 02:00 | 132 | 15:00 | Niamatpur | 132 | 09:00 | 124 | 20:00
Brahmanbaria | 133 | 17:00 | 121 | 23:00 | Noapara | 128 | 11:00 | 114 | 23:00
Cantonment | 130 | 05:00 | 119 | 12:00 | Pabna | 132 | 06:00 | 126 | 15:00
Chandina | 128 | 00:00 | 123 | 20:00 | Palashbari | 133 | 07:00 | 125 | 13:00
Chandpur | 131 | 12:00 | 122 | 05:00 | Panchagarh | 138 | 02:00 | 127 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 133 | 18:00 | 130 | 07:00 | Patiya | 131 | 18:00 | 127 | 07:00
Chapai | 133 | 02:00 | 126 | 15:00 | Patuakhali | 128 | 17:00 | 123 | 22:00
Charsaidpur | 127 | 00:00 | 121 | 13:00 | Payra | 132 | 18:00 | 129 | 22:00
Chauddagram | 129 | 00:00 | 124 | 23:00 | PHP | 131 | 18:30 | 126 | 15:00
Chhatak | 130 | 12:00 | 119 | 00:00 | Postogola | 128 | 03:00 | 119 | 13:00
Chowmuhani | 128 | 00:00 | 123 | 21:00 | Pubail | 130 | 02:00 | 122 | 19:00
Chuadanga | 137 | 18:30 | 113 | 15:00 | Purbachal | 136 | 04:00 | 118 | 15:00
Coxsbazar | 118 | 11:00 | 111 | 18:30 | Purbasadipur | 136 | 02:00 | 128 | 11:00
Cumilla(N) | 128 | 00:00 | 123 | 20:00 | Rahanpur | 134 | 05:00 | 129 | 20:00
Cumilla(S) | 131 | 06:00 | 123 | 13:00 | Rahanpur-400 | 135 | 18:00 | 130 | 15:00
Daganbhuiyan | 130 | 01:00 | 125 | 23:00 | Rahim | 128 | 03:00 | 122 | 11:00
Daudkandi | 124 | 03:00 | 116 | 19:00 | Rajbari | 126 | 18:00 | 117 | 00:00
DhakaUniversity | 137 | 04:00 | 128 | 13:00 | Rajendrapur | 126 | 16:00 | 120 | 19:30
Dhamrai | 130 | 06:00 | 121 | 15:00 | Rajshahi | 132 | 09:00 | 122 | 15:00
Dhanmondi | 136 | 05:00 | 120 | 10:00 | Rajshahi-230 | 133 | 07:00 | 123 | 15:00
Dohazari | 128 | 18:00 | 122 | 06:00 | Ramganj | 126 | 01:00 | 120 | 04:00
Faridpur | 125 | 11:00 | 121 | 23:00 | Rampur | 131 | 00:00 | 127 | 17:00
Fatullah | 137 | 10:00 | 115 | 15:00 | Rampura | 136 | 04:00 | 124 | 12:00
Fenchuganj | 135 | 04:00 | 131 | 19:00 | Rangamati | 131 | 18:00 | 129 | 07:00
Feni | 132 | 18:30 | 125 | 23:00 | Rangpur | 135 | 06:00 | 122 | 13:00
Feni-230 | 132 | 18:30 | 127 | 20:00 | Ruppur | 135 | 05:00 | 129 | 15:00
Ghatail | 124 | 09:00 | 113 | 17:00 | Saidpur | 136 | 06:00 | 126 | 12:00
Ghorashal | 133 | 04:00 | 125 | 13:00 | Santhia | 133 | 09:00 | 128 | 23:00
Goalpara | 131 | 11:00 | 118 | 23:00 | Satkhira | 124 | 11:00 | 109 | 23:00
Gollamari | 131 | 11:00 | 110 | 23:00 | Satmasjid | 129 | 01:00 | 118 | 13:00
Gopalganj | 128 | 11:00 | 118 | 23:00 | Savar | 124 | 00:00 | 116 | 15:00
Gopalganj-400 | 131 | 18:00 | 124 | 23:00 | SevenRings | 132 | 01:00 | 125 | 15:00
Gulshan | 136 | 05:00 | 123 | 14:00 | ShahCement | 127 | 00:00 | 121 | 13:00
Halishahar | 133 | 01:00 | 128 | 10:00 | Shahjadpur | 135 | 06:00 | 130 | 22:00
Haripur | 129 | 05:00 | 121 | 20:00 | Shahjibazar | 133 | 17:00 | 123 | 21:00
HaripurSBU | 129 | 05:00 | 122 | 15:00 | Shahmirpur | 133 | 01:00 | 129 | 08:00
Hasnabad | 127 | 03:00 | 118 | 11:00 | Shariatpur | 128 | 18:00 | 119 | 23:00
Hathazari | 133 | 00:00 | 131 | 15:00 | Sherpur | 133 | 09:00 | 111 | 02:00
Hatirjheel | 136 | 03:00 | 123 | 13:00 | Shikalbaha | 122 | 00:00 | 119 | 08:00
Ishurdi | 136 | 08:00 | 129 | 15:00 | Shikalbaha-230 | 133 | 00:00 | 130 | 08:00
Jaldhaka | 134 | 22:00 | 123 | 02:00 | Shitalakhya | 127 | 05:00 | 113 | 15:00
Jamalpur | 133 | 09:00 | 114 | 02:00 | Sholosohor | 132 | 01:00 | 129 | 10:00
Jashore | 132 | 18:30 | 111 | 15:00 | Shomvuganj | 126 | 18:00 | 113 | 20:00
Jhenaidah | 136 | 18:30 | 117 | 14:00 | Shyampur | 132 | 00:00 | 121 | 15:00
Jhenaidah-230 | 137 | 18:30 | 121 | 23:00 | Shyampur-230 | 133 | 04:00 | 120 | 15:00
Joydebpur | 129 | 06:00 | 119 | 19:30 | Siddhirganj | 129 | 05:00 | 121 | 20:00
Joypurhat | 133 | 22:00 | 124 | 19:30 | Sirajganj | 130 | 05:00 | 125 | 15:00
Juldah | 132 | 00:00 | 129 | 11:00 | Sonargaon | 127 | 04:00 | 119 | 14:00
Kabirpur | 130 | 18:30 | 115 | 15:00 | Sreemongol | 131 | 01:00 | 124 | 19:30
Kachua | 130 | 01:00 | 124 | 04:00 | Sreepur | 130 | 18:00 | 122 | 23:00
Kaliakoir | 133 | 05:00 | 123 | 14:00 | Srinagar | 130 | 02:00 | 121 | 12:00
Kaliganj | 132 | 09:00 | 120 | 15:00 | SSM | 136 | 00:00 | 133 | 06:00
Kallyanpur | 126 | 05:00 | 118 | 12:00 | Sunamganj | 129 | 12:00 | 117 | 00:00
Kalurghat | 134 | 18:00 | 130 | 08:00 | Sylhet | 131 | 06:00 | 125 | 00:00
Kamrangirchar | 131 | 06:00 | 116 | 14:00 | Sylhet-132 | 130 | 05:00 | 125 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Tangail | 124 | 07:00 | 114 | 19:00
Kasba | 123 | 01:00 | 118 | 19:00 | Taraganj | 134 | 03:00 | 126 | 00:00
Kazla | 130 | 05:00 | 118 | 13:00 | Tasnim | 126 | 00:00 | 118 | 14:00
Keranigonj | 131 | 05:00 | 122 | 13:00 | Thakurgaon | 139 | 02:00 | 127 | 11:00
Khagrachori | 131 | 02:00 | 127 | 12:00 | TK | 133 | 18:00 | 130 | 10:00
Khulna | 130 | 11:00 | 115 | 00:00 | Tongi | 134 | 04:00 | 123 | 11:00
Khulna(S) | 131 | 11:00 | 118 | 23:00 | Ullahpara | 131 | 01:00 | 126 | 15:00
Khulshi | 130 | 01:00 | 126 | 10:00 | Ullon | 136 | 05:00 | 123 | 14:00
Kishoreganj | 128 | 16:00 | 118 | 21:00 | Uttara | 131 | 05:00 | 116 | 12:00
Kodda | 130 | 18:00 | 119 | 15:00 | UttaraNew | 130 | 03:00 | 118 | 15:00
Korerhat | 132 | 02:00 | 128 | 15:00 | Zigatola | 131 | 06:00 | 121 | 15:00
KSRM | 134 | 04:00 | 128 | 11:00
Kulaura | 134 | 06:00 | 129 | 21:00
Kurigram | 133 | 23:00 | 120 | 13:00
Kushtia | 134 | 19:30 | 122 | 15:00
Laksam | 128 | 01:00 | 123 | 03:00
Lakshmipur | 127 | 18:30 | 122 | 03:00
Lalbag | 130 | 04:00 | 121 | 13:00
Lalmonirhat | 131 | 03:00 | 120 | 20:00
Madanganj | 127 | 00:00 | 121 | 15:00
Madaripur | 130 | 18:30 | 122 | 00:00
Madartek | 135 | 03:00 | 123 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division