## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 26-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-05-2026 | during | 26-05-2026 | during | 26-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 360 | 377 | 412 | 412 | 392 | 392 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 17 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 320 | 331 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 18 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17.5 | 19 | 33 | 33 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 0 | 52.19 | 52.19 | 16 | 50 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 145 | 300 | 300 | 32 | 32 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 88 | 105 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 15 | 105 | 105 | 17 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 68 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 13 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 510 | 505 | 584 | 584 | 540 | 540 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 262 | 286 | 718 | 718 | 310 | 310 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 68 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1682.5 | 2101 | 5855.22 | 5827.22 | 2276.36 | 2529.36
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 0 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 46 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 60 | 60 | 30 | 30 | 30 | 30 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 224 | 212 | 212 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 48 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 24 | 24 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 25 | 30 | 40 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 24 | 60 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.05 | 0 | 0 | 0 | 0 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 49 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 29 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 35 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 582 | 612 | 612 | 612 | 612 | 612 | U-1 under maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 23 | 20 | 16 | 22 | 16 | 22 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 465 | 445 | 560 | 560 | 550 | 550 | U-1 under maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1371.05 | 1587 | 2757.86 | 2822.86 | 2008.36 | 2234.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 200 | 188 | 221.25 | 221.25 | 205.25 | 205.25
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 358 | 358 | 350.01 | 350.01 | 320 | 320 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 220 | 300 | 342.01 | 342.01 | 250 | 250 | ST Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 230 | 215 | 393 | 393 | 340 | 340 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 40 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 60 | 150 | 150 | 33 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 40 | 40 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 96 | 0 | 163 | 163 | 100 | 100 | ST Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 51 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 120 | 118 | 84 | 80 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 43 | 43 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 17 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 69 | 115 | 115 | 17 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 7 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1297 | 1427 | 2762.44 | 2698.44 | 1923.25 | 2080.25
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-05-2026 | during | 26-05-2026 | during | 26-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 50 | 150
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 2.3 | 0 | 2.3 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 133 | 140 | 140 | 90 | 90 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 10 | 10 | 10 | 110 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 0 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 18 | 142 | 431.3 | 384 | 214.3 | 379
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 42 | 42
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 30 | 0 | 0 | 30 | 30
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 144 | 145 | 163 | 163 | 147 | 147 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 152 | 151 | 152 | 152 | 155 | 155 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 102 | 101 | 102 | 102 | 102 | 102 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 15 | 17 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 368 | 368 | 250 | 250 | 250 | 250 | machine problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1192 | 1223 | 1169 | 1169 | 1166 | 1166
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 932 | 822 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 36 | 36 | 37 | 37 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 153 | 168 | 410 | 410 | 180 | 180 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 16 | 16 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 50 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 81 | 0 | 100 | 0 | 100 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 790 | 592 | 617.1 | 617.1 | 617.1 | 617.1 | U-1 under maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1956 | 1632 | 2989.1 | 2889.1 | 2077.1 | 1977.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 750 | 1245 | 1244 | 1244 | 1200 | 1200 | RRT
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 740 | 1149 | 1244 | 1244 | 1184 | 1184 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 0 | 35 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 180 | 307 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.53 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2010.53 | 3041 | 3406 | 3405 | 3122 | 3156
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 16.49 | 0 | 51 | 0 | 51 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 140 | 140 | 214 | 214 | 45 | 190
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 140 | 220 | 220 | 210 | 210
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 367 | 386 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 97 | 97 | 0 | 50 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 849 | 1447 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 3.43 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 26 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1541.92 | 2113 | 3230.57 | 3012.87 | 2663.19 | 2640.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 50 | 0 | 0 | 50 | 50 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 172 | 152 | 160 | 160 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 69 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.2 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 24 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 26 | 0 | 53.89 | 0 | 53.89 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 277.2 | 321 | 497.89 | 408 | 367.89 | 278
System Total |  |  |  |  | 28823.2 | 29270.237 | 11346.2 | 13587 | 23099.38 | 22616.49 | 15818.45 | 16440.56
Forecast Scenario (26-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13600 |  | 0 |  | 13600
|  |  |  | 1:00 | 12900 |  | 0 |  | 12900
|  |  |  | 2:00 | 12080 |  | 0 |  | 12080
|  |  |  | 3:00 | 11640 |  | 0 |  | 11640
|  |  |  | 4:00 | 11050 |  | 0 |  | 11050
|  |  |  | 5:00 | 10720 |  | 0 |  | 10720
|  |  |  | 6:00 | 9900 |  | 0 |  | 9900
|  |  |  | 7:00 | 9670 |  | 0 |  | 9670
|  |  |  | 8:00 | 9680 |  | 0 |  | 9680
|  |  |  | 9:00 | 9570 |  | 0 |  | 9570
|  |  |  | 10:00 | 9780 |  | 0 |  | 9780
|  |  |  | 11:00 | 10000 |  | 0 |  | 10000
|  |  |  | 12:00 | 10500 |  | 0 |  | 10500
|  |  |  | 13:00 | 10800 |  | 0 |  | 10800
|  |  |  | 14:00 | 11120 |  | 0 |  | 11120
|  |  |  | 15:00 | 12040 |  | 0 |  | 12040
|  |  |  | 16:00 | 11420 |  | 0 |  | 11420
|  |  |  | 17:00 | 11230 |  | 0 |  | 11230
|  |  |  | 18:00 | 11030 |  | 0 |  | 11030
|  |  |  | 18:30 | 11900 |  | 0 |  | 11900
|  |  |  | 19:00 | 12830 |  | 0 |  | 12830
|  |  |  | 19:30 | 13300 |  | 0 |  | 13300
|  |  |  | 20:00 | 13200 |  | 0 |  | 13200
|  |  |  | 21:00 | 13040 |  | 0 |  | 13040
|  |  |  | 22:00 | 12800 |  | 0 |  | 12800
|  |  |  | 23:00 | 12500 |  | 0 |  | 12500
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 10500.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13300.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13300.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 273.10 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:21 hrs on 26-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 25-05-2026 | [28 empty] | Date: | 25-05-2026 | [28 empty] | Date: | 25-05-2026 | [28 empty] | Date: | 25-05-2026 | [28 empty] | Date: | 25-05-2026 | [17 empty] | Date: | 25-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [17 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 277 | 0 | 17 | 127 | 122 | 145 | 15 | 35 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 123 | 17.5 | 21 | 0 | 500 | 66 | 16 | 24 | 0 | 25 | 49 | 0 | 33 | 24 | 24 | 0 | 60 | 74 | 25 | 700 | 45 | 0 | 50 | 0 | 93 | 218 | 0 | 0 | 0 | 580 | 0 | 75 | 0 | 280 | 320 | 260 | 51 | 0 | 204 | 0 | 65 | 99 | 48 | 0 | 17 | 34 | 78 | 34 | 0 | 0 | 305 | 0 | 345 | 0 | 30 | 142 | 0 | 17 | 0 | 86 | 30 | 152 | 0 | 101 | 0 | 78 | 9 | 0 | 0 | 0 | 0 | 7155.5 | 826 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 0 | 0 | 0 | 1404.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 140 | 0 | 0 | 0 | 350 | 0 | 0 | 143 | 54 | 35 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 120 | 180 | 0 | 1000 | 1014 | 0 | 6866.74 | 14022.24 | 75.34
01:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 256 | 0 | 0 | 132 | 95 | 145 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 86 | 17 | 21 | 0 | 440 | 65 | 16 | 25 | 0 | 21 | 3 | 0 | 35 | 24 | 24 | 0 | 60 | 94 | 32 | 650 | 0 | 0 | 50 | 0 | 101 | 217 | 0 | 0 | 0 | 580 | 0 | 80 | 0 | 280 | 320 | 260 | 51 | 0 | 196 | 0 | 40 | 99 | 0 | 0 | 5 | 0 | 94 | 0 | 0 | 0 | 300 | 0 | 345 | 0 | 30 | 151 | 0 | 17 | 0 | 86 | 30 | 153 | 0 | 101 | 0 | 78 | 9 | 0 | 0 | 0 | 0 | 6622 | 783 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1039 | 0 | 0 | 0 | 1399.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 140 | 0 | 0 | 0 | 350 | 0 | 0 | 145 | 54 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 120 | 180 | 0 | 1106 | 1075 | 0 | 7055.83 | 13677.83 | 75.34
02:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 286 | 0 | 0 | 132 | 95 | 95 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 68 | 18 | 22 | 0 | 495 | 62 | 16 | 0 | 0 | 14 | 0 | 0 | 0 | 24 | 24 | 0 | 60 | 95 | 25 | 515 | 0 | 0 | 50 | 0 | 99 | 218 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 280 | 320 | 260 | 51 | 0 | 199 | 0 | 0 | 99 | 0 | 0 | 5 | 0 | 112 | 0 | 0 | 0 | 300 | 0 | 345 | 0 | 30 | 151 | 0 | 17 | 0 | 86 | 30 | 153 | 0 | 101 | 0 | 78 | 9 | 0 | 0 | 0 | 0 | 6352 | 784 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 1392.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 140 | 0 | 0 | 0 | 350 | 0 | 0 | 156 | 53 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 120 | 220 | 0 | 1100 | 1100 | 0 | 7144.87 | 13496.87 | 75.35
03:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 234 | 0 | 0 | 132 | 62 | 45 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 51 | 18 | 22 | 0 | 400 | 30 | 16 | 0 | 0 | 31 | 0 | 0 | 0 | 24 | 24 | 0 | 60 | 99 | 25 | 515 | 0 | 0 | 50 | 0 | 96 | 220 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 280 | 320 | 260 | 51 | 0 | 187 | 0 | 0 | 99 | 0 | 0 | 5 | 0 | 126 | 0 | 0 | 0 | 290 | 0 | 345 | 0 | 30 | 144 | 0 | 17 | 0 | 86 | 30 | 153 | 0 | 101 | 0 | 78 | 9 | 0 | 0 | 0 | 0 | 6093 | 783 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1096 | 0 | 0 | 0 | 1397.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 140 | 0 | 0 | 0 | 350 | 0 | 0 | 144 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 120 | 220 | 0 | 1100 | 1100 | 0 | 7062.62 | 13155.62 | 75.35
04:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 210 | 0 | 0 | 132 | 45 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 51 | 18 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 24 | 24 | 0 | 60 | 34 | 25 | 515 | 0 | 0 | 50 | 0 | 51 | 222 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 280 | 320 | 260 | 51 | 0 | 199 | 0 | 0 | 100 | 0 | 0 | 5 | 0 | 122 | 0 | 0 | 0 | 300 | 0 | 345 | 0 | 30 | 131 | 0 | 17 | 0 | 86 | 30 | 153 | 0 | 101 | 0 | 78 | 9 | 0 | 0 | 0 | 0 | 5779 | 686 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1091 | 0 | 0 | 0 | 1383.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 140 | 0 | 0 | 0 | 300 | 0 | 0 | 148 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 100 | 180 | 0 | 1095 | 1030 | 0 | 6779.74 | 12558.74 | 75.36
05:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 220 | 0 | 0 | 132 | 45 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 51 | 18 | 22 | 0 | 390 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 25 | 515 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 320 | 357 | 260 | 51 | 0 | 193 | 0 | 0 | 100 | 0 | 0 | 5 | 0 | 114 | 0 | 0 | 0 | 295 | 0 | 345 | 0 | 30 | 142 | 0 | 17 | 0 | 86 | 30 | 152 | 0 | 101 | 0 | 78 | 9 | 0 | 0 | 0 | 0 | 5662 | 932 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 961 | 0 | 0 | 0 | 1156.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 149 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 120 | 220 | 0 | 907 | 1020 | 0 | 6577.68 | 12239.68 | 75.36
06:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 231 | 0 | 0 | 132 | 45 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 1 | 51 | 18 | 22 | 0 | 380 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0.17 | 60 | 0 | 28 | 515 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 580 | 2 | 0 | 0 | 295 | 357 | 260 | 51 | 0 | 199 | 0 | 0 | 99 | 0 | 0 | 5 | 0 | 108 | 0 | 3 | 0 | 295 | 0 | 345 | 0 | 30 | 130 | 1 | 17 | 0 | 86 | 30 | 153 | 0 | 101 | 0 | 78 | 9 | 0 | 0.05 | 0.35 | 0 | 5620.57 | 933 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 863 | 0 | 0 | 0 | 914.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46 | 2 | 0 | 0 | 1.86 | 176 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0.14 | 147 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.02 | 0 | 180 | 120 | 220 | 0 | 808 | 980 | 0 | 6108.41 | 11728.98 | 75.37
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 262 | 0 | 0 | 132 | 75 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 3 | 51 | 18 | 22 | 0 | 480 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1.16 | 60 | 0 | 21 | 515 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 582 | 4 | 0 | 0 | 280 | 356 | 260 | 51 | 0 | 195 | 0 | 0 | 98 | 0 | 0 | 5 | 0 | 102 | 0 | 6 | 0 | 300 | 0 | 345 | 0 | 30 | 144 | 1 | 15 | 0 | 86 | 30 | 152 | 0 | 101 | 0 | 78 | 9 | 0 | 0 | 3.94 | 0 | 5786.1 | 933 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 774 | 0 | 0 | 0 | 840.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.76 | 16 | 0 | 0 | 4.07 | 177 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0.46 | 148 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 181 | 120 | 220 | 0 | 700 | 940 | 0 | 5841.02 | 11627.12 | 75.37
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 210 | 0 | 0 | 127 | 75 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 5 | 51 | 18 | 22 | 0 | 355 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 1.54 | 60 | 0 | 6 | 515 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 581 | 12 | 0 | 0 | 270 | 357 | 260 | 51 | 0 | 180 | 0 | 0 | 96 | 0 | 0 | 5 | 0 | 110 | 0 | 13 | 0 | 300 | 0 | 309 | 0 | 30 | 127 | 0 | 15 | 0 | 86 | 30 | 153 | 0 | 101 | 0 | 45 | 9 | 0 | 0 | 2.96 | 0 | 5501.5 | 934 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 751 | 0 | 0 | 0 | 828.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.9 | 25 | 0 | 0 | 8.64 | 176 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0.86 | 151 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 6 | 0.27 | 0 | 177 | 120 | 220 | 0 | 700 | 850 | 0 | 5751.19 | 11252.69 | 75.38
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 271 | 0 | 0 | 96 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 10 | 34 | 17.5 | 22 | 0 | 485 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 3.18 | 60 | 0 | 3 | 510 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 582 | 11 | 0 | 0 | 230 | 357 | 240 | 51 | 0 | 205 | 0 | 0 | 96 | 0 | 0 | 11 | 0 | 120 | 0 | 43 | 0 | 295 | 0 | 332 | 0 | 30 | 140 | 3 | 15 | 0 | 86 | 30 | 153 | 0 | 101 | 0 | 45 | 9 | 0 | 0 | 0 | 0 | 5650.68 | 933 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 766 | 0 | 0 | 0 | 841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.91 | 30 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 370 | 0 | 0 | 175 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 2 | 0.4 | 0 | 183 | 120 | 220 | 0 | 700 | 770 | 0 | 5683.71 | 11334.39 | 75.38
10:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 262 | 0 | 0 | 88 | 15 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 13 | 17 | 17.5 | 21 | 0 | 510 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 4.05 | 60 | 0 | 4 | 465 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 582 | 17 | 0 | 0 | 230 | 358 | 220 | 51 | 0 | 200 | 0 | 0 | 96 | 0 | 0 | 15 | 0 | 120 | 0 | 7 | 0 | 295 | 0 | 368 | 0 | 0 | 144 | 3 | 15 | 0 | 83 | 30 | 152 | 0 | 102 | 0 | 9 | 9 | 0 | 0 | 0 | 0 | 5560.55 | 932 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 790 | 0 | 0 | 0 | 849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.49 | 26 | 0 | 0 | 3.43 | 140 | 0 | 140 | 0 | 0 | 0 | 367 | 0 | 0 | 172 | 50 | 0 | 24 | 0 | 0 | 0 | 0 | 5.2 | 26 | 0.53 | 0 | 180 | 120 | 220 | 0 | 750 | 740 | 0 | 5785.65 | 11346.2 | 75.39
11:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 251 | 0 | 15 | 70 | 15 | 0 | 25 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 1 | 17 | 17 | 21 | 0 | 425 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 1.45 | 60 | 0 | 5 | 433 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 580 | 18 | 0 | 0 | 230 | 330 | 250 | 51 | 0 | 200 | 0 | 0 | 94 | 0 | 0 | 15 | 0 | 136 | 0 | 65 | 0 | 290 | 0 | 332 | 0 | 0 | 138 | 0 | 0 | 0 | 86 | 30 | 154 | 0 | 101 | 0 | 9 | 9 | 0 | 0 | 0.6 | 0 | 5466.05 | 933 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 604 | 0 | 0 | 0 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91 | 25 | 0 | 0 | 53.66 | 140 | 0 | 140 | 0 | 0 | 0 | 393 | 0 | 5.27 | 174 | 51 | 0 | 31 | 0 | 0 | 0 | 0 | 6.8 | 106 | 0.65 | 0 | 179 | 100 | 180 | 0 | 900 | 740 | 0 | 5800.29 | 11266.34 | 75.39
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 219 | 0 | 0 | 36 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 4.59 | 60 | 0 | 9 | 422 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 540 | 13 | 0 | 0 | 230 | 358 | 240 | 5 | 0 | 202 | 0 | 0 | 94 | 0 | 0 | 15 | 0 | 144 | 0 | 70 | 0 | 295 | 0 | 304 | 0 | 20 | 132 | 0 | 0 | 0 | 62 | 30 | 155 | 0 | 101 | 0 | 8 | 9 | 0 | 0 | 5.34 | 0 | 5119.93 | 933 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 556 | 0 | 0 | 0 | 852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.81 | 75 | 0 | 0 | 64.78 | 140 | 0 | 140 | 0 | 0 | 0 | 360 | 0 | 6.34 | 171 | 50 | 0 | 32 | 0 | 0 | 0 | 0 | 6.6 | 174 | 0.23 | 0 | 175 | 100 | 180 | 0 | 855 | 690 | 0 | 5839.76 | 10959.69 | 75.4
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 284 | 0 | 0 | 20 | 7 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 11 | 0 | 17 | 0 | 0 | 535 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 6 | 430 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 500 | 18 | 0 | 0 | 230 | 358 | 220 | 5 | 0 | 195 | 0 | 0 | 94 | 0 | 0 | 15 | 0 | 140 | 0 | 69 | 0 | 295 | 0 | 309 | 0 | 30 | 140 | 0 | 8 | 0 | 62 | 30 | 154 | 0 | 101 | 0 | 12 | 14 | 0 | 1.6 | 5.36 | 0 | 5305.96 | 933 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 517 | 0 | 0 | 0 | 862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.09 | 108 | 0 | 0 | 35.46 | 140 | 0 | 140 | 0 | 0 | 0 | 381 | 0 | 3.96 | 177 | 48 | 0 | 30 | 0 | 0 | 0 | 0 | 3.6 | 136 | 0.71 | 0 | 188 | 100 | 180 | 0 | 850 | 650 | 0 | 5764.82 | 11070.78 | 75.4
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 298 | 0 | 0 | 48 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 11 | 0 | 17 | 0 | 0 | 511 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 1.34 | 60 | 0 | 10 | 435 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 545 | 12 | 0 | 0 | 250 | 358 | 250 | 5 | 0 | 203 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 96 | 0 | 30 | 0 | 295 | 0 | 356 | 0 | 30 | 142 | 0 | 8 | 0 | 62 | 30 | 153 | 0 | 103 | 0 | 56 | 56 | 0 | 0.59 | 9.38 | 0 | 5506.31 | 933 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 515 | 0 | 0 | 0 | 898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.28 | 83 | 0 | 0 | 21.35 | 140 | 0 | 140 | 0 | 0 | 0 | 400 | 0 | 2.44 | 176 | 47 | 0 | 14 | 0 | 0 | 0 | 0 | 3.9 | 66 | 0.16 | 0 | 201 | 100 | 220 | 0 | 850 | 690 | 0 | 5744.13 | 11250.44 | 75.41
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 306 | 0 | 0 | 52 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 11 | 0 | 19 | 0 | 0 | 520 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 1.71 | 60 | 0 | 13 | 470 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 550 | 7 | 0 | 0 | 300 | 357 | 290 | 17 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 40 | 0 | 290 | 0 | 356 | 0 | 30 | 146 | 0 | 13 | 0 | 84 | 28 | 152 | 0 | 103 | 0 | 55 | 56 | 0 | 1.4 | 6.11 | 0 | 5578.22 | 933 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 520 | 0 | 0 | 0 | 1057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.18 | 68 | 0 | 0 | 27.51 | 140 | 0 | 140 | 0 | 0 | 0 | 404 | 0 | 2.74 | 164 | 50 | 0 | 15 | 0 | 0 | 0 | 0 | 4.8 | 74 | 0.31 | 0 | 227 | 120 | 220 | 0 | 900 | 750 | 0 | 6051.54 | 11629.76 | 75.41
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 298 | 0 | 0 | 52 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 11 | 0 | 0 | 10 | 0 | 508 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 1.56 | 60 | 0 | 13 | 460 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 560 | 8 | 0 | 0 | 260 | 358 | 345 | 51 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 108 | 0 | 1 | 0 | 295 | 0 | 361 | 0 | 30 | 140 | 1 | 0 | 0 | 86 | 28 | 152 | 0 | 101 | 0 | 55 | 56 | 0 | 0.68 | 18.31 | 0 | 5603.55 | 933 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 548 | 0 | 0 | 0 | 1087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.56 | 39 | 0 | 0 | 25.57 | 140 | 0 | 140 | 0 | 0 | 0 | 398 | 0 | 1.68 | 160 | 48 | 0 | 4 | 0 | 0 | 0 | 0 | 1.6 | 41 | 0.03 | 0 | 226 | 120 | 220 | 0 | 900 | 850 | 0 | 6099.44 | 11702.99 | 75.42
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 289 | 17 | 0 | 52 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 7 | 0 | 19 | 21 | 0 | 500 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0.42 | 60 | 0 | 13 | 445 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 565 | 0 | 0 | 0 | 215 | 357 | 345 | 51 | 0 | 180 | 0 | 3 | 0 | 0 | 0 | 11 | 0 | 106 | 0 | 0 | 0 | 290 | 0 | 361 | 0 | 30 | 140 | 1 | 0 | 0 | 86 | 28 | 154 | 0 | 101 | 0 | 55 | 45 | 0 | 0.43 | 3.97 | 10 | 5525.82 | 933 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 562 | 0 | 0 | 0 | 1091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.18 | 24 | 0 | 0 | 8.88 | 140 | 0 | 140 | 0 | 0 | 0 | 378 | 0 | 0.84 | 160 | 49 | 0 | 2 | 0 | 0 | 0 | 0 | 0.8 | 28 | 0.09 | 0 | 227 | 120 | 220 | 0 | 900 | 875 | 0 | 6047.79 | 11573.61 | 75.42
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 275 | 18 | 0 | 52 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 2 | 0 | 19 | 22 | 0 | 493 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0.07 | 60 | 0 | 16 | 430 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 215 | 356 | 300 | 51 | 0 | 185 | 0 | 35 | 0 | 0 | 0 | 11 | 0 | 112 | 0 | 0 | 0 | 290 | 0 | 361 | 0 | 30 | 136 | 0 | 0 | 0 | 86 | 30 | 153 | 0 | 101 | 0 | 55 | 45 | 0 | 0 | 1.86 | 12 | 5459.93 | 933 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 563 | 0 | 0 | 0 | 1042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.15 | 6 | 0 | 0 | 3.66 | 140 | 0 | 140 | 0 | 0 | 0 | 385 | 0 | 0.38 | 152 | 48 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 5 | 0.03 | 0 | 224 | 120 | 220 | 0 | 900 | 880 | 0 | 5934.32 | 11394.25 | 75.43
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 269 | 18 | 8 | 56 | 15 | 80 | 10 | 4 | 62 | 0 | 0 | 0 | 0 | 0 | 17 | 330 | 0 | 0 | 0 | 35 | 19 | 22 | 0 | 480 | 7 | 16 | 0 | 0 | 2 | 50 | 0 | 4 | 12 | 24 | 0 | 60 | 3 | 28 | 430 | 25 | 0 | 9 | 5 | 9 | 223 | 0 | 0 | 0 | 580 | 0 | 20 | 0 | 215 | 357 | 300 | 51 | 0 | 191 | 0 | 70 | 0 | 7 | 0 | 17 | 0 | 124 | 0 | 0 | 0 | 295 | 0 | 361 | 0 | 30 | 138 | 0 | 17 | 0 | 86 | 30 | 152 | 0 | 101 | 0 | 56 | 85 | 0 | 0 | 0 | 12 | 5992 | 933 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575 | 0 | 0 | 0 | 1257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 388 | 0 | 0 | 155 | 48 | 50 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 120 | 220 | 0 | 1171 | 922 | 0 | 6628 | 12620 | 75.43
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 236 | 18 | 17 | 105 | 15 | 125 | 55 | 35 | 68 | 0 | 0 | 0 | 0 | 0 | 35 | 333 | 0 | 0 | 0 | 68 | 19 | 22 | 0 | 430 | 30 | 16 | 0 | 0 | 3 | 50 | 0 | 17 | 12 | 24 | 0 | 60 | 34 | 28 | 420 | 51 | 0 | 44 | 17 | 47 | 225 | 0 | 0 | 0 | 580 | 0 | 60 | 0 | 215 | 357 | 300 | 51 | 0 | 190 | 0 | 68 | 0 | 100 | 0 | 17 | 0 | 118 | 0 | 0 | 0 | 290 | 0 | 361 | 0 | 30 | 134 | 0 | 17 | 0 | 86 | 30 | 152 | 0 | 101 | 17 | 56 | 85 | 0 | 0 | 0 | 12 | 6421 | 918 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595 | 0 | 0 | 0 | 1421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 353 | 0 | 0 | 150 | 48 | 50 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 120 | 220 | 0 | 1200 | 1070 | 0 | 6935 | 13356 | 75.43
20:00 | 0 | 1 | 16 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 232 | 18 | 17 | 105 | 0 | 145 | 55 | 35 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 332 | 0 | 0 | 0 | 68 | 19 | 22 | 0 | 422 | 31 | 16 | 0 | 0 | 1 | 50 | 0 | 0 | 12 | 27 | 0 | 60 | 46 | 31 | 426 | 0 | 0 | 45 | 0 | 50 | 224 | 0 | 0 | 0 | 580 | 0 | 60 | 0 | 215 | 358 | 300 | 51 | 0 | 190 | 0 | 69 | 0 | 90 | 0 | 17 | 0 | 102 | 8 | 0 | 0 | 290 | 0 | 361 | 0 | 30 | 133 | 0 | 17 | 0 | 86 | 30 | 153 | 0 | 103 | 17 | 9 | 124 | 0 | 0 | 0 | 12 | 6358 | 822 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 592 | 0 | 0 | 0 | 1448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 366 | 0 | 0 | 150 | 48 | 50 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 120 | 220 | 0 | 1200 | 1105 | 0 | 6935 | 13293 | 75.44
21:00 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 286 | 18 | 17 | 105 | 0 | 145 | 55 | 35 | 68 | 0 | 0 | 0 | 0 | 0 | 35 | 331 | 0 | 0 | 0 | 68 | 19 | 22 | 0 | 505 | 0 | 0 | 0 | 0 | 20 | 17 | 0 | 0 | 12 | 29 | 0 | 60 | 49 | 25 | 445 | 0 | 0 | 46 | 0 | 48 | 224 | 0 | 0 | 0 | 612 | 0 | 60 | 0 | 215 | 358 | 300 | 51 | 0 | 188 | 0 | 69 | 0 | 51 | 0 | 17 | 0 | 118 | 0 | 0 | 0 | 295 | 0 | 368 | 0 | 30 | 145 | 0 | 17 | 0 | 86 | 30 | 151 | 0 | 101 | 0 | 9 | 133 | 0 | 0 | 0 | 0 | 6480 | 822 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 592 | 0 | 0 | 0 | 1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 386 | 0 | 0 | 152 | 50 | 50 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 1245 | 1149 | 0 | 7107 | 13587 | 75.44
22:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 289 | 18 | 17 | 107 | 30 | 145 | 55 | 35 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 68 | 19 | 22 | 0 | 510 | 0 | 0 | 0 | 0 | 36 | 17 | 0 | 0 | 12 | 43 | 0 | 60 | 50 | 28 | 460 | 0 | 0 | 46 | 0 | 50 | 222 | 0 | 0 | 0 | 612 | 0 | 60 | 0 | 215 | 357 | 300 | 51 | 0 | 192 | 0 | 69 | 50 | 49 | 0 | 17 | 0 | 128 | 0 | 0 | 0 | 295 | 0 | 362 | 0 | 30 | 145 | 0 | 17 | 0 | 86 | 30 | 152 | 0 | 101 | 0 | 9 | 77 | 0 | 0 | 0 | 0 | 6545 | 822 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 593 | 0 | 0 | 0 | 1446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 387 | 0 | 0 | 151 | 50 | 50 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 1245 | 1175 | 0 | 7133 | 13678 | 75.45
23:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 310 | 18 | 17 | 114 | 30 | 175 | 55 | 35 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 68 | 20 | 22 | 0 | 505 | 0 | 0 | 0 | 0 | 4 | 17 | 0 | 0 | 12 | 46 | 0 | 60 | 54 | 28 | 477 | 0 | 0 | 46 | 0 | 56 | 223 | 0 | 0 | 0 | 580 | 0 | 70 | 0 | 215 | 357 | 300 | 51 | 0 | 197 | 0 | 40 | 100 | 49 | 0 | 17 | 0 | 120 | 0 | 0 | 0 | 290 | 0 | 362 | 0 | 30 | 142 | 0 | 17 | 0 | 86 | 30 | 150 | 0 | 100 | 0 | 9 | 77 | 20 | 0 | 0 | 0 | 6630 | 822 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 592 | 0 | 0 | 0 | 1450 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 53 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 120 | 220 | 0 | 1246 | 1180 | 0 | 7005 | 13635 | 75.45
Total KWH | 0 | 198720 | 111360 | 0 | 0 | 0 | 0 | 0 | 8719200 | 0 | 6773990 | 129600 | 128880 | 2258640 | 896640 | 1095720 | 642800 | 199002 | 381600 | 0 | 0 | 0 | 0 | 0 | 134751 | 7652522 | 0 | 0 | 105736 | 1030800 | 414000 | 411840 | 0 | 11104545.45 | 223309 | 80291 | 26880 | 0 | 550080 | 163221 | 0 | 97194 | 167040 | 297600 | 20848 | 1413980 | 638982 | 445440 | 11236363.64 | 95345 | 0 | 457440 | 20302.2 | 716763 | 5119829 | 0 | 0 | 0 | 13756362 | 114480 | 500145 | 0 | 6153000 | 8736800 | 6704000 | 1141816 | 0 | 4870000 | 0 | 429120 | 1513980 | 325920 | 0 | 247320 | 20520 | 2749440 | 48922 | 314890 | 0 | 7140000 | 0 | 8478000 | 0 | 639720 | 3368454.55 | 9144 | 285792 | 0 | 2006400 | 709344 | 3543200 | 0 | 2430600 | 20520 | 1129200 | 916800 | 22080 | 5200 | 60810 | 47040 | 142600273.84 | 21377455 | 3915360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202464 | 506160 | 17243641 | 379 | 0 | 0 | 27196364 | 0 | 0 | 0 | 0 | 53376 | 0 | 0 | 0 | 0 | 258288 | 534100 | 0 | 0 | 266896 | 3782455 | 0 | 3623764 | 0 | 0 | 0 | 9230109 | 0 | 22380 | 3664000 | 1174254 | 340579 | 147975 | 525724 | 0 | 0 | 0 | 39615.12 | 735840 | 3475 | 0 | 5432000 | 2600000 | 5311280 | 0 | 23352727 | 23048727.27 | 0 | 154589387.39 | 297189661.23

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 25-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 11346.2 | MW | 10:00 Hr. | Energy Generated |  |  | 297.1897 |  | MKWHr.
| Day Peak Demand |  |  | 11416.22 | MW | 10:00 Hr. | Energy Unserverd |  |  | 1.375 |  | MKWHr.
| Evening Peak Generation |  |  | 13587 | MW | 21:00 Hr. | Energy Demand |  |  | 298.5647 |  | MKWHr.
| Evening Peak Demand |  |  | 13615 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.5 |  | °C
| Minimum Generation of the Day |  |  | 10959.69 | MW | 12:00 Hr. | Total Gas Supplied |  |  | 907.04 |  | MMCFD
| Maximum Generation of the Day |  |  | 14022.24 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.6592 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 35.0761 | 0 | 7.2085 | 0 | 0 | 0.10574 | 0 | 0 | 42.3903 | Gas | 127.0948 | Gas | 444103475.8525
| Chattogram Zone |  |  | 5.5653 | 24.9927 | 2.9844 | 0 | 1.414 | 0.13533 | 0 | 0.55008 | 35.6417 | Coal | 98.9081 | Coal | 651974997.6737
| Cumilla Zone |  |  | 29.3669 | 0 | 1.3246 | 0 | 0 | 0.31489 | 2.7494 | 0 | 33.7559 | HFO | 14.7536 | HFO | 237710058.664
| Mymensingh Zone |  |  | 0.02208 | 0 | 2.1136 | 0 | 0 | 0.06601 | 0 | 0 | 2.2016 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.6015 | 0 | 0 | 0 | 0 | 0.009144 | 0 | 0 | 28.6107 | Hydro | 1.414 | Hydro | 141398
| Khulna Zone |  |  | 3.9154 | 17.2436 | 0.20284 | 0 | 0 | 0.50616 | 21.3775 | 0 | 43.2455 | Solar | 3.1458 | Solar | 49732676.7624
| Barishal Zone |  |  | 7.9113 | 51.8335 | 0 | 0 | 0 | 0.003475 | 0 | 0 | 59.7482 | Import | 51.3233 | Import | 290096989.76
| Rajshahi Zone |  |  | 16.6363 | 0 | 0.053376 | 0 | 0 | 1.0817 | 27.1964 | 0 | 44.9677 | Wind | 0.55008 | Wind | 8091676.8
| Rangpur Zone |  |  | 0 | 4.8383 | 0.8663 | 0 | 0 | 0.92343 | 0 | 0 | 6.628
| Total |  |  | 127.0948 | 98.9081 | 14.7536 | 0 | 1.414 | 3.1458 | 51.3233 | 0.55008 | 297.1897
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 444103475.8525 |  | Hydro | 141398
|  |  |  | Coal | 651974997.6737 |  | Solar | 49732676.7624
|  |  |  | HFO | 237710058.664 |  | Import | 290096989.76
|  |  |  | HSD | 0 |  | Wind | 8091676.8
[5 empty] | Total: | 168,18,51,273 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.3775 | Peak Hr Flow | 822.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47750036.36 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.1964 | Peak Hr Flow | 1447.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2179 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.7494 | Peak Hr Flow | 118.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2585 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 51.3233 | Peak Hr Flow | 2387.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4403
|  |  |  | Chattogram |  | 0 |  | 1348
|  |  |  | Cumilla |  | 0 |  | 1198
|  |  |  | Mymensingh |  | 0 |  | 956
|  |  |  | Sylhet |  | 0 |  | 463
|  |  |  | Khulna |  | 27 |  | 1945
|  |  |  | Barishal |  | 0 |  | 520
|  |  |  | Rajshahi |  | 0 |  | 1436
|  |  |  | Rangpur |  | 0 |  | 860
|  |  |  | Total |  | 27 |  | 13129
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:01 | 14:41 | Baghabari-Ishurdi 230 kV Ckt-1 Scheduled S/D from Baghabari 230/132kV end.
|  | 08:20 | Mymensingh 132/33kV S/S Transformer-2 (414T) HT is restored.
|  | 08:21 | Mymensingh 132/33kV S/S Transformer-2 (414T) LT is restored.
| 09:45 | 10:16 | Jamalpur-Mymensingh 132kV Ckt-2 Tripped from Jamalpur 132/33kV end showing Distance
Z2,Z3 relays Due to Trip
|  | 09:55 | Kachua 230/132/33kV S/S TR-1 HT is restored.
|  | 09:56 | Kachua 230/132/33kV S/S TR-1 LT is restored.
| 10:00 |  | Day Peak Generation: 11344 MW.
| 10:13 | 14:44 | Sreepur 230/132/33kV S/S 132/33 kV T-1 HT Scheduled S/D Due to Neutral Bushing Repair
work.
| 10:24 |  | Rampal 1320 MW (BIFPCL) Forced Shutdown with remarks:- Unit-1
| 10:25 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U - 2 running
|  | 11:04 | Niamatpur 132/33kV S/S Transformer-1(407T) LT is restored.
|  | 11:04 | Niamatpur 132/33kV S/S Transformer-1(407T) HT is restored.
| 11:05 | 16:15 | Lakshmipur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Red hot Maintenance
| 11:06 | 15:46 | Lakshmipur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Redhot Maintenance.
|  | 11:28 | Khulna(C )-Khulna (S) 132kV Ckt-1 is restored.
| 12:04 | 13:01 | Korerhat 400/230/132kV S/S Hathajari-1 Tripped showing 7SA87 relays Due to Lightning
| 12:19 | 13:29 | Korerhat 400/230/132kV S/S Madunaghat-1 Tripped showing RED670 relays Due to Lightning
| 12:19 | 13:02 | Baroirhat-Hathazari 132 kV Ckt-1 Tripped from Hathazari 230/132/33kV end showing
Quadrhamo Relay relays.
| 12:19 | 13:05 | Baroirhat-Hathazari 132 kV Ckt-2 Tripped from Hathazari 230/132/33kV end showing
Quadrhamo Relay relays.
| 12:19 | 13:28 | Madunaghat 400/230kV S/S Madunaghat-Meghnaghat 400kV Ckt.-1 Tripped showing ABB RED 70
relays Due to General Trip, Y phase Fault, Line Differential Trip
| 12:19 | 13:04 | Korerhat 400/230/132kV S/S Hathajari-2 Tripped showing 7SA87 relays Due to Lightning | [7 empty] | 70.0MW load
interrup.
| 13:02 | 20:00 | Madanganj 132/33kV S/S GT-2 LT Tripped showing O/C & E/F relays Due to 33 KV GT-2 Bus 3 | [7 empty] | 20.0MW load
|  |  | Phase Fault | [7 empty] | interrup.
| 13:02 | 20:00 | Madanganj 132/33kV S/S GT-2 HT Tripped showing O/C & E/F Relay relays Due to O/C & E/F | [7 empty] | 20.0MW load
interrup.
| 13:05 | 13:55 | Sonargaon 132/33kV S/S OPSL(IEL-2) Tripped showing Line distance relay relays Due to Bad
weather
|  | 13:11 | Ashuganj-Shahjibazar 132kV Ckt-1 is restored.
|  | 13:11 | Korerhat 400/230/132kV S/S ATR-3(7103T) HT is restored.
| 13:12 | 15:15 | Saidpur 132/33kV S/S TR-2 (404T) LT Forced S/D Due to Red hot maintainance
| 13:12 | 13:54 | Haripur-Madanganj 132kV Ckt-1 Tripped from Haripur 230/132kV end showing Time Delay E/F
relays Due to Rain & Storm
| 13:12 | 15:15 | Saidpur 132/33kV S/S TR-2 (404T) HT Forced S/D Due to Red hot maintainance
|  | 13:12 | Korerhat 400/230/132kV S/S ATR-3(7103T) LT is restored.
| 13:12 | 13:58 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Tripped showing LBB Inatiation relays Due to
heavy rain strom
| 13:14 | 13:40 | Madanganj 132/33kV S/S Madanganj -Haripur 132 kv Ckt-2 Tripped showing Tr protection | [7 empty] | 52.0MW load
|  |  | relay relays Due to Over current & earth fault. | [7 empty] | interrup.
| 14:01 | 14:10 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Tripped showing df/dt relays Due to df/dt | [7 empty] | 29.0MW load
interrup.
| 14:03 | 15:01 | Candpur- Kachua 132kV Ckt-2 Tripped from Chandpur 132/33kV end showing Distance Relay
relays Due to Unknown and from Kachua 230/132/33kV end showing REL 670,REC 650 relays Due
to rain and storm
| 14:41 |  | PTR-3 BKR close (old T-2 132/33KV) in Nauga S/S.
| 17:43 | 19:20 | Lakshmipur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to PDB End Maintenance.
| 17:44 | 19:15 | Lakshmipur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to PDB End Maintenance.
| 18:07 | 20:40 | Chowmuhani 230/132/33kV S/S TR2-425T HT Forced S/D Due to 33kV LBUS BUS DS loop Redhot | [7 empty] | 20.0MW load
|  |  | Maintenance. NPBS will do the maintenance work. | [7 empty] | interrup.
| 18:36 | 20:40 | Chowmuhani 230/132/33kV S/S TR2-425T LT Forced S/D Due to 33kV LBUS BUS DS loop Redhot | [7 empty] | 20.0MW load
|  |  | Maintenance. NPBS will do the maintenance work. | [7 empty] | interrup.
| 20:47 | 21:24 | Bhangura 132/33kV S/S Tr-2(413T) LT Forced S/D Due to Red hot remove 33 kv bkr side
| 20:48 | 21:23 | Bhangura 132/33kV S/S Tr-2(413T) HT Forced S/D Due to Red hot remove 33 kv bkr side
| 22:03 |  | Barapukuria unit-3 tripped.
| 22:23 |  | Mymensingh RPCL CCPP GT-1 was sync.
| 23:12 | 23:41 | Khulna (S)-Satkhira 132kV Ckt-1 Tripped from Satkhira 132/33kV end showing Distance | [7 empty] | 76.0MW load
|  |  | relays Due to Earth fault phase(L-3) distance from khulna south substation at 103.2km and | [7 empty] | interrup. Satkhira
|  |  | from Khulna(S) 230/132kV end showing Distance relay a) Dist. | [7 empty] | 132/33kV end and
|  |  | Pickup-L3E b)Dist.-101.7Km c) Trip time-800ms relays Due to None | [7 empty] | 78.0MW load
interrup. Khulna(S)
230/132kV end
| 23:12 | 23:35 | Khulna (S)-Satkhira 132kV Ckt-2 Tripped from Satkhira 132/33kV end showing Distance | [7 empty] | 76.0MW load
|  |  | relays Due to Earth fault phase(L-3) distance from khulna south substation at 101.7km and | [7 empty] | interrup. Satkhira
|  |  | from Khulna(S) 230/132kV end showing Distance relay a) Dist. | [7 empty] | 132/33kV end and
|  |  | Pickup-L3E b)Dist.-103.2Km c) Trip time-801ms relays Due to None | [7 empty] | 78.0MW load
interrup. Khulna(S)
230/132kV end
| 01:33 |  | BIPTC S/S 20DF13 Tripped showing 21R relays Due to Tripped by impedence 21R
| 01:40 |  | Bogura 400/230kV S/S Bogura - Naogaon 230 kV Ckt-2 Tripped showing Lockout-1
trip Lockout-2 trip relays Due to Zone-1 Trip
| 02:19 |  | Ghorasal- Ishwardi 230 kV Ckt-2 Tripped from Ishurdi 230/132kV end showing Siemence
Siprotec 7SA87 relays.
| 02:38 |  | Bogura 230/132kV S/S Confidance UN-2 Tripped showing Overvoltage tripped ( 143.7kV)
relays Due to None
| 02:45 |  | Sirajgonj 225MW CCPP Unit-1 Tripped with remarks:- ST
| 02:45 |  | Sirajganj unit-1 ST tripped.
| 04:38 | 04:42 | Mirpur-Uttara 3PH 132kV Ckt-1 Tripped from Mirpur 132/33kV end showing OV/DTT Trip
relays Due to Grid Voltage High
| 04:43 |  | Mirpur-Uttara 3PH 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to By NLDC
| 04:45 |  | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) HT Tripped showing WTI/OTI Relay
relays Due to WTI/OTI Fault
| 04:45 |  | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) LT Tripped showing WTI/OTI Relay
relays Due to WTI/OTI Fault
| 04:56 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Forced S/D Due to Reduce system
voltage
| 04:56 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 Forced S/D Due to Reduce system
voltage
| 05:10 | 05:42 | Bhaluka 132/33kV S/S 03. Transformer-03 HT Tripped showing 50N/51N Trip relays. | [7 empty] | 2.0MW load
interrup.
| 05:45 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- False SMS (GT Running & STG SD
at 02.45 am)
| 06:00 |  | Cumilla(N) 230/132/33kV S/S 230KV ATR-02 HT Tripped showing Main-1: Mechanical Fault
trip Main-2: Mechanical Fault Trip AVR: Pressure relif device trip relays.
| 06:00 |  | Minimum Generation is 7746 MW.
| 07:10 |  | Narail 132/33kV S/S TR2 (413-T) LT Scheduled S/D Due to Red hot maintenance | [7 empty] | 15.0MW load
interrup.
| 07:10 |  | Saidpur 132/33kV S/S TR-3 (424T) LT Scheduled S/D Due to Red hot maintainance. | [7 empty] | 20.0MW load
interrup.
| 07:11 |  | Narail 132/33kV S/S TR2 (413-T) HT Scheduled S/D Due to Red hot maintenance | [7 empty] | 15.0MW load
interrup.
| 07:11 |  | Saidpur 132/33kV S/S TR-3 (424T) HT Scheduled S/D Due to Red hot maintainance. | [7 empty] | 20.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 25-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 377 | 8719200 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 642800 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 331 | 7652522 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 18 | 129600 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 896640 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 199002 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 134751 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 414000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 411840 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 111360 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 1095720 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 105 | 2258640 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 15 | 198720 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 68 | 381600 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 105736 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 128880 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 505 | 11104545.45 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 286 | 6773990 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 68 | 1030800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2101 | 42390346.45
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 20302.2 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 114480 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 457440 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 60 | 1413980 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 224 | 5119829 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 48 | 716763 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 163221 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 167040 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 25 | 445440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 26880 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20848 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 80291 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 97194 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 49 | 638982 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 29 | 297600 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 223309 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 95345 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 13756362 | U2 outage added
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 20 | 550080 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 445 | 11236363.64 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 1587 | 35641749.84
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 188 | 4870000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 358 | 8736800 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 300 | 6704000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 215 | 6153000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1141816 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 60 | 500145 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 1513980 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 325920 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 118 | 2749440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 48922 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 247320 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 20520 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 69 | 429120 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 314890 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1427 | 33755873
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 22080 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 5200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 133 | 916800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 1129200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 60810 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 47040 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 20520 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 142 | 2201650
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 9144 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 639720 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 145 | 3368454.55 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 151 | 3543200 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 709344 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2006400 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2430600 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 285792 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7140000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 368 | 8478000 | FGMO not available because of Cooling Tower Fan
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1223 | 28610654.55
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 822 | 21377455 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 168 | 3915360 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 379 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 202464 | FGMO
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 506160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 592 | 17243641 | Rampal U# 1 is out of bar due to maintenance work
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1632 | 43245459
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 1245 | 23352727 | RRT
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2600000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1149 | 23048727.27 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5311280 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5432000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3475 | -
Barishal Area Total |  |  |  |  | 3481.04 | 3041 | 59748209.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 258288 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 140 | 3782455 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 140 | 3623764 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 386 | 9230109 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 53376 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 22380 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1447 | 27196364 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 266896 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 534100 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2113 | 44967732
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1174254 | Plant availability zero, U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 152 | 3664000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 69 | 525724 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 39615.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 340579 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 147975 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 735840 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 321 | 6627987.12
Eastern Grid Total |  |  |  |  | 17418.042 | 6480 | 142600273.84
Western Grid Total |  |  |  |  | 11852.195 | 7107 | 154589387.39
National Grid Total |  |  |  |  | 29270.237 | 13587 | 297189661.23
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 25-05-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8368.35 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4733.9 | MW
i) Dhaka area |  |  | 4403.35 |  | MW | i) Khulna area |  |  |  | 1918 | MW
ii) Chattogram area |  |  | 1348 |  | MW | ii) Barishal area |  |  |  | 519.7 | MW
iii) Cumilla area |  |  | 1198 |  | MW | iii) Rajshahi area |  |  |  | 1436.2 | MW
iv) Mymensingh area |  |  | 956 |  | MW | iv) Rangpur area |  |  |  | 860 | MW
v) Sylhet area |  |  | 463 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13102.25 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 86 | 11:00 | 133 | Natore | 164 | 00:00
2 | AKSML | 115 | 17:00 | 68 | Hathazari | 85 | 00:00 | 134 | Nawabganj | 52.8 | 20:00
3 | Aftabnagar | 34 | 01:00 | 69 | Hatirjheel | 42 | 12:00 | 135 | Netrakona | 127 | 20:00
4 | Agargaon | 94 | 11:00 | 70 | Ishurdi | 82 | 19:30 | 136 | New | 74.9 | 11:00
5 | Agrabad | 70 | 15:00 | 71 | Jaldhaka | 78 | 19:30 | 137 | Niamatpur | 68 | 00:00
6 | Amnura | 35 | 00:00 | 72 | Jamalpur | 97 | 19:00 | 138 | Noapara | 48 | 19:30
7 | Ashuganj | 96 | 20:00 | 73 | Jashore | 174 | 19:30 | 139 | PHP | 7 | 12:00
8 | BSRM | 184 | 21:00 | 74 | Jhenaidah | 139 | 23:00 | 140 | Pabna | 100 | 19:00
9 | Bagerhat | 98 | 01:00 | 75 | Joydebpur | 130 | 09:00 | 141 | Palashbari | 106 | 19:30
10 | Bajitpur | 85 | 22:00 | 76 | Joypurhat | 54 | 19:30 | 142 | Panchagarh | 60 | 20:00
11 | Bakerganj | 12.6 | 22:00 | 77 | Juldah | 16.5 | 00:00 | 143 | Patiya | 11 | 00:00
12 | Bakulia | 96 | 00:00 | 78 | KSRM | 11 | 01:00 | 144 | Patuakhali | 83 | 22:00
13 | Banani | 38.4 | 11:00 | 79 | Kabirpur | 230 | 09:00 | 145 | Payra | 40 | 00:00
14 | Bangabhaban | 7 | 11:00 | 80 | Kachua | 94 | 22:00 | 146 | Postogola | 49 | 13:00
15 | Barapukuria | 59 | 19:30 | 81 | Kaliganj | 12 | 21:00 | 147 | Pubail | 28 | 07:00
16 | Barguna | 28 | 00:00 | 82 | Kallyanpur | 111 | 00:00 | 148 | Purbachal | 28 | 11:00
17 | Barishal | 122 | 00:00 | 83 | Kalurghat | 37 | 00:00 | 149 | Purbasadipur | 122 | 00:00
18 | Barishal-230 | 112 | 23:00 | 84 | Kamrangirchar | 73 | 12:00 | 150 | Rahanpur | 40 | 21:00
19 | Baroaulia | 65 | 11:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 15 | 01:00
20 | Baroirhat | 69 | 00:00 | 86 | Kasba | 37 | 00:00 | 152 | Rajbari | 85.5 | 19:30
21 | Bashundhara | 176 | 11:00 | 87 | Kazla | 107 | 12:00 | 153 | Rajendrapur | 109 | 00:00
22 | BashundharaCement | 6 | 12:00 | 88 | Keranigonj | 73 | 01:00 | 154 | Rajshahi | 117 | 00:00
23 | Beanibazar | 64 | 00:00 | 89 | Khagrachori | 30 | 13:00 | 155 | Rajshahi-230 | 100 | 13:00
24 | Benapole | 81 | 22:00 | 90 | Khulna | 69 | 13:00 | 156 | Ramganj | 100 | 22:00
25 | Bhaluka | 128 | 01:00 | 91 | Khulshi | 186 | 15:00 | 157 | Rampur | 48 | 00:00
26 | Bhandaria | 69 | 00:00 | 92 | Kishoreganj | 115 | 00:00 | 158 | Rangamati | 16 | 19:30
27 | Bhangura | 36 | 19:30 | 93 | Kodda | 275 | 10:00 | 159 | Rangpur | 134 | 19:30
28 | Bheramara(GK) | 69 | 22:00 | 94 | Kulaura | 39 | 00:00 | 160 | Ruppur | 4.4 | 09:00
29 | Bhulta | 218 | 09:00 | 95 | Kurigram | 58 | 19:30 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 78 | 00:00 | 96 | Kushtia | 157 | 21:00 | 162 | Saidpur | 84 | 19:00
31 | Bogura | 153 | 00:00 | 97 | Laksam | 32 | 13:00 | 163 | Santhia | 32 | 19:00
32 | Borhanuddin | 97 | 00:00 | 98 | Lakshmipur | 52 | 21:00 | 164 | Satkhira | 156 | 22:00
33 | Brahmanbaria | 124 | 00:00 | 99 | Lalbag | 72 | 12:00 | 165 | Satmasjid | 94 | 11:00
34 | Cantonment | 112 | 11:00 | 100 | Lalmonirhat | 58 | 19:00 | 166 | Savar | 200 | 09:00
35 | Chandina | 35 | 02:00 | 101 | MI_Cement | 12.6 | 03:00 | 167 | SevenRings | 13.82 | 16:00
36 | Chandpur | 74 | 09:00 | 102 | Madanganj | 25 | 12:00 | 168 | ShahCement | 26 | 19:00
37 | Chandraghona | 33 | 00:00 | 103 | Madaripur | 115 | 22:00 | 169 | Shahjadpur | 76 | 08:00
38 | Chapai | 78 | 00:00 | 104 | Madartek | 70 | 00:00 | 170 | Shahjibazar | 117 | 00:00
39 | Charsaidpur | 28 | 01:00 | 105 | Madunaghat | 55 | 00:00 | 171 | Shahmirpur | 64 | 00:00
40 | Chauddagram | 77 | 00:00 | 106 | Magura | 73 | 19:00 | 172 | Shariatpur | 76 | 02:00
41 | Chhatak | 34 | 00:00 | 107 | Mahasthangarh | 67 | 01:00 | 173 | Sherpur | 116 | 19:00
42 | Chowmuhani | 173 | 00:00 | 108 | Maijdee | 57 | 00:00 | 174 | Shikalbaha | 33 | 00:00
43 | Chuadanga | 129 | 20:00 | 109 | Manikganj | 123 | 19:00 | 175 | Shitalakhya | 89.2 | 12:00
44 | Coxsbazar | 139 | 22:00 | 110 | Maniknagar | 55 | 12:00 | 176 | Sholosohor | 49 | 19:00
45 | Cumilla(N) | 121 | 12:00 | 111 | Matarbari | 61 | 19:30 | 177 | Shomvuganj | 16 | 01:00
46 | Cumilla(S) | 144 | 12:00 | 112 | Matuail | 75 | 12:00 | 178 | Shyampur | 142 | 23:00
47 | Daganbhuiyan | 44 | 00:00 | 113 | Metrorail_Motijheel | 3 | 00:00 | 179 | Siddhirganj | 123 | 12:00
48 | Daudkandi | 112 | 02:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 104 | 20:00
49 | DhakaUniversity | 62 | 11:00 | 115 | Millgate | 86 | 11:00 | 181 | Sonargaon | 134 | 01:00
50 | Dhamrai | 100 | 00:00 | 116 | Mirpur | 135.5 | 11:00 | 182 | Sreemongol | 67 | 00:00
51 | Dhanmondi | 76.5 | 11:00 | 117 | Mirsorai | 44 | 00:00 | 183 | Sreepur | 101 | 09:00
52 | Dohazari | 111 | 00:00 | 118 | Mirzapur | 42 | 19:30 | 184 | Srinagar | 45.4 | 22:00
53 | Faridpur | 167 | 23:00 | 119 | Mithapukur | 57 | 01:00 | 185 | Sunamganj | 48 | 22:00
54 | Fatullah | 85 | 10:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 54 | 19:00
55 | Fenchuganj | 33 | 00:00 | 121 | Mogbazar | 70 | 12:00 | 187 | Sylhet-132 | 84 | 19:00
56 | Feni | 99 | 22:00 | 122 | Mongla | 42 | 01:00 | 188 | TK | 28 | 00:00
57 | GPH | 1 | 00:00 | 123 | Motijheel | 37 | 11:00 | 189 | Tangail | 158 | 19:00
58 | Ghatail | 77 | 19:30 | 124 | Muktagacha | 36 | 07:00 | 190 | Taraganj | 21 | 00:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 106 | 00:00 | 191 | Tasnim | 18 | 12:00
60 | Ghorashal-230 | 105 | 11:00 | 126 | Muradnagar | 47 | 00:00 | 192 | Thakurgaon | 100 | 20:00
61 | Goalpara | 48 | 23:00 | 127 | Mymensingh | 164 | 00:00 | 193 | Tongi | 150 | 00:00
62 | Gollamari | 128 | 00:00 | 128 | Nabinagar | 82 | 10:00 | 194 | Ullahpara | 38 | 00:00
63 | Gopalganj | 121 | 22:00 | 129 | Naogaon | 140 | 00:00 | 195 | Ullon | 57 | 00:00
64 | Gulshan | 100 | 11:00 | 130 | Narail | 67 | 19:00 | 196 | Uttara | 93 | 11:00
65 | Halishahar | 96 | 11:00 | 131 | Narinda | 58 | 12:00 | 197 | UttaraNew | 48 | 00:00
66 | HaripurSBU | 140 | 09:00 | 132 | Narshingdi | 183 | 00:00 | 198 | Zigatola | 82 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 25-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14022.24 | 285 |  | 14320.24
1:00 | 13677.83 | 136 |  | 13819.83
2:00 | 13496.87 | 95 |  | 13595.87
3:00 | 13155.62 | 85 |  | 13244.45
4:00 | 12558.74 | 80 |  | 12642.34
5:00 | 12239.68 | 80 |  | 12323.68
6:00 | 11728.98 | 102 |  | 11835.57
7:00 | 11627.12 | 127 |  | 11760.12
8:00 | 11252.69 | 73 |  | 11328.69
9:00 | 11334.39 | 70 |  | 11407.39
10:00 | 11346.2 | 67 |  | 11416.22
11:00 | 11266.34 | 57 |  | 11326.34
12:00 | 10959.69 | 0 |  | 10959.69
13:00 | 11070.78 | 0 |  | 11070.78
14:00 | 11250.44 | 0 |  | 11250.44
15:00 | 11629.76 | 0 |  | 11629.76
16:00 | 11702.99 | 0 |  | 11702.99
17:00 | 11573.61 | 0 |  | 11573.61
18:00 | 11394.25 | 0 |  | 11394.25
19:00 | 12620 | 0 |  | 12620
19:30 | 13356 | 17 |  | 13374
20:00 | 13293 | 37 |  | 13332
21:00 | 13587 | 27 |  | 13615
22:00 | 13678 | 20 |  | 13699
23:00 | 13635 | 34 |  | 13671
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 25-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7155.5 | 6866.74 | 14022.24 | DAILY GENERATION CURVE
00:30 | 6888.75 | 6961.285 | 13850.035
01:00 | 6622 | 7055.83 | 13677.83 | 25-05-2026
01:30 | 6487 | 7100.35 | 13587.35
02:00 | 6352 | 7144.87 | 13496.87
02:30 | 6222.5 | 7103.745 | 13326.245
03:00 | 6093 | 7062.62 | 13155.62
03:30 | 5936 | 6921.18 | 12857.18
04:00 | 5779 | 6779.74 | 12558.74
04:30 | 5720.5 | 6678.71 | 12399.21
05:00 | 5662 | 6577.68 | 12239.68
05:30 | 5641.285 | 6343.045 | 11984.33
06:00 | 5620.57 | 6108.41 | 11728.98
06:30 | 5703.335 | 5974.715 | 11678.05
07:00 | 5786.1 | 5841.02 | 11627.12
07:30 | 5643.8 | 5796.105 | 11439.905
08:00 | 5501.5 | 5751.19 | 11252.69
08:30 | 5576.09 | 5717.45 | 11293.54
09:00 | 5650.68 | 5683.71 | 11334.39
09:30 | 5605.615 | 5734.68 | 11340.295
10:00 | 5560.55 | 5785.65 | 11346.2
10:30 | 5513.3 | 5792.97 | 11306.27
11:00 | 5466.05 | 5800.29 | 11266.34
11:30 | 5292.99 | 5820.025 | 11113.015
12:00 | 5119.93 | 5839.76 | 10959.69
12:30 | 5212.945 | 5802.29 | 11015.235
13:00 | 5305.96 | 5764.82 | 11070.78
13:30 | 5406.135 | 5754.475 | 11160.61
14:00 | 5506.31 | 5744.13 | 11250.44
14:30 | 5542.265 | 5897.835 | 11440.1
15:00 | 5578.22 | 6051.54 | 11629.76
15:30 | 5590.885 | 6075.49 | 11666.375
16:00 | 5603.55 | 6099.44 | 11702.99
16:30 | 5564.685 | 6073.615 | 11638.3
17:00 | 5525.82 | 6047.79 | 11573.61
17:30 | 5492.875 | 5991.055 | 11483.93
18:00 | 5459.93 | 5934.32 | 11394.25
18:30 | 5725.965 | 6281.16 | 12007.125
19:00 | 5992 | 6628 | 12620
19:30 | 6421 | 6935 | 13356
20:00 | 6358 | 6935 | 13293
20:30 | 6419 | 7021 | 13440 |  | Executive Engineer
21:00 | 6480 | 7107 | 13587 |  | Network Operation Division
21:30 | 6512.5 | 7120 | 13632.5
22:00 | 6545 | 7133 | 13678
22:30 | 6587.5 | 7069 | 13656.5
23:00 | 6630 | 7005 | 13635

## En-Curve
QF-LDC-12
Date | 25-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3654 | 1638.5 | 826 | 0 | 78 | 1404.74 | 60 | 4710 | 0 | 302 | 1324 | 0 | 0 | 25 | 285 | DAILY ENERGY CURVE
00:30 | 3645 | 1597.25 | 804.5 | 0 | 86 | 1402.285 | 60 | 4804 | 0 | 247 | 1181 | 0 | 0 | 23 | 210.5 | 25-05-2026
01:00 | 3636 | 1556 | 783 | 0 | 94 | 1399.83 | 60 | 4898 | 0 | 192 | 1038 | 0 | 0 | 21 | 136
01:30 | 3635 | 1616 | 783.5 | 0 | 103 | 1396.35 | 60 | 4875 | 0 | 181.5 | 919.5 | 0 | 0 | 17.5 | 115.5 | Energy Generated | 297.1897 |  | MKWHr
02:00 | 3634 | 1676 | 784 | 0 | 112 | 1392.87 | 60 | 4852 | 0 | 171 | 801 | 0 | 0 | 14 | 95 | Energy not Served | 1.375 |  | MKWHr
02:30 | 3635 | 1594 | 783.5 | 0 | 119 | 1395.245 | 60 | 4841.5 | 0 | 146 | 729.5 | 0 | 0 | 22.5 | 90 | Total Energy Requirement | 298.5647 |  | MKWHr
03:00 | 3636 | 1512 | 783 | 0 | 126 | 1397.62 | 60 | 4831 | 0 | 121 | 658 | 0 | 0 | 31 | 85
03:30 | 3620 | 1453.5 | 734.5 | 0 | 124 | 1390.68 | 60 | 4796.5 | 0 | 112.5 | 545 | 0 | 0 | 20.5 | 82.5
04:00 | 3604 | 1395 | 686 | 0 | 122 | 1383.74 | 60 | 4762 | 0 | 104 | 432 | 0 | 0 | 10 | 80
04:30 | 3683.5 | 1443 | 809 | 0 | 118 | 1270.21 | 60 | 4563.5 | 0 | 104 | 333 | 0 | 0 | 15 | 80
05:00 | 3763 | 1491 | 932 | 0 | 114 | 1156.68 | 60 | 4365 | 0 | 104 | 234 | 0 | 0 | 20 | 80
05:30 | 3751 | 1487 | 932.5 | 0 | 111 | 1035.805 | 60 | 4244 | 7.525 | 104 | 234 | 0 | 0 | 17.5 | 91
06:00 | 3739 | 1483 | 933 | 0 | 108 | 914.93 | 60 | 4123 | 15.05 | 104 | 234 | 0 | 0 | 15 | 102
06:30 | 3729 | 1553.5 | 933 | 0 | 105 | 877.68 | 60 | 4006.5 | 40.87 | 127.5 | 234 | 0 | 0 | 11 | 114.5
07:00 | 3719 | 1624 | 933 | 0 | 102 | 840.43 | 60 | 3890 | 66.69 | 151 | 234 | 0 | 0 | 7 | 127
07:30 | 3685.5 | 1519.5 | 933.5 | 0 | 106 | 834.275 | 60 | 3832.5 | 92.63 | 151 | 215 | 0 | 0 | 10 | 100
08:00 | 3652 | 1415 | 934 | 0 | 110 | 828.12 | 60 | 3775 | 118.57 | 151 | 196 | 0 | 0 | 13 | 73
08:30 | 3619.5 | 1515.75 | 933.5 | 0 | 115 | 834.56 | 60 | 3755.5 | 154.23 | 112.5 | 180.5 | 0 | 0 | 12.5 | 71.5
09:00 | 3587 | 1616.5 | 933 | 0 | 120 | 841 | 60 | 3736 | 189.89 | 74 | 165 | 0 | 0 | 12 | 70
09:30 | 3579.5 | 1627 | 932.5 | 0 | 120 | 845 | 60 | 3732.5 | 208.295 | 65.5 | 152.5 | 0 | 0 | 17.5 | 68.5
10:00 | 3572 | 1637.5 | 932 | 0 | 120 | 849 | 60 | 3729 | 226.7 | 57 | 140 | 0 | 0 | 23 | 67
10:30 | 3558 | 1558.25 | 932.5 | 0 | 128 | 847.5 | 60 | 3695 | 289.02 | 57 | 142.5 | 0 | 0 | 38.5 | 62
11:00 | 3544 | 1479 | 933 | 0 | 136 | 846 | 60 | 3661 | 351.34 | 57 | 145 | 0 | 0 | 54 | 57
11:30 | 3502.5 | 1408 | 933 | 0 | 140 | 849 | 60 | 3560 | 466.015 | 28.5 | 111.5 | 0 | 0 | 54.5 | 28.5
12:00 | 3461 | 1337 | 933 | 0 | 144 | 852 | 60 | 3459 | 580.69 | 0 | 78 | 0 | 0 | 55 | 0
12:30 | 3473 | 1442 | 933 | 0 | 142 | 857 | 60 | 3409.5 | 564.735 | 3.5 | 74.5 | 0 | 0 | 56 | 0
13:00 | 3485 | 1547 | 933 | 0 | 140 | 862 | 60 | 3360 | 548.78 | 7 | 71 | 0 | 0 | 57 | 0
13:30 | 3573 | 1557.5 | 933 | 0 | 118 | 880 | 60 | 3409.5 | 446.11 | 11 | 115.5 | 0 | 0 | 57 | 0
14:00 | 3661 | 1568 | 933 | 0 | 96 | 898 | 60 | 3459 | 343.44 | 15 | 160 | 0 | 0 | 57 | 0
14:30 | 3668 | 1598 | 933 | 0 | 96 | 977.5 | 60 | 3545 | 341.1 | 15 | 161.5 | 0 | 0 | 45 | 0
15:00 | 3675 | 1628 | 933 | 0 | 96 | 1057 | 60 | 3631 | 338.76 | 15 | 163 | 0 | 0 | 33 | 0
15:30 | 3691.5 | 1627.5 | 933 | 0 | 102 | 1072 | 60 | 3691.5 | 277.375 | 15 | 163 | 0 | 0 | 33.5 | 0
16:00 | 3708 | 1627 | 933 | 0 | 108 | 1087 | 60 | 3752 | 215.99 | 15 | 163 | 0 | 0 | 34 | 0
16:30 | 3666.5 | 1633.5 | 933 | 0 | 107 | 1089 | 60 | 3767.5 | 162.8 | 15 | 172.5 | 0 | 0 | 31.5 | 0
17:00 | 3625 | 1640 | 933 | 0 | 106 | 1091 | 60 | 3783 | 109.61 | 15 | 182 | 0 | 0 | 29 | 0
17:30 | 3611 | 1629.5 | 933 | 0 | 109 | 1066.5 | 60 | 3770 | 70.43 | 15 | 199.5 | 0 | 0 | 20 | 0
18:00 | 3597 | 1619 | 933 | 0 | 112 | 1042 | 60 | 3757 | 31.25 | 15 | 217 | 0 | 0 | 11 | 0
18:30 | 3602.5 | 1630.5 | 933 | 0 | 118 | 1149.5 | 60 | 3957 | 15.625 | 57.5 | 477 | 0 | 0 | 6.5 | 0
19:00 | 3608 | 1642 | 933 | 0 | 124 | 1257 | 60 | 4157 | 0 | 100 | 737 | 0 | 0 | 2 | 0
19:30 | 3547 | 1550 | 918 | 0 | 118 | 1421 | 60 | 4340 | 0 | 133 | 1266 | 0 | 0 | 3 | 17
20:00 | 3576 | 1540 | 822 | 0 | 102 | 1448 | 60 | 4378 | 0 | 158 | 1208 | 0 | 0 | 1 | 37
20:30 | 3601.5 | 1614 | 822 | 0 | 110 | 1447.5 | 60 | 4465 | 0 | 154 | 1155.5 | 0 | 0 | 10.5 | 32
21:00 | 3627 | 1688 | 822 | 0 | 118 | 1447 | 60 | 4552 | 0 | 150 | 1103 | 0 | 0 | 20 | 27
21:30 | 3654 | 1693.5 | 822 | 0 | 123 | 1446.5 | 60 | 4572.5 | 0 | 166 | 1067 | 0 | 0 | 28 | 23.5
22:00 | 3681 | 1699 | 822 | 0 | 128 | 1446 | 60 | 4593 | 0 | 182 | 1031 | 0 | 0 | 36 | 20
22:30 | 3728 | 1703.5 | 822 | 0 | 124 | 1448 | 60 | 4499 | 0 | 199.5 | 1052.5 | 0 | 0 | 20 | 27
23:00 | 3775 | 1708 | 822 | 0 | 120 | 1450 | 60 | 4405 | 0 | 217 | 1074 | 0 | 0 | 4 | 34
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 25-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 64 | 0 | 400 | 90 | 1652 | 378 | Ishurdi-Ghorashal Ckt-1 | Export | 2586036.36
1:00 | 66 | 4 | 428 | 100 | 1775 | 338
2:00 | 81 | 7 | 470 | 116 | 1844 | 352 |  | Import | 0
3:00 | 89 | 3 | 492 | 110 | 1878 | 364
4:00 | 88 | 2 | 492 | 104 | 1828 | 370 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 137 | -10 | 540 | 90 | 1700 | 460
6:00 | 144 | -6 | 580 | 100 | 1690 | 452 |  | Import | 0
7:00 | 136 | -10 | 562 | 90 | 1638 | 496
8:00 | 158 | -5 | 602 | 34 | 1684 | 512 | Sirajganj-Sreepur Ckt-1 | Export | 2773000
9:00 | 182 | 7 | 620 | 114 | 1744 | 582
10:00 | 187 | 3 | 584 | 90 | 1814 | 578 |  | Import | 0
11:00 | 187 | 3 | 474 | 26 | 1638 | 468
12:00 | 129 | -30 | 400 | 4 | 1362 | 390 | Sirajganj-Sreepur Ckt-2 | Export | 2781000
13:00 | 95 | -40 | 340 | 4 | 1434 | 342
14:00 | 84 | -39 | 330 | 10 | 1294 | 360 |  | Import | 0
15:00 | 102 | -32 | 410 | 36 | 1434 | 342
16:00 | 104 | -44 | 430 | 46 | 1508 | 336 | Gopalganj-Aminbazar Ckt-1 | Export | 19780000
17:00 | 116 | -39 | 467 | 54 | 1584 | 334
18:00 | 102 | -39 | 440 | 60 | 1508 | 338 |  | Import | 0
18:30 | 106 | -40 | 450 | 50 | 1672 | 302
19:00 | 67 | -51 | 390 | 44 | 1538 | 142 | Gopalganj-Aminbazar Ckt-2 | Export | 19830000
19:30 | 62 | -52 | 380 | 32 | 1610 | 104
20:00 | 52 | -47 | 370 | 24 | 1632 | 124 |  | Import | 0
21:00 | 58 | -41 | 393 | 32 | 1728 | 142
22:00 | 70 | -38 | 420 | 46 | 1698 | 130 |  | Total Export | 47750036.36
23:00 | 58 | -42 | 390 | 34 | 1624 | 112 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 25-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 380 | 07:00 | 373 | 02:00 | Madunaghat | 402 | 20:00 | 392 | 11:00
Amtali | 413 | 08:00 | 401 | 00:00 | Meghnaghat | 382 | 13:00 | 375 | 10:00
Ashuganj | 422 | 13:00 | 403 | 22:00 | Payra | 414 | 08:00 | 405 | 21:00
Bhulta | 414 | 13:00 | 397 | 22:00 | Rahanpur | 415 | 06:00 | 396 | 19:30
Bibiana | 397 | 13:00 | 391 | 01:00 | Rampal | 399 | 08:00 | 376 | 23:00
BIPTC | 405 | 04:00 | 392 | 00:00
Bogura | 404 | 06:00 | 382 | 20:00
Gopalganj | 394 | 07:00 | 377 | 23:00
Kaliakoir | 378 | 12:00 | 368 | 01:00
Korerhat | 400 | 19:30 | 390 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 236 | 13:00 | 230 | 02:00 | Jhenaidah | 228 | 09:00 | 209 | 23:00
AKSML | 236 | 18:30 | 226 | 09:00 | Kachua | 236 | 15:00 | 227 | 10:00
Aminbazar | 236 | 13:00 | 230 | 10:00 | Kaliakoir | 237 | 12:00 | 230 | 10:00
Ashuganj | 236 | 13:00 | 228 | 02:00 | Keranigonj | 235 | 13:00 | 228 | 10:00
Ashuganj-400 | 236 | 13:00 | 228 | 02:00 | Khulna(S) | 229 | 09:00 | 206 | 23:00
Baghabari | 234 | 07:00 | 224 | 19:30 | Korerhat | 234 | 19:00 | 227 | 10:00
Barapukuria | 232 | 06:00 | 216 | 23:00 | Madunaghat | 235 | 19:30 | 226 | 10:00
Barapukuria-230 | 234 | 07:00 | 224 | 19:30 | Madunaghat-400 | 235 | 20:00 | 228 | 10:00
Barishal | 231 | 08:00 | 222 | 21:00 | Maniknagar | 233 | 13:00 | 226 | 10:00
Bheramara | 234 | 02:00 | 222 | 16:00 | Meghnaghat | 242 | 14:00 | 234 | 00:00
Bhulta | 233 | 13:00 | 225 | 10:00 | Meghnaghat-400 | 236 | 13:00 | 229 | 01:00
Bibiana | 237 | 11:00 | 232 | 03:00 | Mirsorai | 233 | 19:00 | 226 | 09:00
BIPTC | 235 | 01:00 | 221 | 19:00 | Naogaon | 227 | 08:00 | 205 | 20:00
Bogura | 241 | 06:00 | 228 | 19:30 | Purbasadipur | 236 | 06:00 | 214 | 23:00
Bogura-400 | 242 | 06:00 | 227 | 19:30 | Rajshahi | 232 | 08:00 | 219 | 19:00
Borhanuddin | 233 | 12:00 | 227 | 18:30 | Rampal | 227 | 09:00 | 209 | 23:00
BSRM | 236 | 19:00 | 226 | 10:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 236 | 16:00 | 227 | 10:00 | Rampura | 233 | 13:00 | 224 | 10:00
Cumilla(N) | 233 | 13:00 | 227 | 10:00 | Shikalbaha | 234 | 19:30 | 225 | 11:00
Faridpur | 232 | 08:00 | 220 | 23:00 | Shyampur | 235 | 13:00 | 228 | 10:00
Fenchuganj | 241 | 12:00 | 232 | 06:00 | Siddhirganj | 234 | 15:00 | 229 | 00:00
Feni | 231 | 19:00 | 224 | 10:00 | Sirajgonj | 240 | 10:00 | 220 | 18:00
Ghorashal | 230 | 00:00 | 225 | 08:00 | Sreepur | 233 | 13:00 | 222 | 02:00
Ghorashal-230 | 231 | 13:00 | 224 | 01:00 | Tongi | 233 | 12:00 | 224 | 00:00
Gopalganj | 233 | 07:00 | 223 | 21:00
GPH | 234 | 19:00 | 223 | 04:00
Haripur | 235 | 13:00 | 226 | 10:00
Hasnabad | 235 | 13:00 | 228 | 10:00
Hathazari | 234 | 19:00 | 225 | 10:00
Ishurdi | 236 | 09:00 | 224 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 00:00 | 128 | 11:00 | Madunaghat | 136 | 19:00 | 131 | 09:00
Agargaon | 137 | 07:00 | 133 | 10:00 | Magura | 133 | 09:00 | 119 | 19:00
Agrabad | 135 | 19:00 | 128 | 11:00 | Mahasthangarh | 140 | 08:00 | 128 | 19:00
AKS | 133 | 19:00 | 127 | 10:00 | Maijdee | 133 | 01:00 | 127 | 10:00
Aminbazar | 135 | 12:00 | 130 | 10:00 | Manikganj | 133 | 11:00 | 125 | 22:00
Amnura | 134 | 06:00 | 126 | 15:00 | Maniknagar | 137 | 13:00 | 132 | 10:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 133 | 00:00 | 112 | 01:00
Ashuganj-230 | 145 | 13:00 | 135 | 00:00 | Matuail | 139 | 13:00 | 130.5 | 10:00
Bagerhat | 130 | 07:00 | 109 | 23:00 | Metrorail_Motijheel | 137 | 14:00 | 132 | 10:00
Bajitpur | 135 | 12:00 | 127 | 01:00 | Metrorail_Uttara | 137 | 13:00 | 128 | 17:00
Bakerganj | 132 | 08:00 | 124 | 22:00 | Millgate | 139 | 12:00 | 128 | 16:00
Bakulia | 135 | 19:00 | 128 | 12:00 | Mirpur | 135 | 20:00 | 130 | 01:00
Banani | 133 | 13:00 | 127 | 11:00 | Mirzapur | 133 | 11:00 | 124 | 22:00
Bangabhaban | 137 | 13:00 | 131 | 11:00 | Mithapukur | 138 | 08:00 | 125 | 19:30
Barapukuria | 138 | 06:00 | 126 | 19:30 | MI_Cement | 139.7 | 13:00 | 130 | 01:00
Barguna | 132 | 09:00 | 124 | 21:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 133 | 08:00 | 125 | 21:00 | Mogbazar | 135 | 13:00 | 130 | 10:00
Barishal-230 | 133 | 08:00 | 125 | 22:00 | Mongla | 130 | 07:00 | 111 | 23:00
Baroaulia | 135 | 19:00 | 129 | 10:00 | Motijheel | 137 | 13:00 | 131 | 11:00
Baroirhat | 135 | 19:00 | 131 | 09:00 | Muktagacha | 135 | 08:00 | 115 | 22:00
Bashundhara | 139 | 12:00 | 123 | 18:30 | Munshiganj | 134 | 17:00 | 125 | 15:00
BashundharaCement | 136 | 16:00 | 130 | 11:00 | Muradnagar | 138 | 14:00 | 128 | 02:00
Beanibazar | 134 | 11:00 | 127 | 00:00 | Mymensingh | 138 | 09:00 | 113 | 22:00
Benapole | 130 | 10:00 | 109 | 23:00 | Nabinagar | 139 | 11:00 | 129 | 16:00
Bhaluka | 136 | 11:00 | 125 | 15:00 | Naogaon | 140 | 08:00 | 123 | 21:00
Bhandaria | 126 | 08:00 | 115 | 22:00 | Narail | 134 | 09:00 | 117 | 23:00
Bhangura | 134 | 09:00 | 127 | 19:00 | Narinda | 137 | 13:00 | 132 | 10:00
Bheramara | 135 | 03:00 | 130 | 16:00 | Narshingdi | 141 | 13:00 | 124 | 11:00
Bheramara(GK) | 135 | 08:00 | 130 | 19:00 | Natore | 135 | 09:00 | 126 | 19:30
Bhulta | 134 | 13:00 | 126 | 11:00 | Nawabganj | 139 | 13:00 | 134 | 01:00
Bog-Sherpur | 139 | 09:00 | 129 | 19:30 | Netrakona | 131 | 11:00 | 117 | 00:00
Bogura | 140 | 08:00 | 130 | 19:30 | New | 140 | 12:00 | 129 | 16:00
Bogura-230 | 140 | 08:00 | 131 | 19:30 | Niamatpur | 137 | 08:00 | 126 | 19:30
Brahmanbaria | 140 | 13:00 | 128 | 02:00 | Noapara | 132 | 09:00 | 114 | 23:00
Cantonment | 136 | 06:00 | 132 | 10:00 | Pabna | 134 | 09:00 | 127 | 19:00
Chandina | 136 | 14:00 | 131 | 10:00 | Palashbari | 138 | 08:00 | 124 | 19:30
Chandpur | 138 | 19:30 | 127 | 13:00 | Panchagarh | 140 | 05:00 | 127 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 138 | 04:00 | 131 | 10:00 | Patiya | 135 | 19:00 | 128 | 09:00
Chapai | 134 | 06:00 | 128 | 23:00 | Patuakhali | 132 | 07:00 | 125 | 21:00
Charsaidpur | 139 | 13:00 | 130 | 10:00 | Payra | 135 | 09:00 | 130 | 23:00
Chauddagram | 135 | 15:00 | 131 | 09:00 | PHP | 135 | 19:30 | 131 | 10:00
Chhatak | 133 | 11:00 | 124 | 00:00 | Postogola | 137 | 13:00 | 130 | 11:00
Chowmuhani | 134 | 15:00 | 126 | 13:00 | Pubail | 140 | 12:00 | 131 | 01:00
Chuadanga | 132 | 09:00 | 115 | 23:00 | Purbachal | 139 | 12:00 | 127 | 16:00
Coxsbazar | 121 | 17:00 | 112 | 23:00 | Purbasadipur | 140 | 06:00 | 127 | 20:00
Cumilla(N) | 136 | 13:00 | 131 | 02:00 | Rahanpur | 137 | 06:00 | 129 | 23:00
Cumilla(S) | 136 | 14:00 | 125 | 12:00 | Rahanpur-400 | 137 | 07:00 | 130 | 21:00
Daganbhuiyan | 135 | 01:00 | 130 | 10:00 | Rahim | 134 | 07:00 | 132 | 00:00
Daudkandi | 137 | 13:00 | 126 | 10:00 | Rajbari | 131 | 07:00 | 123 | 23:00
DhakaUniversity | 134 | 13:00 | 128 | 11:00 | Rajendrapur | 138 | 11:00 | 126 | 01:00
Dhamrai | 142 | 11:00 | 130 | 16:00 | Rajshahi | 132 | 09:00 | 124 | 19:30
Dhanmondi | 139 | 13:00 | 131 | 11:00 | Rajshahi-230 | 133 | 08:00 | 123 | 13:00
Dohazari | 131 | 19:00 | 124 | 08:00 | Ramganj | 134 | 15:00 | 126 | 10:00
Faridpur | 133 | 06:00 | 125 | 23:00 | Rampur | 135 | 19:00 | 128 | 10:00
Fatullah | 139 | 13:00 | 129 | 10:00 | Rampura | 134 | 13:00 | 128 | 11:00
Fenchuganj | 140 | 12:00 | 133 | 00:00 | Rangamati | 136 | 19:00 | 130 | 10:00
Feni | 135 | 16:00 | 130 | 10:00 | Rangpur | 138 | 06:00 | 126 | 18:00
Feni-230 | 136 | 16:00 | 132 | 09:00 | Ruppur | 135 | 05:00 | 130 | 19:00
Ghatail | 133 | 10:00 | 115 | 22:00 | Saidpur | 138 | 06:00 | 126 | 19:30
Ghorashal | 138 | 18:00 | 135 | 00:00 | Santhia | 136 | 10:00 | 129 | 19:00
Goalpara | 134 | 09:00 | 118 | 23:00 | Satkhira | 129 | 10:00 | 109 | 22:00
Gollamari | 135 | 09:00 | 120 | 21:00 | Satmasjid | 136 | 07:00 | 132 | 11:00
Gopalganj | 133 | 08:00 | 123 | 23:00 | Savar | 135 | 20:00 | 128 | 00:00
Gopalganj-400 | 136 | 07:00 | 129 | 21:00 | SevenRings | 140 | 12:00 | 134 | 10:00
Gulshan | 133 | 13:00 | 128 | 10:00 | ShahCement | 139 | 13:00 | 130 | 10:00
Halishahar | 137 | 04:00 | 129 | 09:00 | Shahjadpur | 135 | 00:00 | 131 | 21:00
Haripur | 139 | 13:00 | 131 | 10:00 | Shahjibazar | 141 | 13:00 | 128 | 00:00
HaripurSBU | 139 | 15:00 | 129 | 17:00 | Shahmirpur | 135 | 19:00 | 129 | 10:00
Hasnabad | 136 | 13:00 | 130 | 09:00 | Shariatpur | 135 | 14:00 | 126 | 22:00
Hathazari | 137 | 20:00 | 131 | 09:00 | Sherpur | 140 | 09:00 | 111 | 06:00
Hatirjheel | 135 | 17:00 | 128 | 11:00 | Shikalbaha | 125 | 19:00 | 119 | 12:00
Ishurdi | 138 | 09:00 | 130 | 19:30 | Shikalbaha-230 | 136 | 19:00 | 130 | 10:00
Jaldhaka | 139 | 06:00 | 124 | 23:00 | Shitalakhya | 139.7 | 13:00 | 129 | 10:00
Jamalpur | 139 | 08:00 | 114 | 02:00 | Sholosohor | 136 | 04:00 | 130 | 10:00
Jashore | 131 | 10:00 | 111 | 23:00 | Shomvuganj | 130 | 11:00 | 122 | 19:00
Jhenaidah | 135 | 09:00 | 116 | 23:00 | Shyampur | 140 | 13:00 | 129 | 10:00
Jhenaidah-230 | 136 | 09:00 | 122 | 22:00 | Shyampur-230 | 141 | 13:00 | 134 | 23:00
Joydebpur | 137 | 12:00 | 130 | 00:00 | Siddhirganj | 138 | 13:00 | 131 | 09:00
Joypurhat | 139 | 08:00 | 124 | 19:30 | Sirajganj | 136 | 10:00 | 126 | 19:30
Juldah | 136 | 18:30 | 128 | 10:00 | Sonargaon | 139 | 13:00 | 129 | 09:00
Kabirpur | 137 | 12:00 | 125 | 16:00 | Sreemongol | 139 | 12:00 | 128 | 00:00
Kachua | 135 | 15:00 | 129 | 10:00 | Sreepur | 135 | 12:00 | 128 | 02:00
Kaliakoir | 142 | 11:00 | 132 | 03:00 | Srinagar | 139 | 13:00 | 133 | 02:00
Kaliganj | 135 | 09:00 | 120 | 23:00 | SSM | 140 | 19:30 | 133 | 00:00
Kallyanpur | 135 | 19:00 | 130 | 02:00 | Sunamganj | 132 | 11:00 | 121 | 00:00
Kalurghat | 136 | 04:00 | 130 | 10:00 | Sylhet | 135 | 12:00 | 128 | 00:00
Kamrangirchar | 139 | 13:00 | 128 | 10:00 | Sylhet-132 | 133 | 12:00 | 128 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Tangail | 133 | 10:00 | 119 | 22:00
Kasba | 137 | 13:00 | 127 | 10:00 | Taraganj | 137 | 06:00 | 124 | 19:30
Kazla | 137 | 14:00 | 132 | 11:00 | Tasnim | 139 | 13:00 | 129 | 08:00
Keranigonj | 139 | 13:00 | 134 | 10:00 | Thakurgaon | 137 | 05:00 | 127 | 12:00
Khagrachori | 136 | 04:00 | 129 | 10:00 | TK | 136 | 18:30 | 131 | 09:00
Khulna | 133 | 09:00 | 118 | 23:00 | Tongi | 141 | 12:00 | 131 | 16:00
Khulna(S) | 135 | 09:00 | 119 | 23:00 | Ullahpara | 136 | 10:00 | 128 | 19:00
Khulshi | 134 | 04:00 | 127 | 09:00 | Ullon | 134 | 13:00 | 128 | 10:00
Kishoreganj | 133 | 12:00 | 125 | 00:00 | Uttara | 138 | 12:00 | 127 | 16:00
Kodda | 135 | 11:00 | 125 | 14:00 | UttaraNew | 137 | 12:00 | 127 | 15:00
Korerhat | 136 | 19:30 | 130 | 14:00 | Zigatola | 139 | 13:00 | 134 | 11:00
KSRM | 136 | 19:00 | 129 | 09:00
Kulaura | 140 | 12:00 | 132 | 00:00
Kurigram | 136 | 08:00 | 121 | 18:00
Kushtia | 132 | 04:00 | 125 | 19:00
Laksam | 134 | 15:00 | 128 | 12:00
Lakshmipur | 133 | 01:00 | 127 | 10:00
Lalbag | 138 | 13:00 | 126 | 07:00
Lalmonirhat | 136 | 07:00 | 120 | 19:30
Madanganj | 140 | 13:00 | 130 | 10:00
Madaripur | 134 | 18:00 | 129 | 21:00
Madartek | 133 | 13:00 | 128 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division