## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 27-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-05-2026 | during | 27-05-2026 | during | 27-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 170 | 230 | 230 | 170 | 170 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 341 | 346 | 412 | 412 | 392 | 392 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 139 | 335 | 335 | 135 | 135 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 235 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 0.01 | 0.01 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 1 | 1 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 13 | 33 | 33 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 14 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 16 | 50 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 32 | 32 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 100 | 100 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 0.01 | 0.01 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 11 | 0 | 15 | 0 | 15 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 530 | 490 | 584 | 584 | 540 | 540 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 312 | 309 | 718 | 718 | 310 | 310 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 17 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1471 | 1833 | 5842.22 | 5827.22 | 2653.38 | 2672.38
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 8 | 8 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 10 | 0 | 14 | 0 | 14 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 65 | 70 | 0 | 0 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 222 | 212 | 212 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 64 | 56 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 24 | 24 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 5 | 42 | 0 | 0 | 5 | 24 | plant availability zero
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 24 | 60 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.36 | 0 | 0 | 0 | 0 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 35 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 312 | 580 | 1224 | 1224 | 612 | 612 | U2 outage added
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 3 | 57 | 14 | 25 | 14 | 25 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 360 | 385 | 575 | 575 | 550 | 550 | U1 under maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 975.36 | 1406 | 3326.86 | 3382.86 | 1988.36 | 2216.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 203 | 202 | 221.25 | 221.25 | 205.25 | 205.25 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 320 | 361 | 350.01 | 350.01 | 320 | 320 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 120 | 0 | 250 | 250 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 310 | 336 | 393 | 393 | 340 | 340 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 36 | 41.65 | 41.65 | 40 | 40 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 20 | 52.82 | 52.82 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 71 | 195 | 195 | 180 | 180 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 2 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 33 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 40 | 40 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 102 | 163 | 163 | 100 | 100 | ST Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 72 | 104 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 43 | 43 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 3 | 8 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 0.01 | 0.01 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 1 | 0 | 15 | 0 | 15 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1131 | 1291 | 2541.43 | 2526.43 | 1717.26 | 1837.26
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-05-2026 | during | 27-05-2026 | during | 27-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 30 | 100 | 157.5 | 157.5 | 210 | 210 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.33 | 0 | 0.6 | 0 | 0.6 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 0 | 45 | 80 | 140 | 80 | 90 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 0 | 9 | 60 | 60 | 10 | 110 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 28.78 | 0 | 12 | 0 | 12 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | From 17:00 to 20:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 60.11 | 154 | 386.6 | 434 | 341.6 | 439
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 42 | 42 | plant availability zero
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 0 | 0 | 30 | 30 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 151 | 139 | 163 | 163 | 147 | 147 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 151 | 150 | 0 | 0 | 155 | 155 | plant availability zero
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 22 | 83 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 101 | 102 | 102 | 102 | 102 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 16 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 319 | 380 | 250 | 250 | 250 | 250 | FGMO not available because of Cooling Tower Fan
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1100 | 1229 | 997 | 997 | 1166 | 1166
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 447 | 923 | 0 | 0 | 0 | 0 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 36 | 36 | 37 | 37 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 383 | 410 | 410 | 400 | 400 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 16 | 16 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 66 | 0 | 65 | 0 | 65 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 390 | 434 | 617.1 | 617.1 | 1234.2 | 617.1 | U1 under maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1153 | 1740 | 1954.1 | 1889.1 | 1879.2 | 1197.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 500 | 732 | 1244 | 1244 | 1244 | 1244 | RRT
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 560 | 974 | 1244 | 1244 | 1184 | 1184 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 0 | 35 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 140 | 185 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.04 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1540.04 | 2231 | 3406 | 3405 | 3166 | 3200
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 21.11 | 0 | 28.97 | 0 | 28.97 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 43 | 158 | 214 | 214 | 190 | 190 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 157 | 164 | 220 | 220 | 210 | 210 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 399 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 100 | 100 | 0 | 50 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.55 | 0 | 3.7 | 0 | 3.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 827.44 | 425.63 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 18.69 | 0 | 35 | 0 | 35 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 59 | 0 | 60 | 0 | 60 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1541.79 | 1146.63 | 3143.54 | 3015.87 | 2718.16 | 2640.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 50 | 0 | 0 | 50 | 50 | Plant availability zero, U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 49 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.9 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 7 | 0 | 15 | 0 | 15 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 138 | 0 | 40.91 | 0 | 40.91 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 196.9 | 134 | 306.91 | 248 | 336.91 | 278
System Total |  |  |  |  | 28823.2 | 29270.237 | 9169.2 | 11164.63 | 21904.66 | 21725.48 | 15966.87 | 15646.59
Forecast Scenario (27-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11100 |  | 0 |  | 11100
|  |  |  | 1:00 | 10392 |  | 0 |  | 10392
|  |  |  | 2:00 | 10010 |  | 0 |  | 10010
|  |  |  | 3:00 | 9702 |  | 0 |  | 9702
|  |  |  | 4:00 | 9136 |  | 0 |  | 9136
|  |  |  | 5:00 | 8299 |  | 0 |  | 8299
|  |  |  | 6:00 | 7376 |  | 0 |  | 7376
|  |  |  | 7:00 | 6893 |  | 0 |  | 6893
|  |  |  | 8:00 | 6322 |  | 0 |  | 6893
|  |  |  | 9:00 | 6000 |  | 0 |  | 6322
|  |  |  | 10:00 | 6800 |  | 0 |  | 6000
|  |  |  | 11:00 | 7500 |  | 0 |  | 6800
|  |  |  | 12:00 | 8200 |  | 0 |  | 7500
|  |  |  | 13:00 | 7945 |  | 0 |  | 8200
|  |  |  | 14:00 | 8519 |  | 0 |  | 8519
|  |  |  | 15:00 | 8755 |  | 0 |  | 8755
|  |  |  | 16:00 | 8843 |  | 0 |  | 8843
|  |  |  | 17:00 | 9000 |  | 0 |  | 9000
|  |  |  | 18:00 | 9200 |  | 0 |  | 9200
|  |  |  | 18:30 | 10100 |  | 0 |  | 10100
|  |  |  | 19:00 | 10900 |  | 0 |  | 10900
|  |  |  | 19:30 | 10950 |  | 0 |  | 10950
|  |  |  | 20:00 | 11000 |  | 0 |  | 11000
|  |  |  | 21:00 | 10980 |  | 0 |  | 10980
|  |  |  | 22:00 | 10950 |  | 0 |  | 10950
|  |  |  | 23:00 | 10900 |  | 0 |  | 10900
Probable Maximum Temperature: |  |  | 36.00°C
Probable Maximum Demand at Day Peak: |  |  | 8200.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11000.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 229.50 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:52 hrs on 27-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 26-05-2026 | [28 empty] | Date: | 26-05-2026 | [28 empty] | Date: | 26-05-2026 | [28 empty] | Date: | 26-05-2026 | [28 empty] | Date: | 26-05-2026 | [17 empty] | Date: | 26-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 224 | 0 | 17 | 115 | 30 | 175 | 55 | 35 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 68 | 22 | 22 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 48 | 0 | 65 | 66 | 28 | 424 | 0 | 0 | 46 | 0 | 85 | 223 | 0 | 0 | 0 | 580 | 0 | 80 | 0 | 215 | 358 | 300 | 51 | 0 | 205 | 0 | 16 | 101 | 17 | 0 | 17 | 0 | 124 | 0 | 0 | 0 | 295 | 0 | 362 | 0 | 30 | 135 | 0 | 17 | 0 | 86 | 30 | 152 | 0 | 100 | 0 | 9 | 78 | 20 | 0 | 0 | 0 | 6402 | 821 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 585 | 4 | 0 | 0 | 1457 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 52 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 120 | 220 | 0 | 1245 | 1155 | 0 | 6936 | 13338 | 75.46
01:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 253 | 0 | 17 | 115 | 15 | 15 | 15 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 17 | 22 | 22 | 0 | 405 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 12 | 24 | 0 | 65 | 32 | 28 | 425 | 0 | 0 | 20 | 0 | 34 | 223 | 0 | 0 | 0 | 570 | 0 | 0 | 0 | 215 | 358 | 300 | 51 | 0 | 212 | 0 | 17 | 101 | 0 | 0 | 17 | 0 | 120 | 0 | 0 | 0 | 295 | 0 | 362 | 0 | 30 | 134 | 0 | 17 | 0 | 86 | 30 | 153 | 0 | 100 | 0 | 9 | 77 | 20 | 0 | 0 | 0 | 5789 | 795 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 586 | 17 | 0 | 0 | 1442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 52 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 120 | 220 | 0 | 1246 | 1070 | 0 | 6671 | 12460 | 75.46
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 287 | 0 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 17 | 23 | 21 | 0 | 490 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 31 | 420 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 513 | 0 | 0 | 0 | 215 | 358 | 300 | 51 | 0 | 215 | 0 | 0 | 101 | 0 | 0 | 17 | 0 | 114 | 0 | 0 | 0 | 290 | 0 | 344 | 0 | 30 | 126 | 0 | 17 | 0 | 86 | 30 | 152 | 0 | 100 | 0 | 9 | 77 | 22 | 0 | 0 | 0 | 5511 | 568 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 564 | 17 | 0 | 0 | 1183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244 | 120 | 220 | 0 | 1022 | 1025 | 0 | 5858 | 11369 | 75.47
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 269 | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 22 | 21 | 0 | 460 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 31 | 420 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 215 | 357 | 300 | 51 | 0 | 220 | 0 | 0 | 100 | 0 | 0 | 17 | 0 | 114 | 0 | 0 | 0 | 295 | 0 | 344 | 0 | 30 | 134 | 0 | 17 | 0 | 86 | 30 | 150 | 0 | 102 | 0 | 9 | 16 | 23 | 0 | 0 | 0 | 5321 | 569 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 447 | 0 | 0 | 0 | 1015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 140 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 120 | 220 | 0 | 900 | 940 | 0 | 5218 | 10539 | 75.47
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 198 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 375 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 31 | 420 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 220 | 335 | 265 | 51 | 0 | 166 | 0 | 0 | 90 | 0 | 0 | 17 | 0 | 112 | 0 | 0 | 0 | 285 | 0 | 344 | 0 | 30 | 128 | 0 | 17 | 0 | 86 | 30 | 152 | 0 | 101 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 4843 | 569 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 140 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 100 | 180 | 0 | 744 | 800 | 0 | 4544 | 9387 | 75.48
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 5 | 360 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 215 | 300 | 230 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 17 | 0 | 98 | 0 | 0 | 0 | 240 | 0 | 270 | 0 | 30 | 126 | 0 | 0 | 0 | 0 | 30 | 152 | 0 | 103 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 4105 | 343 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 140 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 100 | 180 | 0 | 600 | 700 | 0 | 3942 | 8047 | 75.48
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 18.5 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0.3 | 35 | 0 | 5 | 300 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 310 | 1 | 0 | 0 | 215 | 300 | 115 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 68 | 0 | 5 | 0 | 240 | 0 | 295 | 0 | 30 | 133 | 0 | 0 | 0 | 0 | 30 | 154 | 0 | 101 | 0 | 0 | 0 | 5 | 0.07 | 0.14 | 0 | 3966.01 | 441 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.45 | 386 | 0 | 0 | 0 | 826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 43 | 0 | 140 | 0 | 0 | 0 | 250 | 0 | 0.01 | 0 | 48 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 12 | 0.01 | 0 | 143 | 100 | 180 | 0 | 529 | 500 | 0 | 3781.73 | 7747.74 | 75.49
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 1 | 0 | 18 | 10 | 0 | 335 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 1.03 | 35 | 0 | 5 | 300 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 310 | 4 | 0 | 0 | 215 | 300 | 120 | 0 | 0 | 194 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 48 | 0 | 2 | 0 | 250 | 0 | 319 | 0 | 30 | 125 | 0 | 0 | 0 | 0 | 30 | 151 | 0 | 102 | 0 | 0 | 0 | 5 | 0.5 | 5.4 | 0 | 4037.93 | 588 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 385 | 0 | 0 | 0 | 828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.64 | 13 | 0 | 0 | 9 | 43 | 0 | 140 | 0 | 0 | 0 | 260 | 0 | 0.26 | 0 | 51 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 48 | 0.13 | 0 | 145 | 100 | 180 | 0 | 500 | 540 | 0 | 4047.03 | 8084.96 | 75.49
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 10 | 0 | 18 | 22 | 0 | 415 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 2.12 | 35 | 0 | 5 | 310 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 311 | 9 | 0 | 0 | 215 | 300 | 120 | 0 | 0 | 207 | 0 | 0 | 50 | 0 | 0 | 3 | 0 | 72 | 0 | 1 | 0 | 290 | 0 | 319 | 0 | 30 | 130 | 0 | 0 | 0 | 0 | 30 | 152 | 0 | 101 | 0 | 0 | 0 | 46 | 0.55 | 8.15 | 0 | 4338.82 | 784 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 385 | 0 | 0 | 0 | 850 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.18 | 38 | 0 | 0 | 11.26 | 43 | 0 | 140 | 0 | 0 | 0 | 260 | 0 | 1.39 | 0 | 51 | 0 | 13 | 0 | 0 | 0 | 0 | 1 | 68 | 0.11 | 0 | 140 | 100 | 180 | 0 | 500 | 560 | 0 | 4413.94 | 8752.76 | 75.5
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 11 | 0 | 20 | 22 | 0 | 530 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1.36 | 65 | 0 | 5 | 360 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 312 | 10 | 0 | 0 | 310 | 320 | 120 | 2 | 0 | 203 | 0 | 0 | 100 | 0 | 0 | 3 | 0 | 72 | 0 | 1 | 0 | 295 | 0 | 319 | 0 | 30 | 151 | 1 | 0 | 0 | 22 | 30 | 151 | 0 | 101 | 0 | 0 | 0 | 30 | 1.33 | 28.78 | 0 | 4737.47 | 447 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 390 | 0 | 0 | 0 | 827.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.11 | 59 | 0 | 0 | 18.69 | 43 | 0 | 157 | 0 | 0 | 0 | 414 | 0 | 1.55 | 0 | 49 | 0 | 7 | 0 | 0 | 0 | 0 | 2.9 | 138 | 0.04 | 0 | 140 | 120 | 220 | 0 | 500 | 560 | 0 | 4431.73 | 9169.2 | 75.5
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 240 | 0 | 0 | 12 | 0 | 20 | 22 | 0 | 310 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 5 | 360 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 312 | 17 | 0 | 0 | 290 | 310 | 120 | 10 | 0 | 189 | 0 | 0 | 102 | 0 | 0 | 9 | 0 | 72 | 0 | 3 | 0 | 295 | 0 | 320 | 0 | 30 | 146 | 4 | 0 | 0 | 22 | 30 | 154 | 0 | 101 | 0 | 0 | 0 | 27 | 0.49 | 20.66 | 0 | 4434.15 | 731 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 376 | 0 | 0 | 0 | 825.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.58 | 61 | 0 | 0 | 7.59 | 47 | 0 | 186 | 0 | 0 | 0 | 300 | 0 | 0.22 | 0 | 50 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 127 | 0.41 | 0 | 140 | 120 | 180 | 0 | 500 | 560 | 0 | 4511.7 | 8945.85 | 75.51
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 280 | 0 | 0 | 5 | 0 | 20 | 22 | 0 | 345 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0.14 | 67 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 305 | 18 | 0 | 0 | 300 | 280 | 120 | 10 | 0 | 207 | 0 | 0 | 100 | 0 | 0 | 9 | 0 | 88 | 0 | 24 | 0 | 250 | 0 | 320 | 0 | 30 | 140 | 5 | 0 | 0 | 5 | 30 | 153 | 0 | 101 | 0 | 0 | 0 | 27 | 0.2 | 3.89 | 0 | 4530.23 | 922 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 381 | 0 | 0 | 0 | 825.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.41 | 15 | 0 | 0 | 2.17 | 49 | 0 | 150 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 51 | 0 | 7 | 0 | 0 | 0 | 0 | 4.7 | 38 | 0.24 | 0 | 140 | 120 | 180 | 0 | 530 | 500 | 0 | 4554.2 | 9084.43 | 75.51
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 240 | 0 | 0 | 2 | 0 | 0 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 2.17 | 67 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 310 | 17 | 0 | 0 | 220 | 280 | 90 | 0 | 0 | 140 | 0 | 0 | 70 | 0 | 0 | 9 | 0 | 88 | 0 | 14 | 0 | 265 | 0 | 300 | 0 | 10 | 139 | 2 | 0 | 0 | 0 | 30 | 135 | 0 | 101 | 0 | 0 | 0 | 29 | 0.9 | 8.09 | 0 | 4050.16 | 750 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 376 | 0 | 0 | 0 | 823.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.14 | 100 | 0 | 0 | 8.65 | 48 | 0 | 130 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 50 | 0 | 36 | 0 | 0 | 0 | 0 | 6.9 | 108 | 0.49 | 0 | 140 | 100 | 180 | 0 | 530 | 500 | 0 | 4399.06 | 8449.22 | 75.51
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 1.19 | 67 | 0 | 12 | 230 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 308 | 17 | 0 | 0 | 220 | 280 | 0 | 0 | 0 | 140 | 0 | 0 | 50 | 0 | 0 | 9 | 0 | 102 | 0 | 1 | 0 | 240 | 0 | 240 | 0 | 10 | 137 | 0 | 0 | 0 | 0 | 30 | 139 | 0 | 101 | 0 | 0 | 0 | 36 | 1 | 1.78 | 0 | 3771.97 | 681 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.31 | 371 | 0 | 0 | 0 | 840.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.6 | 13 | 0 | 0 | 4.54 | 46 | 0 | 130 | 0 | 0 | 0 | 250 | 0 | 1.45 | 0 | 50 | 0 | 19 | 0 | 0 | 0 | 0 | 7.9 | 14 | 0.47 | 0 | 140 | 100 | 180 | 0 | 530 | 500 | 0 | 4073.47 | 7845.44 | 75.51
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 260 | 0 | 0 | 1 | 0 | 14 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0.81 | 69 | 0 | 26 | 215 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 220 | 270 | 0 | 0 | 0 | 202 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 66 | 0 | 24 | 0 | 240 | 0 | 234 | 0 | 10 | 127 | 0 | 0 | 0 | 0 | 30 | 140 | 0 | 101 | 0 | 0 | 0 | 42 | 1.56 | 2.78 | 0 | 3824.15 | 923 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.34 | 373 | 0 | 0 | 0 | 817.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.45 | 26 | 0 | 0 | 32.23 | 46 | 0 | 130 | 0 | 0 | 0 | 343 | 0 | 2.9 | 0 | 50 | 0 | 30 | 0 | 0 | 0 | 0 | 7.1 | 176 | 0.01 | 0 | 140 | 100 | 180 | 0 | 530 | 500 | 0 | 4594.44 | 8418.59 | 75.51
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 280 | 0 | 0 | 2 | 0 | 0 | 14 | 0 | 458 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0.97 | 69 | 0 | 26 | 215 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 307 | 7 | 0 | 0 | 240 | 300 | 0 | 0 | 0 | 202 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 82 | 0 | 2 | 0 | 250 | 0 | 268 | 0 | 10 | 130 | 1 | 0 | 0 | 0 | 20 | 138 | 0 | 101 | 0 | 0 | 0 | 42 | 1.32 | 21.65 | 0 | 4059.94 | 923 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 375 | 0 | 0 | 0 | 841.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.79 | 25 | 0 | 0 | 17.09 | 47 | 0 | 130 | 0 | 0 | 0 | 384 | 0 | 1.57 | 0 | 50 | 0 | 24 | 0 | 0 | 0 | 0 | 1.2 | 142 | 0.01 | 0 | 140 | 100 | 180 | 0 | 482 | 500 | 0 | 4594.75 | 8654.69 | 75.51
16:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 326 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 280 | 0 | 0 | 6 | 0 | 11 | 14 | 0 | 470 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0.42 | 70 | 0 | 26 | 215 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 307 | 3 | 0 | 0 | 240 | 300 | 0 | 0 | 0 | 200 | 0 | 0 | 51 | 0 | 0 | 10 | 0 | 90 | 0 | 1 | 0 | 270 | 0 | 308 | 0 | 10 | 142 | 1 | 0 | 0 | 0 | 20 | 137 | 0 | 101 | 0 | 0 | 0 | 54 | 0.77 | 13.66 | 0 | 4302.85 | 923 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 368 | 0 | 0 | 0 | 611.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.29 | 39 | 0 | 0 | 11.52 | 47 | 0 | 157 | 0 | 0 | 0 | 385 | 0 | 1.01 | 0 | 50 | 0 | 11 | 0 | 0 | 0 | 0 | 4.2 | 91 | 0.04 | 0 | 170 | 100 | 180 | 0 | 500 | 540 | 0 | 4440.23 | 8743.08 | 75.51
17:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 320 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 333 | 0 | 0 | 3 | 0 | 11 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0.04 | 70 | 0 | 23 | 195 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 307 | 2 | 0 | 0 | 345 | 320 | 0 | 0 | 0 | 205 | 0 | 0 | 51 | 0 | 0 | 10 | 0 | 94 | 0 | 3 | 0 | 270 | 0 | 309 | 0 | 10 | 145 | 1 | 0 | 0 | 0 | 20 | 137 | 0 | 101 | 0 | 0 | 0 | 72 | 0.4 | 3.73 | 0 | 4547.17 | 923 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 368 | 0 | 0 | 0 | 449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.46 | 28 | 0 | 0 | 8.76 | 30 | 0 | 172 | 0 | 0 | 0 | 410 | 0 | 0.65 | 0 | 50 | 0 | 8 | 0 | 0 | 0 | 0 | 2.4 | 20 | 0.1 | 0 | 172 | 100 | 220 | 0 | 500 | 580 | 0 | 4311.37 | 8858.54 | 75.51
18:00 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 330 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 335 | 0 | 0 | 1 | 0 | 11 | 14 | 0 | 470 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0.02 | 70 | 0 | 16 | 221 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 365 | 0 | 0 | 8 | 337 | 349 | 0 | 1 | 1 | 202 | 0 | 0 | 50 | 0 | 0 | 5 | 0 | 96 | 0 | 3 | 0 | 290 | 0 | 309 | 0 | 30 | 154 | 0 | 16 | 0 | 5 | 20 | 138 | 0 | 101 | 0 | 0 | 0 | 73 | 0.14 | 3.01 | 0 | 4779.17 | 923 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6 | 371 | 0 | 0 | 0 | 483.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.96 | 7 | 0 | 0 | 2.95 | 31 | 0 | 180 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 50 | 0 | 2 | 0 | 0 | 0 | 0 | 0.6 | 9 | 0 | 0 | 193 | 100 | 220 | 0 | 562 | 651 | 0 | 4420.59 | 9199.76 | 75.51
19:00 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 335 | 0 | 345 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 13 | 11 | 14 | 0 | 515 | 0 | 0 | 0 | 0 | 6 | 50 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 16 | 355 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 540 | 0 | 0 | 16 | 362 | 362 | 0 | 25 | 10 | 218 | 23 | 0 | 102 | 0 | 0 | 5 | 0 | 116 | 0 | 0 | 0 | 305 | 0 | 330 | 0 | 30 | 141 | 0 | 16 | 0 | 86 | 30 | 150 | 0 | 101 | 0 | 9 | 16 | 85 | 0 | 0 | 0 | 5699 | 923 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 468.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 169 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 49 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 120 | 220 | 0 | 800 | 880 | 0 | 5037.37 | 10736.37 | 75.51
19:30 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 318 | 0 | 270 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 35 | 7 | 14 | 0 | 442 | 0 | 0 | 0 | 0 | 2 | 50 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 22 | 355 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 580 | 0 | 0 | 35 | 331 | 360 | 0 | 51 | 12 | 200 | 25 | 0 | 102 | 0 | 0 | 5 | 0 | 106 | 0 | 0 | 0 | 305 | 0 | 368 | 0 | 30 | 146 | 0 | 16 | 0 | 86 | 30 | 150 | 0 | 101 | 0 | 9 | 55 | 87 | 0 | 0 | 0 | 5657 | 923 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425 | 0 | 0 | 0 | 472.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 175 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 50 | 35 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 120 | 220 | 0 | 1000 | 1020 | 0 | 5470.53 | 11127.53 | 75.51
20:00 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 324 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 44 | 10 | 14 | 0 | 325 | 0 | 0 | 0 | 0 | 14 | 50 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 42 | 420 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 580 | 0 | 0 | 55 | 320 | 360 | 0 | 51 | 17 | 195 | 30 | 0 | 102 | 0 | 0 | 5 | 0 | 106 | 0 | 0 | 0 | 300 | 0 | 374 | 0 | 30 | 139 | 0 | 16 | 0 | 83 | 30 | 150 | 0 | 101 | 0 | 9 | 75 | 86 | 0 | 0 | 0 | 5605 | 924 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 431.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 168 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 50 | 45 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 120 | 220 | 0 | 1000 | 1059 | 0 | 5498.75 | 11103.75 | 75.51
21:00 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 346 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 13 | 14 | 0 | 490 | 0 | 0 | 0 | 0 | 57 | 50 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 42 | 385 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 580 | 0 | 0 | 71 | 336 | 361 | 0 | 51 | 20 | 202 | 36 | 0 | 102 | 0 | 0 | 8 | 0 | 104 | 0 | 0 | 0 | 300 | 0 | 380 | 0 | 30 | 139 | 0 | 16 | 0 | 83 | 30 | 150 | 0 | 101 | 0 | 9 | 45 | 100 | 0 | 0 | 0 | 5913 | 923 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 0 | 0 | 0 | 425.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 164 | 0 | 0 | 0 | 399 | 0 | 0 | 0 | 50 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 120 | 220 | 0 | 732 | 974 | 0 | 5251.63 | 11164.63 | 75.51
22:00 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 381 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 13 | 14 | 0 | 485 | 0 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 42 | 380 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 580 | 0 | 0 | 73 | 336 | 361 | 0 | 51 | 20 | 200 | 39 | 0 | 102 | 0 | 0 | 8 | 0 | 106 | 0 | 0 | 0 | 305 | 0 | 381 | 0 | 30 | 153 | 0 | 16 | 0 | 83 | 30 | 150 | 0 | 101 | 0 | 9 | 45 | 95 | 0 | 0 | 0 | 5954 | 923 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 446.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 175 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 50 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 120 | 220 | 0 | 700 | 990 | 0 | 5243.74 | 11197.74 | 75.51
23:00 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 381 | 0 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 14 | 18 | 0 | 485 | 0 | 0 | 0 | 0 | 9 | 43 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 42 | 380 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 580 | 0 | 0 | 73 | 335 | 360 | 0 | 51 | 20 | 200 | 39 | 0 | 102 | 0 | 0 | 16 | 0 | 108 | 0 | 0 | 0 | 300 | 0 | 381 | 0 | 30 | 150 | 0 | 16 | 0 | 83 | 30 | 150 | 0 | 102 | 0 | 9 | 45 | 97 | 0 | 0 | 0 | 5914 | 923 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 415.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 172 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 50 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 120 | 220 | 0 | 700 | 970 | 0 | 5173.41 | 11087.41 | 75.51
Total KWH | 0 | 68160 | 0 | 0 | 0 | 1264625 | 0 | 0 | 8175600 | 0 | 7250098 | 21600 | 18720 | 356400 | 21120 | 112.41 | 42965 | 6108 | 69120 | 0 | 0 | 883200 | 0 | 0 | 0 | 7123521 | 0 | 0 | 63514 | 199200 | 344400 | 361440 | 0 | 9845000 | 0 | 0 | 0 | 0 | 490560 | 249737 | 0 | 0 | 14400 | 40320 | 9344 | 1515020 | 69418 | 654720 | 7992727.27 | 0 | 0 | 46560 | 0 | 94509 | 5017469 | 0 | 0 | 0 | 9714544 | 83565 | 45163 | 317818 | 6584000 | 8110100 | 2414000 | 595744 | 110400 | 4823000 | 183600 | 25920 | 1877945 | 5760 | 0 | 206530 | 0 | 2166720 | 0 | 81127 | 0 | 6768000 | 0 | 7893000 | 0 | 602880 | 3328936.36 | 17558 | 172128 | 0 | 861120 | 673440 | 3451300 | 0 | 2430000 | 0 | 79200 | 472800 | 1015680 | 8850 | 118470 | 0 | 117548986.04 | 18429091 | 6005952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58608 | 427680 | 96872745 | 37920 | 0 | 0 | 18518181 | 0 | 0 | 0 | 0 | 11808 | 0 | 0 | 0 | 0 | 113744 | 381760 | 0 | 0 | 163056 | 2049091 | 0 | 3945127 | 0 | 0 | 0 | 8326836 | 0 | 11640 | 0 | 1214399 | 258574 | 170674 | 318038 | 0 | 0 | 0 | 38532.12 | 936000 | 1773 | 0 | 4124000 | 2852000 | 5152170 | 0 | 16414545 | 18192000 | 0 | 205025944.12 | 322574930.16

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 26-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 9169.2 | MW | 09:00 Hr. | Energy Generated |  |  | 322.5749 |  | MKWHr.
| Day Peak Demand |  |  | 9169.2 | MW | 09:00 Hr. | Energy Unserverd |  |  | 0.078 |  | MKWHr.
| Evening Peak Generation |  |  | 11164.63 | MW | 21:00 Hr. | Energy Demand |  |  | 322.6529 |  | MKWHr.
| Evening Peak Demand |  |  | 11169.63 | MW | 21:00 Hr. | Maximum Temperature |  |  | 28.9 |  | °C
| Minimum Generation of the Day |  |  | 7747.74 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 918.21 |  | MMCFD
| Maximum Generation of the Day |  |  | 13338 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.6789 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 35.2479 | 0 | 0.80351 | 0 | 0 | 0.063514 | 0 | 0 | 36.1149 | Gas | 121.6709 | Gas | 426588545.6712
| Chattogram Zone |  |  | 5.6722 | 17.7073 | 0.51494 | 0 | 1.515 | 0.092909 | 0 | 0.49056 | 25.9929 | Coal | 154.525 | Coal | 1095442798.5631
| Cumilla Zone |  |  | 25.2231 | 0 | 0.076843 | 0 | 0 | 0.081127 | 2.1667 | 0 | 27.5478 | HFO | 2.6322 | HFO | 43601400.1779
| Mymensingh Zone |  |  | 1.0157 | 0 | 0.552 | 0 | 0 | 0.12732 | 0 | 0 | 1.695 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.1808 | 0 | 0 | 0 | 0 | 0.017558 | 0 | 0 | 26.1984 | Hydro | 1.515 | Hydro | 151502
| Khulna Zone |  |  | 6.006 | 96.8727 | 0.096528 | 0 | 0 | 0.42768 | 18.4291 | 0 | 121.832 | Solar | 2.6273 | Solar | 44376737.5024
| Barishal Zone |  |  | 8.0042 | 38.7305 | 0 | 0 | 0 | 0.001773 | 0 | 0 | 46.7365 | Import | 39.114 | Import | 214503905.72
| Rajshahi Zone |  |  | 14.3211 | 0 | 0.011808 | 0 | 0 | 0.6702 | 18.5182 | 0 | 33.5212 | Wind | 0.49056 | Wind | 7216137.6
| Rangpur Zone |  |  | 0 | 1.2144 | 0.57661 | 0 | 0 | 1.1452 | 0 | 0 | 2.9362
| Total |  |  | 121.6709 | 154.525 | 2.6322 | 0 | 1.515 | 2.6273 | 39.114 | 0.49056 | 322.5749
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 426588545.6712 |  | Hydro | 151502
|  |  |  | Coal | 1095442798.5631 |  | Solar | 44376737.5024
|  |  |  | HFO | 43601400.1779 |  | Import | 214503905.72
|  |  |  | HSD | 0 |  | Wind | 7216137.6
[5 empty] | Total: | 183,18,81,027 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 18.4291 | Peak Hr Flow | 923.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 27932000 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 18.5182 | Peak Hr Flow | 425.63 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1119 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.1667 | Peak Hr Flow | 104.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2448 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 39.114 | Peak Hr Flow | 1452.63 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3336
|  |  |  | Chattogram |  | 5 |  | 1189
|  |  |  | Cumilla |  | 0 |  | 1073
|  |  |  | Mymensingh |  | 0 |  | 908
|  |  |  | Sylhet |  | 0 |  | 449
|  |  |  | Khulna |  | 0 |  | 1491
|  |  |  | Barishal |  | 0 |  | 330
|  |  |  | Rajshahi |  | 0 |  | 1258
|  |  |  | Rangpur |  | 0 |  | 874
|  |  |  | Total |  | 5 |  | 10908
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:30 | Saidpur 132/33kV S/S TR-3 (424T) HT is restored.
|  | 08:31 | Saidpur 132/33kV S/S TR-3 (424T) LT is restored.
| 08:32 | 10:32 | Noapara 132/33kV S/S T-2 LT Scheduled S/D | [7 empty] | 5.0MW load
interrup.
| 08:32 | 10:31 | Noapara 132/33kV S/S T-2 HT Scheduled S/D | [7 empty] | 5.0MW load
interrup.
| 08:36 | 10:36 | Noapara 132/33kV S/S Bus Section-2 Scheduled S/D | [7 empty] | 5.0MW load
interrup.
|  | 08:45 | Narail 132/33kV S/S TR2 (413-T) HT is restored.
|  | 08:46 | Narail 132/33kV S/S TR2 (413-T) LT is restored.
| 09:00 |  | Day Peak Generation: 9165 MW.
| 09:01 | 10:54 | Hathazari-Madunaghat 132kV Ckt-2 Tripped from Hathazari 230/132/33kV end showing Alstrom
Quardrahmo relays.
|  | 09:07 | Bogura 230/132kV S/S Confidance UN-2 is restored.
| 09:13 | 09:26 | Niamatpur 132/33kV S/S Transformer-2 (417T) HT Tripped showing MiCOM P40 Agile (P642) | [7 empty] | 1.0MW load
|  |  | relays Due to Due to Niamatpur 33 kV faulty feeder trip | [7 empty] | interrup.
| 09:13 | 09:27 | Niamatpur 132/33kV S/S Transformer-2 (417T) LT Tripped showing MiCOM P40 Agile (P642) | [7 empty] | 1.0MW load
|  |  | relays Due to Due to Niamatpur-2 33kV faulty feeder trip | [7 empty] | interrup.
| 09:15 | 10:52 | Daganbhuiyan 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Red hot maintenance at
33kv daganbhuiyan feeder
| 09:15 | 10:52 | Daganbhuiyan 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Shutdown Due to 33 kv
Daganbhuiyan Feeder red hot maintenance
| 09:16 | 11:08 | Narail 132/33kV S/S TR1 (403-T) HT Scheduled S/D Due to Red hot maintenance by JPBS-02 | [7 empty] | 30.0MW load
interrup.
| 09:16 | 11:08 | Narail 132/33kV S/S TR1 (403-T) LT Scheduled S/D Due to Red Hot maintenance N3 and N4 | [7 empty] | 30.0MW load
|  |  | feeder by JPBS-02 | [7 empty] | interrup.
| 09:40 | 11:08 | Juldah-Sikalbaha 132kV Ckt-1 Tripped from Juldah 132/33kV end showing Distance relay | [7 empty] | 21.0MW load
|  |  | relays Due to Lightning strike | [7 empty] | interrup. Juldah
132/33kV end
| 09:50 | 10:08 | Niamatpur 132/33kV S/S Transformer-3(426T) LT Tripped showing Siemens 7UT85 relays Due to | [7 empty] | 2.0MW load
|  |  | Due to Manda-1 33kV faulty feeder trip. | [7 empty] | interrup.
|  | 10:05 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) HT is restored.
|  | 10:05 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) LT is restored.
| 10:10 | 10:34 | Khagrachari-Rangamati 132kV Ckt-2 Tripped from Khagrachori 132/33kV end showing REL 670
relays Due to Tripped due to Thundering
|  | 10:37 | Bogura 400/230kV S/S Bogura - Naogaon 230 kV Ckt-2 is restored.
| 10:49 | 11:32 | Tangail 132/33kV S/S Tr-1 LT Tripped showing REF 615 relays Due to 33kv kachuadanga | [7 empty] | 47.0MW load
|  |  | feeder source DS Loop Out from 33kv Bus. | [7 empty] | interrup.
| 10:49 | 13:44 | Tangail 132/33kV S/S Tr-2 LT Tripped showing Ref615 relays Due to 33Kv kachuadanga Feeder | [7 empty] | 47.0MW load
|  |  | source DS loop out from 33Kv bus. | [7 empty] | interrup.
| 11:12 | 12:22 | BIPTC S/S 20DF13 Scheduled S/D Due to Emergency maintenance
| 11:55 | 12:11 | Chowmuhani 230/132/33kV S/S TR3-435T LT Tripped showing O/C relays Due to 33 KV Datter | [7 empty] | 20.0MW load
|  |  | Hat Feeder Fault | [7 empty] | interrup.
| 11:55 | 12:11 | Chowmuhani 230/132/33kV S/S TR2-425T LT Tripped showing O/C relays Due to 33 KV Datter | [7 empty] | 20.0MW load
|  |  | Hat Feeder Fault | [7 empty] | interrup.
| 12:03 | 13:08 | Jhenaidah 132/33kV S/S Transformer T-2 LT Forced S/D Due to 33kV WZPDCL kotchadpur feeder | [7 empty] | 50.0MW load
|  |  | DS bus side Red hot Maintenance. | [7 empty] | interrup.
| 12:05 | 21:22 | Aminbazar-Meghnaghat 400kV Ckt-2 Forced S/D from Aminbazar 400/230/132kV end Due to DS
maintenance Work
| 12:05 | 13:06 | Jhenaidah 132/33kV S/S Transformer T-2 HT Forced S/D Due to 33kV WZPDCL kotchadpur feeder
DS bus side Red hot Maintenance.
| 12:14 |  | Hasnabad-Keraniganj 230kV Ckt-2 Tripped from Keranigonj 230/132/33kV end showing
86.1/86.2 relays Due to SOTF trip,B-phase pick up, and from Hasnabad 230/132kV end
showing Dist: Prot: 1&2 relays Due to Flashing during heavy raining
| 12:14 |  | Hasnabad-Keraniganj 230kV Ckt-2 Tripped from Keranigonj 230/132/33kV end showing
86.1/86.2 relays Due to SOTF trip,B-phase pick up, and from Hasnabad 230/132kV end
showing Dist: Prot: 1&2 relays Due to Flashing during heavy raining
| 12:17 | 13:14 | Keraniganj-Nawabganj 132kV Ckt-2 Tripped from Keranigonj 230/132/33kV end showing 86.1
relays Due to 50-67N Earth fault trip,R-phase pick up,Zone-1 trip(16.3km) and from
Nawabganj 132/33kV end showing Distance protection P443, Overcurrent protection P132
relays Due to Due to heavy storm
| 12:17 | 12:39 | Rajendrapur 132/33kV S/S MTR-1 LT Tripped showing REF630 relays.
| 12:17 | 12:40 | Rajendrapur 132/33kV S/S MTR-2 LT Tripped showing REF630 relays. | [7 empty] | 2.0MW load
interrup.
| 12:17 | 12:40 | Rajendrapur 132/33kV S/S MTR-3 LT Tripped showing REF630 relays. | [7 empty] | 2.0MW load
interrup.
| 12:20 | 13:44 | Tangail 132/33kV S/S Tr-2 LT Forced S/D Due to Kachuadanga feder Fault | [7 empty] | 100.0MW load
interrup.
| 12:20 | 13:43 | Tangail 132/33kV S/S Tr-2 HT Forced S/D Due to 33Kv Kachuadanga feeder Fault | [7 empty] | 100.0MW load
interrup.
| 12:26 |  | Ashuganj 450 MW CCPP(South) Shutdown with remarks:- GT
|  | 12:50 | Cumilla(N) 230/132/33kV S/S 230KV ATR-02 HT is restored.
|  | 12:58 | Ghorasal- Ishwardi 230 kV Ckt-2 is restored.
| 13:34 | 13:39 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing Instt. O/C, Definite O/C relays Due | [7 empty] | 40.0MW load
|  |  | to Polashpur 33kV WZPDCL feeder fault | [7 empty] | interrup.
| 13:37 | 14:17 | Bakerganj-Patuakhali 132 kV Ckt-1 Tripped from Patuakhali 132/33kV end showing Distance | [7 empty] | 30.0MW load
|  |  | Relay relays Due to E/F, Phase -C, 27.4 km, 3.3kA | [7 empty] | interrup.
Patuakhali 132/33kV
end
| 13:46 | 21:20 | Aminbazar-Meghnaghat 400kV Ckt-2 Forced S/D from Meghnaghat 400/230kV end Due to
Requested by Aminbazar SS
|  | 14:18 | Brahmanbaria-Shahjibazar 132 kV Ckt-1 is restored.
| 14:21 | 20:40 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end. and from
Shahjibazar 132/33kV end Due to N/A
|  | 14:35 | Joypurhat 132/33kV S/S Patnitola Ckt.-1 is restored.
|  | 14:37 | Joypurhat 132/33kV S/S Patnitola Ckt.-2 is restored.
|  | 14:39 | Daganbhuiyan 132/33kV S/S Transformer-2 LT is restored.
| 14:39 | 20:09 | Daganbhuiyan 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Bus PT change at
Companiganj 33 kv feeder
| 15:15 | 18:55 | Madanganj 132/33kV S/S BUS Coupler Forced S/D Due to Haripur-1 Main bus DS emergency
maintenance
| 15:32 |  | Ghorasal Repowered CCPP Unit-4 Synchronized
| 15:52 | 16:49 | TK chemical S/S 48/64MVA T-2(415T) HT Forced S/D Due to “Due to sparking fault at the | [7 empty] | 14.0MW load
|  |  | connector of Transformer-2 secondary blue bushing.” | [7 empty] | interrup.
| 15:52 | 16:49 | TK chemical S/S 48/64MVA T-2(415T) HT Forced S/D Due to “Due to sparking fault at the | [7 empty] | 14.0MW load
|  |  | connector of Transformer-2 secondary blue bushing.” | [7 empty] | interrup.
| 16:30 |  | Adani Power Jharkhand Ltd. Unit-1 was shutdown due to low demand.
|  | 17:16 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 is restored.
|  | 17:16 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 is restored.
| 17:36 | 05:54 | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D Due to As per NLDC's
Instruction
| 19:13 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- ST
| 19:43 | 22:18 | Chowmuhani 230/132/33kV S/S TR3-435T LT Forced S/D Due to Redhot | [7 empty] | 10.0MW load
interrup.
| 19:44 | 22:18 | Chowmuhani 230/132/33kV S/S TR3-435T HT Forced S/D Due to Redhot | [7 empty] | 10.0MW load
interrup.
| 20:25 | 21:03 | Bhangura 132/33kV S/S Tr-2(413T) LT Forced S/D Due to Red hot 33 kv bkr
| 20:26 | 21:02 | Bhangura 132/33kV S/S Tr-2(413T) HT Forced S/D Due to Red hot 33 kv bkr
| 21:00 |  | Evening Peak Generation is 11164 MW.
| 23:25 | 00:46 | Chowmuhani 230/132/33kV S/S TR2-425T HT Forced S/D Due to Emergency shutdown taken for | [7 empty] | 20.0MW load
|  |  | 132/33 kV, TR-02 X-former today at 18:07 for 33kV LBUS BUS DS loop Redhot Maintenance. | [7 empty] | interrup.
20MW Load shed will occur. Informed all utilities. NPBS will do the maintenance work.
| 23:25 | 00:46 | Chowmuhani 230/132/33kV S/S TR2-425T LT Forced S/D Due to Emergency shutdown taken for | [7 empty] | 20.0MW load
|  |  | 132/33 kV, TR-02 X-former today at 18:07 for 33kV LBUS BUS DS loop Redhot Maintenance. | [7 empty] | interrup.
20MW Load shed will occur. Informed all utilities. NPBS will do the maintenance work.
| 00:56 | 01:37 | Lalmonirhat-Rangpur 132 kV Ckt-2 Forced S/D from Kurigram 132/33kV end Due to Emergency
tree trimming
| 01:05 | 01:37 | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat Forced S/D Due to Kurigram grid work
| 05:35 |  | Bogura 230/132kV S/S Confidance UN-2 Tripped showing over voltage trip relays Due to
Raining, Storming, Thundering
| 05:42 |  | Bogura 230/132kV S/S T-03 LT Tripped showing Over Voltage relays Due to Raining,
Storming, Thundering
| 05:42 |  | Bogura 230/132kV S/S T-03 HT Tripped showing None relays Due to Raining, Storming,
Thundering
| 06:05 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 Tripped showing Main-1 and Main-2
relays Due to Directional Earth Fault
| 06:07 |  | Ghorasal- Ishwardi 230 kV Ckt-2 Tripped from Ishurdi 230/132kV end showing Distance
protection Relay relays.
| 06:57 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- ST
| 06:58 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized with remarks:- GT-(False sms)
|  | 07:10 | Rampal 400/230kV S/S Gopalganj Line-1 Reactor is restored.
|  | 07:12 | Rampal 400/230kV S/S Gopalganj Line-2 Reactor is restored.
| 07:21 |  | Ghorasal Repowered CCPP Unit-4 Shutdown
| 07:48 |  | Khulna (C) S/S TR-1 425T LT Tripped showing Siprotec multifunctional relay relays Due to
Due to wz tr-4 feeder fault
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 26-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 170 | 1264625 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 346 | 8175600 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 139 | 883200 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 42965 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7123521 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 21600 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 21120 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 6108 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 13 | 344400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 361440 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 112.41 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 356400 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 68160 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 69120 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 63514 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 18720 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 490 | 9845000 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 309 | 7250098 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 17 | 199200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1833 | 36114903.41
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 83565 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 46560 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1515020 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 222 | 5017469 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 94509 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 249737 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 14400 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 42 | 654720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 9344 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 69418 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 40320 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 580 | 9714544 | U2 outage added
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 57 | 490560 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 385 | 7992727.27 | U1 under maintenance
Chattogram Area Total |  |  |  |  | 4898.863 | 1406 | 25992893.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 202 | 4823000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 361 | 8110100 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 0 | 2414000 | ST Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 336 | 6584000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 36 | 183600 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 20 | 110400 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 71 | 317818 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 595744 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 45163 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 102 | 1877945 | ST Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 5760 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 104 | 2166720 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 8 | 206530 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 25920 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 81127 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1291 | 27547827
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 100 | 1015680 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8850 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 45 | 472800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 79200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 118470 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 154 | 1695000
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 17558 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 602880 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 139 | 3328936.36 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 150 | 3451300 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 673440 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 861120 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2430000 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 172128 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 6768000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 380 | 7893000 | FGMO not available because of Cooling Tower Fan
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1229 | 26198362.36
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 923 | 18429091 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 383 | 6005952 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 37920 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 58608 | FGMO
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 427680 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 434 | 96872745 | U1 under maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1740 | 121831996
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 732 | 16414545 | RRT
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2852000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 974 | 18192000 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5152170 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 185 | 4124000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1773 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2231 | 46736488
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 113744 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 158 | 2049091 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 164 | 3945127 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 399 | 8326836 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 11808 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 11640 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 425.63 | 18518181 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 163056 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 381760 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1146.63 | 33521243
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1214399 | Plant availability zero, U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 318038 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 38532.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 258574 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 170674 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 936000 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 134 | 2936217.12
Eastern Grid Total |  |  |  |  | 17418.042 | 5913 | 117548986.04
Western Grid Total |  |  |  |  | 11852.195 | 5251.63 | 205025944.12
National Grid Total |  |  |  |  | 29270.237 | 11164.63 | 322574930.16
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 26-05-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6950.47 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3953 | MW
i) Dhaka area |  |  | 3336.47 |  | MW | i) Khulna area |  |  |  | 1491 | MW
ii) Chattogram area |  |  | 1184 |  | MW | ii) Barishal area |  |  |  | 330 | MW
iii) Cumilla area |  |  | 1073 |  | MW | iii) Rajshahi area |  |  |  | 1258 | MW
iv) Mymensingh area |  |  | 908 |  | MW | iv) Rangpur area |  |  |  | 874 | MW
v) Sylhet area |  |  | 449 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10903.47 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 70 | 01:00 | 133 | Natore | 139 | 00:00
2 | AKSML | 127 | 00:00 | 68 | Hathazari | 79 | 00:00 | 134 | Nawabganj | 50 | 00:00
3 | Aftabnagar | 32 | 00:00 | 69 | Hatirjheel | 33 | 12:00 | 135 | Netrakona | 130 | 20:00
4 | Agargaon | 96 | 06:00 | 70 | Ishurdi | 77 | 00:00 | 136 | New | 51.4 | 00:00
5 | Agrabad | 64 | 23:00 | 71 | Jaldhaka | 84 | 19:30 | 137 | Niamatpur | 67 | 00:00
6 | Amnura | 32 | 00:00 | 72 | Jamalpur | 110 | 20:00 | 138 | Noapara | 47 | 00:00
7 | Ashuganj | 82 | 00:00 | 73 | Jashore | 178 | 00:00 | 139 | PHP | 10 | 14:00
8 | BSRM | 183 | 19:00 | 74 | Jhenaidah | 133 | 00:00 | 140 | Pabna | 92 | 00:00
9 | Bagerhat | 98 | 03:00 | 75 | Joydebpur | 101 | 00:00 | 141 | Palashbari | 98 | 00:00
10 | Bajitpur | 84 | 00:00 | 76 | Joypurhat | 51 | 20:00 | 142 | Panchagarh | 58 | 20:00
11 | Bakerganj | 12.4 | 00:00 | 77 | Juldah | 15.5 | 09:00 | 143 | Patiya | 12 | 21:00
12 | Bakulia | 80 | 00:00 | 78 | KSRM | 13 | 14:00 | 144 | Patuakhali | 82 | 01:00
13 | Banani | 26.6 | 11:00 | 79 | Kabirpur | 153 | 00:00 | 145 | Payra | 40 | 00:00
14 | Bangabhaban | 6 | 11:00 | 80 | Kachua | 98 | 02:00 | 146 | Postogola | 42 | 00:00
15 | Barapukuria | 59 | 19:30 | 81 | Kaliganj | 12 | 00:00 | 147 | Pubail | 21 | 00:00
16 | Barguna | 24 | 00:00 | 82 | Kallyanpur | 90 | 00:00 | 148 | Purbachal | 24 | 00:00
17 | Barishal | 113 | 00:00 | 83 | Kalurghat | 32 | 00:00 | 149 | Purbasadipur | 120 | 20:00
18 | Barishal-230 | 114 | 00:00 | 84 | Kamrangirchar | 56 | 00:00 | 150 | Rahanpur | 41 | 00:00
19 | Baroaulia | 58 | 00:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 0 | 00:00
20 | Baroirhat | 59 | 00:00 | 86 | Kasba | 31 | 21:00 | 152 | Rajbari | 78 | 01:00
21 | Bashundhara | 133 | 12:00 | 87 | Kazla | 88 | 01:00 | 153 | Rajendrapur | 93 | 00:00
22 | BashundharaCement | 6 | 00:00 | 88 | Keranigonj | 64 | 00:00 | 154 | Rajshahi | 108 | 00:00
23 | Beanibazar | 58 | 22:00 | 89 | Khagrachori | 28 | 19:00 | 155 | Rajshahi-230 | 86 | 00:00
24 | Benapole | 80 | 00:00 | 90 | Khulna | 70 | 12:00 | 156 | Ramganj | 98 | 00:00
25 | Bhaluka | 103 | 00:00 | 91 | Khulshi | 153 | 21:00 | 157 | Rampur | 38 | 00:00
26 | Bhandaria | 66 | 00:00 | 92 | Kishoreganj | 110 | 19:00 | 158 | Rangamati | 14 | 19:00
27 | Bhangura | 32 | 00:00 | 93 | Kodda | 214 | 00:00 | 159 | Rangpur | 124 | 21:00
28 | Bheramara(GK) | 67 | 00:00 | 94 | Kulaura | 36 | 19:00 | 160 | Ruppur | 3 | 09:00
29 | Bhulta | 211 | 00:00 | 95 | Kurigram | 62 | 19:30 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 62 | 00:00 | 96 | Kushtia | 155 | 00:00 | 162 | Saidpur | 83 | 19:30
31 | Bogura | 140 | 00:00 | 97 | Laksam | 31 | 00:00 | 163 | Santhia | 28 | 00:00
32 | Borhanuddin | 96 | 00:00 | 98 | Lakshmipur | 47 | 02:00 | 164 | Satkhira | 157 | 22:00
33 | Brahmanbaria | 93 | 22:00 | 99 | Lalbag | 58 | 00:00 | 165 | Satmasjid | 77 | 00:00
34 | Cantonment | 88 | 00:00 | 100 | Lalmonirhat | 62 | 19:00 | 166 | Savar | 148 | 00:00
35 | Chandina | 28 | 13:00 | 101 | MI_Cement | 11.7 | 01:00 | 167 | SevenRings | 3.03 | 18:30
36 | Chandpur | 62 | 00:00 | 102 | Madanganj | 28 | 09:00 | 168 | ShahCement | 23 | 23:00
37 | Chandraghona | 29 | 00:00 | 103 | Madaripur | 107 | 00:00 | 169 | Shahjadpur | 61 | 00:00
38 | Chapai | 77 | 00:00 | 104 | Madartek | 66 | 00:00 | 170 | Shahjibazar | 86 | 23:00
39 | Charsaidpur | 11 | 01:00 | 105 | Madunaghat | 48 | 00:00 | 171 | Shahmirpur | 50 | 00:00
40 | Chauddagram | 63 | 00:00 | 106 | Magura | 72 | 02:00 | 172 | Shariatpur | 65 | 22:00
41 | Chhatak | 27 | 21:00 | 107 | Mahasthangarh | 70 | 20:00 | 173 | Sherpur | 106 | 21:00
42 | Chowmuhani | 141 | 01:00 | 108 | Maijdee | 40 | 21:00 | 174 | Shikalbaha | 27 | 01:00
43 | Chuadanga | 129 | 02:00 | 109 | Manikganj | 120 | 00:00 | 175 | Shitalakhya | 65.8 | 11:00
44 | Coxsbazar | 147 | 19:00 | 110 | Maniknagar | 48 | 00:00 | 176 | Sholosohor | 37 | 00:00
45 | Cumilla(N) | 103 | 01:00 | 111 | Matarbari | 52 | 00:00 | 177 | Shomvuganj | 23 | 18:30
46 | Cumilla(S) | 125 | 00:00 | 112 | Matuail | 60 | 00:00 | 178 | Shyampur | 140 | 09:00
47 | Daganbhuiyan | 31 | 23:00 | 113 | Metrorail_Motijheel | 19 | 22:00 | 179 | Siddhirganj | 90 | 12:00
48 | Daudkandi | 102 | 00:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 88 | 00:00
49 | DhakaUniversity | 44 | 11:00 | 115 | Millgate | 60 | 00:00 | 181 | Sonargaon | 108 | 00:00
50 | Dhamrai | 88 | 00:00 | 116 | Mirpur | 103 | 00:00 | 182 | Sreemongol | 58 | 19:30
51 | Dhanmondi | 59 | 12:00 | 117 | Mirsorai | 9 | 00:00 | 183 | Sreepur | 84 | 02:00
52 | Dohazari | 103 | 00:00 | 118 | Mirzapur | 38 | 00:00 | 184 | Srinagar | 42.8 | 00:00
53 | Faridpur | 167 | 00:00 | 119 | Mithapukur | 58 | 19:30 | 185 | Sunamganj | 46 | 23:00
54 | Fatullah | 68 | 00:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 50 | 12:00
55 | Fenchuganj | 31 | 18:30 | 121 | Mogbazar | 56 | 00:00 | 187 | Sylhet-132 | 80 | 19:00
56 | Feni | 97 | 01:00 | 122 | Mongla | 35 | 01:00 | 188 | TK | 25 | 00:00
57 | GPH | 1 | 00:00 | 123 | Motijheel | 28 | 00:00 | 189 | Tangail | 144 | 00:00
58 | Ghatail | 73 | 19:30 | 124 | Muktagacha | 34 | 19:00 | 190 | Taraganj | 21 | 19:30
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 100 | 00:00 | 191 | Tasnim | 23 | 07:00
60 | Ghorashal-230 | 91 | 00:00 | 126 | Muradnagar | 38 | 01:00 | 192 | Thakurgaon | 111 | 20:00
61 | Goalpara | 45 | 00:00 | 127 | Mymensingh | 148 | 22:00 | 193 | Tongi | 111 | 00:00
62 | Gollamari | 130 | 00:00 | 128 | Nabinagar | 66 | 16:00 | 194 | Ullahpara | 34 | 19:30
63 | Gopalganj | 118 | 00:00 | 129 | Naogaon | 122 | 00:00 | 195 | Ullon | 50 | 00:00
64 | Gulshan | 72 | 12:00 | 130 | Narail | 68 | 01:00 | 196 | Uttara | 63 | 11:00
65 | Halishahar | 62 | 01:00 | 131 | Narinda | 40 | 00:00 | 197 | UttaraNew | 40 | 00:00
66 | HaripurSBU | 126 | 00:00 | 132 | Narshingdi | 162 | 00:00 | 198 | Zigatola | 67 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 26-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13338 | 44 |  | 13383.98
1:00 | 12460 | 29 |  | 12490
2:00 | 11369 | 0 |  | 11369
3:00 | 10539 | 0 |  | 10539
4:00 | 9387 | 0 |  | 9387
5:00 | 8047 | 0 |  | 8047
6:00 | 7747.74 | 0 |  | 7747.74
7:00 | 8084.96 | 0 |  | 8084.96
8:00 | 8752.76 | 0 |  | 8752.76
9:00 | 9169.2 | 0 |  | 9169.2
10:00 | 8945.85 | 0 |  | 8945.85
11:00 | 9084.43 | 0 |  | 9084.43
12:00 | 8449.22 | 0 |  | 8449.22
13:00 | 7845.44 | 0 |  | 7845.44
14:00 | 8418.59 | 0 |  | 8418.59
15:00 | 8654.69 | 0 |  | 8654.69
16:00 | 8743.08 | 0 |  | 8743.08
17:00 | 8858.54 | 0 |  | 8858.54
18:00 | 9199.76 | 0 |  | 9199.76
19:00 | 10736.37 | 0 |  | 10736.37
19:30 | 11127.53 | 0 |  | 11127.53
20:00 | 11103.75 | 0 |  | 11103.75
21:00 | 11164.63 | 5 |  | 11169.63
22:00 | 11197.74 | 0 |  | 11197.74
23:00 | 11087.41 | 0 |  | 11087.41
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 26-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 78 | -38 | 438 | 38 | 1710 | 166 | Ishurdi-Ghorashal Ckt-1 | Export | 1932000
1:00 | 103 | -32 | 520 | 70 | 1790 | 218
2:00 | 146 | -15 | 630 | 112 | 1672 | 332 |  | Import | 0
3:00 | 148 | -12 | 660 | 114 | 1402 | 296
4:00 | 103 | -29 | 360 | 18 | 1154 | 276 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 19 | -43 | 180 | 62 | 666 | 108
6:00 | 34 | -42 | 230 | 36 | 642 | 134 |  | Import | 0
7:00 | 55 | -38 | 320 | 6 | 726 | 162
8:00 | 105 | -34 | 370 | 4 | 914 | 170 | Sirajganj-Sreepur Ckt-1 | Export | 0
9:00 | 86 | -20 | 420 | 36 | 976 | 192
10:00 | 145 | -20 | 510 | 64 | 1124 | 210 |  | Import | 0
11:00 | 159 | -20 | 510 | 58 | 1120 | 214
12:00 | 127 | -42 | 340 | 30 | 1032 | 128 | Sirajganj-Sreepur Ckt-2 | Export | 0
13:00 | 73 | -52 | 276 | 24 | 966 | 104
14:00 | 116 | -54 | 398 | 4 | 1248 | 170 |  | Import | 0
15:00 | 109 | -56 | 418 | 20 | 1054 | 132
16:00 | 87 | -58 | 354 | 16 | 1054 | 132 | Gopalganj-Aminbazar Ckt-1 | Export | 13000000
17:00 | 74 | -57 | 298 | 8 | 980 | 124
18:00 | 57 | -53 | 268 | 36 | 1048 | 104 |  | Import | 0
18:30 | 48 | -52 | 248 | 34 | 1120 | 88
19:00 | 27 | -57 | 228 | 52 | 1084 | 40 | Gopalganj-Aminbazar Ckt-2 | Export | 13000000
19:30 | 24 | -57 | 190 | 22 | 1288 | -4
20:00 | 26 | -58 | 188 | 18 | 1254 | -4 |  | Import | 0
21:00 | 25 | -55 | 210 | 26 | 884 | 42
22:00 | 23 | -57 | 222 | 22 | 872 | 2 |  | Total Export | 27932000
23:00 | 24 | -57 | 214 | 22 | 838 | 8 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 26-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6402 | 6936 | 13338 | DAILY GENERATION CURVE
00:30 | 6095.5 | 6803.5 | 12899
01:00 | 5789 | 6671 | 12460 | 26-05-2026
01:30 | 5650 | 6264.5 | 11914.5
02:00 | 5511 | 5858 | 11369
02:30 | 5416 | 5538 | 10954
03:00 | 5321 | 5218 | 10539
03:30 | 5082 | 4881 | 9963
04:00 | 4843 | 4544 | 9387
04:30 | 4474 | 4243 | 8717
05:00 | 4105 | 3942 | 8047
05:30 | 4035.505 | 3861.865 | 7897.37
06:00 | 3966.01 | 3781.73 | 7747.74
06:30 | 4001.97 | 3914.38 | 7916.35
07:00 | 4037.93 | 4047.03 | 8084.96
07:30 | 4188.375 | 4230.485 | 8418.86
08:00 | 4338.82 | 4413.94 | 8752.76
08:30 | 4538.145 | 4422.835 | 8960.98
09:00 | 4737.47 | 4431.73 | 9169.2
09:30 | 4585.81 | 4471.715 | 9057.525
10:00 | 4434.15 | 4511.7 | 8945.85
10:30 | 4482.19 | 4532.95 | 9015.14
11:00 | 4530.23 | 4554.2 | 9084.43
11:30 | 4290.195 | 4476.63 | 8766.825
12:00 | 4050.16 | 4399.06 | 8449.22
12:30 | 3911.065 | 4236.265 | 8147.33
13:00 | 3771.97 | 4073.47 | 7845.44
13:30 | 3798.06 | 4333.955 | 8132.015
14:00 | 3824.15 | 4594.44 | 8418.59
14:30 | 3942.045 | 4594.595 | 8536.64
15:00 | 4059.94 | 4594.75 | 8654.69
15:30 | 4181.395 | 4517.49 | 8698.885
16:00 | 4302.85 | 4440.23 | 8743.08
16:30 | 4425.01 | 4375.8 | 8800.81
17:00 | 4547.17 | 4311.37 | 8858.54
17:30 | 4663.17 | 4365.98 | 9029.15
18:00 | 4779.17 | 4420.59 | 9199.76
18:30 | 5239.085 | 4728.98 | 9968.065
19:00 | 5699 | 5037.37 | 10736.37
19:30 | 5657 | 5470.53 | 11127.53
20:00 | 5605 | 5498.75 | 11103.75
20:30 | 5759 | 5375.19 | 11134.19 |  | Executive Engineer
21:00 | 5913 | 5251.63 | 11164.63 |  | Network Operation Division
21:30 | 5933.5 | 5247.685 | 11181.185
22:00 | 5954 | 5243.74 | 11197.74
22:30 | 5934 | 5208.575 | 11142.575
23:00 | 5914 | 5173.41 | 11087.41

## En-Curve
QF-LDC-12
Date | 26-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3696 | 1577 | 821 | 0 | 124 | 1457 | 65 | 4318 | 0 | 200 | 1080 | 0 | 0 | 0 | 44 | DAILY ENERGY CURVE
00:30 | 3691 | 1563.5 | 808 | 0 | 122 | 1449.5 | 65 | 4269.5 | 0 | 149 | 776.5 | 0 | 0 | 5 | 36.5 | 26-05-2026
01:00 | 3686 | 1550 | 795 | 0 | 120 | 1442 | 65 | 4221 | 0 | 98 | 473 | 0 | 0 | 10 | 29
01:30 | 3692.5 | 1604.5 | 681.5 | 0 | 117 | 1312.5 | 65 | 4031.5 | 0 | 57.5 | 340 | 0 | 0 | 12.5 | 14.5 | Energy Generated | 322.5749 |  | MKWHr
02:00 | 3699 | 1659 | 568 | 0 | 114 | 1183 | 65 | 3842 | 0 | 17 | 207 | 0 | 0 | 15 | 0 | Energy not Served | 0.078 |  | MKWHr
02:30 | 3679.5 | 1641 | 568.5 | 0 | 114 | 1099 | 65 | 3601.5 | 0 | 8.5 | 160.5 | 0 | 0 | 16.5 | 0 | Total Energy Requirement | 322.6529 |  | MKWHr
03:00 | 3660 | 1623 | 569 | 0 | 114 | 1015 | 65 | 3361 | 0 | 0 | 114 | 0 | 0 | 18 | 0
03:30 | 3538 | 1506 | 569 | 0 | 113 | 931.5 | 65 | 3149.5 | 0 | 0 | 74 | 0 | 0 | 17 | 0
04:00 | 3416 | 1389 | 569 | 0 | 112 | 848 | 65 | 2938 | 0 | 0 | 34 | 0 | 0 | 16 | 0
04:30 | 3228 | 1263.5 | 456 | 0 | 105 | 833.5 | 50 | 2736.5 | 0 | 0 | 17 | 0 | 0 | 27.5 | 0
05:00 | 3040 | 1138 | 343 | 0 | 98 | 819 | 35 | 2535 | 0 | 0 | 0 | 0 | 0 | 39 | 0
05:30 | 2995 | 1152.75 | 392 | 0 | 83 | 822.5 | 35 | 2375.5 | 11.12 | 0 | 0 | 0 | 0 | 30.5 | 0
06:00 | 2950 | 1167.5 | 441 | 0 | 68 | 826 | 35 | 2216 | 22.24 | 0 | 0 | 0 | 0 | 22 | 0
06:30 | 3001 | 1178.25 | 514.5 | 0 | 58 | 827 | 35 | 2223.5 | 61.6 | 0 | 0 | 0 | 0 | 17.5 | 0
07:00 | 3052 | 1189 | 588 | 0 | 48 | 828 | 35 | 2231 | 100.96 | 0 | 0 | 0 | 0 | 13 | 0
07:30 | 3095 | 1281.5 | 686 | 0 | 60 | 839 | 35 | 2244 | 161.36 | 0 | 0 | 0 | 0 | 17 | 0
08:00 | 3138 | 1374 | 784 | 0 | 72 | 850 | 35 | 2257 | 221.76 | 0 | 0 | 0 | 0 | 21 | 0
08:30 | 3315.5 | 1478 | 615.5 | 0 | 72 | 838.72 | 50 | 2284 | 295.26 | 0 | 0 | 0 | 0 | 12 | 0
09:00 | 3493 | 1582 | 447 | 0 | 72 | 827.44 | 65 | 2311 | 368.76 | 0 | 0 | 0 | 0 | 3 | 0
09:30 | 3408.5 | 1427 | 589 | 0 | 72 | 826.67 | 67 | 2304.5 | 360.855 | 0 | 0 | 0 | 0 | 2 | 0
10:00 | 3324 | 1272 | 731 | 0 | 72 | 825.9 | 69 | 2298 | 352.95 | 0 | 0 | 0 | 0 | 1 | 0
10:30 | 3371.5 | 1291.5 | 826.5 | 0 | 80 | 825.79 | 68 | 2282.5 | 267.35 | 0 | 0 | 0 | 0 | 2 | 0
11:00 | 3419 | 1311 | 922 | 0 | 88 | 825.68 | 67 | 2267 | 181.75 | 0 | 0 | 0 | 0 | 3 | 0
11:30 | 3178 | 1221 | 836 | 0 | 88 | 824.78 | 67 | 2266.5 | 274.545 | 0 | 0 | 0 | 0 | 11 | 0
12:00 | 2937 | 1131 | 750 | 0 | 88 | 823.88 | 67 | 2266 | 367.34 | 0 | 0 | 0 | 0 | 19 | 0
12:30 | 2793.5 | 1173 | 715.5 | 0 | 95 | 832.04 | 67 | 2197.5 | 232.29 | 0 | 0 | 0 | 0 | 41.5 | 0
13:00 | 2650 | 1215 | 681 | 0 | 102 | 840.2 | 67 | 2129 | 97.24 | 0 | 0 | 0 | 0 | 64 | 0
13:30 | 2737.5 | 1226.5 | 802 | 0 | 84 | 828.805 | 68 | 2121 | 204.71 | 0 | 0 | 0 | 0 | 59.5 | 0
14:00 | 2825 | 1238 | 923 | 0 | 66 | 817.41 | 69 | 2113 | 312.18 | 0 | 0 | 0 | 0 | 55 | 0
14:30 | 2910 | 1310.5 | 923 | 0 | 74 | 829.25 | 69 | 2091 | 295.39 | 0 | 0 | 0 | 0 | 34.5 | 0
15:00 | 2995 | 1383 | 923 | 0 | 82 | 841.09 | 69 | 2069 | 278.6 | 0 | 0 | 0 | 0 | 14 | 0
15:30 | 3108 | 1408 | 923 | 0 | 86 | 726.13 | 69.5 | 2109.5 | 256.755 | 0 | 0 | 0 | 0 | 12 | 0
16:00 | 3221 | 1433 | 923 | 0 | 90 | 611.17 | 70 | 2150 | 234.91 | 0 | 0 | 0 | 0 | 10 | 0
16:30 | 3350.5 | 1481.5 | 923 | 0 | 92 | 530.085 | 70 | 2161 | 172.725 | 0 | 0 | 0 | 0 | 20 | 0
17:00 | 3480 | 1530 | 923 | 0 | 94 | 449 | 70 | 2172 | 110.54 | 0 | 0 | 0 | 0 | 30 | 0
17:30 | 3516.5 | 1550 | 923 | 0 | 95 | 466.24 | 70 | 2292.5 | 73.91 | 0 | 0 | 0 | 0 | 42 | 0
18:00 | 3553 | 1570 | 923 | 0 | 96 | 483.48 | 70 | 2413 | 37.28 | 0 | 0 | 0 | 0 | 54 | 0
18:30 | 3744.5 | 1715.5 | 923 | 0 | 106 | 475.925 | 70 | 2798.5 | 18.64 | 31.5 | 54.5 | 0 | 0 | 30 | 0
19:00 | 3936 | 1861 | 923 | 0 | 116 | 468.37 | 70 | 3184 | 0 | 63 | 109 | 0 | 0 | 6 | 0
19:30 | 3908 | 1770 | 923 | 0 | 106 | 472.53 | 70 | 3616 | 0 | 85 | 175 | 0 | 0 | 2 | 0
20:00 | 3908 | 1628 | 924 | 0 | 106 | 431.75 | 70 | 3731 | 0 | 94 | 197 | 0 | 0 | 14 | 0
20:30 | 4016.5 | 1771.5 | 923.5 | 0 | 105 | 428.69 | 70 | 3535.5 | 0 | 80.5 | 167.5 | 0 | 0 | 35.5 | 2.5
21:00 | 4125 | 1915 | 923 | 0 | 104 | 425.63 | 70 | 3340 | 0 | 67 | 138 | 0 | 0 | 57 | 5
21:30 | 4161.5 | 1933 | 923 | 0 | 105 | 436.185 | 69 | 3310 | 0 | 67 | 130.5 | 0 | 0 | 46 | 2.5
22:00 | 4198 | 1951 | 923 | 0 | 106 | 446.74 | 68 | 3280 | 0 | 67 | 123 | 0 | 0 | 35 | 0
22:30 | 4195.5 | 1947 | 923 | 0 | 107 | 431.075 | 67.5 | 3263 | 0 | 63.5 | 123 | 0 | 0 | 22 | 0
23:00 | 4193 | 1943 | 923 | 0 | 108 | 415.41 | 67 | 3246 | 0 | 60 | 123 | 0 | 0 | 9 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 26-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 404 | 12:00 | 374 | 01:00 | Madunaghat | 405 | 14:00 | 393 | 02:00
Amtali | 418 | 12:00 | 401 | 00:00 | Meghnaghat | 399 | 06:00 | 377 | 01:00
Ashuganj | 406 | 13:00 | 380 | 01:00 | Payra | 418 | 13:00 | 406 | 01:00
Bhulta | 422 | 05:00 | 396 | 01:00 | Rahanpur | 421 | 04:00 | 400 | 00:00
Bibiana | 410 | 05:00 | 393 | 02:00 | Rampal | 407 | 13:00 | 380 | 00:00
BIPTC | 408 | 03:00 | 388 | 15:00
Bogura | 412 | 04:00 | 387 | 00:00
Gopalganj | 406 | 13:00 | 380 | 01:00
Kaliakoir | 403 | 12:00 | 372 | 01:00
Korerhat | 407 | 07:00 | 388 | 02:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 246 | 05:00 | 233 | 01:00 | Jhenaidah | 232 | 13:00 | 214 | 00:00
AKSML | 239 | 10:00 | 225 | 02:00 | Kachua | 242 | 07:00 | 226 | 02:00
Aminbazar | 245 | 05:00 | 235 | 00:00 | Kaliakoir | 244 | 04:00 | 233 | 01:00
Ashuganj | 242 | 06:00 | 125 | 04:00 | Keranigonj | 245 | 05:00 | 231 | 01:00
Ashuganj-400 | 242 | 06:00 | 125 | 04:00 | Khulna(S) | 235 | 13:00 | 213 | 00:00
Baghabari | 237 | 05:00 | 227 | 18:30 | Korerhat | 239 | 07:00 | 228 | 02:00
Barapukuria | 238 | 04:00 | 213 | 19:00 | Madunaghat | 236 | 10:00 | 227 | 02:00
Barapukuria-230 | 238 | 04:00 | 213 | 19:00 | Madunaghat-400 | 237 | 10:00 | 228 | 02:00
Barishal | 238 | 14:00 | 223 | 00:00 | Maniknagar | 243 | 06:00 | 230 | 00:00
Bheramara | 235 | 02:00 | 221 | 19:00 | Meghnaghat | 247 | 12:00 | 236 | 03:00
Bhulta | 243 | 05:00 | 229 | 01:00 | Meghnaghat-400 | 244 | 05:00 | 232 | 01:00
Bibiana | 245 | 06:00 | 234 | 01:00 | Mirsorai | 236 | 14:00 | 224 | 03:00
BIPTC | 236 | 12:00 | 223 | 19:00 | Naogaon | 231 | 04:00 | 208 | 00:00
Bogura | 245 | 04:00 | 230 | 19:30 | Purbasadipur | 237 | 03:00 | 210 | 19:30
Bogura-400 | 246 | 05:00 | 229 | 19:30 | Rajshahi | 235 | 02:00 | 219 | 19:00
Borhanuddin | 238 | 15:00 | 227 | 00:00 | Rampal | 234 | 13:00 | 213 | 00:00
BSRM | 239 | 14:00 | 226 | 02:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 241 | 14:00 | 226 | 02:00 | Rampura | 243 | 05:00 | 228 | 02:00
Cumilla(N) | 241 | 05:00 | 228 | 02:00 | Shikalbaha | 235 | 10:00 | 226 | 03:00
Faridpur | 240 | 12:00 | 222 | 00:00 | Shyampur | 244 | 05:00 | 231 | 01:00
Fenchuganj | 246 | 06:00 | 238 | 00:00 | Siddhirganj | 244 | 06:00 | 232 | 00:00
Feni | 238 | 15:00 | 224 | 02:00 | Sirajgonj | 245 | 05:00 | 235 | 01:00
Ghorashal | 245 | 03:00 | 230 | 00:00 | Sreepur | 240 | 05:00 | 223 | 01:00
Ghorashal-230 | 240 | 05:00 | 227 | 02:00 | Tongi | 242 | 04:00 | 231 | 00:00
Gopalganj | 240 | 13:00 | 224 | 00:00
GPH | 237 | 10:00 | 226 | 02:00
Haripur | 243 | 05:00 | 230 | 01:00
Hasnabad | 241 | 13:00 | 232 | 00:00
Hathazari | 238 | 12:00 | 228 | 00:00
Ishurdi | 237 | 12:00 | 225 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 04:00 | 132 | 01:00 | Madunaghat | 138 | 10:00 | 131 | 02:00
Agargaon | 144 | 05:00 | 133 | 11:00 | Magura | 137 | 08:00 | 122 | 00:00
Agrabad | 137 | 10:00 | 129 | 01:00 | Mahasthangarh | 142 | 02:00 | 128 | 19:00
AKS | 134 | 08:00 | 130 | 00:00 | Maijdee | 137 | 07:00 | 126 | 02:00
Aminbazar | 141 | 05:00 | 135 | 00:00 | Manikganj | 142 | 12:00 | 126 | 19:00
Amnura | 137 | 09:00 | 127 | 00:00 | Maniknagar | 143 | 13:00 | 136 | 00:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 130 | 10:00 | 109 | 02:00
Ashuganj-230 | 150 | 05:00 | 140 | 00:00 | Matuail | 142.6 | 05:00 | 125 | 10:00
Bagerhat | 141 | 13:00 | 116 | 00:00 | Metrorail_Motijheel | 142 | 05:00 | 134 | 11:00
Bajitpur | 142 | 05:00 | 128 | 19:00 | Metrorail_Uttara | 138 | 04:00 | 129 | 00:00
Bakerganj | 138 | 15:00 | 126 | 00:00 | Millgate | 138 | 04:00 | 130 | 00:00
Bakulia | 138 | 10:00 | 129 | 02:00 | Mirpur | 142 | 05:00 | 133 | 01:00
Banani | 140 | 04:00 | 131 | 11:00 | Mirzapur | 142 | 05:00 | 127 | 19:00
Bangabhaban | 143 | 13:00 | 136 | 00:00 | Mithapukur | 142 | 04:00 | 124 | 19:30
Barapukuria | 140 | 02:00 | 123 | 19:00 | MI_Cement | 140.7 | 05:00 | 132 | 00:00
Barguna | 137 | 15:00 | 125 | 00:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 140 | 14:00 | 126 | 00:00 | Mogbazar | 137 | 07:00 | 133 | 11:00
Barishal-230 | 139 | 14:00 | 126 | 00:00 | Mongla | 139 | 13:00 | 118 | 00:00
Baroaulia | 138 | 10:00 | 131 | 01:00 | Motijheel | 143 | 13:00 | 136 | 00:00
Baroirhat | 138 | 14:00 | 132 | 00:00 | Muktagacha | 140 | 03:00 | 121 | 00:00
Bashundhara | 139 | 04:00 | 129 | 01:00 | Munshiganj | 141 | 06:00 | 133 | 00:00
BashundharaCement | 143 | 06:00 | 131 | 00:00 | Muradnagar | 142 | 06:00 | 130 | 01:00
Beanibazar | 132 | 04:00 | 127 | 19:00 | Mymensingh | 143 | 04:00 | 119 | 00:00
Benapole | 138 | 13:00 | 115 | 00:00 | Nabinagar | 141 | 04:00 | 131 | 01:00
Bhaluka | 140 | 04:00 | 125 | 19:00 | Naogaon | 143 | 03:00 | 125 | 00:00
Bhandaria | 140 | 14:00 | 116 | 00:00 | Narail | 138 | 13:00 | 120 | 00:00
Bhangura | 138 | 03:00 | 128 | 00:00 | Narinda | 142 | 12:00 | 126 | 19:00
Bheramara | 137 | 03:00 | 131 | 00:00 | Narshingdi | 145 | 05:00 | 128 | 00:00
Bheramara(GK) | 137 | 03:00 | 130 | 00:00 | Natore | 137 | 02:00 | 128 | 00:00
Bhulta | 138 | 05:00 | 128 | 00:00 | Nawabganj | 140 | 04:00 | 131 | 11:00
Bog-Sherpur | 142 | 03:00 | 130 | 19:30 | Netrakona | 137 | 04:00 | 118 | 19:00
Bogura | 142 | 03:00 | 131 | 19:00 | New | 138 | 04:00 | 131 | 11:00
Bogura-230 | 143 | 03:00 | 132 | 19:00 | Niamatpur | 139 | 05:00 | 127 | 00:00
Brahmanbaria | 146 | 05:00 | 133 | 00:00 | Noapara | 140 | 13:00 | 119 | 00:00
Cantonment | 141 | 04:00 | 133 | 11:00 | Pabna | 137 | 03:00 | 129 | 00:00
Chandina | 141 | 06:00 | 132 | 01:00 | Palashbari | 141 | 03:00 | 122 | 19:00
Chandpur | 138 | 14:00 | 127 | 02:00 | Panchagarh | 142 | 03:00 | 124 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 139 | 10:00 | 132 | 02:00 | Patiya | 137 | 10:00 | 126 | 02:00
Chapai | 137 | 02:00 | 128 | 00:00 | Patuakhali | 137 | 14:00 | 125 | 00:00
Charsaidpur | 144 | 05:00 | 132 | 01:00 | Payra | 137 | 14:00 | 130 | 00:00
Chauddagram | 140 | 07:00 | 131 | 01:00 | PHP | 138 | 08:00 | 130 | 02:00
Chhatak | 131 | 03:00 | 122 | 06:00 | Postogola | 143 | 05:00 | 134 | 00:00
Chowmuhani | 136 | 15:00 | 128 | 00:00 | Pubail | 146 | 05:00 | 136 | 00:00
Chuadanga | 135 | 13:00 | 119 | 00:00 | Purbachal | 139 | 04:00 | 129 | 01:00
Coxsbazar | 130 | 10:00 | 111 | 00:00 | Purbasadipur | 141 | 02:00 | 124 | 14:00
Cumilla(N) | 141 | 05:00 | 132 | 01:00 | Rahanpur | 139 | 04:00 | 131 | 00:00
Cumilla(S) | 141 | 06:00 | 125 | 19:00 | Rahanpur-400 | 139 | 03:00 | 131 | 00:00
Daganbhuiyan | 139 | 07:00 | 130 | 02:00 | Rahim | 0 | 00:00 | N/A | N/A
Daudkandi | 141 | 06:00 | 129 | 00:00 | Rajbari | 137 | 13:00 | 125 | 00:00
DhakaUniversity | 136 | 13:00 | 132 | 09:00 | Rajendrapur | 140 | 04:00 | 126 | 19:00
Dhamrai | 142 | 05:00 | 133 | 00:00 | Rajshahi | 134 | 02:00 | 125 | 19:30
Dhanmondi | 143 | 05:00 | 134 | 11:00 | Rajshahi-230 | 135 | 02:00 | 126 | 19:00
Dohazari | 135 | 10:00 | 123 | 00:00 | Ramganj | 138 | 14:00 | 126 | 01:00
Faridpur | 138 | 12:00 | 125 | 00:00 | Rampur | 138 | 10:00 | 131 | 03:00
Fatullah | 142 | 05:00 | 132 | 01:00 | Rampura | 141 | 05:00 | 131 | 11:00
Fenchuganj | 142 | 05:00 | 133 | 18:30 | Rangamati | 139 | 10:00 | 130 | 02:00
Feni | 139 | 07:00 | 132 | 00:00 | Rangpur | 141 | 03:00 | 123 | 19:00
Feni-230 | 140 | 07:00 | 132 | 01:00 | Ruppur | 137 | 05:00 | 131 | 00:00
Ghatail | 141 | 05:00 | 120 | 00:00 | Saidpur | 142 | 04:00 | 122 | 19:00
Ghorashal | 145 | 03:00 | 137 | 01:00 | Santhia | 138 | 03:00 | 131 | 19:00
Goalpara | 141 | 13:00 | 124 | 01:00 | Satkhira | 137 | 13:00 | 116 | 01:00
Gollamari | 140 | 13:00 | 124 | 01:00 | Satmasjid | 144 | 05:00 | 133 | 11:00
Gopalganj | 140 | 13:00 | 125 | 01:00 | Savar | 140 | 05:00 | 132 | 11:00
Gopalganj-400 | 141 | 13:00 | 130 | 00:00 | SevenRings | 147 | 05:00 | 137 | 01:00
Gulshan | 140 | 05:00 | 131 | 11:00 | ShahCement | 144 | 05:00 | 132 | 01:00
Halishahar | 137 | 10:00 | 129 | 02:00 | Shahjadpur | 141 | 10:00 | 134 | 00:00
Haripur | 142 | 05:00 | 134 | 01:00 | Shahjibazar | 143 | 05:00 | 133 | 14:00
HaripurSBU | 142 | 05:00 | 134 | 02:00 | Shahmirpur | 137 | 10:00 | 132 | 00:00
Hasnabad | 143 | 05:00 | 134 | 00:00 | Shariatpur | 140 | 14:00 | 127 | 00:00
Hathazari | 138 | 09:00 | 133 | 01:00 | Sherpur | 141 | 03:00 | 112 | 19:00
Hatirjheel | 141 | 05:00 | 131 | 11:00 | Shikalbaha | 127 | 10:00 | 118 | 02:00
Ishurdi | 139 | 03:00 | 132 | 00:00 | Shikalbaha-230 | 139 | 10:00 | 131 | 02:00
Jaldhaka | 141 | 02:00 | 118 | 19:00 | Shitalakhya | 140.7 | 05:00 | 132 | 00:00
Jamalpur | 143 | 03:00 | 116 | 19:00 | Sholosohor | 138 | 10:00 | 130 | 02:00
Jashore | 140 | 13:00 | 114 | 00:00 | Shomvuganj | 136 | 05:00 | 121 | 19:00
Jhenaidah | 137 | 07:00 | 118 | 00:00 | Shyampur | 141 | 05:00 | 130 | 11:00
Jhenaidah-230 | 139 | 13:00 | 123 | 00:00 | Shyampur-230 | 142 | 05:00 | 134 | 01:00
Joydebpur | 146 | 12:00 | 134 | 00:00 | Siddhirganj | 143 | 05:00 | 134 | 01:00
Joypurhat | 141 | 02:00 | 127 | 19:30 | Sirajganj | 140 | 03:00 | 128 | 19:30
Juldah | 137 | 14:00 | 128 | 01:00 | Sonargaon | 141 | 05:00 | 132 | 01:00
Kabirpur | 144 | 12:00 | 128 | 00:00 | Sreemongol | 140 | 05:00 | 132 | 19:00
Kachua | 138 | 07:00 | 128 | 02:00 | Sreepur | 139 | 04:00 | 128 | 19:00
Kaliakoir | 145 | 12:00 | 131 | 19:00 | Srinagar | 140 | 03:00 | 131 | 11:00
Kaliganj | 138 | 13:00 | 124 | 00:00 | SSM | 137 | 07:00 | 135 | 00:00
Kallyanpur | 143 | 05:00 | 134 | 01:00 | Sunamganj | 136 | 05:00 | 124 | 17:00
Kalurghat | 138 | 10:00 | 132 | 01:00 | Sylhet | 137 | 05:00 | 129 | 18:30
Kamrangirchar | 141 | 04:00 | 131 | 11:00 | Sylhet-132 | 133 | 06:00 | 128 | 19:00
Kaptai | N/A | N/A | N/A | N/A | Tangail | 141 | 12:00 | 123 | 00:00
Kasba | 142 | 06:00 | 129 | 01:00 | Taraganj | 140 | 04:00 | 123 | 19:30
Kazla | 143 | 13:00 | 135 | 01:00 | Tasnim | 142 | 05:00 | 132 | 00:00
Keranigonj | 141 | 04:00 | 131 | 11:00 | Thakurgaon | 142 | 03:00 | 123 | 14:00
Khagrachori | 139 | 10:00 | 130 | 02:00 | TK | 138 | 09:00 | 133 | 00:00
Khulna | 139 | 13:00 | 122 | 00:00 | Tongi | 139 | 04:00 | 132 | 00:00
Khulna(S) | 141 | 13:00 | 123 | 01:00 | Ullahpara | 140 | 03:00 | 129 | 19:30
Khulshi | 136 | 10:00 | 129 | 01:00 | Ullon | 141 | 05:00 | 131 | 11:00
Kishoreganj | 141 | 05:00 | 126 | 19:00 | Uttara | 138 | 05:00 | 129 | 02:00
Kodda | 142 | 12:00 | 126 | 19:00 | UttaraNew | 138 | 04:00 | 129 | 11:00
Korerhat | 138 | 07:00 | 130 | 02:00 | Zigatola | 141 | 05:00 | 132 | 11:00
KSRM | 137 | 10:00 | 132 | 00:00
Kulaura | 139 | 04:00 | 132 | 19:00
Kurigram | 141 | 02:00 | 117 | 19:00
Kushtia | 134 | 06:00 | 126 | 00:00
Laksam | 140 | 14:00 | 129 | 00:00
Lakshmipur | 137 | 07:00 | 125 | 02:00
Lalbag | 137 | 00:00 | 132 | 11:00
Lalmonirhat | 135 | 05:00 | 119 | 19:30
Madanganj | 143 | 06:00 | 133 | 11:00
Madaripur | 140 | 13:00 | 129 | 00:00
Madartek | 141 | 05:00 | 131 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division