## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 28-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-05-2026 | during | 28-05-2026 | during | 28-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 170 | 170 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 0
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 303 | 333 | 412 | 412 | 392 | 392 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 152 | 151 | 335 | 335 | 150 | 150
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 210 | 210 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 180 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 0.01 | 0.01 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 1 | 1 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 5 | 5 | 33 | 33 | 20 | 20
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 5 | 3 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 16 | 50 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 32 | 32 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 100 | 100 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 0.01 | 0.01 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 19 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 470 | 390 | 584 | 584 | 540 | 540 | AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 17 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1134 | 1234 | 5855.22 | 5827.22 | 2581.38 | 2587.38
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 8 | 8 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 15 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 0 | 35 | 0 | 0 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 50 | 150 | 150 | 150 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 24 | 24 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 25 | 0 | 0 | 5 | 25 | plant availability zero
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 24 | 60 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0 | 0 | 2.16 | 0 | 2.16 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 35 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 302 | 580 | 1224 | 1224 | 612 | 612 | U2 outage added
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 10 | 0 | 0 | 3 | 0 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 300 | 565 | 575 | 575 | 575 | 575 | U1 under maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 677 | 1355 | 3249.02 | 3298.86 | 1997.52 | 2220.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 194 | 200 | 221.25 | 221.25 | 205.25 | 205.25
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 300 | 361 | 350.01 | 350.01 | 320 | 320 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 0 | 0 | 250 | 250 | 0 | 0
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 342 | 325 | 393 | 393 | 340 | 340 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 34 | 41.65 | 41.65 | 40 | 40 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 23 | 52.82 | 52.82 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 187 | 195 | 195 | 180 | 180 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 0 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 33 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 40 | 40 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 12 | 98 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 43 | 43 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 3 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 0.01 | 0.01 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 0 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 848 | 1282 | 2586.43 | 2526.43 | 1671.26 | 1737.26
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-05-2026 | during | 28-05-2026 | during | 28-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 84 | 156 | 157.5 | 157.5 | 210 | 210
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.5 | 0 | 1.4 | 0 | 1.4 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 0 | 16 | 140 | 140 | 90 | 90 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 0 | 35 | 60 | 60 | 10 | 110 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 22.07 | 0 | 36 | 0 | 36 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | From 17:00 to 20:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 107.57 | 207 | 471.4 | 434 | 376.4 | 439
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 42 | 42
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 30 | 30
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 127 | 135 | 163 | 163 | 147 | 147 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 110 | 110 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 102 | 102 | 102 | 102 | 102 | 102 | STG Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 17 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 341 | 341 | 0 | 0
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 233 | 381 | 260 | 260 | 250 | 250
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 463 | 751 | 1135 | 1135 | 704 | 704
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 250 | 620 | 0 | 0 | 500 | 950 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 32 | 32 | 37 | 37 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 280 | 383 | 410 | 410 | 400 | 400
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 16 | 16 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 0 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 366 | 556 | 1234.2 | 1234.2 | 617.1 | 617.1 | Unit1 Under Maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 896 | 1559 | 2581.2 | 2496.2 | 1782.1 | 2147.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 500 | 1100 | 1244 | 1244 | 622 | 622 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 50 | 60 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 250 | 546 | 1244 | 1244 | 622 | 622 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 0 | 35 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 140 | 173 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1160 | 2099 | 3406 | 3405 | 1982 | 2016
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 65.88 | 0 | 51 | 0 | 51 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 130 | 180 | 214 | 214 | 190 | 190
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 210 | 210
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 388 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 97 | 97 | 0 | 50 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 3.3 | 0 | 3.3 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 521.72 | 770 | 1435.88 | 1435.88 | 749 | 749 | AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 41.12 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 26 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1172.72 | 1364 | 3228.17 | 3012.87 | 2118.91 | 1953.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 52 | 49 | 52 | 52 | 50 | 50 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 33 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.6 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 16 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 43 | 0 | 131.57 | 0 | 131.57 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 118.6 | 117 | 467.57 | 300 | 445.57 | 278
System Total |  |  |  |  | 28823.2 | 29270.237 | 6576.89 | 9968 | 22980.01 | 22435.58 | 13659.14 | 14082.71
Forecast Scenario (28-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9600 |  | 0 |  | 9600
|  |  |  | 1:00 | 9400 |  | 0 |  | 9400
|  |  |  | 2:00 | 9010 |  | 0 |  | 9010
|  |  |  | 3:00 | 8740 |  | 0 |  | 8740
|  |  |  | 4:00 | 8470 |  | 0 |  | 8470
|  |  |  | 5:00 | 8220 |  | 0 |  | 8220
|  |  |  | 6:00 | 7810 |  | 0 |  | 7810
|  |  |  | 7:00 | 7690 |  | 0 |  | 7690
|  |  |  | 8:00 | 6950 |  | 0 |  | 6950
|  |  |  | 9:00 | 6400 |  | 0 |  | 6400
|  |  |  | 10:00 | 6410 |  | 0 |  | 6410
|  |  |  | 11:00 | 6450 |  | 0 |  | 6450
|  |  |  | 12:00 | 6740 |  | 0 |  | 6740
|  |  |  | 13:00 | 6780 |  | 0 |  | 6780
|  |  |  | 14:00 | 6820 |  | 0 |  | 6820
|  |  |  | 15:00 | 7150 |  | 0 |  | 7150
|  |  |  | 16:00 | 7400 |  | 0 |  | 7400
|  |  |  | 17:00 | 7310 |  | 0 |  | 7310
|  |  |  | 18:00 | 7380 |  | 0 |  | 7380
|  |  |  | 18:30 | 7800 |  | 0 |  | 7800
|  |  |  | 19:00 | 8460 |  | 0 |  | 8460
|  |  |  | 19:30 | 9320 |  | 0 |  | 9320
|  |  |  | 20:00 | 9500 |  | 0 |  | 9500
|  |  |  | 21:00 | 9830 |  | 0 |  | 9830
|  |  |  | 22:00 | 9800 |  | 0 |  | 9800
|  |  |  | 23:00 | 9780 |  | 0 |  | 9780
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 6740.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 9830.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 9830.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 192.10 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:20 hrs on 28-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 27-05-2026 | [28 empty] | Date: | 27-05-2026 | [28 empty] | Date: | 27-05-2026 | [28 empty] | Date: | 27-05-2026 | [28 empty] | Date: | 27-05-2026 | [17 empty] | Date: | 27-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [17 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 366 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 14 | 18 | 0 | 480 | 0 | 0 | 0 | 0 | 10 | 17 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 42 | 370 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 580 | 0 | 0 | 73 | 335 | 361 | 0 | 51 | 20 | 201 | 40 | 0 | 102 | 0 | 0 | 16 | 0 | 104 | 0 | 0 | 0 | 305 | 0 | 380 | 0 | 30 | 149 | 0 | 16 | 0 | 83 | 30 | 150 | 0 | 101 | 0 | 9 | 24 | 98 | 0 | 0 | 0 | 5758 | 923 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 409.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 172 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 50 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 120 | 220 | 0 | 647 | 930 | 0 | 5028.95 | 10786.95 | 75.51
01:00 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 341 | 0 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 14 | 18 | 0 | 445 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 42 | 370 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 520 | 0 | 0 | 73 | 335 | 360 | 0 | 51 | 20 | 199 | 40 | 0 | 102 | 0 | 0 | 16 | 0 | 96 | 0 | 0 | 0 | 310 | 0 | 380 | 0 | 30 | 141 | 0 | 16 | 0 | 83 | 30 | 151 | 0 | 101 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 5529 | 923 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 405.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 167 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 120 | 220 | 0 | 600 | 880 | 0 | 4863.81 | 10392.81 | 75.5
02:00 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 325 | 0 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 18 | 0 | 360 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 42 | 360 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 420 | 0 | 0 | 73 | 335 | 361 | 0 | 51 | 20 | 201 | 40 | 0 | 102 | 0 | 0 | 16 | 0 | 88 | 0 | 0 | 0 | 305 | 0 | 380 | 0 | 30 | 133 | 0 | 16 | 0 | 41 | 30 | 151 | 0 | 101 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 5253 | 923 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 400.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 161 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 120 | 220 | 0 | 600 | 780 | 0 | 4757.67 | 10010.67 | 75.49
03:00 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 325 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 18 | 0 | 390 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 42 | 360 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 403 | 0 | 0 | 26 | 330 | 360 | 0 | 5 | 20 | 199 | 37 | 0 | 102 | 0 | 0 | 16 | 0 | 86 | 0 | 0 | 0 | 300 | 0 | 380 | 0 | 30 | 132 | 0 | 16 | 0 | 42 | 20 | 151 | 0 | 101 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 5144 | 923 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 402.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 160 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 126 | 220 | 0 | 500 | 680 | 0 | 4558.6 | 9702.6 | 75.48
04:00 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 325 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 18 | 0 | 374 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 10 | 360 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 305 | 0 | 0 | 8 | 310 | 360 | 0 | 5 | 12 | 201 | 10 | 0 | 50 | 0 | 0 | 16 | 0 | 84 | 0 | 0 | 0 | 290 | 0 | 380 | 0 | 30 | 132 | 0 | 0 | 0 | 5 | 20 | 151 | 0 | 102 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 4764 | 923 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 404.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 161 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 100 | 180 | 0 | 500 | 590 | 0 | 4372.48 | 9136.48 | 75.47
05:00 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 312 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 12 | 18 | 0 | 335 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 304 | 0 | 0 | 8 | 240 | 300 | 0 | 5 | 6 | 150 | 10 | 0 | 50 | 0 | 0 | 10 | 0 | 80 | 0 | 0 | 0 | 280 | 0 | 325 | 0 | 30 | 124 | 0 | 0 | 0 | 5 | 20 | 150 | 0 | 101 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | 4296 | 822 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 401.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 155 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 100 | 180 | 0 | 500 | 520 | 0 | 4003.06 | 8299.06 | 75.46
06:00 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 311 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 180 | 0 | 0 | 3 | 0 | 10.5 | 12 | 0 | 340 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0.29 | 69 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 300 | 1 | 0 | 0 | 220 | 300 | 0 | 0 | 1 | 150 | 0 | 0 | 40 | 0 | 0 | 10 | 0 | 76 | 0 | 3 | 0 | 240 | 0 | 233 | 0 | 20 | 121 | 0 | 0 | 0 | 0 | 7 | 150 | 0 | 101 | 0 | 0 | 0 | 108 | 0 | 0.23 | 0 | 4007.02 | 369 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.37 | 378 | 0 | 0 | 0 | 402.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.69 | 0 | 0 | 0 | 0.92 | 130 | 0 | 130 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.04 | 0 | 140 | 100 | 180 | 0 | 500 | 500 | 0 | 3372.83 | 7379.85 | 75.45
07:00 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 312 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 180 | 0 | 0 | 7 | 0 | 0 | 3 | 0 | 300 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 1.21 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 304 | 5 | 0 | 0 | 220 | 300 | 0 | 0 | 0 | 150 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 74 | 0 | 17 | 0 | 180 | 0 | 233 | 0 | 0 | 123 | 2 | 0 | 0 | 0 | 7 | 124 | 0 | 102 | 0 | 0 | 0 | 31 | 0 | 5.72 | 0 | 3694.93 | 369 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 372 | 0 | 0 | 0 | 415.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 130 | 0 | 50 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 51 | 0 | 2 | 0 | 0 | 0 | 0 | 0.4 | 3 | 0.02 | 0 | 140 | 60 | 180 | 0 | 500 | 500 | 0 | 3200.65 | 6895.58 | 75.44
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 305 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 302 | 9 | 0 | 0 | 220 | 300 | 0 | 0 | 0 | 150 | 0 | 0 | 40 | 0 | 0 | 10 | 0 | 80 | 0 | 1 | 0 | 110 | 0 | 234 | 0 | 0 | 127 | 1 | 0 | 0 | 0 | 0 | 113 | 0 | 101 | 0 | 0 | 0 | 36 | 0.03 | 1.26 | 0 | 3440.69 | 212 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 401.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 1 | 0 | 0 | 0 | 130 | 0 | 50 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 52 | 0 | 5 | 0 | 0 | 0 | 0 | 0.8 | 5 | 0 | 0 | 140 | 50 | 180 | 0 | 500 | 500 | 0 | 2993.23 | 6433.92 | 75.43
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 290 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 3.18 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 300 | 14 | 0 | 0 | 220 | 300 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 86 | 0 | 2 | 0 | 0 | 0 | 234 | 0 | 0 | 108 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 36 | 0.03 | 0.62 | 0 | 2829.83 | 152 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 421.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94 | 3 | 0 | 0 | 1.05 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 52 | 0 | 5 | 0 | 0 | 0 | 0 | 2.1 | 6 | 0 | 0 | 140 | 50 | 180 | 0 | 480 | 475 | 0 | 2925.69 | 5755.52 | 75.42
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 180 | 0 | 0 | 4 | 0 | 5 | 3 | 0 | 350 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 310 | 17 | 0 | 0 | 250 | 300 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 233 | 0 | 0 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 38 | 0.75 | 2.14 | 0 | 2842.39 | 211 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 434.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.18 | 7 | 0 | 0 | 16.18 | 130 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0.5 | 0 | 52 | 0 | 9 | 0 | 0 | 0 | 0 | 2.5 | 5 | 0 | 0 | 140 | 50 | 180 | 0 | 520 | 400 | 0 | 3117.1 | 5959.49 | 75.41
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 180 | 0 | 0 | 18 | 0 | 5 | 3 | 0 | 360 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 4.43 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 302 | 10 | 0 | 0 | 230 | 300 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 107 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 40 | 0.89 | 5.91 | 0 | 2868.23 | 449 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 462.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.12 | 20 | 0 | 0 | 22.43 | 130 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0.76 | 0 | 50 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 10 | 0 | 0 | 140 | 50 | 180 | 0 | 525 | 250 | 0 | 3305.71 | 6173.94 | 75.41
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 180 | 0 | 0 | 19 | 0 | 5 | 5 | 0 | 470 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 302 | 15 | 0 | 0 | 342 | 300 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 127 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 84 | 1.5 | 22.07 | 0 | 3229.57 | 250 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 521.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.88 | 26 | 0 | 0 | 41.12 | 130 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 0 | 0 | 52 | 0 | 16 | 0 | 0 | 0 | 0 | 7.6 | 43 | 0 | 0 | 140 | 50 | 220 | 0 | 500 | 250 | 0 | 3347.32 | 6576.89 | 75.41
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 332 | 0 | 0 | 32 | 0 | 5 | 3 | 0 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.23 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 325 | 360 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 9 | 0 | 0 | 0 | 308 | 0 | 0 | 149 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 110 | 1.49 | 18.8 | 0 | 3596.52 | 196 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 367 | 0 | 0 | 0 | 547.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.86 | 104 | 0 | 0 | 28.95 | 155 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 2.45 | 0 | 51 | 0 | 15 | 0 | 0 | 0 | 0 | 6.5 | 122 | 0 | 0 | 171 | 50 | 220 | 0 | 500 | 250 | 0 | 3641.12 | 7237.64 | 75.41
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 335 | 0 | 0 | 29 | 0 | 5 | 3 | 0 | 480 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0.43 | 34 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 340 | 0 | 0 | 38 | 328 | 360 | 0 | 5 | 1 | 199 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 18 | 0 | 0 | 0 | 353 | 0 | 0 | 156 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 145 | 1.9 | 47.78 | 0 | 4035.11 | 195 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 368 | 0 | 0 | 0 | 546.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.05 | 96 | 0 | 0 | 42 | 173 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 3.45 | 0 | 51 | 0 | 24 | 0 | 0 | 0 | 0 | 4.2 | 68 | 0.26 | 0 | 168 | 60 | 220 | 0 | 500 | 257 | 0 | 3665.32 | 7700.43 | 75.41
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 331 | 0 | 0 | 23 | 0 | 5 | 3 | 0 | 490 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0.87 | 35 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 353 | 0 | 0 | 63 | 335 | 360 | 0 | 33 | 10 | 203 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 21 | 0 | 0 | 0 | 381 | 0 | 0 | 146 | 3 | 0 | 0 | 42 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 154 | 1.5 | 38.41 | 0 | 4135.78 | 196 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 371 | 0 | 0 | 0 | 558.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.29 | 75 | 0 | 0 | 40.25 | 167 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.54 | 0 | 50 | 0 | 19 | 0 | 0 | 0 | 0 | 2.3 | 102 | 0.43 | 0 | 193 | 60 | 220 | 0 | 500 | 295 | 0 | 3726.01 | 7861.79 | 75.41
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 330 | 0 | 0 | 15 | 0 | 5 | 3 | 0 | 490 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0.85 | 35 | 0 | 13 | 300 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 355 | 0 | 0 | 63 | 345 | 361 | 0 | 44 | 10 | 207 | 33 | 0 | 0 | 0 | 0 | 4 | 0 | 16 | 0 | 20 | 0 | 0 | 0 | 381 | 0 | 0 | 154 | 4 | 0 | 0 | 42 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 154 | 0.7 | 14.65 | 0 | 4185.2 | 195 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 375 | 0 | 0 | 0 | 565.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.05 | 51 | 0 | 0 | 25.08 | 168 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.42 | 0 | 50 | 0 | 12 | 0 | 0 | 0 | 0 | 2 | 89 | 0.33 | 0 | 221 | 60 | 220 | 0 | 500 | 318 | 0 | 3687.43 | 7872.63 | 75.41
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 328 | 0 | 0 | 7 | 0 | 5 | 3 | 0 | 490 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0.66 | 35 | 0 | 26 | 364 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 355 | 2 | 0 | 63 | 345 | 359 | 0 | 46 | 10 | 206 | 33 | 0 | 0 | 0 | 0 | 3 | 0 | 80 | 0 | 18 | 0 | 0 | 0 | 381 | 0 | 0 | 155 | 2 | 17 | 0 | 42 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 154 | 0.4 | 10.97 | 0 | 4325.03 | 196 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 370 | 0 | 0 | 0 | 569.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.65 | 22 | 0 | 0 | 6.02 | 168 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.74 | 0 | 50 | 0 | 6 | 0 | 0 | 0 | 0 | 2 | 40 | 0.1 | 0 | 252 | 60 | 220 | 0 | 500 | 342 | 0 | 3609.27 | 7934.3 | 75.41
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 330 | 0 | 0 | 2 | 0 | 5 | 3 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32 | 35 | 0 | 27 | 363 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 450 | 0 | 0 | 85 | 335 | 360 | 0 | 51 | 10 | 202 | 33 | 0 | 0 | 0 | 0 | 4 | 0 | 90 | 0 | 3 | 0 | 0 | 0 | 381 | 0 | 0 | 147 | 1 | 17 | 0 | 42 | 20 | 0 | 0 | 102 | 0 | 0 | 0 | 154 | 0.1 | 2.61 | 0 | 4320.03 | 311 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 370 | 0 | 0 | 0 | 657.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.63 | 3 | 0 | 0 | 0.6 | 167 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.13 | 0 | 50 | 0 | 1 | 0 | 0 | 0 | 0 | 0.6 | 9 | 0.04 | 0 | 246 | 60 | 220 | 0 | 700 | 400 | 0 | 3964.87 | 8284.9 | 75.41
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 7 | 5 | 3 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 28 | 560 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 580 | 0 | 0 | 167 | 340 | 359 | 0 | 51 | 15 | 202 | 34 | 0 | 0 | 0 | 0 | 3 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 137 | 0 | 17 | 0 | 76 | 30 | 0 | 0 | 102 | 0 | 24 | 8 | 154 | 0 | 0 | 0 | 4877 | 620 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 424 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 60 | 220 | 0 | 1000 | 500 | 0 | 4773 | 9650 | 75.41
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 5 | 3 | 0 | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 24 | 565 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 580 | 0 | 0 | 184 | 345 | 360 | 0 | 51 | 15 | 203 | 34 | 0 | 0 | 0 | 0 | 3 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 140 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 102 | 0 | 35 | 16 | 157 | 0 | 0 | 0 | 4891 | 620 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 504 | 0 | 0 | 0 | 767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 48 | 32 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 60 | 220 | 0 | 1100 | 545 | 0 | 5076 | 9967 | 75.41
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 5 | 3 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 565 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 580 | 0 | 0 | 187 | 325 | 361 | 0 | 51 | 23 | 200 | 34 | 0 | 0 | 0 | 0 | 3 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 135 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 102 | 0 | 35 | 16 | 156 | 0 | 0 | 0 | 4829 | 620 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 49 | 35 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 60 | 220 | 0 | 1100 | 546 | 0 | 5139 | 9968 | 75.41
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 5 | 3 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 36 | 565 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 580 | 0 | 0 | 187 | 330 | 361 | 0 | 51 | 42 | 200 | 33 | 0 | 0 | 0 | 0 | 3 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 135 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 102 | 0 | 24 | 8 | 158 | 0 | 0 | 0 | 4843 | 620 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 564 | 0 | 0 | 0 | 769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 49 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 60 | 220 | 0 | 1000 | 545 | 0 | 5022 | 9865 | 75.41
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 335 | 39 | 0 | 0 | 0 | 5 | 3 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 38 | 565 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 580 | 0 | 0 | 187 | 335 | 361 | 0 | 51 | 45 | 200 | 33 | 0 | 0 | 0 | 0 | 10 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 131 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 102 | 0 | 16 | 8 | 158 | 0 | 0 | 0 | 4936 | 621 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 60 | 220 | 0 | 859 | 550 | 0 | 4858 | 9794 | 75.41
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 335 | 80 | 0 | 0 | 0 | 5 | 3 | 0 | 537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 38 | 520 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 547 | 0 | 0 | 187 | 336 | 360 | 0 | 51 | 44 | 201 | 33 | 0 | 0 | 0 | 0 | 10 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 138 | 0 | 0 | 0 | 86 | 30 | 0 | 0 | 102 | 0 | 16 | 8 | 159 | 0 | 0 | 0 | 4997 | 620 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 730 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 60 | 220 | 0 | 800 | 540 | 0 | 4748 | 9745 | 75.41
Total KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8060400 | 0 | 2013800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3374895 | 0 | 0 | 0 | 6629230 | 211000 | 0 | 160643 | 27600 | 147000 | 232560 | 0 | 10072727.27 | 0 | 0 | 0 | 0 | 254400 | 6473 | 0 | 0 | 0 | 0 | 17785 | 845700 | 0 | 501600 | 9149090.91 | 0 | 0 | 0 | 0 | 0 | 3692865 | 0 | 0 | 0 | 9714544 | 80460 | 0 | 1572364 | 7381500 | 8494200 | 0 | 652488 | 338400 | 4597000 | 500184 | 0 | 594432 | 0 | 0 | 182870 | 0 | 1632000 | 0 | 118136 | 0 | 2011740 | 0 | 8089000 | 0 | 211560 | 3248018.18 | 20933 | 156288 | 0 | 896640 | 343776 | 1184000 | 0 | 2443920 | 0 | 147600 | 67200 | 2631360 | 8550 | 168750 | 0 | 102885682.36 | 11984724 | 8122176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334080 | 9869095 | 0 | 0 | 0 | 13051649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261640 | 423040 | 0 | 0 | 233760 | 3947636 | 0 | 1131182 | 0 | 0 | 0 | 8591127 | 0 | 15960 | 0 | 1204363 | 37008 | 120416 | 80419 | 0 | 0 | 0 | 34429.44 | 528480 | 1840 | 0 | 4298000 | 1707000 | 5276960 | 0 | 14998645 | 11976727.27 | 0 | 98230356.71 | 201116039.07

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 27-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 6576.89 | MW | 12:00 Hr. | Energy Generated |  |  | 201.116 |  | MKWHr.
| Day Peak Demand |  |  | 6576.89 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 9968 | MW | 20:00 Hr. | Energy Demand |  |  | 201.116 |  | MKWHr.
| Evening Peak Demand |  |  | 9968 | MW | 20:00 Hr. | Maximum Temperature |  |  | 29 |  | °C
| Minimum Generation of the Day |  |  | 5755.52 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 800.42 |  | MMCFD
| Maximum Generation of the Day |  |  | 10786.95 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 4.903 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 30.7416 | 0 | 0.0276 | 0 | 0 | 0.16064 | 0 | 0 | 30.9299 | Gas | 109.2419 | Gas | 383123748.6815
| Chattogram Zone |  |  | 4.1945 | 18.8636 | 0.006473 | 0 | 0.8457 | 0.098245 | 0 | 0.2544 | 24.2629 | Coal | 61.2105 | Coal | 403725715.8368
| Cumilla Zone |  |  | 24.3134 | 0 | 0 | 0 | 0 | 0.11814 | 1.632 | 0 | 26.0636 | HFO | 0.3663 | HFO | 6006500.89
| Mymensingh Zone |  |  | 2.6314 | 0 | 0.2148 | 0 | 0 | 0.1773 | 0 | 0 | 3.0235 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 18.5849 | 0 | 0 | 0 | 0 | 0.020933 | 0 | 0 | 18.6059 | Hydro | 0.8457 | Hydro | 84570
| Khulna Zone |  |  | 8.1222 | 9.8691 | 0 | 0 | 0 | 0.33408 | 11.9847 | 0 | 30.3101 | Solar | 2.5289 | Solar | 40923975.6588
| Barishal Zone |  |  | 6.984 | 31.2734 | 0 | 0 | 0 | 0.00184 | 0 | 0 | 38.2592 | Import | 26.6684 | Import | 148456743.48
| Rajshahi Zone |  |  | 13.6699 | 0 | 0 | 0 | 0 | 0.9344 | 13.0516 | 0 | 27.656 | Wind | 0.2544 | Wind | 3742224
| Rangpur Zone |  |  | 0 | 1.2044 | 0.11743 | 0 | 0 | 0.68333 | 0 | 0 | 2.0051
| Total |  |  | 109.2419 | 61.2105 | 0.3663 | 0 | 0.8457 | 2.5289 | 26.6684 | 0.2544 | 201.116
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 383123748.6815 |  | Hydro | 84570
|  |  |  | Coal | 403725715.8368 |  | Solar | 40923975.6588
|  |  |  | HFO | 6006500.89 |  | Import | 148456743.48
|  |  |  | HSD | 0 |  | Wind | 3742224
[5 empty] | Total: | 98,60,63,478 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 70254.55 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 11.9847 | Peak Hr Flow | 620.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 19997418.18 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 13.0516 | Peak Hr Flow | 770.00 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1277 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.632 | Peak Hr Flow | 98.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1289 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 26.6684 | Peak Hr Flow | 1488.00 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 2821
|  |  |  | Chattogram |  | 0 |  | 872
|  |  |  | Cumilla |  | 0 |  | 946
|  |  |  | Mymensingh |  | 0 |  | 878
|  |  |  | Sylhet |  | 0 |  | 431
|  |  |  | Khulna |  | 0 |  | 1309
|  |  |  | Barishal |  | 0 |  | 305
|  |  |  | Rajshahi |  | 0 |  | 1186
|  |  |  | Rangpur |  | 0 |  | 867
|  |  |  | Total |  | 0 |  | 9615
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:06 | 08:35 | Gopalganj 132/33kV S/S T1 LT Tripped showing Siptotec 7SJ82 relays Due to 33kv feeder
fault with stormy weather.
| 08:06 | 08:35 | Gopalganj 132/33kV S/S T2 LT Tripped showing Siprotec 7SJ82 relays Due to 33kv feeder
fault with stormy weather
| 08:17 |  | Hasnabad-Keraniganj 230kV Ckt-2 Tripped from Keranigonj 230/132/33kV end showing 86.2
relays Due to Zone-1 trip, R,Y,B phase pick up (7.9Km) and from Hasnabad 230/132kV end
showing Distance Relay Main-1: 1. Relay Trip L1 2. Relay Trip L1 3. Relay Trip L3 4.
Dis. Trip Z1B 5. Dis. Trip Z1/1p 6. AR Not Ready Distance Relay Main-2: 1. Gen
Trip 2. B-phase Trip 3. Zone-1 Trip 4. Z COM/ EF COM 5. DT/Cat. Rec. 6. AR Block
relays Due to Building construction within the right-of-way.
| 08:22 | 08:40 | Niamatpur 132/33kV S/S Transformer-2 (417T) LT Tripped showing SIEMENS SIPROTEC 7UT85 | [7 empty] | 13.0MW load
|  |  | relays Due to Niamatpur-2 feeder faulty | [7 empty] | interrup.
| 08:25 | 12:52 | Bagerhat-Bhandaria 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing General
Trip OV Alarm OV Trip relays Due to Over Voltage Trip
| 08:26 | 08:46 | Mymensingh 132/33kV S/S Transformer-1 (404T) LT Tripped showing O/C relays Due to 33 kv | [7 empty] | 30.0MW load
|  |  | Akua feeder fault. | [7 empty] | interrup.
| 08:26 | 08:46 | Mymensingh 132/33kV S/S Transformer-2 (414T) LT Tripped showing O/C relays Due to 33 Kv | [7 empty] | 30.0MW load
|  |  | Akua feeder fault. | [7 empty] | interrup.
| 08:29 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- GT
| 08:30 | 08:54 | Madanganj 132/33kV S/S Madanganj -Summit 55 MW 132 kv Ckt Tripped showing OC/EF relay
relays.
| 08:31 | 12:50 | Jhenaidah-Khulna 230kV Ckt-1 Forced S/D from Jhenaidah 230/132kV end Due to Aldc order
and from Khulna(S) 230/132kV end Due to Due to High Voltage.
|  | 08:40 | Khulna (C) S/S TR-1 425T LT is restored.
| 08:44 | 09:00 | Korerhat 400/230/132kV S/S Meghnaghat-1 Forced S/D Due to Shutdown taken by NLDC due to
voltage control
| 08:57 | 09:08 | Bheramara(GK) 132/33kV S/S TR-3 LT Tripped showing Trip Relay relays Due to 33kV PBS Amla | [7 empty] | 12.0MW load
|  |  | Feeder Fault | [7 empty] | interrup.
| 08:57 | 09:07 | Bheramara(GK) 132/33kV S/S TR-3 HT Tripped showing Instantaneous O/C B phase relays Due | [7 empty] | 11.0MW load
|  |  | to 33kV PBS Amla Feeder Fault | [7 empty] | interrup.
| 09:05 | 09:34 | Bakerganj-Patuakhali 132 kV Ckt-1 Tripped from Patuakhali 132/33kV end showing E/F ,O/C | [7 empty] | 24.0MW load
|  |  | relays Due to E/F ,O/C | [7 empty] | interrup.
Patuakhali 132/33kV
end
| 09:12 | 14:34 | Chowmuhani 230/132/33kV S/S TR3 Scheduled S/D Due to Emergency shutdown taken for 132/33
kV, TR-03 X-former today at 09:12 for 132kVJack BUS Maintenance.
|  | 09:45 | Bogura 230/132kV S/S Confidance UN-2 is restored.
| 10:14 | 12:06 | Kushtia 132/33kV S/S T-3 LT Forced S/D Due to Khoksha feeder red hot maintenance | [7 empty] | 15.0MW load
interrup.
| 10:16 | 12:05 | Kushtia 132/33kV S/S T-3 HT Forced S/D Due to Khoksha feeder red hot maintenance | [7 empty] | 15.0MW load
interrup.
| 10:20 | 11:19 | Munshiganj 132/33kV S/S Transformer-1 LT Tripped showing DIF E/F Trip relays. | [7 empty] | 20.0MW load
interrup.
| 10:20 | 11:08 | Munshiganj 132/33kV S/S Transformer-2 LT Tripped showing DIF E/F Trip relays. | [7 empty] | 20.0MW load
interrup.
| 10:24 |  | Payra 1320 MW Shutdown with remarks:- unit-2
| 10:25 |  | Payra 1320 MW Synchronized with remarks:- Unit-1 False Sms)
| 10:25 | 12:18 | Goalpara 132/33kV S/S T1 LT Scheduled S/D Due to Red hot Khulna pbs shutdown | [7 empty] | 12.0MW load
interrup.
| 10:26 | 12:16 | Goalpara 132/33kV S/S T1 HT Scheduled S/D Due to Red hot Khulna pbs shutdown
| 10:28 | 12:18 | Goalpara 132/33kV S/S T-5 LT Scheduled S/D Due to Red hot Khulna pbs shutdown
| 10:29 | 12:17 | Goalpara 132/33kV S/S T-5 HT Scheduled S/D Due to Red hot Khulna pbs shutdown
| 10:33 | 12:12 | Goalpara 132/33kV S/S T-6 LT Scheduled S/D Due to Red hot Khulna pbs shutdown
| 10:34 | 12:10 | Goalpara 132/33kV S/S T-6 HT Scheduled S/D Due to Red hot Khulna pbs shutdown
| 10:35 | 11:16 | Korerhat 400/230/132kV S/S Hathajari-2 Tripped showing 7SA87 relays Due to R-Y Phase
fault
| 10:45 | 12:58 | Bogura 230/132kV S/S T-03 HT Forced S/D Due to Maintenance work (Oil Refill)
| 10:45 | 12:58 | Bogura 230/132kV S/S T-03 LT Forced S/D Due to Maintenance work (Oil Refill)
|  | 10:48 | Rajbari 132/33kV S/S Transformer-3 HT is restored.
|  | 10:50 | Rajbari 132/33kV S/S Transformer-3 LT is restored.
| 11:02 | 11:10 | Maijdee 132/33kV S/S TR-01 HT Tripped showing 132KV Transformer Main 1 Relay relays Due
to 33 kv Sobornachar feeder closed and Trip. 132kv x-former T-1 Primary GCB403B,
Secondary VCB407B Trip
| 11:02 | 11:11 | Maijdee 132/33kV S/S TR-01 LT Tripped showing 33KV Trasformer F51 Relay, BCU1 Bay
Control Unit, relays Due to 33 kv Sobornachar feeder closed and Trip. 132kv x-former T-1
Primary GCB403B, Secondary VCB407B Trip
| 11:03 | 11:50 | Baroaulia-Hathazari 132 kV Ckt-1 Tripped from Baroaulia 132/33kV end showing 1.C relays
Due to Thunder storm and heavy rain.
| 11:14 | 15:46 | Hathazari-Kaptai 132kV Ckt-2 Tripped from Hathazari 230/132/33kV end showing Siprotec
7SA87 relays Due to heavy rain, thunderstrome
| 11:14 | 15:46 | Hathazari-Kaptai 132kV Ckt-2 Tripped from Hathazari 230/132/33kV end showing Siprotec
7SA87 relays Due to heavy rain, thunderstrome
| 11:31 | 14:12 | Halishahar-Khulshi 132kV Ckt-1 Tripped from Halishahar 132/33kV end showing Line black
relay relays.
| 11:36 | 12:53 | Dohazari-Sikalbaha 132 kV Ckt-1 Tripped from Dohazari 132/33kV end showing Distance
Relay, O/C Relay relays Due to Storm & thundering
| 11:37 | 12:52 | Patiya 132/33kV S/S Patiya-Dohazari Ckt-01 Tripped showing Line distance relay, BCU
relays.
| 11:55 | 12:32 | Cox'sbazar-Dohazari 132 kV Ckt-2 Tripped from Dohazari 132/33kV end showing Distance, O/C
relays Due to Storm & thundering
| 12:10 | 13:33 | Kushtia 132/33kV S/S T2 LT Forced S/D Due to T-2A 33kV side R-phase CT source end red hot
maintenance.
| 12:11 | 13:15 | Kushtia 132/33kV S/S T2 HT Forced S/D Due to T-2A 33kV side R-phase CT source end red hot
maintenance.
| 12:36 | 12:50 | Baroaulia 132/33kV S/S SASM HT Tripped showing 1.Earth Fault relays Due to Bad weather
|  | 13:43 | Ghorasal- Ishwardi 230 kV Ckt-2 is restored.
| 14:01 | 14:14 | Munshiganj 132/33kV S/S Transformer-1 LT Tripped showing Heavy speed Trip Relay relays | [7 empty] | 50.0MW load
|  |  | Due to Due to detect a Fault | [7 empty] | interrup.
| 14:01 | 14:16 | Munshiganj 132/33kV S/S Transformer-2 LT Tripped showing Heavy speed relay relays Due to | [7 empty] | 50.0MW load
|  |  | Due to detect a Fault | [7 empty] | interrup.
|  | 14:41 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 is restored.
| 14:48 | 16:12 | Hasnabad 230/132kV S/S AUTO TR-2 HT Forced S/D Due to 132kv reserve bus mintennce work
| 14:48 | 16:12 | Hasnabad 230/132kV S/S AUTO TR-2 LT Forced S/D Due to 132 kv mintennce work
| 14:53 | 03:30 | Maijdee 132/33kV S/S TR-01 LT Scheduled S/D Due to due to the burning of the CT clamp and
wire at the 33 kV bus source side of BREB.
| 14:53 | 03:30 | Maijdee 132/33kV S/S TR-01 HT Scheduled S/D Due to due to the burning of the CT clamp and
wire at the 33 kV bus source side of BREB.
| 15:36 |  | Hasnabad-Keraniganj 230kV Ckt-2 Forced S/D from Hasnabad 230/132kV end Due to line
conductor maintenace work and from Keranigonj 230/132/33kV end Due to Maintenance at
Hasnabad end.
| 15:37 |  | Hasnabad-Keraniganj 230kV Ckt-2 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Maintenance at Hasnabad end.
| 15:47 | 20:31 | Hathazari-Kaptai 132kV Ckt-2 Scheduled S/D from Hathazari 230/132/33kV end Due to Disk
blast
| 19:02 |  | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D Due to Voltage Up.
| 20:00 |  | Evening Peak Generation is 9968 MW.
| 20:51 | 21:38 | Srinagar 132/33kV S/S Tr-01 LT Scheduled S/D Due to Red hot maintenance in 33 KV side in | [7 empty] | 24.0MW load
|  |  | TR-01 | [7 empty] | interrup.
| 20:52 | 21:36 | Srinagar 132/33kV S/S Tr-01 HT Scheduled S/D Due to Red hot maintenance in 33 KV side in | [7 empty] | 24.0MW load
|  |  | TR-01 | [7 empty] | interrup.
| 23:45 | 00:45 | Chowmuhani 230/132/33kV S/S TR3-435T HT Scheduled S/D Due to Red Hot Maintenance Of 33 kV | [7 empty] | 10.0MW load
|  |  | Tr-03 Bus | [7 empty] | interrup.
| 23:45 | 00:46 | Chowmuhani 230/132/33kV S/S TR3-435T LT Scheduled S/D Due to Red Hot Maintenance Of 33 kV | [7 empty] | 10.0MW load
|  |  | Tr-03 Bus | [7 empty] | interrup.
| 01:10 | 01:55 | Chowmuhani 230/132/33kV S/S TR2-425T HT Scheduled S/D Due to Red Hot Maintenance of 33KV | [7 empty] | 20.0MW load
|  |  | L Bus Incoming Loop | [7 empty] | interrup.
| 01:10 | 01:56 | Chowmuhani 230/132/33kV S/S TR3-435T LT Scheduled S/D Due to Red Hot Maintenance of 33KV | [7 empty] | 20.0MW load
|  |  | L Bus Incoming Loop | [7 empty] | interrup.
| 05:00 |  | Minimum generation 8284 MW
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 27-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 333 | 8060400 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 151 | 3374895 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 211000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 6629230 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 5 | 147000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 3 | 232560 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 0 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 0 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 160643 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 390 | 10072727.27 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 2013800 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 17 | 27600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1234 | 30929855.27
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 80460 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 35 | 845700 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 150 | 3692865 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 6473 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 25 | 501600 | plant availability zero
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 17785 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 580 | 9714544 | U2 outage added
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 254400 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 565 | 9149090.91 | U1 under maintenance
Chattogram Area Total |  |  |  |  | 4898.863 | 1355 | 24262917.91
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 200 | 4597000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 361 | 8494200 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 325 | 7381500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 34 | 500184 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 23 | 338400 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 187 | 1572364 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 652488 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 594432 | ST Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 98 | 1632000 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 3 | 182870 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 118136 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1282 | 26063574
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 156 | 2631360 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8550 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 16 | 67200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 35 | 147600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 168750 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | From 17:00 to 20:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 207 | 3023460
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 20933 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 211560 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 135 | 3248018.18 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 1184000 | plant availability zero
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 343776 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 896640 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 102 | 2443920 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 156288 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 2011740 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 381 | 8089000 | FGMO not available because of Cooling Tower Fan
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 751 | 18605875.18
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 620 | 11984724 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 383 | 8122176 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | FGMO
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 334080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 556 | 9869095 | U1 under maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1559 | 30310075
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 1100 | 14998645 | RRT
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 60 | 1707000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 546 | 11976727.27 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5276960 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 173 | 4298000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1840 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2099 | 38259172.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 261640 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 180 | 3947636 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 1131182 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 8591127 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 15960 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 770 | 13051649 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 233760 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 423040 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1364 | 27655994
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1204363 | Plant availability zero, U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 33 | 80419 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 34429.44 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 37008 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 120416 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 528480 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 117 | 2005115.44
Eastern Grid Total |  |  |  |  | 17418.042 | 4829 | 102885682.36
Western Grid Total |  |  |  |  | 11852.195 | 5139 | 98230356.71
National Grid Total |  |  |  |  | 29270.237 | 9968 | 201116039.07
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 27-05-2026
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 5947.74 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3666.6 | MW
i) Dhaka area |  |  | 2820.94 |  | MW | i) Khulna area |  |  |  | 1309 | MW
ii) Chattogram area |  |  | 871.8 |  | MW | ii) Barishal area |  |  |  | 305 | MW
iii) Cumilla area |  |  | 946 |  | MW | iii) Rajshahi area |  |  |  | 1185.6 | MW
iv) Mymensingh area |  |  | 878 |  | MW | iv) Rangpur area |  |  |  | 867 | MW
v) Sylhet area |  |  | 431 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 9614.34 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 58 | 17:00 | 133 | Natore | 123 | 00:00
2 | AKSML | 16.5 | 11:00 | 68 | Hathazari | 60 | 00:00 | 134 | Nawabganj | 49.4 | 22:00
3 | Aftabnagar | 26 | 00:00 | 69 | Hatirjheel | 27 | 13:00 | 135 | Netrakona | 123 | 19:30
4 | Agargaon | 63 | 19:30 | 70 | Ishurdi | 58 | 19:30 | 136 | New | 34 | 00:00
5 | Agrabad | 50 | 19:30 | 71 | Jaldhaka | 75 | 00:00 | 137 | Niamatpur | 65 | 23:00
6 | Amnura | 29 | 00:00 | 72 | Jamalpur | 96 | 20:00 | 138 | Noapara | 25 | 22:00
7 | Ashuganj | 75 | 19:00 | 73 | Jashore | 133 | 19:30 | 139 | PHP | 7 | 06:00
8 | BSRM | 189 | 17:00 | 74 | Jhenaidah | 96 | 01:00 | 140 | Pabna | 77 | 19:00
9 | Bagerhat | 72 | 22:00 | 75 | Joydebpur | 74 | 22:00 | 141 | Palashbari | 108 | 19:00
10 | Bajitpur | 64 | 15:00 | 76 | Joypurhat | 56 | 19:30 | 142 | Panchagarh | 58 | 19:30
11 | Bakerganj | 11.6 | 22:00 | 77 | Juldah | 11 | 00:00 | 143 | Patiya | 9 | 00:00
12 | Bakulia | 71 | 10:00 | 78 | KSRM | 9 | 06:00 | 144 | Patuakhali | 56 | 00:00
13 | Banani | 24 | 13:00 | 79 | Kabirpur | 83 | 01:00 | 145 | Payra | 36 | 00:00
14 | Bangabhaban | 3 | 00:00 | 80 | Kachua | 66 | 00:00 | 146 | Postogola | 31 | 00:00
15 | Barapukuria | 56 | 20:00 | 81 | Kaliganj | 23 | 14:00 | 147 | Pubail | 15 | 20:00
16 | Barguna | 22 | 00:00 | 82 | Kallyanpur | 75 | 14:00 | 148 | Purbachal | 21 | 19:30
17 | Barishal | 80 | 00:00 | 83 | Kalurghat | 23 | 18:30 | 149 | Purbasadipur | 114 | 00:00
18 | Barishal-230 | 74 | 01:00 | 84 | Kamrangirchar | 37 | 00:00 | 150 | Rahanpur | 38 | 00:00
19 | Baroaulia | 44 | 00:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 0 | 00:00
20 | Baroirhat | 48 | 21:00 | 86 | Kasba | 29 | 22:00 | 152 | Rajbari | 61 | 00:00
21 | Bashundhara | 114 | 13:00 | 87 | Kazla | 62 | 00:00 | 153 | Rajendrapur | 75 | 01:00
22 | BashundharaCement | 6 | 00:00 | 88 | Keranigonj | 51 | 22:00 | 154 | Rajshahi | 88 | 00:00
23 | Beanibazar | 60 | 19:00 | 89 | Khagrachori | 32 | 19:30 | 155 | Rajshahi-230 | 76 | 13:00
24 | Benapole | 62 | 00:00 | 90 | Khulna | 54 | 12:00 | 156 | Ramganj | 78 | 00:00
25 | Bhaluka | 93 | 19:00 | 91 | Khulshi | 137 | 00:00 | 157 | Rampur | 32 | 00:00
26 | Bhandaria | 56 | 00:00 | 92 | Kishoreganj | 114 | 19:30 | 158 | Rangamati | 14 | 11:00
27 | Bhangura | 34 | 19:30 | 93 | Kodda | 118 | 19:00 | 159 | Rangpur | 114 | 19:30
28 | Bheramara(GK) | 54 | 00:00 | 94 | Kulaura | 37 | 19:00 | 160 | Ruppur | 2.6 | 12:00
29 | Bhulta | 128 | 01:00 | 95 | Kurigram | 64 | 19:30 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 52 | 00:00 | 96 | Kushtia | 112 | 00:00 | 162 | Saidpur | 81 | 19:30
31 | Bogura | 131 | 01:00 | 97 | Laksam | 26 | 00:00 | 163 | Santhia | 30 | 19:30
32 | Borhanuddin | 91 | 06:00 | 98 | Lakshmipur | 31 | 00:00 | 164 | Satkhira | 153 | 00:00
33 | Brahmanbaria | 105 | 19:00 | 99 | Lalbag | 38 | 00:00 | 165 | Satmasjid | 62 | 13:00
34 | Cantonment | 76 | 14:00 | 100 | Lalmonirhat | 60 | 19:30 | 166 | Savar | 74 | 00:00
35 | Chandina | 20 | 18:30 | 101 | MI_Cement | 2 | 16:00 | 167 | SevenRings | 1.31 | 03:00
36 | Chandpur | 62 | 00:00 | 102 | Madanganj | 26 | 13:00 | 168 | ShahCement | 21 | 00:00
37 | Chandraghona | 28 | 11:00 | 103 | Madaripur | 84 | 00:00 | 169 | Shahjadpur | 67 | 20:00
38 | Chapai | 61 | 00:00 | 104 | Madartek | 52 | 22:00 | 170 | Shahjibazar | 85 | 19:00
39 | Charsaidpur | 12 | 00:00 | 105 | Madunaghat | 40 | 00:00 | 171 | Shahmirpur | 37 | 00:00
40 | Chauddagram | 51 | 20:00 | 106 | Magura | 56 | 19:00 | 172 | Shariatpur | 66 | 00:00
41 | Chhatak | 27 | 22:00 | 107 | Mahasthangarh | 70 | 20:00 | 173 | Sherpur | 124 | 19:30
42 | Chowmuhani | 115 | 23:00 | 108 | Maijdee | 37 | 00:00 | 174 | Shikalbaha | 17.5 | 22:00
43 | Chuadanga | 106 | 22:00 | 109 | Manikganj | 90 | 00:00 | 175 | Shitalakhya | 44.1 | 19:30
44 | Coxsbazar | 131 | 01:00 | 110 | Maniknagar | 39 | 13:00 | 176 | Sholosohor | 32 | 22:00
45 | Cumilla(N) | 79 | 23:00 | 111 | Matarbari | 48 | 03:00 | 177 | Shomvuganj | 14 | 00:00
46 | Cumilla(S) | 103 | 21:00 | 112 | Matuail | 35 | 00:00 | 178 | Shyampur | 82 | 00:00
47 | Daganbhuiyan | 29 | 00:00 | 113 | Metrorail_Motijheel | 20 | 17:00 | 179 | Siddhirganj | 63 | 13:00
48 | Daudkandi | 92 | 19:30 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 88 | 19:30
49 | DhakaUniversity | 28 | 12:00 | 115 | Millgate | 98 | 04:00 | 181 | Sonargaon | 62 | 00:00
50 | Dhamrai | 72 | 00:00 | 116 | Mirpur | 92 | 19:30 | 182 | Sreemongol | 55 | 00:00
51 | Dhanmondi | 49.2 | 19:00 | 117 | Mirsorai | 7 | 19:30 | 183 | Sreepur | 66 | 00:00
52 | Dohazari | 96 | 11:00 | 118 | Mirzapur | 32 | 20:00 | 184 | Srinagar | 43.2 | 22:00
53 | Faridpur | 124 | 00:00 | 119 | Mithapukur | 58 | 19:00 | 185 | Sunamganj | 46 | 00:00
54 | Fatullah | 40 | 00:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 44 | 00:00
55 | Fenchuganj | 30 | 19:00 | 121 | Mogbazar | 44.6 | 19:30 | 187 | Sylhet-132 | 77 | 19:00
56 | Feni | 85 | 22:00 | 122 | Mongla | 25 | 08:00 | 188 | TK | 20 | 11:00
57 | GPH | 1 | 00:00 | 123 | Motijheel | 24 | 19:00 | 189 | Tangail | 126 | 21:00
58 | Ghatail | 73 | 18:30 | 124 | Muktagacha | 30 | 18:00 | 190 | Taraganj | 16 | 18:30
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 84 | 00:00 | 191 | Tasnim | 5 | 03:00
60 | Ghorashal-230 | 68 | 00:00 | 126 | Muradnagar | 39 | 20:00 | 192 | Thakurgaon | 96 | 20:00
61 | Goalpara | 30 | 19:00 | 127 | Mymensingh | 134 | 19:00 | 193 | Tongi | 69 | 00:00
62 | Gollamari | 90 | 00:00 | 128 | Nabinagar | 66 | 19:30 | 194 | Ullahpara | 30 | 19:30
63 | Gopalganj | 82 | 07:00 | 129 | Naogaon | 112 | 00:00 | 195 | Ullon | 43 | 14:00
64 | Gulshan | 62 | 19:00 | 130 | Narail | 45 | 00:00 | 196 | Uttara | 57 | 19:00
65 | Halishahar | 51 | 11:00 | 131 | Narinda | 32 | 22:00 | 197 | UttaraNew | 32 | 14:00
66 | HaripurSBU | 86 | 02:00 | 132 | Narshingdi | 123 | 00:00 | 198 | Zigatola | 56 | 14:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 27-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 10786.95 | 0 |  | 10786.95
1:00 | 10392.81 | 0 |  | 10392.81
2:00 | 10010.67 | 0 |  | 10010.67
3:00 | 9702.6 | 0 |  | 9702.6
4:00 | 9136.48 | 0 |  | 9136.48
5:00 | 8299.06 | 0 |  | 8299.06
6:00 | 7379.85 | 0 |  | 7379.85
7:00 | 6895.58 | 0 |  | 6895.58
8:00 | 6433.92 | 0 |  | 6433.92
9:00 | 5755.52 | 0 |  | 5755.52
10:00 | 5959.49 | 0 |  | 5959.49
11:00 | 6173.94 | 0 |  | 6173.94
12:00 | 6576.89 | 0 |  | 6576.89
13:00 | 7237.64 | 0 |  | 7237.64
14:00 | 7700.43 | 0 |  | 7700.43
15:00 | 7861.79 | 0 |  | 7861.79
16:00 | 7872.63 | 0 |  | 7872.63
17:00 | 7934.3 | 0 |  | 7934.3
18:00 | 8284.9 | 0 |  | 8284.9
19:00 | 9650 | 0 |  | 9650
19:30 | 9967 | 0 |  | 9967
20:00 | 9968 | 0 |  | 9968
21:00 | 9865 | 0 |  | 9865
22:00 | 9794 | 0 |  | 9794
23:00 | 9745 | 0 |  | 9745
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 27-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5758 | 5028.95 | 10786.95 | DAILY GENERATION CURVE
00:30 | 5643.5 | 4946.38 | 10589.88
01:00 | 5529 | 4863.81 | 10392.81 | 27-05-2026
01:30 | 5391 | 4810.74 | 10201.74
02:00 | 5253 | 4757.67 | 10010.67
02:30 | 5198.5 | 4658.135 | 9856.635
03:00 | 5144 | 4558.6 | 9702.6
03:30 | 4954 | 4465.54 | 9419.54
04:00 | 4764 | 4372.48 | 9136.48
04:30 | 4530 | 4187.77 | 8717.77
05:00 | 4296 | 4003.06 | 8299.06
05:30 | 4151.51 | 3687.945 | 7839.455
06:00 | 4007.02 | 3372.83 | 7379.85
06:30 | 3850.975 | 3286.74 | 7137.715
07:00 | 3694.93 | 3200.65 | 6895.58
07:30 | 3567.81 | 3096.94 | 6664.75
08:00 | 3440.69 | 2993.23 | 6433.92
08:30 | 3135.26 | 2959.46 | 6094.72
09:00 | 2829.83 | 2925.69 | 5755.52
09:30 | 2836.11 | 3021.395 | 5857.505
10:00 | 2842.39 | 3117.1 | 5959.49
10:30 | 2855.31 | 3211.405 | 6066.715
11:00 | 2868.23 | 3305.71 | 6173.94
11:30 | 3048.9 | 3326.515 | 6375.415
12:00 | 3229.57 | 3347.32 | 6576.89
12:30 | 3413.045 | 3494.22 | 6907.265
13:00 | 3596.52 | 3641.12 | 7237.64
13:30 | 3815.815 | 3653.22 | 7469.035
14:00 | 4035.11 | 3665.32 | 7700.43
14:30 | 4085.445 | 3695.665 | 7781.11
15:00 | 4135.78 | 3726.01 | 7861.79
15:30 | 4160.49 | 3706.72 | 7867.21
16:00 | 4185.2 | 3687.43 | 7872.63
16:30 | 4255.115 | 3648.35 | 7903.465
17:00 | 4325.03 | 3609.27 | 7934.3
17:30 | 4322.53 | 3787.07 | 8109.6
18:00 | 4320.03 | 3964.87 | 8284.9
18:30 | 4598.515 | 4368.935 | 8967.45
19:00 | 4877 | 4773 | 9650
19:30 | 4891 | 5076 | 9967
20:00 | 4829 | 5139 | 9968
20:30 | 4836 | 5080.5 | 9916.5 |  | Executive Engineer
21:00 | 4843 | 5022 | 9865 |  | Network Operation Division
21:30 | 4889.5 | 4940 | 9829.5
22:00 | 4936 | 4858 | 9794
22:30 | 4966.5 | 4803 | 9769.5
23:00 | 4997 | 4748 | 9745

## En-Curve
QF-LDC-12
Date | 27-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4123 | 1931 | 923 | 0 | 104 | 409.95 | 67 | 3135 | 0 | 17 | 67 | 0 | 0 | 10 | 0 | DAILY ENERGY CURVE
00:30 | 4097.5 | 1884 | 923 | 0 | 100 | 407.88 | 67 | 3057.5 | 0 | 8.5 | 33.5 | 0 | 0 | 11 | 0 | 27-05-2026
01:00 | 4072 | 1837 | 923 | 0 | 96 | 405.81 | 67 | 2980 | 0 | 0 | 0 | 0 | 0 | 12 | 0
01:30 | 4066 | 1762.5 | 923 | 0 | 92 | 403.24 | 67 | 2874.5 | 0 | 0 | 0 | 0 | 0 | 13.5 | 0 | Energy Generated | 201.116 |  | MKWHr
02:00 | 4060 | 1688 | 923 | 0 | 88 | 400.67 | 67 | 2769 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 4046.5 | 1655 | 923 | 0 | 87 | 401.635 | 68 | 2662.5 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | Total Energy Requirement | 201.116 |  | MKWHr
03:00 | 4033 | 1622 | 923 | 0 | 86 | 402.6 | 69 | 2556 | 0 | 0 | 0 | 0 | 0 | 11 | 0
03:30 | 3945 | 1523.5 | 923 | 0 | 85 | 403.54 | 69 | 2459.5 | 0 | 0 | 0 | 0 | 0 | 11 | 0
04:00 | 3857 | 1425 | 923 | 0 | 84 | 404.48 | 69 | 2363 | 0 | 0 | 0 | 0 | 0 | 11 | 0
04:30 | 3586 | 1368 | 872.5 | 0 | 82 | 402.77 | 69 | 2321.5 | 0 | 0 | 0 | 0 | 0 | 16 | 0
05:00 | 3315 | 1311 | 822 | 0 | 80 | 401.06 | 69 | 2280 | 0 | 0 | 0 | 0 | 0 | 21 | 0
05:30 | 3150 | 1260.75 | 595.5 | 0 | 78 | 401.935 | 69 | 2255 | 9.27 | 0 | 0 | 0 | 0 | 20 | 0
06:00 | 2985 | 1210.5 | 369 | 0 | 76 | 402.81 | 69 | 2230 | 18.54 | 0 | 0 | 0 | 0 | 19 | 0
06:30 | 2791 | 1165.25 | 369 | 0 | 75 | 408.965 | 34.5 | 2228.5 | 45 | 0 | 0 | 0 | 0 | 20.5 | 0
07:00 | 2597 | 1120 | 369 | 0 | 74 | 415.12 | 0 | 2227 | 71.46 | 0 | 0 | 0 | 0 | 22 | 0
07:30 | 2508 | 1097 | 290.5 | 0 | 77 | 408.25 | 0 | 2221 | 49 | 0 | 0 | 0 | 0 | 14 | 0
08:00 | 2419 | 1074 | 212 | 0 | 80 | 401.38 | 0 | 2215 | 26.54 | 0 | 0 | 0 | 0 | 6 | 0
08:30 | 2300.5 | 897.5 | 182 | 0 | 83 | 411.49 | 0 | 2179.5 | 32.73 | 0 | 0 | 0 | 0 | 8 | 0
09:00 | 2182 | 721 | 152 | 0 | 86 | 421.6 | 0 | 2144 | 38.92 | 0 | 0 | 0 | 0 | 10 | 0
09:30 | 2256 | 756.5 | 181.5 | 0 | 44.5 | 428.17 | 0 | 2116.5 | 60.335 | 0 | 0 | 0 | 0 | 14 | 0
10:00 | 2330 | 792 | 211 | 0 | 3 | 434.74 | 0 | 2089 | 81.75 | 0 | 0 | 0 | 0 | 18 | 0
10:30 | 2342.5 | 799.5 | 330 | 0 | 7.5 | 448.57 | 0 | 2011 | 113.145 | 0 | 0 | 0 | 0 | 14.5 | 0
11:00 | 2355 | 807 | 449 | 0 | 12 | 462.4 | 0 | 1933 | 144.54 | 0 | 0 | 0 | 0 | 11 | 0
11:30 | 2495.5 | 893 | 349.5 | 0 | 12 | 492.06 | 0 | 1921.5 | 201.355 | 0 | 0 | 0 | 0 | 10.5 | 0
12:00 | 2636 | 979 | 250 | 0 | 12 | 521.72 | 0 | 1910 | 258.17 | 0 | 0 | 0 | 0 | 10 | 0
12:30 | 2845 | 986 | 223 | 0 | 12 | 534.54 | 0 | 1929.5 | 372.225 | 0 | 0 | 0 | 0 | 5 | 0
13:00 | 3054 | 993 | 196 | 0 | 12 | 547.36 | 0 | 1949 | 486.28 | 0 | 0 | 0 | 0 | 0 | 0
13:30 | 3216 | 1042.5 | 195.5 | 0 | 12 | 546.86 | 17 | 1964 | 471.175 | 0 | 0 | 0 | 0 | 4 | 0
14:00 | 3378 | 1092 | 195 | 0 | 12 | 546.36 | 34 | 1979 | 456.07 | 0 | 0 | 0 | 0 | 8 | 0
14:30 | 3385.5 | 1125 | 195.5 | 0 | 13 | 552.28 | 34.5 | 2020.5 | 449.33 | 0 | 0 | 0 | 0 | 5.5 | 0
15:00 | 3393 | 1158 | 196 | 0 | 14 | 558.2 | 35 | 2062 | 442.59 | 0 | 0 | 0 | 0 | 3 | 0
15:30 | 3409 | 1176.5 | 195.5 | 0 | 15 | 561.875 | 35 | 2090.5 | 374.335 | 0 | 0 | 0 | 0 | 9.5 | 0
16:00 | 3425 | 1195 | 195 | 0 | 16 | 565.55 | 35 | 2119 | 306.08 | 0 | 0 | 0 | 0 | 16 | 0
16:30 | 3426.5 | 1212 | 195.5 | 0 | 48 | 567.655 | 35 | 2176 | 232.31 | 0 | 0 | 0 | 0 | 10.5 | 0
17:00 | 3428 | 1229 | 196 | 0 | 80 | 569.76 | 35 | 2233 | 158.54 | 0 | 0 | 0 | 0 | 5 | 0
17:30 | 3421.5 | 1197.5 | 253.5 | 0 | 85 | 613.815 | 35 | 2406 | 94.785 | 0 | 0 | 0 | 0 | 2.5 | 0
18:00 | 3415 | 1166 | 311 | 0 | 90 | 657.87 | 35 | 2579 | 31.03 | 0 | 0 | 0 | 0 | 0 | 0
18:30 | 3425.5 | 1248 | 465.5 | 0 | 95 | 708.935 | 35 | 2954.5 | 15.515 | 3.5 | 16 | 0 | 0 | 0 | 0
19:00 | 3436 | 1330 | 620 | 0 | 100 | 760 | 35 | 3330 | 0 | 7 | 32 | 0 | 0 | 0 | 0
19:30 | 3459 | 1339 | 620 | 0 | 100 | 767 | 35 | 3538 | 0 | 17 | 92 | 0 | 0 | 0 | 0
20:00 | 3444 | 1296 | 620 | 0 | 98 | 770 | 35 | 3569 | 0 | 17 | 119 | 0 | 0 | 0 | 0
20:30 | 3454.5 | 1314 | 620 | 0 | 101 | 769.5 | 35 | 3521.5 | 0 | 8.5 | 92.5 | 0 | 0 | 0 | 0
21:00 | 3465 | 1332 | 620 | 0 | 104 | 769 | 35 | 3474 | 0 | 0 | 66 | 0 | 0 | 0 | 0
21:30 | 3482 | 1367.5 | 620.5 | 0 | 102 | 769.5 | 35 | 3408 | 0 | 0 | 45 | 0 | 0 | 0 | 0
22:00 | 3499 | 1403 | 621 | 0 | 100 | 770 | 35 | 3342 | 0 | 0 | 24 | 0 | 0 | 0 | 0
22:30 | 3529.5 | 1438.5 | 620.5 | 0 | 103 | 750 | 35 | 3269 | 0 | 0 | 24 | 0 | 0 | 0 | 0
23:00 | 3560 | 1474 | 620 | 0 | 106 | 730 | 35 | 3196 | 0 | 0 | 24 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 27-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 22 | -58 | 194 | 20 | 714 | 14 | Ishurdi-Ghorashal Ckt-1 | Export | 667418.18
1:00 | 24 | -57 | 190 | 24 | 674 | 28
2:00 | 36 | -57 | 204 | 20 | 684 | 44 |  | Import | 70254.55
3:00 | 45 | -55 | 224 | 22 | 596 | 68
4:00 | 60 | -55 | 314 | 22 | 628 | 86 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 80 | -48 | 328 | 28 | 754 | 106
6:00 | 59 | -48 | 366 | 26 | 746 | 80 |  | Import | 0
7:00 | 89 | -35 | 362 | 18 | 0 | -82
8:00 | 60 | -20 | 256 | 18 | 944 | 28 | Sirajganj-Sreepur Ckt-1 | Export | 0
9:00 | 33 | -21 | 188 | 8 | 1048 | 10
10:00 | 22 | -25 | 172 | 2 | 1010 | 32 |  | Import | 0
11:00 | 48 | -31 | 184 | -6 | 940 | 10
12:00 | 0 | -19 | 134 | 26 | 752 | 20 | Sirajganj-Sreepur Ckt-2 | Export | 0
13:00 | -3 | -25 | 164 | 36 | 686 | 2
14:00 | -15 | -35 | 114 | 32 | 620 | -32 |  | Import | 0
15:00 | -14 | -36 | 130 | 28 | 610 | -24
16:00 | -10 | -33 | 154 | 42 | 644 | -22 | Gopalganj-Aminbazar Ckt-1 | Export | 9650000
17:00 | -11 | -31 | 156 | 46 | 664 | -16
18:00 | 2 | -38 | 178 | 30 | 872 | -52 |  | Import | 0
18:30 | 15 | -39 | 196 | 28 | 1078 | -69
19:00 | 21 | -51 | 194 | 24 | 1070 | -80 | Gopalganj-Aminbazar Ckt-2 | Export | 9680000
19:30 | 12 | -44 | 154 | 24 | 1082 | -104
20:00 | 15 | -44 | 166 | 26 | 1096 | -102 |  | Import | 0
21:00 | 23 | -41 | 188 | 32 | 0 | -78
22:00 | 19 | -42 | 178 | 32 | 902 | -54 |  | Total Export | 19997418.18
23:00 | 24 | -39 | 184 | 36 | 862 | -36 |  | Total Import | 70254.55
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 27-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 414 | 09:00 | 394 | 00:00 | Madunaghat | 417 | 12:00 | 398 | 00:00
Amtali | 422 | 09:00 | 412 | 00:00 | Meghnaghat | 415 | 09:00 | 395 | 00:00
Ashuganj | 424 | 8:00 | 410 | 19:00 | Payra | 423 | 10:00 | 413 | 19:30
Bhulta | 419 | 07:00 | 404 | 19:00 | Rahanpur | 424 | 05:00 | 393 | 19:00
Bibiana | 417 | 11:00 | 405 | 00:00 | Rampal | 415 | 09:00 | 391 | 00:00
BIPTC | 408 | 06:00 | 389 | 00:00
Bogura | 417 | 06:00 | 383 | 19:30
Gopalganj | 417 | 09:00 | 397 | 00:00
Kaliakoir | 415 | 09:00 | 395 | 00:00
Korerhat | 422 | 12:00 | 401 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 244 | 07:00 | 233 | 19:00 | Jhenaidah | 244 | 08:00 | 218 | 00:00
AKSML | 242 | 12:00 | 231 | 00:00 | Kachua | 246 | 10:00 | 233 | 19:00
Aminbazar | 245 | 08:00 | 233 | 18:00 | Kaliakoir | 247 | 08:00 | 231 | 19:00
Ashuganj | 242 | 08:00 | 233 | 19:00 | Keranigonj | 244 | 09:00 | 232 | 19:00
Ashuganj-400 | 242 | 08:00 | 233 | 19:00 | Khulna(S) | 245 | 08:00 | 222 | 00:00
Baghabari | 241 | 07:00 | 228 | 18:30 | Korerhat | 244 | 10:00 | 233 | 19:00
Barapukuria | 236 | 04:00 | 208 | 19:00 | Madunaghat | 240 | 12:00 | 231 | 00:00
Barapukuria-230 | 236 | 04:00 | 208 | 19:00 | Madunaghat-400 | 241 | 12:00 | 232 | 00:00
Barishal | 242 | 08:00 | 231 | 00:00 | Maniknagar | 243 | 08:00 | 236 | 18:00
Bheramara | 243 | 08:00 | 221 | 19:00 | Meghnaghat | 249 | 10:00 | 241 | 23:00
Bhulta | 246 | 08:00 | 235 | 19:00 | Meghnaghat-400 | 245 | 06:00 | 235 | 19:00
Bibiana | 246 | 08:00 | 236 | 19:00 | Mirsorai | 245 | 12:00 | 232 | 00:00
BIPTC | 244 | 08:00 | 222 | 19:00 | Naogaon | 235 | 06:00 | 209 | 19:00
Bogura | 249 | 06:00 | 227 | 19:00 | Purbasadipur | 233 | 06:00 | 205 | 19:00
Bogura-400 | 248 | 06:00 | 227 | 19:00 | Rajshahi | 242 | 08:00 | 220 | 19:00
Borhanuddin | 241 | 08:00 | 233 | 00:00 | Rampal | 242 | 08:00 | 220 | 00:00
BSRM | 242 | 10:00 | 233 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 246 | 10:00 | 220 | 22:00 | Rampura | 244 | 06:00 | 234 | 19:00
Cumilla(N) | 243 | 10:00 | 233 | 19:30 | Shikalbaha | 239 | 12:00 | 228 | 00:00
Faridpur | 247 | 08:00 | 232 | 19:00 | Shyampur | 244 | 06:00 | 234 | 19:00
Fenchuganj | 249 | 10:00 | 239 | 19:00 | Siddhirganj | 245 | 08:00 | 227 | 19:30
Feni | 244 | 10:00 | 232 | 19:30 | Sirajgonj | 248 | 08:00 | 235 | 19:00
Ghorashal | 248 | 08:00 | 240 | 00:00 | Sreepur | 240 | 09:00 | 226 | 19:00
Ghorashal-230 | 242 | 06:00 | 231 | 19:00 | Tongi | 241 | 08:00 | 232 | 19:00
Gopalganj | 246 | 08:00 | 232 | 19:30
GPH | 237 | 08:00 | 232 | 00:00
Haripur | 243 | 06:00 | 235 | 19:00
Hasnabad | 246 | 07:00 | 235 | 20:00
Hathazari | 237 | 11:00 | 231 | 00:00
Ishurdi | 245 | 08:00 | 225 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 05:00 | 133 | 18:30 | Madunaghat | 141 | 12:00 | 134 | 00:00
Agargaon | 140 | 07:00 | 131 | 19:00 | Magura | 143 | 08:00 | 121 | 19:00
Agrabad | 141 | 12:00 | 132 | 00:00 | Mahasthangarh | 143 | 06:00 | 126 | 19:00
AKS | 140 | 12:00 | 131 | 00:00 | Maijdee | 139 | 10:00 | 130 | 00:00
Aminbazar | 143 | 08:00 | 135 | 18:00 | Manikganj | 139 | 09:00 | 129 | 00:00
Amnura | 140 | 08:00 | 128 | 19:30 | Maniknagar | 138 | 00:00 | 133 | 19:00
Ashuganj | 146 | 09:00 | 140 | 13:00 | Matarbari | 138 | 13:00 | 114 | 01:00
Ashuganj-230 | 146 | 09:00 | 140 | 13:00 | Matuail | 140 | 10:00 | 135 | 19:00
Bagerhat | 141 | 09:00 | 119 | 19:00 | Metrorail_Motijheel | 138 | 00:00 | 133 | 19:00
Bajitpur | 139 | 09:00 | 130 | 19:00 | Metrorail_Uttara | 137 | 05:00 | 131 | 19:00
Bakerganj | 140 | 10:00 | 132 | 00:00 | Millgate | 139 | 08:00 | 131 | 19:00
Bakulia | 142 | 12:00 | 132 | 00:00 | Mirpur | 142 | 05:00 | 134 | 19:00
Banani | 139 | 06:00 | 132 | 19:00 | Mirzapur | 139 | 08:00 | 128 | 19:00
Bangabhaban | 138 | 00:00 | 132 | 19:00 | Mithapukur | 142 | 06:00 | 125 | 19:00
Barapukuria | 140 | 04:00 | 120 | 19:00 | MI_Cement | 144 | 09:00 | 135 | 16:00
Barguna | 142 | 10:00 | 132 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 142 | 10:00 | 132 | 00:00 | Mogbazar | 139 | 09:00 | 13 | 07:00
Barishal-230 | 141 | 10:00 | 132 | 00:00 | Mongla | 140 | 09:00 | 120 | 19:00
Baroaulia | 142 | 12:00 | 133 | 00:00 | Motijheel | 138 | 00:00 | 132 | 19:00
Baroirhat | 140 | 11:00 | 134 | 00:00 | Muktagacha | 135 | 08:00 | 124 | 00:00
Bashundhara | 139 | 08:00 | 131 | 14:00 | Munshiganj | 140 | 09:00 | 134 | 00:00
BashundharaCement | 141 | 09:00 | 134 | 19:00 | Muradnagar | 143 | 10:00 | 133 | 19:00
Beanibazar | 132 | 07:00 | 126 | 18:30 | Mymensingh | 134 | 09:00 | 122 | 19:00
Benapole | 141 | 08:00 | 116 | 19:00 | Nabinagar | 144 | 08:00 | 125 | 19:00
Bhaluka | 137 | 09:00 | 126 | 19:00 | Naogaon | 144 | 06:00 | 126 | 19:00
Bhandaria | 143 | 09:00 | 126 | 00:00 | Narail | 145 | 08:00 | 119 | 19:00
Bhangura | 139 | 08:00 | 129 | 00:00 | Narinda | 138 | 00:00 | 133 | 19:00
Bheramara | 141 | 08:00 | 131 | 19:00 | Narshingdi | 140 | 09:00 | 133 | 00:00
Bheramara(GK) | 141 | 08:00 | 132 | 19:00 | Natore | 141 | 07:00 | 127 | 19:00
Bhulta | 137 | 09:00 | 132 | 00:00 | Nawabganj | 138 | 07:00 | 131 | 19:00
Bog-Sherpur | 143 | 06:00 | 129 | 19:00 | Netrakona | 132 | 09:00 | 120 | 19:00
Bogura | 145 | 06:00 | 131 | 19:00 | New | 141 | 08:00 | 132 | 19:00
Bogura-230 | 145 | 06:00 | 131 | 19:00 | Niamatpur | 141 | 05:00 | 127 | 19:00
Brahmanbaria | 141 | 10:00 | 133 | 19:00 | Noapara | 141 | 08:00 | 120 | 19:00
Cantonment | 140 | 08:00 | 131 | 19:00 | Pabna | 141 | 07:00 | 129 | 19:00
Chandina | 144 | 10:00 | 135 | 19:00 | Palashbari | 139 | 06:00 | 121 | 19:00
Chandpur | 141 | 10:00 | 131 | 00:00 | Panchagarh | 139 | 06:00 | 122 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 142 | 12:00 | 134 | 00:00 | Patiya | 141 | 13:00 | 130 | 00:00
Chapai | 140 | 05:00 | 128 | 19:00 | Patuakhali | 139 | 10:00 | 132 | 01:00
Charsaidpur | 141 | 09:00 | 134 | 19:00 | Payra | 139 | 10:00 | 134 | 00:00
Chauddagram | 141 | 10:00 | 126 | 02:00 | PHP | 140 | 12:00 | 132 | 07:00
Chhatak | 130 | 06:00 | 124 | 19:00 | Postogola | 144 | 09:00 | 137 | 19:30
Chowmuhani | 140 | 10:00 | 130 | 19:00 | Pubail | 146 | 09:00 | 139 | 19:00
Chuadanga | 142 | 08:00 | 119 | 19:00 | Purbachal | 139 | 06:00 | 131 | 19:00
Coxsbazar | 136 | 13:00 | 117 | 00:00 | Purbasadipur | 139 | 06:00 | 120 | 19:00
Cumilla(N) | 144 | 10:00 | 135 | 19:30 | Rahanpur | 142 | 05:00 | 130 | 19:30
Cumilla(S) | 143 | 10:00 | 125 | 09:00 | Rahanpur-400 | 141 | 05:00 | 130 | 19:00
Daganbhuiyan | 140 | 10:00 | 133 | 00:00 | Rahim | N/A | N/A | N/A | N/A
Daudkandi | 141 | 10:00 | 131 | 21:00 | Rajbari | 142 | 08:00 | 131 | 00:00
DhakaUniversity | 138 | 05:00 | 130 | 14:00 | Rajendrapur | 137 | 09:00 | 127 | 19:00
Dhamrai | 141 | 08:00 | 127 | 18:30 | Rajshahi | 138 | 08:00 | 126 | 00:00
Dhanmondi | 142 | 09:00 | 136 | 00:00 | Rajshahi-230 | 139 | 08:00 | 127 | 00:00
Dohazari | 140 | 13:00 | 125 | 00:00 | Ramganj | 139 | 10:00 | 129 | 00:00
Faridpur | 142 | 09:00 | 133 | 19:30 | Rampur | 141 | 12:00 | 133 | 00:00
Fatullah | 143 | 09:00 | 134 | 00:00 | Rampura | 138 | 06:00 | 132 | 19:00
Fenchuganj | 137 | 07:00 | 132 | 19:00 | Rangamati | 142 | 12:00 | 127 | 16:00
Feni | 139 | 10:00 | 133 | 00:00 | Rangpur | 138 | 06:00 | 121 | 19:00
Feni-230 | 141 | 10:00 | 134 | 00:00 | Ruppur | 141 | 08:00 | 132 | 19:00
Ghatail | 137 | 09:00 | 123 | 19:00 | Saidpur | 140 | 06:00 | 121 | 19:00
Ghorashal | 145 | 06:00 | 140 | 19:00 | Santhia | 142 | 07:00 | 131 | 19:00
Goalpara | 142 | 08:00 | 124 | 19:00 | Satkhira | 139 | 08:00 | 115 | 19:00
Gollamari | 142 | 08:00 | 124 | 19:00 | Satmasjid | 139 | 06:00 | 132 | 19:00
Gopalganj | 141 | 08:00 | 128 | 19:00 | Savar | 141 | 09:00 | 133 | 19:00
Gopalganj-400 | 144 | 08:00 | 135 | 19:00 | SevenRings | 146 | 09:00 | 140 | 19:00
Gulshan | 138 | 08:00 | 132 | 19:00 | ShahCement | 141 | 09:00 | 134 | 19:00
Halishahar | 141 | 12:00 | 133 | 00:00 | Shahjadpur | 142 | 09:00 | 134 | 19:00
Haripur | 141 | 09:00 | 135 | 19:00 | Shahjibazar | 138 | 09:00 | 133 | 13:00
HaripurSBU | 141 | 09:00 | 135 | 19:00 | Shahmirpur | 142 | 12:00 | 130 | 06:00
Hasnabad | 143 | 07:00 | 137 | 23:00 | Shariatpur | 142 | 09:00 | 132 | 00:00
Hathazari | 141 | 14:00 | 134 | 00:00 | Sherpur | 133 | 10:00 | 110 | 19:00
Hatirjheel | 138 | 06:00 | 133 | 19:00 | Shikalbaha | 130 | 12:00 | 121 | 00:00
Ishurdi | 143 | 08:00 | 132 | 19:00 | Shikalbaha-230 | 142 | 12:00 | 133 | 00:00
Jaldhaka | 139 | 06:00 | 118 | 19:00 | Shitalakhya | 144 | 09:00 | 135 | 16:00
Jamalpur | 133 | 09:00 | 116 | 18:30 | Sholosohor | 141 | 12:00 | 133 | 00:00
Jashore | 142 | 08:00 | 118 | 19:00 | Shomvuganj | 133 | 10:00 | 125 | 15:00
Jhenaidah | 144 | 08:00 | 123 | 19:00 | Shyampur | 140 | 09:00 | 134 | 00:00
Jhenaidah-230 | 143 | 08:00 | 123 | 19:30 | Shyampur-230 | 140 | 06:00 | 134 | 19:00
Joydebpur | 144 | 08:00 | 137 | 14:00 | Siddhirganj | 142 | 09:00 | 135 | 23:00
Joypurhat | 141 | 07:00 | 125 | 19:00 | Sirajganj | 141 | 07:00 | 128 | 19:00
Juldah | 141 | 12:00 | 132 | 00:00 | Sonargaon | 141 | 09:00 | 135 | 00:00
Kabirpur | 141 | 09:00 | 130 | 19:00 | Sreemongol | 136 | 09:00 | 131 | 19:00
Kachua | 141 | 10:00 | 132 | 00:00 | Sreepur | 138 | 09:00 | 128 | 19:00
Kaliakoir | 145 | 08:00 | 129 | 19:00 | Srinagar | 139 | 08:00 | 131 | 19:00
Kaliganj | 143 | 08:00 | 122 | 19:00 | SSM | 148 | 13:00 | 138 | 19:30
Kallyanpur | 142 | 08:00 | 135 | 19:00 | Sunamganj | 129 | 13:00 | 122 | 18:30
Kalurghat | 141 | 12:00 | 134 | 00:00 | Sylhet | 132 | 07:00 | 127 | 19:00
Kamrangirchar | 140 | 06:00 | 132 | 20:00 | Sylhet-132 | 131 | 06:00 | 127 | 19:00
Kaptai | N/A | N/A | N/A | N/A | Tangail | 138 | 09:00 | 124 | 19:00
Kasba | 143 | 10:00 | 133 | 19:00 | Taraganj | 138 | 05:00 | 118 | 19:00
Kazla | 138 | 00:00 | 133 | 18:30 | Tasnim | 141 | 09:00 | 131 | 19:30
Keranigonj | 139 | 09:00 | 132 | 19:00 | Thakurgaon | 139 | 06:00 | 120 | 19:00
Khagrachori | 142 | 12:00 | 133 | 00:00 | TK | 140 | 12:00 | 134 | 00:00
Khulna | 142 | 08:00 | 123 | 19:00 | Tongi | 141 | 08:00 | 134 | 19:00
Khulna(S) | 141 | 09:00 | 123 | 19:00 | Ullahpara | 142 | 07:00 | 129 | 19:00
Khulshi | 141 | 12:00 | 131 | 16:00 | Ullon | 138 | 08:00 | 132 | 19:00
Kishoreganj | 137 | 10:00 | 127 | 16:00 | Uttara | 140 | 08:00 | 131 | 19:00
Kodda | 138 | 08:00 | 128 | 01:00 | UttaraNew | 137 | 05:00 | 131 | 19:00
Korerhat | 140 | 11:00 | 135 | 00:00 | Zigatola | 139 | 09:00 | 132 | 19:30
KSRM | 142 | 12:00 | 133 | 00:00
Kulaura | 136 | 07:00 | 131 | 19:00
Kurigram | 136 | 06:00 | 116 | 19:00
Kushtia | 142 | 07:00 | 128 | 19:00
Laksam | 142 | 10:00 | 132 | 00:00
Lakshmipur | 140 | 10:00 | 130 | 00:00
Lalbag | 139 | 08:00 | 132 | 19:00
Lalmonirhat | 130 | 04:00 | 114 | 19:00
Madanganj | 141 | 09:00 | 134 | 19:00
Madaripur | 141 | 09:00 | 134 | 00:00
Madartek | 138 | 06:00 | 132 | 19:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division