## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 28-05-2026 | [28 empty] | Date: | 28-05-2026 | [28 empty] | Date: | 28-05-2026 | [28 empty] | Date: | 28-05-2026 | [28 empty] | Date: | 28-05-2026 | [17 empty] | Date: | 28-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [17 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 335 | 130 | 0 | 0 | 0 | 5 | 3 | 0 | 574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 39 | 360 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 502 | 0 | 0 | 187 | 347 | 360 | 0 | 51 | 45 | 209 | 27 | 0 | 0 | 0 | 0 | 10 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 158 | 0 | 0 | 0 | 86 | 30 | 0 | 0 | 101 | 0 | 16 | 5 | 158 | 0 | 0 | 0 | 4912 | 620 | 394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 441 | 0 | 0 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 60 | 220 | 0 | 751 | 540 | 0 | 4682 | 9594 | 75.41
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 335 | 136 | 0 | 0 | 0 | 5 | 3 | 0 | 558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 39 | 270 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 501 | 0 | 0 | 184 | 344 | 361 | 0 | 51 | 48 | 206 | 30 | 0 | 0 | 0 | 0 | 10 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 157 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 101 | 0 | 16 | 16 | 158 | 0 | 0 | 0 | 4821 | 620 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 60 | 220 | 0 | 614 | 530 | 0 | 4476 | 9297 | 75.41
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 335 | 136 | 0 | 0 | 0 | 5 | 3 | 0 | 538 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 39 | 215 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 501 | 0 | 0 | 184 | 316 | 360 | 0 | 51 | 48 | 201 | 30 | 0 | 0 | 0 | 0 | 10 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 143 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 101 | 0 | 16 | 16 | 158 | 0 | 0 | 0 | 4696 | 621 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251 | 60 | 220 | 0 | 605 | 520 | 0 | 4349 | 9045 | 75.41
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 335 | 136 | 0 | 0 | 0 | 5 | 3 | 0 | 555 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 39 | 215 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 501 | 0 | 0 | 184 | 316 | 360 | 0 | 51 | 48 | 203 | 30 | 0 | 0 | 0 | 0 | 10 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 146 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 102 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 4664 | 336 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 60 | 220 | 0 | 507 | 508 | 0 | 3983 | 8647 | 75.41
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 335 | 136 | 0 | 0 | 0 | 5 | 3 | 0 | 540 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 39 | 215 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 500 | 0 | 0 | 184 | 316 | 360 | 0 | 51 | 48 | 203 | 30 | 0 | 0 | 0 | 0 | 10 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 140 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 102 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 4636 | 242 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 60 | 220 | 0 | 397 | 518 | 0 | 3692 | 8328 | 75.41
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 335 | 136 | 0 | 0 | 0 | 5 | 3 | 0 | 544 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 39 | 215 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 502 | 0 | 0 | 184 | 317 | 361 | 0 | 51 | 48 | 201 | 30 | 0 | 0 | 0 | 0 | 10 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 146 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 104 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 4665 | 241 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 60 | 220 | 0 | 250 | 510 | 0 | 3619 | 8284 | 75.41
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 335 | 140 | 0 | 1 | 0 | 5 | 3 | 0 | 570 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0.26 | 35 | 0 | 39 | 215 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 540 | 1 | 0 | 184 | 393 | 361 | 0 | 51 | 48 | 203 | 30 | 0 | 0 | 0 | 0 | 10 | 0 | 102 | 0 | 3 | 0 | 0 | 0 | 381 | 0 | 0 | 151 | 0 | 17 | 0 | 86 | 30 | 0 | 0 | 102 | 0 | 2 | 2 | 158 | 0.1 | 0.53 | 0 | 4884.89 | 196 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.49 | 387 | 0 | 0 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.62 | 4 | 0 | 0 | 1.03 | 185 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.05 | 0 | 50 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 6 | 0.03 | 0 | 293 | 60 | 220 | 0 | 431 | 525 | 0 | 3907.22 | 8792.11 | 75.41
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 335 | 139 | 0 | 8 | 0 | 7 | 3 | 0 | 412 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 1.58 | 35 | 0 | 39 | 360 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 612 | 4 | 0 | 184 | 393 | 360 | 0 | 51 | 48 | 196 | 27 | 0 | 0 | 0 | 0 | 11 | 0 | 100 | 0 | 13 | 0 | 0 | 0 | 380 | 0 | 0 | 149 | 2 | 17 | 0 | 86 | 30 | 0 | 0 | 102 | 0 | 16 | 16 | 158 | 0 | 4.33 | 0 | 5026.91 | 195 | 391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 520 | 0 | 0 | 0 | 767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.03 | 17 | 0 | 0 | 5.29 | 212 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0.14 | 0 | 50 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 26 | 0.2 | 0 | 307 | 60 | 220 | 0 | 500 | 565 | 0 | 4194.66 | 9221.57 | 75.41
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 280 | 139 | 0 | 9 | 0 | 5 | 3 | 0 | 380 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 2.63 | 35 | 0 | 39 | 400 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 506 | 8 | 0 | 184 | 300 | 360 | 0 | 51 | 47 | 192 | 30 | 0 | 0 | 0 | 0 | 11 | 0 | 86 | 0 | 18 | 0 | 0 | 0 | 306 | 0 | 0 | 125 | 3 | 17 | 0 | 86 | 30 | 0 | 0 | 103 | 0 | 0 | 0 | 158 | 0.5 | 1.39 | 0 | 4497.52 | 196 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 533 | 0 | 0 | 0 | 679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.61 | 42 | 0 | 0 | 29.98 | 177 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0.46 | 0 | 50 | 0 | 14 | 0 | 0 | 0 | 0 | 1.4 | 105 | 0.36 | 0 | 245 | 50 | 180 | 0 | 460 | 488 | 0 | 3979.81 | 8477.33 | 75.41
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 280 | 79 | 0 | 24 | 0 | 5 | 3 | 0 | 380 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 3.4 | 35 | 0 | 39 | 372 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 423 | 14 | 0 | 138 | 305 | 360 | 0 | 51 | 33 | 198 | 30 | 0 | 0 | 0 | 0 | 11 | 0 | 74 | 0 | 31 | 0 | 0 | 0 | 306 | 0 | 0 | 124 | 3 | 17 | 0 | 41 | 30 | 0 | 0 | 103 | 0 | 0 | 0 | 160 | 0.8 | 14.66 | 0 | 4246.86 | 195 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 398 | 0 | 0 | 0 | 616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.39 | 65 | 0 | 0 | 38.33 | 162 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 1.21 | 0 | 50 | 0 | 5 | 0 | 0 | 0 | 0 | 2.9 | 20 | 0.51 | 0 | 178 | 50 | 180 | 0 | 313 | 418 | 0 | 3465.34 | 7712.2 | 75.42
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 280 | 80 | 0 | 31 | 0 | 5 | 3 | 0 | 380 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 4.02 | 35 | 0 | 39 | 371 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 370 | 18 | 0 | 55 | 310 | 360 | 0 | 5 | 13 | 198 | 5 | 0 | 0 | 0 | 0 | 10 | 0 | 78 | 0 | 48 | 0 | 0 | 0 | 309 | 0 | 0 | 127 | 9 | 0 | 0 | 5 | 20 | 0 | 0 | 102 | 0 | 0 | 0 | 160 | 1.4 | 43.12 | 0 | 4042.54 | 195 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 378 | 0 | 0 | 0 | 535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.27 | 90 | 0 | 0 | 48.02 | 165 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 1.12 | 0 | 50 | 0 | 4 | 0 | 0 | 0 | 0 | 3.8 | 100 | 0.62 | 0 | 172 | 50 | 180 | 0 | 250 | 380 | 0 | 3369.83 | 7412.37 | 75.42
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 280 | 80 | 0 | 31 | 0 | 5 | 3 | 0 | 450 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 2.65 | 35 | 0 | 39 | 370 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 325 | 18 | 0 | 53 | 315 | 360 | 0 | 5 | 5 | 202 | 5 | 0 | 0 | 0 | 0 | 10 | 0 | 82 | 0 | 69 | 0 | 0 | 0 | 309 | 0 | 0 | 128 | 2 | 8 | 0 | 5 | 20 | 0 | 0 | 102 | 0 | 0 | 0 | 157 | 2.5 | 39.93 | 0 | 4111.08 | 195 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 376 | 0 | 0 | 0 | 439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.92 | 101 | 0 | 0 | 57.61 | 166 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 1.76 | 0 | 50 | 0 | 11 | 0 | 0 | 0 | 0 | 6.1 | 200 | 0.57 | 0 | 180 | 50 | 180 | 0 | 250 | 309 | 0 | 3428.96 | 7540.04 | 75.43
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 280 | 80 | 0 | 33 | 0 | 5 | 3 | 0 | 550 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 3.14 | 34 | 0 | 20 | 370 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 300 | 17 | 0 | 8 | 315 | 360 | 0 | 5 | 5 | 202 | 5 | 0 | 0 | 0 | 0 | 12 | 0 | 74 | 0 | 70 | 0 | 0 | 0 | 309 | 0 | 0 | 140 | 6 | 8 | 0 | 5 | 20 | 0 | 0 | 102 | 0 | 0 | 0 | 157 | 2.4 | 41.76 | 0 | 4145.3 | 431 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 375 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.33 | 105 | 0 | 0 | 57.05 | 168 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 1.8 | 0 | 50 | 0 | 15 | 0 | 0 | 0 | 0 | 6.1 | 196 | 0.72 | 0 | 157 | 50 | 180 | 0 | 250 | 300 | 0 | 3674 | 7819.3 | 75.43
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 325 | 96 | 0 | 32 | 0 | 5 | 3 | 0 | 560 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1.71 | 33 | 0 | 33 | 390 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 330 | 17 | 0 | 43 | 340 | 360 | 0 | 10 | 9 | 205 | 30 | 0 | 50 | 0 | 0 | 13 | 0 | 86 | 0 | 42 | 0 | 0 | 0 | 369 | 0 | 0 | 154 | 8 | 16 | 0 | 41 | 30 | 0 | 0 | 103 | 0 | 0 | 0 | 153 | 2.3 | 48.02 | 0 | 4581.03 | 431 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 381 | 0 | 0 | 0 | 486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.07 | 104 | 0 | 0 | 55.75 | 172 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 1.72 | 0 | 50 | 0 | 21 | 0 | 0 | 0 | 0 | 5.7 | 185 | 0 | 0 | 200 | 63 | 220 | 0 | 280 | 320 | 0 | 3901.24 | 8482.27 | 75.43
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 324 | 96 | 0 | 18 | 0 | 5 | 3 | 0 | 550 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 3.61 | 62 | 0 | 38 | 390 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 420 | 9 | 0 | 180 | 335 | 360 | 0 | 51 | 35 | 202 | 27 | 0 | 93 | 0 | 0 | 13 | 0 | 88 | 0 | 43 | 0 | 0 | 0 | 370 | 0 | 0 | 152 | 11 | 16 | 0 | 86 | 30 | 0 | 0 | 103 | 0 | 0 | 0 | 153 | 2 | 45.68 | 0 | 5011.29 | 431 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 434 | 0 | 0 | 0 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.1 | 94 | 0 | 0 | 51.54 | 186 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 3.27 | 0 | 50 | 0 | 26 | 0 | 0 | 0 | 0 | 6.7 | 168 | 0 | 0 | 226 | 63 | 220 | 0 | 350 | 360 | 0 | 4072.61 | 9083.9 | 75.44
15:00 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 7 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 324 | 185 | 0 | 22 | 0 | 5 | 3 | 0 | 550 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 3.27 | 63 | 0 | 38 | 565 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 500 | 13 | 0 | 184 | 330 | 357 | 0 | 51 | 46 | 202 | 27 | 0 | 93 | 0 | 0 | 13 | 0 | 106 | 0 | 45 | 0 | 0 | 0 | 370 | 0 | 20 | 155 | 7 | 16 | 0 | 86 | 30 | 35 | 0 | 102 | 0 | 0 | 0 | 152 | 1.5 | 36.12 | 0 | 5505.89 | 431 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 475 | 0 | 0 | 0 | 540 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.68 | 83 | 0 | 0 | 40.7 | 191 | 0 | 7 | 0 | 0 | 0 | 388 | 0 | 2.62 | 0 | 46 | 0 | 23 | 0 | 0 | 0 | 0 | 4.8 | 134 | 0.47 | 0 | 266 | 60 | 220 | 0 | 411 | 400 | 0 | 4218.27 | 9724.16 | 75.45
16:00 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 11 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 320 | 133 | 0 | 17 | 0 | 5 | 3 | 0 | 560 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0.64 | 66 | 0 | 38 | 565 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 508 | 7 | 0 | 184 | 355 | 354 | 0 | 51 | 47 | 213 | 27 | 0 | 93 | 0 | 0 | 13 | 0 | 112 | 0 | 29 | 0 | 0 | 0 | 357 | 0 | 20 | 154 | 5 | 16 | 0 | 85 | 30 | 100 | 0 | 102 | 0 | 0 | 0 | 151 | 1.1 | 24.49 | 0 | 5665.23 | 431 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 547 | 0 | 0 | 0 | 576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.12 | 46 | 0 | 0 | 19.23 | 190 | 0 | 11 | 0 | 0 | 0 | 405 | 0 | 1.26 | 0 | 46 | 0 | 12 | 0 | 0 | 0 | 0 | 2.9 | 90 | 0.2 | 0 | 281 | 60 | 220 | 0 | 414 | 450 | 0 | 4250.71 | 9915.94 | 75.45
17:00 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 11 | 385 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 322 | 134 | 0 | 7 | 0 | 7 | 3 | 0 | 550 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0.97 | 67 | 0 | 38 | 565 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 580 | 0 | 0 | 182 | 337 | 357 | 0 | 51 | 47 | 204 | 25 | 0 | 93 | 0 | 0 | 13 | 0 | 116 | 0 | 13 | 0 | 0 | 0 | 357 | 0 | 30 | 155 | 2 | 16 | 0 | 85 | 30 | 100 | 0 | 102 | 0 | 0 | 0 | 151 | 0.3 | 11.46 | 0 | 5672.73 | 431 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 585 | 0 | 0 | 0 | 730 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.91 | 23 | 0 | 0 | 13.59 | 188 | 0 | 15 | 0 | 0 | 0 | 389 | 0 | 1.22 | 0 | 50 | 0 | 6 | 0 | 0 | 0 | 0 | 2 | 42 | 0.16 | 0 | 271 | 120 | 220 | 0 | 568 | 490 | 0 | 4566.88 | 10239.61 | 75.45
18:00 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 23 | 336 | 0 | 6 | 30 | 0 | 0 | 0 | 40 | 0 | 4 | 50 | 0 | 0 | 151 | 0 | 0 | 0 | 322 | 134 | 0 | 2 | 10 | 12 | 3 | 0 | 470 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.12 | 67 | 0 | 38 | 565 | 0 | 0 | 0 | 0 | 1 | 145 | 0 | 0 | 0 | 580 | 0 | 2 | 184 | 337 | 358 | 0 | 51 | 46 | 204 | 25 | 18 | 95 | 0 | 0 | 13 | 0 | 120 | 0 | 3 | 0 | 0 | 0 | 357 | 0 | 30 | 153 | 0 | 16 | 0 | 86 | 30 | 100 | 0 | 101 | 0 | 9 | 5 | 152 | 0.1 | 2.24 | 0 | 5707.46 | 447 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 590 | 0 | 0 | 0 | 765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25 | 4 | 0 | 0 | 3.44 | 184 | 0 | 20 | 0 | 0 | 0 | 360 | 0 | 0.3 | 0 | 52 | 0 | 2 | 0 | 0 | 0 | 0 | 0.3 | 10 | 0.03 | 0 | 238 | 120 | 220 | 0 | 622 | 500 | 0 | 4528.32 | 10235.78 | 75.46
19:00 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 38 | 382 | 0 | 11 | 33 | 0 | 16 | 0 | 130 | 5 | 22 | 110 | 0 | 0 | 152 | 0 | 0 | 17 | 322 | 133 | 0 | 0 | 41 | 12 | 3 | 0 | 560 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 20 | 12 | 0 | 65 | 9 | 38 | 565 | 0 | 0 | 9 | 0 | 29 | 145 | 0 | 0 | 0 | 590 | 0 | 43 | 184 | 343 | 356 | 0 | 51 | 47 | 212 | 26 | 40 | 97 | 1 | 0 | 13 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 30 | 142 | 0 | 16 | 0 | 85 | 30 | 100 | 0 | 102 | 0 | 57 | 51 | 154 | 0 | 0 | 0 | 6373 | 906 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590 | 0 | 0 | 0 | 729 | 0 | 0 | 0 | 30 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 62 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 52 | 100 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246 | 120 | 220 | 0 | 622 | 465 | 0 | 5221 | 11594 | 75.46
19:30 | 0 | 0 | 2 | 0 | 0 | 220 | 0 | 40 | 317 | 0 | 33 | 35 | 4 | 50 | 0 | 185 | 35 | 35 | 145 | 0 | 0 | 151 | 0 | 0 | 35 | 325 | 75 | 0 | 0 | 71 | 12 | 3 | 0 | 420 | 40 | 0 | 0 | 0 | 0 | 34 | 0 | 17 | 24 | 24 | 0 | 65 | 30 | 38 | 565 | 2 | 0 | 42 | 1 | 83 | 145 | 0 | 0 | 0 | 612 | 0 | 110 | 184 | 404 | 360 | 0 | 51 | 47 | 200 | 28 | 77 | 97 | 30 | 0 | 13 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 30 | 140 | 0 | 16 | 0 | 85 | 30 | 101 | 0 | 102 | 0 | 57 | 103 | 155 | 0 | 0 | 0 | 6826 | 930 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 598 | 26 | 0 | 0 | 707 | 0 | 0 | 0 | 90 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 105 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 52 | 110 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 622 | 535 | 0 | 5533 | 12359 | 75.47
20:00 | 0 | 4 | 16 | 0 | 0 | 220 | 0 | 40 | 336 | 0 | 33 | 35 | 12 | 48 | 0 | 195 | 32 | 35 | 148 | 0 | 0 | 149 | 0 | 0 | 35 | 328 | 77 | 0 | 0 | 85 | 12 | 3 | 0 | 380 | 30 | 32 | 0 | 0 | 2 | 34 | 0 | 19 | 24 | 24 | 0 | 65 | 47 | 38 | 520 | 10 | 0 | 40 | 7 | 88 | 145 | 0 | 0 | 0 | 580 | 0 | 98 | 180 | 347 | 360 | 0 | 51 | 46 | 199 | 28 | 76 | 96 | 38 | 0 | 16 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 30 | 131 | 0 | 16 | 0 | 86 | 30 | 101 | 0 | 103 | 0 | 57 | 103 | 154 | 0 | 0 | 0 | 6729 | 922 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 593 | 34 | 0 | 0 | 665 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 108 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 52 | 110 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 276 | 120 | 220 | 0 | 590 | 530 | 0 | 5314 | 12043 | 75.47
21:00 | 0 | 17 | 24 | 0 | 0 | 220 | 0 | 37 | 347 | 0 | 173 | 33.7 | 17 | 60 | 0 | 212 | 55 | 35 | 126 | 0 | 0 | 149 | 0 | 0 | 17 | 328 | 76 | 0 | 0 | 86 | 12 | 3 | 0 | 530 | 45 | 32 | 0 | 0 | 7 | 34 | 0 | 17 | 50 | 50 | 0 | 66 | 89 | 38 | 475 | 0 | 0 | 50 | 16 | 90 | 147 | 0 | 0 | 0 | 580 | 0 | 142 | 190 | 310 | 361 | 0 | 51 | 47 | 202 | 29 | 90 | 97 | 34 | 0 | 16 | 0 | 138 | 8 | 0 | 0 | 0 | 0 | 321 | 0 | 30 | 139 | 0 | 16 | 0 | 86 | 30 | 101 | 0 | 103 | 0 | 57 | 55 | 155 | 0 | 0 | 0 | 7151.7 | 923 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 597 | 34 | 0 | 0 | 637 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 165 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 52 | 50 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 277 | 128 | 220 | 0 | 504 | 525 | 0 | 5213 | 12364.7 | 75.48
22:00 | 0 | 17 | 24 | 0 | 0 | 220 | 0 | 34 | 380 | 0 | 218 | 0 | 0 | 40 | 0 | 145 | 15 | 17 | 35 | 0 | 0 | 148 | 0 | 0 | 17 | 328 | 78 | 0 | 0 | 86 | 12 | 3 | 0 | 550 | 15 | 32 | 0 | 0 | 4 | 34 | 0 | 17 | 24 | 50 | 0 | 70 | 90 | 38 | 488 | 0 | 0 | 50 | 16 | 100 | 147 | 0 | 0 | 0 | 580 | 0 | 142 | 190 | 335 | 360 | 73 | 51 | 47 | 203 | 29 | 85 | 98 | 34 | 0 | 16 | 0 | 146 | 16 | 0 | 0 | 0 | 0 | 344 | 0 | 30 | 153 | 0 | 16 | 0 | 86 | 30 | 100 | 0 | 103 | 0 | 57 | 55 | 155 | 0 | 0 | 0 | 7076 | 922 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 598 | 34 | 0 | 0 | 666 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 177 | 0 | 4 | 0 | 395 | 0 | 0 | 0 | 52 | 50 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 277 | 128 | 220 | 0 | 541 | 520 | 0 | 5331 | 12407 | 75.48
23:00 | 0 | 17 | 24 | 0 | 0 | 220 | 0 | 33 | 383 | 0 | 246 | 0 | 0 | 34 | 0 | 145 | 15 | 17 | 35 | 0 | 0 | 149 | 0 | 0 | 17 | 330 | 78 | 0 | 0 | 86 | 12 | 7 | 0 | 540 | 16 | 32 | 0 | 0 | 3 | 34 | 0 | 17 | 24 | 50 | 0 | 65 | 91 | 38 | 476 | 0 | 0 | 50 | 16 | 98 | 147 | 0 | 0 | 0 | 580 | 0 | 150 | 185 | 330 | 360 | 220 | 51 | 48 | 201 | 29 | 69 | 98 | 33 | 0 | 18 | 0 | 146 | 16 | 0 | 0 | 0 | 0 | 344 | 0 | 30 | 153 | 0 | 8 | 0 | 86 | 30 | 101 | 0 | 103 | 0 | 57 | 55 | 155 | 0 | 0 | 8 | 7209 | 902 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 603 | 34 | 0 | 0 | 676 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 192 | 0 | 4 | 0 | 382 | 0 | 0 | 0 | 52 | 50 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 277 | 128 | 220 | 0 | 505 | 520 | 0 | 5309 | 12518 | 75.49
Total KWH | 0 | 74880 | 107040 | 0 | 0 | 1924063 | 0 | 230000 | 8582400 | 0 | 847392 | 130320 | 41400 | 249984 | 0 | 920084 | 156932 | 157591 | 426240 | 0 | 0 | 3531462 | 0 | 0 | 131939 | 7727585 | 3019000 | 0 | 235841 | 463200 | 252000 | 171720 | 0 | 12240000 | 176891 | 148036 | 0 | 0 | 343200 | 167985 | 0 | 121226 | 160320 | 222720 | 31441 | 1169880 | 420691 | 915840 | 9454545.45 | 13382 | 0 | 252960 | 72462.6 | 500145 | 3098589 | 0 | 0 | 0 | 11961817 | 128250 | 727636 | 3763636 | 8003000 | 8979000 | 398000 | 1108016 | 950400 | 5016000 | 614664 | 426240 | 1026992 | 192000 | 0 | 419350 | 0 | 2505600 | 60533 | 452264 | 0 | 0 | 0 | 8686000 | 0 | 238680 | 3471954.5 | 53794 | 327696 | 0 | 1702080 | 683136 | 890000 | 0 | 2459480 | 0 | 409200 | 477600 | 3671040 | 14950 | 305500 | 20880 | 129036775.55 | 11613818 | 9069696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 707760 | 11461816 | 154080 | 0 | 0 | 15510747 | 0 | 0 | 0 | 296928 | 309696 | 0 | 0 | 0 | 0 | 400296 | 782920 | 0 | 0 | 416144 | 4334455 | 0 | 1062436 | 0 | 22100 | 0 | 9220072 | 0 | 17880 | 0 | 1174254 | 412493 | 167456 | 499555 | 0 | 0 | 0 | 48301.44 | 1258560 | 4596 | 58560 | 5956000 | 1880000 | 5305120 | 0 | 10800000 | 11425454.55 | 0 | 104371193.99 | 233407969.54

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 29-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-05-2026 | during | 29-05-2026 | during | 29-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 220 | 0 | 0 | 170 | 170 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 37 | 97.7 | 97.7 | 35 | 35 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 346 | 347 | 412 | 412 | 392 | 392 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 450 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 148 | 149 | 335 | 335 | 150 | 150 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 80 | 76 | 210 | 210 | 210 | 210 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 328 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 33.7 | 53.97 | 53.97 | 36 | 36 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 1 | 1 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 5 | 12 | 33 | 33 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 3 | 3 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 24 | 52.19 | 52.19 | 16 | 50 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 212 | 300 | 300 | 32 | 32 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 60 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 100 | 100 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 126 | 162 | 162 | 0.01 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 550 | 530 | 584 | 584 | 540 | 540 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 173 | 718 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 86 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1445 | 2557.7 | 5625.22 | 5597.22 | 2652.37 | 2820.36
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 16 | 25.5 | 25.5 | 8 | 8 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 34 | 66 | 0 | 0 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 101 | 147 | 150 | 150 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 90 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 0 | 0 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 50 | 0 | 0 | 24 | 24 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 20 | 38 | 5 | 25 | 5 | 25 | plant availability zero
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 24 | 60 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.14 | 0 | 0 | 0 | 0 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 32 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 89 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 45 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 35 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 300 | 580 | 1224 | 1224 | 612 | 612 | U2 outage added
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 8 | 7 | 5 | 1 | 5 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 370 | 475 | 575 | 575 | 575 | 575 | U1 under maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 853.14 | 1786 | 3108.86 | 3106.86 | 2000.36 | 2218.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 202 | 202 | 221.25 | 221.25 | 205.25 | 205.25 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 360 | 361 | 350.01 | 350.01 | 320 | 320 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 0 | 0 | 250 | 250 | 0 | 230 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 315 | 310 | 393 | 393 | 340 | 340 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 5 | 29 | 41.65 | 41.65 | 40 | 40 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 5 | 47 | 52.82 | 52.82 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 190 | 195 | 195 | 180 | 180.03 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 5 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 142 | 150 | 150 | 33 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 97 | 163 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 34 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 74 | 138 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 43 | 43 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 16 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 90 | 115 | 115 | 95 | 95 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 70 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1056 | 1715 | 2541.43 | 2486.43 | 1761.25 | 2062.28
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-05-2026 | during | 29-05-2026 | during | 29-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 157 | 155 | 157.5 | 157.5 | 160 | 160 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.4 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 0 | 55 | 140 | 140 | 90 | 90 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 0 | 57 | 60 | 60 | 10 | 110 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 41.76 | 0 | 36 | 0 | 36 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 12 | 12 | From 17:00 to 20:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 201.16 | 267 | 471.9 | 434 | 326.9 | 389
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 42 | 42 | plant availability zero
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 30 | 0 | 0 | 30 | 30 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 140 | 139 | 163 | 163 | 147 | 147 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 101 | 0 | 0 | 100 | 100 | plant availability zero
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 20 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 102 | 103 | 0 | 0 | 102 | 102 | plant availability zero
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 16 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0.01 | Plant shutdown as per NLDC requirement.
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 309 | 321 | 0 | 0 | 250 | 250 | plant availability zero
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 590 | 826 | 324 | 324 | 804 | 804.01
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 431 | 923 | 0 | 0 | 0 | 0 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 36 | 36 | 37 | 37 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 344 | 344 | 410 | 410 | 400 | 400 | -
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 34 | 105 | 105 | 16 | 16 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 101 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 375 | 597 | 1234.2 | 1234.2 | 617.1 | 617.1 | Unit1 Under Maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1251 | 1898 | 2580.2 | 2500.2 | 1277.1 | 1197.1
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 250 | 504 | 1244 | 1244 | 622 | 622.02 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 14 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 50 | 128 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 300 | 525 | 0 | 0 | 622 | 622 | plant availability zero
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 0 | 35 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 157 | 277 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.72 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 937.72 | 1668 | 2162 | 2161 | 1982 | 2016.02
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 56.33 | 0 | 63 | 0 | 63 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 168 | 172 | 214 | 214 | 190 | 190 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 165 | 220 | 220 | 210 | 210 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 400 | 373 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 97 | 97 | 50 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.8 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 430 | 637 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 57.05 | 0 | 0 | 0 | 0 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 105 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1218.18 | 1447 | 3117.57 | 2948.87 | 2809.19 | 2640.49
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 52 | 0 | 0 | 50 | 50 | Plant availability zero, U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 98 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.1 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 196 | 0 | 189.46 | 0 | 189.46 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 267.1 | 200 | 473.46 | 248 | 503.46 | 278
System Total |  |  |  |  | 28823.2 | 29270.237 | 7819.3 | 12364.7 | 20404.64 | 19806.58 | 14116.63 | 14425.62
Forecast Scenario (29-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11900 |  | 0 |  | 11900
|  |  |  | 1:00 | 11430 |  | 0 |  | 11430
|  |  |  | 2:00 | 11040 |  | 0 |  | 11040
|  |  |  | 3:00 | 10580 |  | 0 |  | 10580
|  |  |  | 4:00 | 10150 |  | 0 |  | 10150
|  |  |  | 5:00 | 9770 |  | 0 |  | 9770
|  |  |  | 6:00 | 9110 |  | 0 |  | 9110
|  |  |  | 7:00 | 9010 |  | 0 |  | 9010
|  |  |  | 8:00 | 10200 |  | 0 |  | 10200
|  |  |  | 9:00 | 10300 |  | 0 |  | 10300
|  |  |  | 10:00 | 10400 |  | 0 |  | 10400
|  |  |  | 11:00 | 10800 |  | 0 |  | 10800
|  |  |  | 12:00 | 11300 |  | 0 |  | 11300
|  |  |  | 13:00 | 11940 |  | 0 |  | 11940
|  |  |  | 14:00 | 12560 |  | 0 |  | 12560
|  |  |  | 15:00 | 12590 |  | 0 |  | 12590
|  |  |  | 16:00 | 12410 |  | 0 |  | 12410
|  |  |  | 17:00 | 11880 |  | 0 |  | 11880
|  |  |  | 18:00 | 11200 |  | 0 |  | 11200
|  |  |  | 18:30 | 11850 |  | 0 |  | 11850
|  |  |  | 19:00 | 12570 |  | 0 |  | 12570
|  |  |  | 19:30 | 13510 |  | 0 |  | 13510
|  |  |  | 20:00 | 13680 |  | 0 |  | 13680
|  |  |  | 21:00 | 14120 |  | 0 |  | 14120
|  |  |  | 22:00 | 14300 |  | 0 |  | 14300
|  |  |  | 23:00 | 14500 |  | 0 |  | 14500
Probable Maximum Temperature: |  |  | 31.00°C
Probable Maximum Demand at Day Peak: |  |  | 9500.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14120.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12120.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 248.17 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 12:50 hrs on 29-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 28-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 7819.3 | MW | 12:00 Hr. | Energy Generated |  |  | 233.408 |  | MKWHr.
| Day Peak Demand |  |  | 7819.3 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.03 |  | MKWHr.
| Evening Peak Generation |  |  | 12364.7 | MW | 21:00 Hr. | Energy Demand |  |  | 233.438 |  | MKWHr.
| Evening Peak Demand |  |  | 12379.7 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33 |  | °C
| Minimum Generation of the Day |  |  | 7412.37 | MW | 10:00 Hr. | Total Gas Supplied |  |  | 1017.79 |  | MMCFD
| Maximum Generation of the Day |  |  | 12518 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 5.4447 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 38.5256 | 0 | 2.8596 | 0 | 0 | 0.23584 | 0 | 0 | 41.6211 | Gas | 125.8431 | Gas | 457283698.94
| Chattogram Zone |  |  | 4.0144 | 21.4164 | 2.2568 | 0 | 1.1699 | 0.15969 | 0 | 0.3432 | 29.3604 | Coal | 62.2339 | Coal | 410831165.561
| Cumilla Zone |  |  | 30.2791 | 0 | 1.4064 | 0 | 0 | 0.45226 | 2.5056 | 0 | 34.6433 | HFO | 9.1618 | HFO | 144848200.962
| Mymensingh Zone |  |  | 3.671 | 0 | 0.90768 | 0 | 0 | 0.32045 | 0 | 0 | 4.8992 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 18.459 | 0 | 0 | 0 | 0 | 0.053794 | 0 | 0 | 18.5128 | Hydro | 1.1699 | Hydro | 116988
| Khulna Zone |  |  | 9.0697 | 11.4618 | 0.15408 | 0 | 0 | 0.70776 | 11.6138 | 0 | 33.0072 | Solar | 5.026 | Solar | 80732860.2588
| Barishal Zone |  |  | 7.1851 | 28.1815 | 0.05856 | 0 | 0 | 0.004596 | 0 | 0 | 35.4297 | Import | 29.6302 | Import | 171984103.72
| Rajshahi Zone |  |  | 14.6391 | 0 | 0.60662 | 0 | 0 | 1.6172 | 15.5107 | 0 | 32.3737 | Wind | 0.3432 | Wind | 5048472
| Rangpur Zone |  |  | 0 | 1.1743 | 0.91205 | 0 | 0 | 1.4743 | 0 | 0 | 3.5606
| Total |  |  | 125.8431 | 62.2339 | 9.1618 | 0 | 1.1699 | 5.026 | 29.6302 | 0.3432 | 233.408
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 457283698.94 |  | Hydro | 116988
|  |  |  | Coal | 410831165.561 |  | Solar | 80732860.2588
|  |  |  | HFO | 144848200.962 |  | Import | 171984103.72
|  |  |  | HSD | 0 |  | Wind | 5048472
[5 empty] | Total: | 127,08,45,489 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 123781.82 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 11.6138 | Peak Hr Flow | 923.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 13372581.82 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 15.5107 | Peak Hr Flow | 637.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 697 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.5056 | Peak Hr Flow | 138.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 991 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 29.6302 | Peak Hr Flow | 1698.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3346
|  |  |  | Chattogram |  | 0 |  | 1149
|  |  |  | Cumilla |  | 14 |  | 1522
|  |  |  | Mymensingh |  | 0 |  | 1046
|  |  |  | Sylhet |  | 0 |  | 555
|  |  |  | Khulna |  | 0 |  | 1492
|  |  |  | Barishal |  | 0 |  | 474
|  |  |  | Rajshahi |  | 0 |  | 1460
|  |  |  | Rangpur |  | 0 |  | 885
|  |  |  | Total |  | 14 |  | 11929
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 10:30 | 12:58 | Narshingdi 132/33kV S/S T-4 HT Scheduled S/D Due to 33 kv redhot | [7 empty] | 35.0MW load
interrup.
| 11:29 | 12:58 | Narshingdi 132/33kV S/S T-4 LT Scheduled S/D Due to 33 kv side redhot | [7 empty] | 35.0MW load
interrup.
| 11:30 | 12:17 | Sirajganj 132/33kV S/S T4-(445) LT Forced S/D Due to Red hot bolt Replacement work at | [7 empty] | 8.0MW load
|  |  | Tarash 33 kv incoming DS. | [7 empty] | interrup.
| 11:30 | 12:16 | Sirajganj 132/33kV S/S T4-(445) HT Forced S/D | [7 empty] | 8.0MW load
interrup.
| 12:00 |  | Day Peak Generation: 7816 MW.
| 14:23 | 19:00 | TK chemical S/S 50/75 MVA T-1(405T) LT Tripped showing Over current relays Due to Cable | [7 empty] | 1.0MW load
|  |  | problem in LT side of T-1 transformer | [7 empty] | interrup.
| 14:48 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized with remarks:- GT
| 14:56 |  | Ghorasal Repowered CCPP Unit-4 Synchronized
| 17:47 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized with remarks:- ST
| 18:06 | 18:28 | Tangail 132/33kV S/S Tr-2 LT Tripped showing REF 616 relays Due to 33 kv Bus PT Fail | [7 empty] | 50.0MW load
interrup.
| 18:06 | 18:16 | Tangail 132/33kV S/S Tr-1 LT Tripped showing REF 615 relays Due to 33Kv bus PT Fail | [7 empty] | 50.0MW load
interrup.
| 20:14 | 20:56 | Shahjadpur 132/33kV S/S T-1(405T) LT Forced S/D Due to Emergency redhot maintenance
| 20:15 | 20:55 | Shahjadpur 132/33kV S/S T-1(405T) HT Forced S/D Due to Emergency redhot maintenance.
| 21:43 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 23:04 |  | BIPTC S/S 10CF15 Tripped showing Differential Relay relays Due to Tripped by C1
unbalance 60/61 instant L3
| 01:38 |  | Ashuganj 450 MW CCPP(South) Tripped with remarks:- GT
| 02:36 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 06:00 |  | Minimum Generation is 9884 MW.
| 07:40 |  | Bogura 132/33kV S/S Transformer-3 LT Forced S/D Due to 33kV Incoming DS (R-Phase) Red-Hot | [7 empty] | 25.0MW load
|  |  | Maintenance work | [7 empty] | interrup.
| 07:40 |  | Bogura 132/33kV S/S Transformer-3 HT Forced S/D Due to 33kV Incoming DS (R-Phase) Red-Hot | [7 empty] | 25.0MW load
|  |  | Maintenance work | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 28-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 220 | 1924063 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 37 | 230000 | -
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 347 | 8582400 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 149 | 3531462 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 156932 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 76 | 3019000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 328 | 7727585 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 33.7 | 130320 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 157591 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 131939 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 12 | 252000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 3 | 171720 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 107040 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 212 | 920084 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 60 | 249984 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 74880 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 426240 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 235841 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 41400 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 530 | 12240000 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 173 | 847392 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 86 | 463200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2557.7 | 41621073
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 16 | 72462.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 128250 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 252960 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 66 | 1169880 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 147 | 3098589 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 90 | 500145 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 167985 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 160320 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 38 | 915840 | plant availability zero
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 31441 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 32 | 148036 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 17 | 121226 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 89 | 420691 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 222720 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 45 | 176891 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 13382 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 580 | 11961817 | U2 outage added
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 7 | 343200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 475 | 9454545.45 | U1 under maintenance
Chattogram Area Total |  |  |  |  | 4898.863 | 1786 | 29360381.05
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 202 | 5016000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 361 | 8979000 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 0 | 398000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 310 | 8003000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 29 | 614664 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 47 | 950400 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 190 | 3763636 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1108016 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 142 | 727636 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 97 | 1026992 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 192000 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 138 | 2505600 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 60533 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 16 | 419350 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 426240 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 452264 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1715 | 34643331
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 155 | 3671040 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 55 | 477600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 57 | 409200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 305500 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 20880 | From 17:00 to 20:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 267 | 4899170
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 53794 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 238680 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 139 | 3471954.5 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 101 | 890000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 683136 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1702080 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 103 | 2459480 | STG Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 327696 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 321 | 8686000 | FGMO not available because of Cooling Tower Fan
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 826 | 18512820.5
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 923 | 11613818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 344 | 9069696 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 34 | 154080 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | FGMO
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 707760 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 597 | 11461816 | Unit1 Under Maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1898 | 33007170
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 504 | 10800000 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 14 | 58560 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 128 | 1880000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 525 | 11425454.55 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5305120 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 277 | 5956000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4596 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1668 | 35429730.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 400296 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 172 | 4334455 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 165 | 1062436 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 22100 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 373 | 9220072 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 309696 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 50 | 296928 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 17880 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 637 | 15510747 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 416144 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 782920 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1447 | 32373674
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 52 | 1174254 | Plant availability zero, U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 499555 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 48301.44 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 412493 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 167456 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1258560 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 200 | 3560619.44
Eastern Grid Total |  |  |  |  | 17418.042 | 7151.7 | 129036775.55
Western Grid Total |  |  |  |  | 11852.195 | 5213 | 104371193.99
National Grid Total |  |  |  |  | 29270.237 | 12364.7 | 233407969.54
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 28-05-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7604.36 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4310.6 | MW
i) Dhaka area |  |  | 3346.06 |  | MW | i) Khulna area |  |  |  | 1492 | MW
ii) Chattogram area |  |  | 1149.3 |  | MW | ii) Barishal area |  |  |  | 473.6 | MW
iii) Cumilla area |  |  | 1508 |  | MW | iii) Rajshahi area |  |  |  | 1460 | MW
iv) Mymensingh area |  |  | 1046 |  | MW | iv) Rangpur area |  |  |  | 885 | MW
v) Sylhet area |  |  | 555 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11914.96 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 76 | 23:00 | 133 | Natore | 145 | 23:00
2 | AKSML | 14 | 03:00 | 68 | Hathazari | 93 | 21:00 | 134 | Nawabganj | 64.8 | 22:00
3 | Aftabnagar | 32 | 22:00 | 69 | Hatirjheel | 21 | 19:00 | 135 | Netrakona | 138 | 19:30
4 | Agargaon | 72 | 21:00 | 70 | Ishurdi | 68 | 20:00 | 136 | New | 48 | 20:00
5 | Agrabad | 54 | 22:00 | 71 | Jaldhaka | 86 | 20:00 | 137 | Niamatpur | 81 | 23:00
6 | Amnura | 32 | 23:00 | 72 | Jamalpur | 121 | 19:30 | 138 | Noapara | 32 | 20:00
7 | Ashuganj | 80 | 21:00 | 73 | Jashore | 156 | 19:30 | 139 | PHP | 3 | 18:00
8 | BSRM | 3 | 01:00 | 74 | Jhenaidah | 109 | 23:00 | 140 | Pabna | 93 | 20:00
9 | Bagerhat | 87 | 20:00 | 75 | Joydebpur | 79 | 22:00 | 141 | Palashbari | 114 | 19:30
10 | Bajitpur | 89 | 19:00 | 76 | Joypurhat | 60 | 21:00 | 142 | Panchagarh | 52 | 20:00
11 | Bakerganj | 16.4 | 22:00 | 77 | Juldah | 11.5 | 19:30 | 143 | Patiya | 14.8 | 22:00
12 | Bakulia | 76 | 23:00 | 78 | KSRM | 6 | 01:00 | 144 | Patuakhali | 81.8 | 23:00
13 | Banani | 26 | 19:00 | 79 | Kabirpur | 85 | 19:00 | 145 | Payra | 40 | 23:00
14 | Bangabhaban | 3 | 00:00 | 80 | Kachua | 112 | 22:00 | 146 | Postogola | 38 | 21:00
15 | Barapukuria | 58 | 20:00 | 81 | Kaliganj | 27 | 21:00 | 147 | Pubail | 18 | 19:00
16 | Barguna | 26 | 22:00 | 82 | Kallyanpur | 87 | 19:00 | 148 | Purbachal | 24 | 19:00
17 | Barishal | 100 | 22:00 | 83 | Kalurghat | 28 | 23:00 | 149 | Purbasadipur | 110 | 21:00
18 | Barishal-230 | 90 | 22:00 | 84 | Kamrangirchar | 40 | 23:00 | 150 | Rahanpur | 43 | 21:00
19 | Baroaulia | 46 | 18:30 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 1 | 20:00
20 | Baroirhat | 80 | 22:00 | 86 | Kasba | 42 | 21:00 | 152 | Rajbari | 84 | 21:00
21 | Bashundhara | 127 | 19:00 | 87 | Kazla | 59 | 00:00 | 153 | Rajendrapur | 91 | 19:30
22 | BashundharaCement | 1 | 15:00 | 88 | Keranigonj | 66 | 21:00 | 154 | Rajshahi | 107 | 23:00
23 | Beanibazar | 72 | 19:00 | 89 | Khagrachori | 34 | 19:00 | 155 | Rajshahi-230 | 80 | 21:00
24 | Benapole | 66 | 19:30 | 90 | Khulna | 55 | 19:00 | 156 | Ramganj | 120 | 23:00
25 | Bhaluka | 111 | 21:00 | 91 | Khulshi | 95 | 20:00 | 157 | Rampur | 40 | 19:00
26 | Bhandaria | 63 | 21:00 | 92 | Kishoreganj | 138 | 21:00 | 158 | Rangamati | 16 | 18:30
27 | Bhangura | 42 | 19:30 | 93 | Kodda | 134 | 20:00 | 159 | Rangpur | 126 | 19:30
28 | Bheramara(GK) | 68 | 22:00 | 94 | Kulaura | 48 | 19:00 | 160 | Ruppur | 2.4 | 12:00
29 | Bhulta | 95 | 21:00 | 95 | Kurigram | 65 | 20:00 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 56 | 20:00 | 96 | Kushtia | 124 | 21:00 | 162 | Saidpur | 86 | 19:30
31 | Bogura | 150 | 22:00 | 97 | Laksam | 36 | 21:00 | 163 | Santhia | 38 | 20:00
32 | Borhanuddin | 100 | 21:00 | 98 | Lakshmipur | 45 | 15:00 | 164 | Satkhira | 126 | 16:00
33 | Brahmanbaria | 145 | 20:00 | 99 | Lalbag | 25 | 21:00 | 165 | Satmasjid | 69 | 21:00
34 | Cantonment | 86 | 19:30 | 100 | Lalmonirhat | 58 | 19:00 | 166 | Savar | 86 | 22:00
35 | Chandina | 22 | 23:00 | 101 | MI_Cement | 1.1 | 00:00 | 167 | SevenRings | 0.49 | 11:00
36 | Chandpur | 84 | 23:00 | 102 | Madanganj | 24 | 23:00 | 168 | ShahCement | 3 | 01:00
37 | Chandraghona | 39 | 21:00 | 103 | Madaripur | 117 | 21:00 | 169 | Shahjadpur | 82 | 22:00
38 | Chapai | 70 | 21:00 | 104 | Madartek | 62 | 22:00 | 170 | Shahjibazar | 114 | 20:00
39 | Charsaidpur | 8 | 00:00 | 105 | Madunaghat | 49 | 17:00 | 171 | Shahmirpur | 47 | 21:00
40 | Chauddagram | 82 | 22:00 | 106 | Magura | 68 | 19:30 | 172 | Shariatpur | 75 | 20:00
41 | Chhatak | 34 | 21:00 | 107 | Mahasthangarh | 80 | 19:30 | 173 | Sherpur | 134 | 20:00
42 | Chowmuhani | 170 | 22:00 | 108 | Maijdee | 40 | 19:00 | 174 | Shikalbaha | 25 | 22:00
43 | Chuadanga | 126 | 21:00 | 109 | Manikganj | 100 | 21:00 | 175 | Shitalakhya | 48.4 | 21:00
44 | Coxsbazar | 143 | 21:00 | 110 | Maniknagar | 45 | 21:00 | 176 | Sholosohor | 35 | 23:00
45 | Cumilla(N) | 119 | 21:00 | 111 | Matarbari | 58 | 20:00 | 177 | Shomvuganj | 16 | 19:30
46 | Cumilla(S) | 146 | 22:00 | 112 | Matuail | 38 | 23:00 | 178 | Shyampur | 44 | 22:00
47 | Daganbhuiyan | 35 | 22:00 | 113 | Metrorail_Motijheel | 3 | 15:00 | 179 | Siddhirganj | 72 | 21:00
48 | Daudkandi | 136 | 21:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 104 | 19:30
49 | DhakaUniversity | 26 | 20:00 | 115 | Millgate | 37 | 23:00 | 181 | Sonargaon | 63 | 21:00
50 | Dhamrai | 62 | 22:00 | 116 | Mirpur | 101 | 20:00 | 182 | Sreemongol | 71 | 19:30
51 | Dhanmondi | 43 | 19:00 | 117 | Mirsorai | 9 | 20:00 | 183 | Sreepur | 46 | 19:00
52 | Dohazari | 108 | 21:00 | 118 | Mirzapur | 42 | 19:30 | 184 | Srinagar | 55.4 | 21:00
53 | Faridpur | 161 | 23:00 | 119 | Mithapukur | 58 | 20:00 | 185 | Sunamganj | 55 | 19:00
54 | Fatullah | 43 | 23:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 54 | 19:00
55 | Fenchuganj | 37 | 19:00 | 121 | Mogbazar | 50.4 | 19:30 | 187 | Sylhet-132 | 83 | 19:00
56 | Feni | 126 | 21:00 | 122 | Mongla | 24 | 23:00 | 188 | TK | 29 | 23:00
57 | GPH | 1 | 01:00 | 123 | Motijheel | 25 | 18:30 | 189 | Tangail | 150 | 22:00
58 | Ghatail | 93 | 22:00 | 124 | Muktagacha | 37 | 19:00 | 190 | Taraganj | 20 | 19:30
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 110 | 22:00 | 191 | Tasnim | 2 | 01:00
60 | Ghorashal-230 | 67 | 21:00 | 126 | Muradnagar | 54 | 19:00 | 192 | Thakurgaon | 101 | 20:00
61 | Goalpara | 42 | 19:30 | 127 | Mymensingh | 144 | 21:00 | 193 | Tongi | 59 | 00:00
62 | Gollamari | 88 | 19:30 | 128 | Nabinagar | 66 | 21:00 | 194 | Ullahpara | 39 | 21:00
63 | Gopalganj | 112 | 23:00 | 129 | Naogaon | 126 | 22:00 | 195 | Ullon | 48 | 19:00
64 | Gulshan | 62 | 19:00 | 130 | Narail | 55 | 20:00 | 196 | Uttara | 57 | 21:00
65 | Halishahar | 55.5 | 00:00 | 131 | Narinda | 35 | 22:00 | 197 | UttaraNew | 38 | 21:00
66 | HaripurSBU | 45 | 22:00 | 132 | Narshingdi | 135 | 22:00 | 198 | Zigatola | 62 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 28-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 9594 | 0 |  | 9594
1:00 | 9297 | 0 |  | 9297
2:00 | 9045 | 0 |  | 9045
3:00 | 8647 | 0 |  | 8647
4:00 | 8328 | 0 |  | 8328
5:00 | 8284 | 0 |  | 8284
6:00 | 8792.11 | 0 |  | 8792.11
7:00 | 9221.57 | 0 |  | 9221.57
8:00 | 8477.33 | 0 |  | 8477.33
9:00 | 7712.2 | 0 |  | 7712.2
10:00 | 7412.37 | 0 |  | 7412.37
11:00 | 7540.04 | 0 |  | 7540.04
12:00 | 7819.3 | 0 |  | 7819.3
13:00 | 8482.27 | 0 |  | 8482.27
14:00 | 9083.9 | 0 |  | 9083.9
15:00 | 9724.16 | 0 |  | 9724.16
16:00 | 9915.94 | 0 |  | 9915.94
17:00 | 10239.61 | 0 |  | 10239.61
18:00 | 10235.78 | 0 |  | 10235.78
19:00 | 11594 | 0 |  | 11594
19:30 | 12359 | 0 |  | 12359
20:00 | 12043 | 0 |  | 12043
21:00 | 12364.7 | 14 |  | 12379.7
22:00 | 12407 | 8 |  | 12415
23:00 | 12518 | 8 |  | 12526
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 28-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4912 | 4682 | 9594 | DAILY GENERATION CURVE
00:30 | 4866.5 | 4579 | 9445.5
01:00 | 4821 | 4476 | 9297 | 28-05-2026
01:30 | 4758.5 | 4412.5 | 9171
02:00 | 4696 | 4349 | 9045
02:30 | 4680 | 4166 | 8846
03:00 | 4664 | 3983 | 8647
03:30 | 4650 | 3837.5 | 8487.5
04:00 | 4636 | 3692 | 8328
04:30 | 4650.5 | 3655.5 | 8306
05:00 | 4665 | 3619 | 8284
05:30 | 4774.945 | 3763.11 | 8538.055
06:00 | 4884.89 | 3907.22 | 8792.11
06:30 | 4955.9 | 4050.94 | 9006.84
07:00 | 5026.91 | 4194.66 | 9221.57
07:30 | 4762.215 | 4087.235 | 8849.45
08:00 | 4497.52 | 3979.81 | 8477.33
08:30 | 4372.19 | 3722.575 | 8094.765
09:00 | 4246.86 | 3465.34 | 7712.2
09:30 | 4144.7 | 3417.585 | 7562.285
10:00 | 4042.54 | 3369.83 | 7412.37
10:30 | 4076.81 | 3399.395 | 7476.205
11:00 | 4111.08 | 3428.96 | 7540.04
11:30 | 4128.19 | 3551.48 | 7679.67
12:00 | 4145.3 | 3674 | 7819.3
12:30 | 4363.165 | 3787.62 | 8150.785
13:00 | 4581.03 | 3901.24 | 8482.27
13:30 | 4796.16 | 3986.925 | 8783.085
14:00 | 5011.29 | 4072.61 | 9083.9
14:30 | 5258.59 | 4145.44 | 9404.03
15:00 | 5505.89 | 4218.27 | 9724.16
15:30 | 5585.56 | 4234.49 | 9820.05
16:00 | 5665.23 | 4250.71 | 9915.94
16:30 | 5668.98 | 4408.795 | 10077.775
17:00 | 5672.73 | 4566.88 | 10239.61
17:30 | 5690.095 | 4547.6 | 10237.695
18:00 | 5707.46 | 4528.32 | 10235.78
18:30 | 6040.23 | 4874.66 | 10914.89
19:00 | 6373 | 5221 | 11594
19:30 | 6826 | 5533 | 12359
20:00 | 6729 | 5314 | 12043
20:30 | 6940.35 | 5263.5 | 12203.85 |  | Executive Engineer
21:00 | 7151.7 | 5213 | 12364.7 |  | Network Operation Division
21:30 | 7113.85 | 5272 | 12385.85
22:00 | 7076 | 5331 | 12407
22:30 | 7142.5 | 5320 | 12462.5
23:00 | 7209 | 5309 | 12518

## En-Curve
QF-LDC-12
Date | 28-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3641 | 1529 | 620 | 0 | 106 | 744 | 35 | 2898 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3638.5 | 1529 | 620 | 0 | 103 | 739.5 | 33.5 | 2755.5 | 0 | 0 | 26.5 | 0 | 0 | 0 | 0 | 28-05-2026
01:00 | 3636 | 1529 | 620 | 0 | 100 | 735 | 32 | 2613 | 0 | 0 | 32 | 0 | 0 | 0 | 0
01:30 | 3582.5 | 1507.5 | 620.5 | 0 | 96 | 726 | 32 | 2563 | 0 | 0 | 32 | 0 | 0 | 11.5 | 0 | Energy Generated | 233.408 |  | MKWHr
02:00 | 3529 | 1486 | 621 | 0 | 92 | 717 | 32 | 2513 | 0 | 0 | 32 | 0 | 0 | 23 | 0 | Energy not Served | 0.03 |  | MKWHr
02:30 | 3518.5 | 1496 | 478.5 | 0 | 90 | 724 | 33 | 2472.5 | 0 | 0 | 16 | 0 | 0 | 17.5 | 0 | Total Energy Requirement | 233.438 |  | MKWHr
03:00 | 3508 | 1506 | 336 | 0 | 88 | 731 | 34 | 2432 | 0 | 0 | 0 | 0 | 0 | 12 | 0
03:30 | 3487 | 1494.5 | 289 | 0 | 88 | 718 | 34 | 2362 | 0 | 0 | 0 | 0 | 0 | 15 | 0
04:00 | 3466 | 1483 | 242 | 0 | 88 | 705 | 34 | 2292 | 0 | 0 | 0 | 0 | 0 | 18 | 0
04:30 | 3478 | 1488 | 241.5 | 0 | 87 | 720.5 | 34.5 | 2232.5 | 0 | 0 | 0 | 0 | 0 | 24 | 0
05:00 | 3490 | 1493 | 241 | 0 | 86 | 736 | 35 | 2173 | 0 | 0 | 0 | 0 | 0 | 30 | 0
05:30 | 3575.5 | 1513.5 | 218.5 | 0 | 94 | 740 | 35 | 2307 | 14.055 | 0 | 2 | 0 | 0 | 38.5 | 0
06:00 | 3661 | 1534 | 196 | 0 | 102 | 744 | 35 | 2441 | 28.11 | 0 | 4 | 0 | 0 | 47 | 0
06:30 | 3653 | 1453.5 | 195.5 | 0 | 101 | 755.5 | 35 | 2677.5 | 68.34 | 0 | 18 | 0 | 0 | 49.5 | 0
07:00 | 3645 | 1373 | 195 | 0 | 100 | 767 | 35 | 2914 | 108.57 | 0 | 32 | 0 | 0 | 52 | 0
07:30 | 3445 | 1318 | 195.5 | 0 | 93 | 723 | 35 | 2798 | 196.45 | 0 | 16 | 0 | 0 | 29.5 | 0
08:00 | 3245 | 1263 | 196 | 0 | 86 | 679 | 35 | 2682 | 284.33 | 0 | 0 | 0 | 0 | 7 | 0
08:30 | 3198.5 | 1210.5 | 195.5 | 0 | 80 | 647.5 | 35 | 2417 | 302.765 | 0 | 0 | 0 | 0 | 8 | 0
09:00 | 3152 | 1158 | 195 | 0 | 74 | 616 | 35 | 2152 | 321.2 | 0 | 0 | 0 | 0 | 9 | 0
09:30 | 3143.5 | 1060.5 | 195 | 0 | 76 | 575.5 | 35 | 2061.5 | 405.285 | 0 | 0 | 0 | 0 | 10 | 0
10:00 | 3135 | 963 | 195 | 0 | 78 | 535 | 35 | 1971 | 489.37 | 0 | 0 | 0 | 0 | 11 | 0
10:30 | 3153 | 999.5 | 195 | 0 | 80 | 487 | 35 | 1915.5 | 590.705 | 0 | 0 | 0 | 0 | 20.5 | 0
11:00 | 3171 | 1036 | 195 | 0 | 82 | 439 | 35 | 1860 | 692.04 | 0 | 0 | 0 | 0 | 30 | 0
11:30 | 3205 | 1062.5 | 313 | 0 | 78 | 434.5 | 34.5 | 1831 | 702.17 | 0 | 0 | 0 | 0 | 19 | 0
12:00 | 3239 | 1089 | 431 | 0 | 74 | 430 | 34 | 1802 | 712.3 | 0 | 0 | 0 | 0 | 8 | 0
12:30 | 3396 | 1174.5 | 431 | 0 | 80 | 458 | 33.5 | 1876.5 | 693.285 | 0 | 0 | 0 | 0 | 8 | 0
13:00 | 3553 | 1260 | 431 | 0 | 86 | 486 | 33 | 1951 | 674.27 | 0 | 0 | 0 | 0 | 8 | 0
13:30 | 3595.5 | 1381.5 | 431 | 0 | 87 | 493.5 | 47.5 | 2090.5 | 645.085 | 0 | 0 | 0 | 0 | 11.5 | 0
14:00 | 3638 | 1503 | 431 | 0 | 88 | 501 | 62 | 2230 | 615.9 | 0 | 0 | 0 | 0 | 15 | 0
14:30 | 3749.5 | 1514 | 431 | 0 | 97 | 520.5 | 62.5 | 2446.5 | 570.03 | 0 | 0 | 0 | 0 | 13 | 0
15:00 | 3861 | 1525 | 431 | 0 | 106 | 540 | 63 | 2663 | 524.16 | 0 | 0 | 0 | 0 | 11 | 0
15:30 | 3955.5 | 1531.5 | 431 | 0 | 109 | 558 | 64.5 | 2737 | 421.05 | 0 | 0 | 0 | 0 | 12.5 | 0
16:00 | 4050 | 1538 | 431 | 0 | 112 | 576 | 66 | 2811 | 317.94 | 0 | 0 | 0 | 0 | 14 | 0
16:30 | 4069 | 1536.5 | 431 | 0 | 114 | 653 | 66.5 | 2960 | 238.275 | 0 | 0 | 0 | 0 | 9.5 | 0
17:00 | 4088 | 1535 | 431 | 0 | 116 | 730 | 67 | 3109 | 158.61 | 0 | 0 | 0 | 0 | 5 | 0
17:30 | 4051 | 1503.5 | 439 | 0 | 118 | 747.5 | 67 | 3128 | 96.195 | 5 | 79.5 | 0 | 0 | 3 | 0
18:00 | 4014 | 1472 | 447 | 0 | 120 | 765 | 67 | 3147 | 33.78 | 10 | 159 | 0 | 0 | 1 | 0
18:30 | 4091 | 1522 | 676.5 | 0 | 128 | 747 | 66 | 3138.5 | 16.89 | 31 | 497.5 | 0 | 0 | 0.5 | 0
19:00 | 4168 | 1572 | 906 | 0 | 136 | 729 | 65 | 3130 | 0 | 52 | 836 | 0 | 0 | 0 | 0
19:30 | 4084 | 1453 | 930 | 0 | 134 | 707 | 65 | 3291 | 0 | 107 | 1588 | 0 | 0 | 0 | 0
20:00 | 3999 | 1401 | 922 | 0 | 136 | 665 | 65 | 3141 | 0 | 139 | 1573 | 0 | 0 | 2 | 0
20:30 | 4019 | 1554 | 922.5 | 0 | 137 | 651 | 65.5 | 3075.5 | 0 | 150 | 1624.85 | 0 | 0 | 4.5 | 7
21:00 | 4039 | 1707 | 923 | 0 | 138 | 637 | 66 | 3010 | 0 | 161 | 1676.7 | 0 | 0 | 7 | 14
21:30 | 4146.5 | 1744.5 | 922.5 | 0 | 142 | 651.5 | 68 | 3033 | 0 | 161 | 1511.35 | 0 | 0 | 5.5 | 11
22:00 | 4254 | 1782 | 922 | 0 | 146 | 666 | 70 | 3056 | 0 | 161 | 1346 | 0 | 0 | 4 | 8
22:30 | 4338.5 | 1788 | 912 | 0 | 146 | 671 | 67.5 | 3034.5 | 0 | 161 | 1340.5 | 0 | 0 | 3.5 | 8
23:00 | 4423 | 1794 | 902 | 0 | 146 | 676 | 65 | 3013 | 0 | 161 | 1335 | 0 | 0 | 3 | 8
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 28-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 22 | -40 | 164 | 30 | 654 | -42 | Ishurdi-Ghorashal Ckt-1 | Export | 252581.82
1:00 | 18 | -41 | 168 | 24 | 720 | -52
2:00 | 13 | -41 | 138 | 20 | 660 | -52 |  | Import | 123781.82
3:00 | -17 | -27 | 114 | 32 | 580 | -48
4:00 | -29 | -29 | 78 | 22 | 460 | -46 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | -20 | -28 | 100 | 24 | 438 | -46
6:00 | -15 | -24 | 132 | 34 | 608 | -38 |  | Import | 0
7:00 | -26 | -24 | 94 | 30 | 668 | -64
8:00 | -6 | -25 | 142 | 34 | 596 | -44 | Sirajganj-Sreepur Ckt-1 | Export | 0
9:00 | 9 | -27 | 140 | 28 | 438 | -32
10:00 | 20 | -28 | 156 | 32 | 394 | -16 |  | Import | 0
11:00 | 20 | -27 | 174 | 48 | 384 | -16
12:00 | 46 | -39 | 294 | 52 | 396 | -14 | Sirajganj-Sreepur Ckt-2 | Export | 0
13:00 | 36 | -38 | 214 | 60 | 404 | -10
14:00 | 22 | -39 | 164 | 54 | 528 | -28 |  | Import | 0
15:00 | 8 | -30 | 144 | 76 | 478 | -30
16:00 | -10 | -32 | 136 | 68 | 492 | -46 | Gopalganj-Aminbazar Ckt-1 | Export | 6560000
17:00 | 0 | -33 | 178 | 78 | 712 | -52
18:00 | -6 | -33 | 160 | 72 | 634 | -68 |  | Import | 0
18:30 | -7 | -35 | 278 | 78 | 648 | -68
19:00 | 34 | -55 | 166 | 76 | 634 | -136 | Gopalganj-Aminbazar Ckt-2 | Export | 6560000
19:30 | 7 | -48 | 360 | 76 | 624 | -162
20:00 | -3 | -46 | 136 | 68 | 538 | -162 |  | Import | 0
21:00 | 9 | -43 | 164 | 70 | 524 | -128
22:00 | 10 | -50 | 168 | 60 | 582 | -120 |  | Total Export | 13372581.82
23:00 | 7 | -49 | 132 | 38 | 448 | -156 |  | Total Import | 123781.82
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 28-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 412 | 09:00 | 398 | 19:00 | Madunaghat | 413 | 09:00 | 402 | 17:00
Amtali | 420 | 09:00 | 409 | 19:30 | Meghnaghat | 414 | 10:00 | 400 | 19:00
Ashuganj | 423 | 5:00 | 406 | 19:00 | Payra | 421 | 10:00 | 408 | 19:00
Bhulta | 417 | 05:00 | 400 | 19:00 | Rahanpur | 412 | 10:00 | 393 | 22:00
Bibiana | 417 | 09:00 | 404 | 19:00 | Rampal | 409 | 09:00 | 390 | 19:30
BIPTC | 409 | 06:00 | 395 | 21:00
Bogura | 407 | 11:00 | 385 | 22:00
Gopalganj | 414 | 10:00 | 396 | 19:00
Kaliakoir | 413 | 09:00 | 399 | 17:00
Korerhat | 418 | 10:00 | 404 | 17:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 240 | 05:00 | 232 | 19:00 | Jhenaidah | 237 | 09:00 | 217 | 19:00
AKSML | 238 | 09:00 | 227 | 17:00 | Kachua | 237 | 08:00 | 226 | 17:00
Aminbazar | 240 | 09:00 | 232 | 19:00 | Kaliakoir | 239 | 09:00 | 231 | 17:00
Ashuganj | 241 | 04:00 | 231 | 19:00 | Keranigonj | 239 | 04:00 | 231 | 19:00
Ashuganj-400 | 241 | 04:00 | 231 | 19:00 | Khulna(S) | 239 | 09:00 | 221 | 19:30
Baghabari | 242 | 10:00 | 229 | 19:00 | Korerhat | 238 | 09:00 | 228 | 17:00
Barapukuria | 230 | 10:00 | 214 | 22:00 | Madunaghat | 235 | 09:00 | 227 | 17:00
Barapukuria-230 | 230 | 10:00 | 214 | 22:00 | Madunaghat-400 | 236 | 09:00 | 229 | 17:00
Barishal | 238 | 04:00 | 227 | 19:00 | Maniknagar | 241 | 09:00 | 234 | 17:00
Bheramara | 238 | 08:00 | 221 | 19:00 | Meghnaghat | 247 | 09:00 | 240 | 17:00
Bhulta | 242 | 08:00 | 234 | 17:00 | Meghnaghat-400 | 241 | 04:00 | 233 | 19:00
Bibiana | 242 | 08:00 | 234 | 19:00 | Mirsorai | 239 | 09:00 | 231 | 17:00
BIPTC | 240 | 09:00 | 221 | 19:00 | Naogaon | 225 | 11:00 | 207 | 20:00
Bogura | 247 | 11:00 | 233 | 22:00 | Purbasadipur | 229 | 10:00 | 210 | 22:00
Bogura-400 | 246 | 10:00 | 232 | 22:00 | Rajshahi | 236 | 08:00 | 219 | 19:00
Borhanuddin | 238 | 09:00 | 230 | 18:30 | Rampal | 237 | 09:00 | 221 | 19:00
BSRM | 238 | 09:00 | 228 | 17:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 236 | 08:00 | 220 | 00:00 | Rampura | 242 | 08:00 | 232 | 19:00
Cumilla(N) | 240 | 09:00 | 229 | 19:00 | Shikalbaha | 234 | 08:00 | 226 | 17:00
Faridpur | 240 | 09:00 | 226 | 22:00 | Shyampur | 240 | 05:00 | 232 | 19:00
Fenchuganj | 245 | 04:00 | 236 | 19:00 | Siddhirganj | 243 | 06:00 | 235 | 16:00
Feni | 237 | 09:00 | 227 | 17:00 | Sirajgonj | 245 | 08:00 | 238 | 22:00
Ghorashal | 242 | 11:00 | 238 | 14:00 | Sreepur | 237 | 05:00 | 226 | 19:00
Ghorashal-230 | 239 | 04:00 | 231 | 19:00 | Tongi | 238 | 08:00 | 233 | 23:00
Gopalganj | 243 | 00:00 | 228 | 19:00
GPH | 237 | 09:00 | 228 | 17:00
Haripur | 242 | 09:00 | 234 | 19:00
Hasnabad | 241 | 09:00 | 232 | 23:00
Hathazari | 234 | 05:00 | 226 | 13:00
Ishurdi | 241 | 09:00 | 225 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 03:00 | 131 | 19:00 | Madunaghat | 137 | 09:00 | 131 | 17:00
Agargaon | 136 | 04:00 | 130 | 19:00 | Magura | 134 | 09:00 | 119 | 19:00
Agrabad | 137 | 08:00 | 131 | 16:00 | Mahasthangarh | 140 | 10:00 | 129 | 22:00
AKS | 134 | 04:00 | 130 | 16:00 | Maijdee | 133 | 05:00 | 126 | 17:00
Aminbazar | 139 | 04:00 | 135 | 16:00 | Manikganj | 135 | 09:00 | 128 | 19:00
Amnura | 137 | 09:00 | 127 | 19:00 | Maniknagar | 137 | 09:00 | 131 | 19:00
Ashuganj | 145 | 08:00 | 137 | 18:30 | Matarbari | 124 | 09:00 | 110 | 23:00
Ashuganj-230 | 145 | 08:00 | 137 | 18:30 | Matuail | 139 | 08:00 | 134 | 18:30
Bagerhat | 133 | 09:00 | 116 | 19:00 | Metrorail_Motijheel | 137 | 09:00 | 131 | 19:00
Bajitpur | 137 | 10:00 | 127 | 19:00 | Metrorail_Uttara | 135 | 02:00 | 131 | 18:30
Bakerganj | 137 | 09:00 | 129 | 19:00 | Millgate | 136 | 03:00 | 131 | 19:00
Bakulia | 136 | 08:00 | 130 | 17:00 | Mirpur | 139 | 05:00 | 134 | 23:00
Banani | 136 | 08:00 | 131 | 19:00 | Mirzapur | 135 | 10:00 | 127 | 22:00
Bangabhaban | 136 | 03:00 | 131 | 18:30 | Mithapukur | 137 | 10:00 | 126 | 22:00
Barapukuria | 140 | 11:00 | 127 | 22:00 | MI_Cement | 139 | 04:00 | 134 | 17:00
Barguna | 136 | 09:00 | 126 | 19:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 138 | 10:00 | 129 | 18:30 | Mogbazar | 138 | 04:00 | 132 | 19:00
Barishal-230 | 138 | 04:00 | 129 | 19:00 | Mongla | 134 | 09:00 | 114 | 19:00
Baroaulia | 136 | 07:00 | 131 | 17:00 | Motijheel | 138 | 07:00 | 131 | 18:30
Baroirhat | 138 | 09:00 | 132 | 18:30 | Muktagacha | 132 | 10:00 | 125 | 00:00
Bashundhara | 136 | 01:00 | 131 | 18:30 | Munshiganj | 137 | 08:00 | 132 | 22:00
BashundharaCement | 138 | 11:00 | 134 | 18:30 | Muradnagar | 137 | 05:00 | 128 | 19:00
Beanibazar | 130 | 08:00 | 122 | 19:00 | Mymensingh | 132 | 10:00 | 115 | 19:30
Benapole | 132 | 08:00 | 114 | 19:00 | Nabinagar | 131 | 10:00 | 124 | 19:00
Bhaluka | 134 | 10:00 | 123 | 19:30 | Naogaon | 141 | 08:00 | 124 | 20:00
Bhandaria | 134 | 09:00 | 120 | 19:00 | Narail | 136 | 08:00 | 118 | 19:00
Bhangura | 139 | 09:00 | 131 | 20:00 | Narinda | 137 | 09:00 | 131 | 19:00
Bheramara | 139 | 09:00 | 131 | 19:00 | Narshingdi | 138 | 09:00 | 127 | 19:00
Bheramara(GK) | 139 | 08:00 | 131 | 22:00 | Natore | 138 | 09:00 | 128 | 19:00
Bhulta | 136 | 08:00 | 130 | 19:00 | Nawabganj | 135 | 05:00 | 128 | 19:00
Bog-Sherpur | 141 | 10:00 | 131 | 22:00 | Netrakona | 130 | 10:00 | 113 | 19:00
Bogura | 142 | 10:00 | 133 | 22:00 | New | 137 | 09:00 | 132 | 17:00
Bogura-230 | 142 | 09:00 | 134 | 22:00 | Niamatpur | 136 | 11:00 | 127 | 22:00
Brahmanbaria | 139 | 08:00 | 128 | 19:00 | Noapara | 134 | 08:00 | 120 | 19:00
Cantonment | 136 | 10:00 | 130 | 19:00 | Pabna | 138 | 08:00 | 129 | 21:00
Chandina | 140 | 09:00 | 132 | 19:00 | Palashbari | 137 | 10:00 | 126 | 22:00
Chandpur | 133 | 09:00 | 126 | 17:00 | Panchagarh | 141 | 05:00 | 127 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 138 | 09:00 | 133 | 16:00 | Patiya | 135 | 08:00 | 128 | 17:00
Chapai | 135 | 08:00 | 127 | 22:00 | Patuakhali | 135 | 03:00 | 128 | 19:00
Charsaidpur | 138 | 04:00 | 133 | 22:00 | Payra | 138 | 04:00 | 132 | 19:00
Chauddagram | 137 | 09:00 | 129 | 19:00 | PHP | 137 | 05:00 | 131 | 17:00
Chhatak | 129 | 09:00 | 119 | 23:00 | Postogola | 140 | 09:00 | 135 | 22:00
Chowmuhani | 133 | 07:00 | 127 | 17:00 | Pubail | 144 | 09:00 | 138 | 19:00
Chuadanga | 132 | 05:00 | 114 | 23:00 | Purbachal | 137 | 03:00 | 131 | 17:00
Coxsbazar | 126 | 09:00 | 113 | 19:00 | Purbasadipur | 135 | 05:00 | 124 | 22:00
Cumilla(N) | 139 | 08:00 | 131 | 19:00 | Rahanpur | 137 | 10:00 | 129 | 22:00
Cumilla(S) | 138 | 08:00 | 121 | 19:00 | Rahanpur-400 | 137 | 10:00 | 129 | 22:00
Daganbhuiyan | 135 | 04:00 | 129 | 17:00 | Rahim | 136 | 20:00 | 134 | 19:00
Daudkandi | 136 | 04:00 | 126 | 19:30 | Rajbari | 137 | 09:00 | 126 | 23:00
DhakaUniversity | 137 | 09:00 | 131 | 19:00 | Rajendrapur | 135 | 09:00 | 124 | 19:00
Dhamrai | 132 | 09:00 | 125 | 19:00 | Rajshahi | 136 | 07:00 | 125 | 22:00
Dhanmondi | 139.7 | 05:00 | 135 | 19:00 | Rajshahi-230 | 137 | 10:00 | 126 | 19:00
Dohazari | 131 | 08:00 | 124 | 18:00 | Ramganj | 131 | 08:00 | 123 | 17:00
Faridpur | 138 | 09:00 | 127 | 23:00 | Rampur | 136 | 08:00 | 130 | 17:00
Fatullah | 139 | 05:00 | 133 | 22:00 | Rampura | 136 | 04:00 | 131 | 19:00
Fenchuganj | 135 | 04:00 | 130 | 19:00 | Rangamati | 137 | 09:00 | 132 | 15:00
Feni | 135 | 00:00 | 129 | 17:00 | Rangpur | 136 | 10:00 | 128 | 23:00
Feni-230 | 136 | 04:00 | 130 | 17:00 | Ruppur | 139 | 08:00 | 132 | 18:30
Ghatail | 130 | 05:00 | 123 | 15:00 | Saidpur | 135 | 10:00 | 127 | 18:00
Ghorashal | 144 | 04:00 | 138 | 19:00 | Santhia | 139 | 09:00 | 130 | 22:00
Goalpara | 137 | 09:00 | 121 | 19:00 | Satkhira | 131 | 09:00 | 118 | 19:00
Gollamari | 136 | 08:00 | 124 | 19:00 | Satmasjid | 136 | 10:00 | 131 | 18:00
Gopalganj | 136 | 05:00 | 126 | 19:00 | Savar | 138 | 08:00 | 133 | 23:00
Gopalganj-400 | 139 | 05:00 | 131 | 19:00 | SevenRings | 144 | 04:00 | 139 | 19:00
Gulshan | 136 | 04:00 | 130 | 19:00 | ShahCement | 138 | 04:00 | 133 | 22:00
Halishahar | 137 | 08:00 | 131 | 17:00 | Shahjadpur | 140 | 07:00 | 133 | 23:00
Haripur | 139 | 09:00 | 134 | 19:00 | Shahjibazar | 139 | 11:00 | 129 | 19:00
HaripurSBU | 139 | 09:00 | 135 | 00:00 | Shahmirpur | 137 | 09:00 | 130 | 17:00
Hasnabad | 141 | 09:00 | 135 | 17:00 | Shariatpur | 138 | 09:00 | 127 | 23:00
Hathazari | 139 | 08:00 | 132 | 17:00 | Sherpur | 128 | 07:00 | 114 | 15:00
Hatirjheel | 137 | 04:00 | 131 | 19:00 | Shikalbaha | 127 | 09:00 | 119 | 19:00
Ishurdi | 141 | 10:00 | 132 | 19:00 | Shikalbaha-230 | 138 | 09:00 | 131 | 17:00
Jaldhaka | 134 | 11:00 | 122 | 23:00 | Shitalakhya | 139 | 04:00 | 134 | 17:00
Jamalpur | 131 | 07:00 | 119 | 16:00 | Sholosohor | 137 | 09:00 | 131 | 17:00
Jashore | 133 | 08:00 | 116 | 19:00 | Shomvuganj | 132 | 11:00 | 122 | 19:30
Jhenaidah | 136 | 03:00 | 121 | 22:00 | Shyampur | 138 | 10:00 | 134 | 23:00
Jhenaidah-230 | 136 | 10:00 | 122 | 23:00 | Shyampur-230 | 138 | 04:00 | 133 | 19:00
Joydebpur | 142 | 08:00 | 136 | 19:00 | Siddhirganj | 139 | 09:00 | 135 | 16:00
Joypurhat | 140 | 10:00 | 127 | 22:00 | Sirajganj | 138 | 10:00 | 128 | 22:00
Juldah | 137 | 00:00 | 131 | 18:00 | Sonargaon | 140 | 11:00 | 135 | 01:00
Kabirpur | 138 | 10:00 | 130 | 19:00 | Sreemongol | 136 | 04:00 | 127 | 19:00
Kachua | 135 | 09:00 | 128 | 17:00 | Sreepur | 135 | 04:00 | 127 | 19:00
Kaliakoir | 139 | 09:00 | 128 | 17:00 | Srinagar | 135 | 08:00 | 128 | 22:00
Kaliganj | 135 | 07:00 | 121 | 19:30 | SSM | 140 | 00:00 | 136 | 01:00
Kallyanpur | 139 | 09:00 | 134 | 21:00 | Sunamganj | 127 | 09:00 | 117 | 19:00
Kalurghat | 137 | 09:00 | 132 | 16:00 | Sylhet | 131 | 05:00 | 125 | 19:00
Kamrangirchar | 138 | 05:00 | 129 | 19:00 | Sylhet-132 | 130 | 03:00 | 125 | 19:00
Kaptai | 140 | 8:00 | 136 | 17:00 | Tangail | 131 | 09:00 | 124 | 19:00
Kasba | 137 | 09:00 | 127 | 19:00 | Taraganj | 135 | 10:00 | 124 | 22:00
Kazla | 136 | 05:00 | 132 | 17:00 | Tasnim | 138 | 08:00 | 134 | 15:00
Keranigonj | 136 | 09:00 | 130 | 19:00 | Thakurgaon | 138 | 05:00 | 125 | 22:00
Khagrachori | 136 | 09:00 | 130 | 19:00 | TK | 138 | 08:00 | 132 | 17:00
Khulna | 136 | 09:00 | 122 | 19:00 | Tongi | 138 | 08:00 | 134 | 23:00
Khulna(S) | 137 | 09:00 | 123 | 19:00 | Ullahpara | 139 | 08:00 | 129 | 22:00
Khulshi | 136 | 09:00 | 129 | 17:00 | Ullon | 136 | 04:00 | 131 | 19:00
Kishoreganj | 136 | 09:00 | 122 | 19:00 | Uttara | 135 | 03:00 | 131 | 17:00
Kodda | 135 | 09:00 | 129 | 17:00 | UttaraNew | 136 | 03:00 | 131 | 17:00
Korerhat | 140 | 05:00 | 134 | 17:00 | Zigatola | 136 | 10:00 | 130 | 22:00
KSRM | 137 | 08:00 | 131 | 17:00
Kulaura | 135 | 09:00 | 128 | 19:00
Kurigram | 131 | 02:00 | 119 | 22:00
Kushtia | 137 | 08:00 | 127 | 19:00
Laksam | 134 | 08:00 | 127 | 17:00
Lakshmipur | 133 | 09:00 | 126 | 17:00
Lalbag | 136 | 08:00 | 130 | 19:00
Lalmonirhat | 128 | 05:00 | 122 | 22:00
Madanganj | 138 | 09:00 | 134 | 17:00
Madaripur | 138 | 10:00 | 125 | 01:00
Madartek | 136 | 04:00 | 132 | 16:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division