## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 30-05-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-05-2026 | during | 30-05-2026 | during | 30-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 230 | 0 | 0 | 0 | 220 | 220 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Machine Problem
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 51 | 0 | 97.7 | 97.7 | 50 | 50
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 376 | 384 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 225 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 148 | 139 | 335 | 335 | 335 | 335
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | -
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 94 | 0 | 210 | 210 | 105 | 105
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 320 | 330 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 102 | 102 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 12.5 | 12 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 7 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | -
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 565 | 520 | 584 | 584 | 584 | 584 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 668 | 625 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 19 | 63 | 160 | 160 | 160 | 160 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2521.5 | 2305 | 5815.22 | 5787.22 | 4849.52 | 4821.52
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 16 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 6 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 35 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 143 | 146 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 51 | 51 | 51 | 51 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 22 | 38 | 38 | 38 | 38 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.58 | 0 | 3.13 | 0 | 3.13 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 12 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 163 | 163 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 352 | 701 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 393 | 355 | 158 | 575 | 575 | 575 | U1 under maintenance
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 977.58 | 1319 | 3001.99 | 3413.86 | 3418.99 | 3413.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 206 | 201 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 355 | 360 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 140 | 240 | 250 | 250 | 250 | 250 | ST under maint
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 280 | 335 | 393 | 393 | 363 | 363 | FGMO
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 29 | 33 | 41.65 | 41.65 | 25 | 25 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 10 | 32 | 52.82 | 52.82 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 16 | 147 | 195 | 195 | 50 | 50 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 41 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 95 | 0 | 163 | 163 | 100 | 100 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 126 | 134 | 84 | 78 | 84 | 78 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 18 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 69 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1396 | 1541 | 2665.43 | 2604.43 | 2371.96 | 2310.96
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-05-2026 | during | 30-05-2026 | during | 30-05-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 146 | 153 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.1 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 75 | 35 | 140 | 140 | 140 | 140 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 45 | 60 | 60 | 60 | 60 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.55 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 22 | 22 | From 17:00 to 20:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 282.65 | 233 | 481.2 | 434 | 481.2 | 434
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 29 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 148 | 149 | 163 | 163 | 147 | 147 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 100 | 0 | 110 | 110 | 110 | 110 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 100 | 102 | 102 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 341 | -
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 327 | 332 | 260 | 260 | 260 | 260 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 830 | 772 | 866 | 866 | 748 | 1089
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 902 | 617 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 36 | 36 | 36 | 36 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 385 | 388 | 410 | 410 | 410 | 410 | -
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 99 | 0 | 100 | 0 | 100 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 629 | 810 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2015 | 1815 | 3606.2 | 3506.2 | 3040.2 | 2940.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 385 | 425 | 1244 | 1244 | 622 | 622 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 124 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 310 | 385 | 1244 | 1244 | 622 | 622 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 150 | 257 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.31 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1189.31 | 1417 | 3406 | 3405 | 2142 | 2141
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 45.05 | 0 | 63 | 0 | 63 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | 1 unit is under maintenance
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 173 | 0 | 214 | 214 | 0 | 0
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 173 | 177 | 220 | 220 | 220 | 220 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 176 | 172 | 220 | 220 | 220 | 220 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 406 | 402 | 413.79 | 413.79 | 413.79 | 413.79 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 97 | 97 | 97 | 97 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.08 | 0 | 3.3 | 0 | 3.3 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 548.31 | 553.11 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | U#1 RSD
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 56.42 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 105 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1687.86 | 1304.11 | 3242.17 | 3014.87 | 3028.17 | 2800.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 52 | 52 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.1 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 23 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 178 | 0 | 195.52 | 0 | 195.52 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 207.1 | 70 | 545.52 | 314 | 459.52 | 228
System Total |  |  |  |  | 28823.2 | 29270.237 | 11107 | 10776.11 | 23629.73 | 23345.58 | 20539.56 | 20179.41
Forecast Scenario (30-05-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 10900 |  | 0 |  | 10900
|  |  |  | 1:00 | 10500 |  | 0 |  | 10500
|  |  |  | 2:00 | 10100 |  | 0 |  | 10100
|  |  |  | 3:00 | 9600 |  | 0 |  | 9600
|  |  |  | 4:00 | 9200 |  | 0 |  | 9200
|  |  |  | 5:00 | 9790 |  | 0 |  | 9790
|  |  |  | 6:00 | 9820 |  | 0 |  | 9820
|  |  |  | 7:00 | 9910 |  | 0 |  | 9910
|  |  |  | 8:00 | 10100 |  | 0 |  | 10100
|  |  |  | 9:00 | 10300 |  | 0 |  | 10300
|  |  |  | 10:00 | 10400 |  | 0 |  | 10400
|  |  |  | 11:00 | 10500 |  | 0 |  | 10500
|  |  |  | 12:00 | 11200 |  | 0 |  | 11200
|  |  |  | 13:00 | 11500 |  | 0 |  | 11500
|  |  |  | 14:00 | 11700 |  | 0 |  | 11700
|  |  |  | 15:00 | 11800 |  | 0 |  | 11800
|  |  |  | 16:00 | 11850 |  | 0 |  | 11850
|  |  |  | 17:00 | 11500 |  | 0 |  | 11500
|  |  |  | 18:00 | 11200 |  | 0 |  | 11200
|  |  |  | 18:30 | 13000 |  | 0 |  | 13000
|  |  |  | 19:00 | 13500 |  | 0 |  | 13500
|  |  |  | 19:30 | 13800 |  | 0 |  | 13800
|  |  |  | 20:00 | 14000 |  | 0 |  | 14000
|  |  |  | 21:00 | 14100 |  | 0 |  | 14100
|  |  |  | 22:00 | 14000 |  | 0 |  | 14000
|  |  |  | 23:00 | 13800 |  | 0 |  | 13800
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 11200.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14100.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14100.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 271.27 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:57 hrs on 30-05-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 29-05-2026 | [28 empty] | Date: | 29-05-2026 | [28 empty] | Date: | 29-05-2026 | [28 empty] | Date: | 29-05-2026 | [28 empty] | Date: | 29-05-2026 | [17 empty] | Date: | 29-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [17 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 24 | 0 | 0 | 220 | 0 | 35 | 371 | 0 | 334 | 0 | 0 | 34 | 0 | 145 | 15 | 17 | 17 | 0 | 0 | 147 | 0 | 0 | 17 | 330 | 138 | 0 | 0 | 51 | 12 | 7 | 0 | 515 | 15 | 32 | 0 | 0 | 9 | 34 | 0 | 17 | 24 | 50 | 0 | 65 | 90 | 38 | 412 | 0 | 0 | 50 | 16 | 96 | 147 | 0 | 0 | 0 | 580 | 0 | 150 | 185 | 320 | 360 | 235 | 51 | 48 | 191 | 30 | 45 | 99 | 34 | 0 | 18 | 0 | 142 | 16 | 0 | 0 | 0 | 0 | 344 | 0 | 30 | 144 | 0 | 16 | 0 | 86 | 30 | 100 | 0 | 103 | 0 | 57 | 55 | 157 | 0 | 0 | 12 | 7179 | 901 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 601 | 34 | 0 | 0 | 654 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 191 | 0 | 3 | 0 | 355 | 0 | 0 | 0 | 52 | 50 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 277 | 128 | 220 | 0 | 446 | 485 | 0 | 5159 | 12338 | 75.49
01:00 | 0 | 17 | 8 | 0 | 0 | 220 | 0 | 33 | 363 | 0 | 346 | 0 | 0 | 34 | 0 | 145 | 15 | 17 | 17 | 0 | 0 | 148 | 0 | 0 | 17 | 330 | 138 | 0 | 0 | 34 | 5 | 7 | 0 | 545 | 15 | 32 | 0 | 0 | 2 | 0 | 0 | 17 | 24 | 24 | 0 | 64 | 91 | 38 | 374 | 0 | 0 | 50 | 16 | 100 | 148 | 0 | 0 | 0 | 580 | 0 | 150 | 128 | 225 | 360 | 235 | 51 | 20 | 168 | 30 | 17 | 98 | 34 | 0 | 19 | 0 | 138 | 16 | 0 | 0 | 0 | 0 | 344 | 0 | 30 | 143 | 0 | 16 | 0 | 86 | 30 | 100 | 0 | 103 | 0 | 57 | 55 | 156 | 0 | 0 | 12 | 6835 | 902 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 37 | 0 | 0 | 613 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 191 | 0 | 3 | 0 | 380 | 0 | 0 | 0 | 52 | 50 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 277 | 128 | 220 | 0 | 357 | 440 | 0 | 5017 | 11852 | 75.5
02:00 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 32 | 376 | 0 | 448 | 0 | 0 | 17 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 330 | 139 | 0 | 0 | 17 | 5 | 7 | 0 | 540 | 15 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 24 | 24 | 0 | 64 | 90 | 38 | 387 | 0 | 0 | 50 | 16 | 89 | 148 | 0 | 0 | 0 | 580 | 0 | 100 | 128 | 235 | 360 | 0 | 51 | 10 | 135 | 30 | 0 | 99 | 0 | 0 | 19 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 30 | 151 | 0 | 16 | 0 | 86 | 30 | 100 | 0 | 103 | 0 | 9 | 55 | 156 | 0 | 0 | 12 | 6339 | 901 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 593 | 35 | 0 | 0 | 620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 192 | 0 | 16 | 0 | 384 | 0 | 0 | 0 | 52 | 35 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 275 | 128 | 220 | 0 | 396 | 425 | 0 | 4942 | 11281 | 75.5
03:00 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 32 | 377 | 0 | 472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 330 | 139 | 0 | 0 | 0 | 5 | 7 | 0 | 545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 0 | 64 | 72 | 38 | 376 | 0 | 0 | 50 | 8 | 90 | 148 | 0 | 0 | 0 | 500 | 0 | 0 | 128 | 380 | 360 | 69 | 51 | 10 | 220 | 30 | 0 | 99 | 0 | 0 | 19 | 0 | 132 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 30 | 148 | 0 | 16 | 0 | 86 | 30 | 100 | 0 | 102 | 0 | 9 | 55 | 157 | 0 | 0 | 0 | 6232 | 902 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 551 | 0 | 0 | 0 | 586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 194 | 0 | 45 | 0 | 390 | 0 | 0 | 0 | 52 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 128 | 220 | 0 | 380 | 431 | 0 | 4719 | 10951 | 75.51
04:00 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 32 | 379 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 331 | 139 | 0 | 0 | 0 | 5 | 7 | 0 | 540 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 24 | 0 | 64 | 0 | 38 | 384 | 0 | 0 | 18 | 0 | 17 | 148 | 0 | 0 | 0 | 420 | 0 | 0 | 90 | 315 | 360 | 172 | 51 | 10 | 221 | 30 | 0 | 98 | 0 | 0 | 19 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 30 | 147 | 0 | 16 | 0 | 86 | 30 | 100 | 0 | 102 | 0 | 9 | 35 | 157 | 0 | 0 | 0 | 5978 | 902 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 427 | 0 | 0 | 0 | 579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 197 | 0 | 88 | 0 | 391 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 128 | 220 | 0 | 404 | 416 | 0 | 4595 | 10573 | 75.51
05:00 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 32 | 370 | 0 | 578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 331 | 139 | 0 | 0 | 0 | 5 | 7 | 0 | 515 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 38 | 371 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 421 | 0 | 0 | 16 | 260 | 360 | 215 | 51 | 10 | 210 | 30 | 0 | 98 | 0 | 0 | 19 | 0 | 124 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 30 | 141 | 0 | 16 | 0 | 86 | 30 | 100 | 0 | 103 | 0 | 9 | 35 | 157 | 0 | 0 | 0 | 5848 | 902 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 196 | 0 | 150 | 0 | 338 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 128 | 220 | 0 | 326 | 420 | 0 | 4407 | 10255 | 75.52
06:00 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 32 | 317 | 0 | 566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 332 | 139 | 0 | 1 | 0 | 5 | 7 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23 | 65 | 0 | 38 | 371 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 352 | 0 | 0 | 16 | 280 | 360 | 235 | 51 | 10 | 197 | 30 | 0 | 98 | 0 | 0 | 19 | 0 | 118 | 0 | 5 | 0 | 0 | 0 | 356 | 0 | 30 | 139 | 1 | 16 | 0 | 86 | 30 | 101 | 0 | 102 | 0 | 9 | 35 | 158 | 0 | 3.58 | 0 | 5604.81 | 902 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.49 | 370 | 0 | 0 | 0 | 552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38 | 4 | 0 | 0 | 0.05 | 165 | 0 | 192 | 0 | 150 | 0 | 330 | 0 | 0 | 0 | 52 | 0 | 1 | 0 | 0 | 0 | 0 | 0.6 | 11 | 0.04 | 0 | 143 | 128 | 220 | 0 | 315 | 366 | 0 | 4281.56 | 9886.37 | 75.52
07:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 32 | 317 | 0 | 581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 331 | 139 | 0 | 3 | 0 | 12 | 7 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 65 | 0 | 38 | 372 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 353 | 0 | 0 | 16 | 250 | 360 | 242 | 51 | 10 | 190 | 30 | 0 | 98 | 0 | 0 | 19 | 0 | 118 | 0 | 18 | 0 | 0 | 0 | 356 | 0 | 30 | 139 | 3 | 16 | 0 | 22 | 30 | 99 | 0 | 102 | 0 | 9 | 35 | 157 | 0.3 | 14.64 | 0 | 5628.11 | 902 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 365 | 0 | 0 | 0 | 558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.56 | 23 | 0 | 0 | 4.64 | 167 | 0 | 196 | 0 | 150 | 0 | 357 | 0 | 0.49 | 0 | 52 | 0 | 7 | 0 | 0 | 0 | 0 | 2 | 46 | 0.17 | 0 | 148 | 128 | 220 | 0 | 326 | 320 | 0 | 4384.86 | 10012.97 | 75.53
08:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 32 | 350 | 0 | 512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 330 | 138 | 0 | 15 | 13 | 14 | 7 | 0 | 510 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.33 | 65 | 0 | 38 | 372 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 355 | 7 | 0 | 16 | 215 | 361 | 242 | 51 | 10 | 194 | 30 | 0 | 97 | 0 | 0 | 19 | 0 | 116 | 0 | 35 | 0 | 0 | 0 | 356 | 0 | 30 | 154 | 7 | 16 | 0 | 22 | 30 | 100 | 0 | 102 | 0 | 9 | 35 | 154 | 1.1 | 26.03 | 0 | 5714.46 | 902 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 375 | 0 | 0 | 0 | 557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.04 | 32 | 0 | 0 | 29.87 | 170 | 0 | 197 | 0 | 150 | 0 | 346 | 0 | 2.67 | 0 | 52 | 0 | 17 | 0 | 0 | 0 | 0 | 3.3 | 39 | 0.18 | 0 | 148 | 128 | 220 | 0 | 322 | 305 | 0 | 4453.06 | 10167.52 | 75.53
09:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 35 | 364 | 0 | 488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 17 | 327 | 96 | 0 | 22 | 17 | 12.5 | 7 | 0 | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.55 | 66 | 0 | 38 | 372 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 352 | 11 | 0 | 16 | 225 | 361 | 239 | 51 | 10 | 195 | 27 | 0 | 97 | 0 | 0 | 19 | 0 | 114 | 0 | 53 | 0 | 0 | 0 | 344 | 0 | 30 | 153 | 8 | 16 | 0 | 22 | 30 | 100 | 0 | 102 | 0 | 9 | 45 | 153 | 1.6 | 26.91 | 0 | 5736.56 | 901 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 373 | 0 | 0 | 0 | 559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.35 | 60 | 0 | 0 | 40.87 | 171 | 0 | 190 | 0 | 150 | 0 | 358 | 0 | 3.63 | 0 | 52 | 0 | 14 | 0 | 0 | 0 | 0 | 5.6 | 114 | 0.47 | 0 | 148 | 127 | 220 | 0 | 321 | 310 | 0 | 4615.92 | 10352.48 | 75.54
10:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 40 | 361 | 0 | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 321 | 96 | 0 | 28 | 17 | 12.5 | 7 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.56 | 71 | 0 | 21 | 372 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 355 | 14 | 0 | 16 | 220 | 360 | 140 | 51 | 10 | 202 | 28 | 0 | 97 | 0 | 0 | 19 | 0 | 118 | 0 | 62 | 0 | 0 | 0 | 333 | 0 | 30 | 139 | 10 | 16 | 0 | 64 | 30 | 100 | 0 | 101 | 0 | 9 | 45 | 150 | 2 | 45.19 | 0 | 5613.25 | 902 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 396 | 0 | 0 | 0 | 566.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.02 | 89 | 0 | 0 | 49.62 | 171 | 0 | 158 | 0 | 153 | 0 | 337 | 0 | 4.5 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 6.8 | 169 | 0.59 | 0 | 148 | 125 | 220 | 0 | 320 | 315 | 0 | 4667.82 | 10281.07 | 75.55
11:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 42 | 351 | 0 | 448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 0 | 0 | 317 | 95 | 0 | 29 | 17 | 12.5 | 7 | 0 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.59 | 71 | 0 | 6 | 372 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 352 | 0 | 0 | 16 | 220 | 356 | 140 | 51 | 10 | 206 | 29 | 0 | 97 | 0 | 0 | 16 | 0 | 124 | 0 | 68 | 0 | 0 | 0 | 327 | 0 | 30 | 134 | 11 | 16 | 0 | 86 | 30 | 100 | 0 | 101 | 0 | 9 | 45 | 147 | 2.1 | 48.48 | 0 | 5674.67 | 902 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 522 | 0 | 0 | 0 | 530.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.17 | 101 | 0 | 0 | 54.81 | 172 | 0 | 155 | 0 | 165 | 0 | 369 | 0 | 5.05 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 6.2 | 179 | 0.55 | 0 | 150 | 125 | 220 | 0 | 324 | 311 | 0 | 4857.32 | 10531.99 | 75.56
12:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 51 | 376 | 0 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 320 | 94 | 0 | 31 | 19 | 12.5 | 7 | 0 | 565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.58 | 70 | 0 | 0 | 393 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 352 | 16 | 0 | 16 | 280 | 355 | 140 | 51 | 10 | 206 | 29 | 0 | 95 | 0 | 0 | 19 | 0 | 126 | 0 | 69 | 0 | 0 | 0 | 327 | 0 | 30 | 148 | 11 | 0 | 0 | 83 | 30 | 100 | 0 | 101 | 0 | 9 | 75 | 146 | 2.1 | 50.55 | 0 | 6007.73 | 902 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 629 | 0 | 0 | 0 | 548.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.05 | 105 | 0 | 0 | 56.42 | 173 | 0 | 173 | 0 | 176 | 0 | 406 | 0 | 5.08 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 6.1 | 178 | 0.31 | 0 | 150 | 124 | 220 | 0 | 385 | 310 | 0 | 5099.27 | 11107 | 75.57
13:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 53 | 396 | 0 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 316 | 93 | 0 | 31 | 41 | 12.5 | 7 | 0 | 565 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 3.64 | 70 | 0 | 2 | 445 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 675 | 16 | 0 | 95 | 335 | 355 | 140 | 51 | 17 | 206 | 31 | 0 | 93 | 0 | 0 | 19 | 0 | 130 | 0 | 65 | 0 | 0 | 0 | 327 | 0 | 30 | 150 | 11 | 16 | 0 | 83 | 30 | 100 | 0 | 100 | 0 | 9 | 80 | 145 | 2.1 | 39.18 | 0 | 6566.42 | 902 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 728 | 0 | 0 | 0 | 624.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.5 | 101 | 0 | 0 | 45.84 | 186 | 0 | 189 | 0 | 183 | 0 | 405 | 0 | 4.41 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 7.5 | 180 | 0.26 | 0 | 194 | 124 | 220 | 0 | 540 | 370 | 0 | 5552.11 | 12118.53 | 75.58
14:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 49 | 381 | 0 | 573 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 150 | 0 | 0 | 0 | 310 | 93 | 0 | 23 | 68 | 13 | 7 | 0 | 535 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 4.04 | 68 | 0 | 7 | 375 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 790 | 16 | 0 | 102 | 335 | 355 | 140 | 51 | 42 | 202 | 26 | 0 | 93 | 0 | 0 | 19 | 0 | 138 | 0 | 58 | 0 | 0 | 0 | 320 | 0 | 30 | 139 | 10 | 16 | 0 | 82 | 30 | 100 | 0 | 100 | 0 | 9 | 125 | 145 | 1.9 | 43.2 | 0 | 6587.14 | 902 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 855 | 0 | 0 | 0 | 574.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.54 | 90 | 0 | 0 | 47.76 | 188 | 0 | 162 | 0 | 174 | 0 | 360 | 0 | 4.31 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 6.7 | 161 | 0.63 | 0 | 158 | 124 | 220 | 0 | 403 | 415 | 0 | 5318.16 | 11905.3 | 75.59
15:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 40 | 365 | 0 | 451 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 150 | 0 | 0 | 0 | 312 | 132 | 0 | 22 | 68 | 13 | 7 | 0 | 420 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 2.63 | 67 | 0 | 5 | 375 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 780 | 6 | 0 | 55 | 350 | 355 | 140 | 20 | 10 | 200 | 29 | 0 | 93 | 0 | 0 | 18 | 0 | 136 | 0 | 46 | 0 | 0 | 0 | 320 | 29 | 30 | 134 | 8 | 16 | 0 | 82 | 25 | 100 | 0 | 99 | 0 | 9 | 85 | 145 | 1.2 | 38.36 | 0 | 6202.19 | 901 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 860 | 0 | 0 | 0 | 505.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.39 | 37 | 0 | 0 | 38.24 | 188 | 0 | 180 | 0 | 174 | 0 | 347 | 0 | 3.43 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 4.7 | 129 | 0.55 | 0 | 150 | 124 | 180 | 0 | 313 | 365 | 0 | 4963.75 | 11165.94 | 75.6
16:00 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 12 | 316 | 0 | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 174 | 0 | 0 | 0 | 250 | 74 | 0 | 5 | 51 | 13 | 7 | 0 | 370 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 1.03 | 69 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 683 | 7 | 0 | 16 | 250 | 300 | 140 | 20 | 10 | 196 | 10 | 0 | 70 | 0 | 0 | 15 | 0 | 94 | 0 | 30 | 0 | 0 | 0 | 244 | 29 | 30 | 124 | 5 | 16 | 0 | 42 | 25 | 100 | 0 | 99 | 0 | 9 | 65 | 145 | 0.9 | 12.6 | 0 | 5264.53 | 901 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 775 | 0 | 0 | 0 | 426.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72 | 0 | 0 | 0 | 24.23 | 173 | 0 | 147 | 0 | 135 | 0 | 330 | 0 | 1.7 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 2.3 | 45 | 0.41 | 0 | 152 | 100 | 180 | 0 | 293 | 310 | 0 | 4277.63 | 9542.16 | 75.61
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 195 | 0 | 0 | 0 | 240 | 37 | 0 | 1 | 54 | 13 | 7 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94 | 70 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 603 | 2 | 0 | 0 | 215 | 280 | 100 | 0 | 0 | 150 | 0 | 0 | 40 | 0 | 0 | 6 | 0 | 112 | 0 | 7 | 0 | 0 | 0 | 234 | 30 | 30 | 123 | 2 | 0 | 0 | 5 | 7 | 35 | 0 | 99 | 0 | 9 | 45 | 147 | 0.3 | 10.91 | 0 | 4363.15 | 635 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 751 | 0 | 0 | 0 | 430.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.77 | 2 | 0 | 0 | 0.59 | 130 | 0 | 130 | 0 | 130 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 1.5 | 19 | 0.02 | 0 | 140 | 100 | 180 | 0 | 253 | 295 | 0 | 3590.41 | 7953.56 | 75.61
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 203 | 0 | 0 | 0 | 240 | 0 | 0 | 1 | 51 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0.16 | 35 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 607 | 1 | 0 | 0 | 215 | 290 | 100 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 112 | 0 | 1 | 0 | 0 | 0 | 234 | 29 | 30 | 125 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 99 | 0 | 9 | 8 | 107 | 0 | 1.06 | 0 | 4155.22 | 251 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.21 | 750 | 0 | 0 | 0 | 426.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.54 | 4 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.6 | 4 | 0 | 0 | 140 | 100 | 180 | 0 | 254 | 300 | 0 | 3186.17 | 7341.39 | 75.63
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 139 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 51 | 6.5 | 0 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 7 | 0 | 35 | 0 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 655 | 0 | 0 | 16 | 350 | 345 | 100 | 0 | 1 | 190 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 320 | 29 | 30 | 129 | 0 | 0 | 0 | 42 | 30 | 0 | 0 | 99 | 0 | 8 | 8 | 152 | 0 | 0 | 0 | 5027.5 | 703 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 763 | 0 | 0 | 0 | 441.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 130 | 220 | 0 | 300 | 290 | 0 | 3865.77 | 8893.27 | 75.64
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 570 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 141 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 51 | 5 | 7 | 0 | 525 | 0 | 0 | 0 | 0 | 4 | 34 | 0 | 0 | 0 | 12 | 0 | 35 | 0 | 15 | 320 | 0 | 0 | 6 | 1 | 0 | 101 | 0 | 0 | 0 | 680 | 0 | 0 | 16 | 330 | 355 | 125 | 0 | 10 | 206 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 332 | 29 | 30 | 141 | 0 | 8 | 0 | 52 | 30 | 0 | 0 | 99 | 0 | 9 | 8 | 153 | 0 | 0 | 0 | 5463 | 685 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 476.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 150 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 130 | 220 | 0 | 317 | 310 | 0 | 4115.93 | 9578.93
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 143 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 51 | 12 | 7 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 12 | 0 | 35 | 0 | 18 | 365 | 0 | 0 | 6 | 4 | 0 | 101 | 0 | 0 | 0 | 700 | 0 | 0 | 80 | 355 | 355 | 235 | 3 | 12 | 210 | 25 | 0 | 0 | 0 | 0 | 5 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 332 | 30 | 30 | 142 | 0 | 16 | 0 | 85 | 30 | 0 | 0 | 100 | 0 | 8 | 8 | 154 | 0 | 0 | 0 | 5933 | 378 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773 | 0 | 0 | 0 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 161 | 0 | 390 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 130 | 220 | 0 | 350 | 325 | 0 | 4022 | 9955 | 75.65
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 139 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 63 | 12 | 7 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 12 | 0 | 35 | 0 | 22 | 355 | 0 | 0 | 6 | 8 | 0 | 146 | 0 | 0 | 0 | 701 | 0 | 0 | 147 | 335 | 360 | 240 | 41 | 32 | 201 | 33 | 0 | 0 | 0 | 0 | 18 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 332 | 29 | 30 | 149 | 0 | 16 | 0 | 86 | 30 | 0 | 0 | 100 | 0 | 45 | 35 | 153 | 0 | 0 | 0 | 6170 | 617 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 0 | 0 | 0 | 553.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 172 | 0 | 402 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257 | 130 | 220 | 0 | 425 | 385 | 0 | 4606.11 | 10776.11 | 75.66
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 137 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 68 | 12 | 7 | 0 | 520 | 0 | 0 | 0 | 0 | 2 | 34 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 37 | 358 | 0 | 0 | 0 | 8 | 0 | 147 | 0 | 0 | 0 | 700 | 0 | 0 | 95 | 300 | 360 | 200 | 51 | 44 | 196 | 33 | 0 | 0 | 0 | 0 | 18 | 0 | 132 | 0 | 0 | 0 | 0 | 0 | 320 | 29 | 30 | 154 | 0 | 16 | 0 | 86 | 30 | 0 | 0 | 101 | 0 | 45 | 35 | 154 | 0 | 0 | 0 | 6055 | 901 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 801 | 0 | 0 | 0 | 566.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 181 | 0 | 403 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 130 | 220 | 0 | 506 | 420 | 0 | 5037.63 | 11092.63 | 75.67
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 145 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 68 | 12 | 7 | 0 | 565 | 0 | 0 | 0 | 0 | 18 | 34 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 36 | 250 | 0 | 0 | 0 | 8 | 0 | 150 | 0 | 0 | 0 | 700 | 0 | 0 | 26 | 230 | 360 | 180 | 51 | 20 | 195 | 33 | 0 | 0 | 0 | 0 | 19 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 320 | 30 | 30 | 152 | 0 | 16 | 0 | 86 | 30 | 0 | 0 | 100 | 0 | 9 | 55 | 154 | 0 | 0 | 0 | 5897 | 902 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 0 | 0 | 580.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 193 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 128 | 220 | 0 | 541 | 430 | 0 | 5120.02 | 11017.02 | 75.68
Total KWH | 0 | 20160 | 8640 | 0 | 0 | 3748375 | 0 | 590681.82 | 8618400 | 0 | 12429620 | 0 | 0 | 97200 | 0 | 298833 | 19527 | 22722 | 31680 | 0 | 1402600 | 3754269 | 0 | 0 | 28091 | 7553621 | 3019000 | 0 | 195809 | 898800 | 286200 | 162360 | 0 | 11741363.64 | 42655 | 90327 | 0 | 0 | 78720 | 222574 | 0 | 40919 | 63360 | 138240 | 29160 | 1446240 | 311127 | 564480 | 8647272.73 | 0 | 0 | 208320 | 79137 | 352945 | 3143178 | 0 | 0 | 0 | 13150908 | 107595 | 292727 | 1371636 | 6818000 | 8709400 | 4124000 | 1026880 | 360960 | 4765000 | 608544 | 22080 | 1605.91 | 39840 | 0 | 417110 | 0 | 2902080 | 19152 | 521891 | 0 | 0 | 0 | 7816000 | 276000 | 729240 | 3423027.27 | 86992 | 323328 | 0 | 1521600 | 650592 | 1728000 | 0 | 2399100 | 0 | 343200 | 1231200 | 3485760 | 14850 | 369780 | 31200 | 140075885.37 | 20009455 | 8765568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 630720 | 15039999 | 94080 | 0 | 0 | 12975495 | 0 | 0 | 0 | 76896 | 92448 | 0 | 0 | 0 | 0 | 318552 | 672620 | 0 | 0 | 391696 | 3140545 | 0 | 4431755 | 0 | 3606955 | 0 | 8673090 | 0 | 34680 | 0 | 0 | 440981 | 214906 | 311251 | 0 | 0 | 0 | 53516.28 | 1266480 | 4432 | 34272 | 4670000 | 2961000 | 5337010 | 0 | 8821818 | 9217454.55 | 0 | 112287674.83 | 252363560.2

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 29-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 11107 | MW | 12:00 Hr. | Energy Generated |  |  | 252.3636 |  | MKWHr.
| Day Peak Demand |  |  | 11107 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.018 |  | MKWHr.
| Evening Peak Generation |  |  | 10776.11 | MW | 21:00 Hr. | Energy Demand |  |  | 252.3816 |  | MKWHr.
| Evening Peak Demand |  |  | 10781.11 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.4 |  | °C
| Minimum Generation of the Day |  |  | 7953.56 | MW | 17:00 Hr. | Total Gas Supplied |  |  | 1059.89 |  | MMCFD
| Maximum Generation of the Day |  |  | 12338 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.0965 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 53.3065 | 0 | 1.4257 | 0 | 0 | 0.19581 | 0 | 0 | 54.928 | Gas | 144.4859 | Gas | 523255563.0758
| Chattogram Zone |  |  | 3.7077 | 21.7982 | 1.5496 | 0 | 1.4462 | 0.13675 | 0 | 0.07872 | 28.7172 | Coal | 59.5475 | Coal | 393424957.7694
| Cumilla Zone |  |  | 28.2031 | 0 | 0.3738 | 0 | 0 | 0.52189 | 2.9021 | 0 | 32.0009 | HFO | 6.0046 | HFO | 99663386.37
| Mymensingh Zone |  |  | 3.4858 | 0 | 1.6056 | 0 | 0 | 0.38463 | 0 | 0 | 5.476 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 18.8669 | 0 | 0 | 0 | 0 | 0.086992 | 0 | 0 | 18.9539 | Hydro | 1.4462 | Hydro | 144624
| Khulna Zone |  |  | 8.7656 | 15.04 | 0.09408 | 0 | 0 | 0.63072 | 20.0095 | 0 | 44.5398 | Solar | 4.9137 | Solar | 79319297.0356
| Barishal Zone |  |  | 8.298 | 22.7093 | 0.034272 | 0 | 0 | 0.004432 | 0 | 0 | 31.046 | Import | 35.887 | Import | 189202399.4
| Rajshahi Zone |  |  | 19.8523 | 0 | 0.16934 | 0 | 0 | 1.4175 | 12.9755 | 0 | 34.4147 | Wind | 0.07872 | Wind | 1157971.2
| Rangpur Zone |  |  | 0 | 0 | 0.75223 | 0 | 0 | 1.5349 | 0 | 0 | 2.2871
| Total |  |  | 144.4859 | 59.5475 | 6.0046 | 0 | 1.4462 | 4.9137 | 35.887 | 0.07872 | 252.3636
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 523255563.0758 |  | Hydro | 144624
|  |  |  | Coal | 393424957.7694 |  | Solar | 79319297.0356
|  |  |  | HFO | 99663386.37 |  | Import | 189202399.4
|  |  |  | HSD | 0 |  | Wind | 1157971.2
[5 empty] | Total: | 128,61,68,198 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.0095 | Peak Hr Flow | 617.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 22584800 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 12.9755 | Peak Hr Flow | 553.11 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1360 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.9021 | Peak Hr Flow | 134.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2208 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 35.887 | Peak Hr Flow | 1304.11 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3199
|  |  |  | Chattogram |  | 5 |  | 1312
|  |  |  | Cumilla |  | 0 |  | 1281
|  |  |  | Mymensingh |  | 0 |  | 952
|  |  |  | Sylhet |  | 0 |  | 615
|  |  |  | Khulna |  | 0 |  | 1011
|  |  |  | Barishal |  | 0 |  | 250
|  |  |  | Rajshahi |  | 0 |  | 1040
|  |  |  | Rangpur |  | 0 |  | 818
|  |  |  | Total |  | 5 |  | 10478
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:56 | 09:55 | BIPTC S/S 10CF15 Scheduled S/D Due to For Corrective Maintenance
| 09:18 | 10:03 | Munshiganj 132/33kV S/S Transformer-2 LT Forced S/D Due to Red hot on 33KV incoming bus | [7 empty] | 40.0MW load
|  |  | to PBS 33KV feeder | [7 empty] | interrup.
| 09:32 |  | Barapukuria PS unit-1 tripped
| 09:55 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1
| 11:06 |  | Meghnaghat Summit 335 MW CCPP GT-1 tripeed
| 11:07 | 11:53 | Ishwardi-Natore 132kV Ckt-2 Scheduled S/D from Ishurdi 132/33kV end Due to Red hot
maintenance R-Phase line DS and from Natore 132/33kV end Due to ALDC
|  | 11:39 | Bogura 132/33kV S/S Transformer-3 HT is restored.
|  | 11:40 | Bogura 132/33kV S/S Transformer-3 LT is restored.
| 12:00 |  | Day Peak Generation is 11104 MW.
| 12:11 |  | SS Power Synchronized with remarks:- unit2
| 13:55 |  | Meghnaghat 450 MW CCPP GT1 was synchronized
| 13:55 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- GT-1
| 14:48 | 18:44 | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 LT Forced S/D Due to Red hot maintenance
| 14:49 | 18:42 | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 HT Forced S/D Due to Red hot maintenance
| 15:09 | 18:17 | Aminbazar 400/230/132kV S/S 132 kv Bus 02 Forced S/D Due to Red hot maintenance
| 16:00 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- ST
| 16:21 | 17:17 | Gopalganj-Madhumati 132kV Ckt-1 Tripped from Gopalganj 132/33kV end showing O/c, e/f
relays Due to D/T due to heavy storm.
| 16:29 | 21:02 | Bagerhat-Bhandaria 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing OV relay
relays Due to Bad weather,Over Voltage
| 16:38 | 18:49 | Bogura 230/132kV S/S Confidance UN-2 Tripped showing Over Voltage relays.
| 16:52 | 17:33 | Bhandaria 132/33kV S/S Transformer-1 LT Tripped showing Over current relays Due to PBS | [7 empty] | 28.0MW load
|  |  | Mathbaria 33kV Load side DS fault | [7 empty] | interrup.
| 16:52 | 17:33 | Bhandaria 132/33kV S/S Transformer-2 LT Tripped showing O/C relays Due to PBS Mathbaria | [7 empty] | 28.0MW load
|  |  | 33kV Load side DS fault | [7 empty] | interrup.
| 16:53 | 17:03 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Lockout relay, Overcurrent protection
relay relays Due to 33kV Agla feeder earth fault.
| 17:09 | 00:36 | Barishal(N)-Madaripur 132 kV Ckt-2 Tripped from Barishal 230/132kV end showing REL650
relays Due to Distance trip and from Madaripur 132/33kV end showing Siemens relays Due to
E/F Z-1 Distance:18:98kM
| 17:12 |  | Ghorasal Repowered CCPP Unit-4 Shutdown
| 17:45 | 19:36 | Siddhirganj 132/33kV S/S 120MW EGCB GT2 Tripped showing LBB Initiation,86 relays Due to
Unknown
| 17:45 | 19:28 | Siddhirganj-Siddhirganj (Orion)132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing
Gen trip,DEF,E/F,Lock out relay relays Due to DPDC'S earthing wire breaks and falls in to
the line
| 17:45 | 17:57 | Haripur-Siddirganj 132kV Ckt-1 Tripped from Haripur 230/132kV end showing Optimho: Z3,
CN, DEF Start. OC/EF: C Inst, EF Inst. relays Due to Unknown.
| 17:53 | 18:05 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Lockout relay, Overcurrent protection
relay relays Due to Agla feeder earth fault
| 18:05 | 18:19 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing Inst O/C, Difin O/C. relays Due to | [7 empty] | 6.0MW load
|  |  | Dopdapia -2 WZPDCL (33kV feeder fault) | [7 empty] | interrup.
| 18:20 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- ST
| 18:25 | 19:26 | Bogura 230/132kV S/S T-03 LT Tripped showing N/A relays.
| 18:25 | 19:26 | Bogura 230/132kV S/S T-03 HT Tripped showing Over Voltage relays.
| 18:29 | 19:38 | Chowmuhani 230/132/33kV S/S TR2-425T LT Tripped showing MCGG relays Due to Stromy weather
REB Sadar feeder fault.
| 18:31 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- GT
| 18:59 | 20:15 | Bhulta-Ghorasal 230 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end.
| 19:01 | 20:20 | Sunamganj 132/33kV S/S Tr-1 HT Tripped showing Main 1 protection FN1, Main 2 protection | [7 empty] | 20.0MW load
|  |  | FN2. relays Due to OC phase L2, OC phase L1, General trip,HV OC, Mechanical protection | [7 empty] | interrup.
etc
| 19:14 | 19:30 | Maijdee 132/33kV S/S Tr-02 LT Tripped showing 33KV Transformer-2 F51 Relay & BCU1
relays Due to 33kv mohabbatpur feeder closed and Trip. 132kv X-former Tr-2 primary
GCB413B Trip & secondary VCB 417B Trip.
| 19:14 | 19:30 | Maijdee 132/33kV S/S Tr-02 HT Tripped showing 132kv Transformer -02 F87T1 & F87T2 132KV
Transformer -02 BCU1 relays Due to 33kv mohabbatpur feeder closed and Trip. 132kv
X-former Tr-2 primary GCB 413B Trip & secondary VCB 417B Trip.
| 19:21 |  | Chandpur 132/33kV S/S 412T (T-2) LT Tripped showing O/C relay relays.
| 19:21 |  | Chandpur 132/33kV S/S 412T (T-2) HT Tripped showing O/C relay relays.
|  | 20:30 | Chandpur 132/33kV S/S 422T(T-5) HT is restored.
|  | 20:30 | Chandpur 132/33kV S/S 422T(T-5) LT is restored.
| 21:27 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:-
| 22:30 | 23:15 | Chowmuhani 230/132/33kV S/S TR1 Forced S/D Due to 33kV maijdee Feeder BUS DS redhot | [7 empty] | 30.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 23:38 | 02:40 | Chowmuhani 230/132/33kV S/S TR3 Forced S/D Due to 33kv Bus loop Red-hot maintenance. | [7 empty] | 25.0MW load
interrup.
| 06:00 |  | Minimum Generation is 9520 MW.
| 07:33 |  | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D | [7 empty] | 6.0MW load
interrup.
| 07:33 |  | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Red Hot Maintenance | [7 empty] | 6.0MW load
interrup.
| 07:36 | 07:42 | Satkhira 132/33kV S/S Transformer-1 (T-1) LT Tripped showing Over current relays Due to | [7 empty] | 36.0MW load
|  |  | Due to kalaroa 33 kV feeder fault | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 29-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 3748375 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 590681.82 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 384 | 8618400 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 1402600 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 139 | 3754269 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 19527 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 3019000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7553621 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 22722 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 28091 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 12 | 286200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 7 | 162360 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 8640 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 298833 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 97200 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 20160 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 31680 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 195809 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 520 | 11741363.64 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 625 | 12429620 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 63 | 898800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2305 | 54927952.46
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 79137 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 107595 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 208320 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 35 | 1446240 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 146 | 3143178 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 352945 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 222574 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 63360 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 22 | 564480 | plant availability zero
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 29160 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 90327 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 40919 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 311127 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 138240 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 42655 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 701 | 13150908 | U2 outage added
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 78720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 355 | 8647272.73 | U1 under maintenance
Chattogram Area Total |  |  |  |  | 4898.863 | 1319 | 28717157.73
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 201 | 4765000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 360 | 8709400 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 240 | 4124000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 335 | 6818000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 33 | 608544 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 32 | 360960 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 147 | 1371636 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 41 | 1026880 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 292727 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 1605.91 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 39840 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 134 | 2902080 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 19152 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 18 | 417110 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 22080 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 521891 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1541 | 32000905.91
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 153 | 3485760 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14850 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 35 | 1231200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 45 | 343200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 369780 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 31200 | From 17:00 to 20:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 233 | 5475990
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 86992 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 29 | 276000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 729240 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 149 | 3423027.27 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 1728000 | plant availability zero
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 650592 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1521600 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2399100 | plant availability zero
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 323328 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Plant shutdown as per NLDC requirement.
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 332 | 7816000 | plant availability zero
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 772 | 18953879.27
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 617 | 20009455 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 388 | 8765568 | -
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 94080 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | FGMO
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 630720 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 810 | 15039999 | Unit1 Under Maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1815 | 44539822
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 425 | 8821818 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 34272 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 2961000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 385 | 9217454.55 | plant availability zero
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5337010 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 257 | 4670000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4432 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1417 | 31045986.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 318552 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 3140545 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 177 | 4431755 | Plant is on standby as per NLDC instruction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 172 | 3606955 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 402 | 8673090 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 92448 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 76896 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 34680 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 553.11 | 12975495 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 391696 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 672620 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1304.11 | 34414732
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Plant availability zero, U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 311251 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 53516.28 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 440981 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 214906 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1266480 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 70 | 2287134.28
Eastern Grid Total |  |  |  |  | 17418.042 | 6170 | 140075885.37
Western Grid Total |  |  |  |  | 11852.195 | 4606.11 | 112287674.83
National Grid Total |  |  |  |  | 29270.237 | 10776.11 | 252363560.2
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 29-05-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7353.72 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3118.6 | MW
i) Dhaka area |  |  | 3199.12 |  | MW | i) Khulna area |  |  |  | 1011 | MW
ii) Chattogram area |  |  | 1306.6 |  | MW | ii) Barishal area |  |  |  | 249.5 | MW
iii) Cumilla area |  |  | 1281 |  | MW | iii) Rajshahi area |  |  |  | 1040.1 | MW
iv) Mymensingh area |  |  | 952 |  | MW | iv) Rangpur area |  |  |  | 818 | MW
v) Sylhet area |  |  | 615 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10472.32 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 74 | 00:00 | 133 | Natore | 142 | 00:00
2 | AKSML | 11.3 | 11:00 | 68 | Hathazari | 96 | 00:00 | 134 | Nawabganj | 62.2 | 13:00
3 | Aftabnagar | 30 | 00:00 | 69 | Hatirjheel | 21 | 15:00 | 135 | Netrakona | 147 | 22:00
4 | Agargaon | 73 | 13:00 | 70 | Ishurdi | 64 | 00:00 | 136 | New | 48.7 | 13:00
5 | Agrabad | 54 | 19:30 | 71 | Jaldhaka | 82 | 00:00 | 137 | Niamatpur | 80 | 00:00
6 | Amnura | 29 | 00:00 | 72 | Jamalpur | 108 | 20:00 | 138 | Noapara | 28 | 13:00
7 | Ashuganj | 76 | 00:00 | 73 | Jashore | 136 | 14:00 | 139 | PHP | 5 | 09:00
8 | BSRM | 197 | 11:00 | 74 | Jhenaidah | 107 | 00:00 | 140 | Pabna | 91 | 00:00
9 | Bagerhat | 87 | 00:00 | 75 | Joydebpur | 78 | 21:00 | 141 | Palashbari | 106 | 20:00
10 | Bajitpur | 90 | 19:00 | 76 | Joypurhat | 56 | 21:00 | 142 | Panchagarh | 47 | 00:00
11 | Bakerganj | 17 | 01:00 | 77 | Juldah | 12 | 19:00 | 143 | Patiya | 14 | 23:00
12 | Bakulia | 76 | 00:00 | 78 | KSRM | 6 | 02:00 | 144 | Patuakhali | 87.6 | 00:00
13 | Banani | 26 | 13:00 | 79 | Kabirpur | 80 | 19:30 | 145 | Payra | 40 | 01:00
14 | Bangabhaban | 3 | 00:00 | 80 | Kachua | 108 | 00:00 | 146 | Postogola | 38 | 00:00
15 | Barapukuria | 57 | 00:00 | 81 | Kaliganj | 24 | 00:00 | 147 | Pubail | 19 | 13:00
16 | Barguna | 26 | 00:00 | 82 | Kallyanpur | 87 | 00:00 | 148 | Purbachal | 24 | 13:00
17 | Barishal | 101 | 00:00 | 83 | Kalurghat | 28 | 00:00 | 149 | Purbasadipur | 109 | 13:00
18 | Barishal-230 | 88 | 00:00 | 84 | Kamrangirchar | 39 | 00:00 | 150 | Rahanpur | 41 | 01:00
19 | Baroaulia | 56 | 19:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 1 | 01:00
20 | Baroirhat | 76 | 00:00 | 86 | Kasba | 39 | 00:00 | 152 | Rajbari | 83 | 00:00
21 | Bashundhara | 128 | 13:00 | 87 | Kazla | 69 | 13:00 | 153 | Rajendrapur | 91 | 13:00
22 | BashundharaCement | 1 | 21:00 | 88 | Keranigonj | 66 | 13:00 | 154 | Rajshahi | 106 | 00:00
23 | Beanibazar | 84 | 19:00 | 89 | Khagrachori | 36 | 19:00 | 155 | Rajshahi-230 | 80 | 13:00
24 | Benapole | 72 | 13:00 | 90 | Khulna | 57 | 13:00 | 156 | Ramganj | 120 | 01:00
25 | Bhaluka | 105 | 00:00 | 91 | Khulshi | 148 | 19:00 | 157 | Rampur | 42 | 00:00
26 | Bhandaria | 67 | 00:00 | 92 | Kishoreganj | 136 | 23:00 | 158 | Rangamati | 17 | 19:30
27 | Bhangura | 38 | 01:00 | 93 | Kodda | 129 | 19:30 | 159 | Rangpur | 121 | 13:00
28 | Bheramara(GK) | 66 | 00:00 | 94 | Kulaura | 54 | 19:00 | 160 | Ruppur | 2.6 | 10:00
29 | Bhulta | 108 | 22:00 | 95 | Kurigram | 66 | 20:00 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 54 | 00:00 | 96 | Kushtia | 122 | 00:00 | 162 | Saidpur | 81 | 00:00
31 | Bogura | 137 | 22:00 | 97 | Laksam | 34 | 01:00 | 163 | Santhia | 36 | 00:00
32 | Borhanuddin | 100 | 01:00 | 98 | Lakshmipur | 43 | 00:00 | 164 | Satkhira | 139 | 13:00
33 | Brahmanbaria | 150 | 21:00 | 99 | Lalbag | 26 | 13:00 | 165 | Satmasjid | 68 | 14:00
34 | Cantonment | 88 | 13:00 | 100 | Lalmonirhat | 60 | 19:30 | 166 | Savar | 84 | 00:00
35 | Chandina | 26 | 19:30 | 101 | MI_Cement | 0.6 | 08:00 | 167 | SevenRings | 0.84 | 15:00
36 | Chandpur | 88 | 00:00 | 102 | Madanganj | 24 | 00:00 | 168 | ShahCement | 3 | 00:00
37 | Chandraghona | 37 | 19:00 | 103 | Madaripur | 119 | 13:00 | 169 | Shahjadpur | 78 | 00:00
38 | Chapai | 66 | 00:00 | 104 | Madartek | 62 | 13:00 | 170 | Shahjibazar | 123 | 21:00
39 | Charsaidpur | 9 | 16:00 | 105 | Madunaghat | 57 | 20:00 | 171 | Shahmirpur | 45 | 00:00
40 | Chauddagram | 77 | 00:00 | 106 | Magura | 68 | 00:00 | 172 | Shariatpur | 89 | 03:00
41 | Chhatak | 38 | 21:00 | 107 | Mahasthangarh | 82 | 00:00 | 173 | Sherpur | 126 | 14:00
42 | Chowmuhani | 167 | 01:00 | 108 | Maijdee | 46 | 00:00 | 174 | Shikalbaha | 25 | 21:00
43 | Chuadanga | 121 | 13:00 | 109 | Manikganj | 98 | 00:00 | 175 | Shitalakhya | 50.3 | 13:00
44 | Coxsbazar | 143 | 13:00 | 110 | Maniknagar | 46 | 13:00 | 176 | Sholosohor | 37 | 19:00
45 | Cumilla(N) | 118 | 00:00 | 111 | Matarbari | 59 | 19:00 | 177 | Shomvuganj | 16 | 16:00
46 | Cumilla(S) | 141 | 00:00 | 112 | Matuail | 36 | 00:00 | 178 | Shyampur | 44 | 13:00
47 | Daganbhuiyan | 35 | 00:00 | 113 | Metrorail_Motijheel | 17 | 17:00 | 179 | Siddhirganj | 71 | 14:00
48 | Daudkandi | 122 | 00:00 | 114 | Metrorail_Uttara | 9 | 14:00 | 180 | Sirajganj | 100 | 00:00
49 | DhakaUniversity | 26 | 15:00 | 115 | Millgate | 36 | 22:00 | 181 | Sonargaon | 63 | 19:00
50 | Dhamrai | 62 | 22:00 | 116 | Mirpur | 98.5 | 13:00 | 182 | Sreemongol | 81 | 21:00
51 | Dhanmondi | 43.8 | 13:00 | 117 | Mirsorai | 9 | 00:00 | 183 | Sreepur | 59 | 20:00
52 | Dohazari | 116 | 19:00 | 118 | Mirzapur | 40 | 13:00 | 184 | Srinagar | 52 | 13:00
53 | Faridpur | 160 | 00:00 | 119 | Mithapukur | 60 | 22:00 | 185 | Sunamganj | 60 | 23:00
54 | Fatullah | 42 | 00:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 63 | 19:30
55 | Fenchuganj | 44 | 19:00 | 121 | Mogbazar | 49.4 | 00:00 | 187 | Sylhet-132 | 94 | 20:00
56 | Feni | 119 | 00:00 | 122 | Mongla | 23 | 01:00 | 188 | TK | 29 | 00:00
57 | GPH | 1 | 00:00 | 123 | Motijheel | 26 | 13:00 | 189 | Tangail | 142 | 00:00
58 | Ghatail | 89 | 00:00 | 124 | Muktagacha | 33 | 22:00 | 190 | Taraganj | 19 | 19:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 112 | 13:00 | 191 | Tasnim | 6 | 15:00
60 | Ghorashal-230 | 61 | 00:00 | 126 | Muradnagar | 54 | 22:00 | 192 | Thakurgaon | 95 | 00:00
61 | Goalpara | 42 | 13:00 | 127 | Mymensingh | 153 | 13:00 | 193 | Tongi | 64 | 22:00
62 | Gollamari | 86 | 13:00 | 128 | Nabinagar | 64 | 13:00 | 194 | Ullahpara | 36 | 13:00
63 | Gopalganj | 109 | 00:00 | 129 | Naogaon | 124 | 00:00 | 195 | Ullon | 48 | 00:00
64 | Gulshan | 64 | 14:00 | 130 | Narail | 51 | 12:00 | 196 | Uttara | 57 | 12:00
65 | Halishahar | 57.5 | 22:00 | 131 | Narinda | 37 | 13:00 | 197 | UttaraNew | 37 | 00:00
66 | HaripurSBU | 47 | 17:00 | 132 | Narshingdi | 140 | 21:00 | 198 | Zigatola | 64 | 14:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 29-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 12338 | 8 |  | 12346.36
1:00 | 11852 | 0 |  | 11852
2:00 | 11281 | 0 |  | 11281
3:00 | 10951 | 0 |  | 10951
4:00 | 10573 | 0 |  | 10573
5:00 | 10255 | 0 |  | 10255
6:00 | 9886.37 | 0 |  | 9886.37
7:00 | 10012.97 | 0 |  | 10012.97
8:00 | 10167.52 | 0 |  | 10167.52
9:00 | 10352.48 | 0 |  | 10352.48
10:00 | 10281.07 | 0 |  | 10281.07
11:00 | 10531.99 | 0 |  | 10531.99
12:00 | 11107 | 0 |  | 11107
13:00 | 12118.53 | 0 |  | 12118.53
14:00 | 11905.3 | 5 |  | 11910.3
15:00 | 11165.94 | 0 |  | 11165.94
16:00 | 9542.16 | 0 |  | 9542.16
17:00 | 7953.56 | 0 |  | 7953.56
18:00 | 7341.39 | 0 |  | 7341.39
19:00 | 8893.27 | 0 |  | 8893.27
19:30 | 9578.93 | 0 |  | 9578.93
20:00 | 9955 | 0 |  | 9955
21:00 | 10776.11 | 5 |  | 10781.11
22:00 | 11092.63 | 0 |  | 11092.63
23:00 | 11017.02 | 0 |  | 11017.02
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 29-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7179 | 5159 | 12338 | DAILY GENERATION CURVE
00:30 | 7007 | 5088 | 12095
01:00 | 6835 | 5017 | 11852 | 29-05-2026
01:30 | 6587 | 4979.5 | 11566.5
02:00 | 6339 | 4942 | 11281
02:30 | 6285.5 | 4830.5 | 11116
03:00 | 6232 | 4719 | 10951
03:30 | 6105 | 4657 | 10762
04:00 | 5978 | 4595 | 10573
04:30 | 5913 | 4501 | 10414
05:00 | 5848 | 4407 | 10255
05:30 | 5726.405 | 4344.28 | 10070.685
06:00 | 5604.81 | 4281.56 | 9886.37
06:30 | 5616.46 | 4333.21 | 9949.67
07:00 | 5628.11 | 4384.86 | 10012.97
07:30 | 5671.285 | 4418.96 | 10090.245
08:00 | 5714.46 | 4453.06 | 10167.52
08:30 | 5725.51 | 4534.49 | 10260
09:00 | 5736.56 | 4615.92 | 10352.48
09:30 | 5674.905 | 4641.87 | 10316.775
10:00 | 5613.25 | 4667.82 | 10281.07
10:30 | 5643.96 | 4762.57 | 10406.53
11:00 | 5674.67 | 4857.32 | 10531.99
11:30 | 5841.2 | 4978.295 | 10819.495
12:00 | 6007.73 | 5099.27 | 11107
12:30 | 6287.075 | 5325.69 | 11612.765
13:00 | 6566.42 | 5552.11 | 12118.53
13:30 | 6576.78 | 5435.135 | 12011.915
14:00 | 6587.14 | 5318.16 | 11905.3
14:30 | 6394.665 | 5140.955 | 11535.62
15:00 | 6202.19 | 4963.75 | 11165.94
15:30 | 5733.36 | 4620.69 | 10354.05
16:00 | 5264.53 | 4277.63 | 9542.16
16:30 | 4813.84 | 3934.02 | 8747.86
17:00 | 4363.15 | 3590.41 | 7953.56
17:30 | 4259.185 | 3388.29 | 7647.475
18:00 | 4155.22 | 3186.17 | 7341.39
18:30 | 4591.36 | 3525.97 | 8117.33
19:00 | 5027.5 | 3865.77 | 8893.27
19:30 | 5463 | 4115.93 | 9578.93
20:00 | 5933 | 4022 | 9955
20:30 | 6051.5 | 4314.055 | 10365.555 |  | Executive Engineer
21:00 | 6170 | 4606.11 | 10776.11 |  | Network Operation Division
21:30 | 6112.5 | 4821.87 | 10934.37
22:00 | 6055 | 5037.63 | 11092.63
22:30 | 5976 | 5078.825 | 11054.825
23:00 | 5897 | 5120.02 | 11017.02

## En-Curve
QF-LDC-12
Date | 29-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4437 | 1856 | 901 | 0 | 142 | 654 | 65 | 2853 | 0 | 126 | 1295 | 0 | 0 | 9 | 8 | DAILY ENERGY CURVE
00:30 | 4386 | 1830.5 | 901.5 | 0 | 140 | 633.5 | 64.5 | 2766.5 | 0 | 92.5 | 1274.5 | 0 | 0 | 5.5 | 4 | 29-05-2026
01:00 | 4335 | 1805 | 902 | 0 | 138 | 613 | 64 | 2680 | 0 | 59 | 1254 | 0 | 0 | 2 | 0
01:30 | 4224 | 1851 | 901.5 | 0 | 136 | 616.5 | 64 | 2694 | 0 | 38 | 1040.5 | 0 | 0 | 1 | 0 | Energy Generated | 252.3636 |  | MKWHr
02:00 | 4113 | 1897 | 901 | 0 | 134 | 620 | 64 | 2708 | 0 | 17 | 827 | 0 | 0 | 0 | 0 | Energy not Served | 0.018 |  | MKWHr
02:30 | 4280 | 1911 | 901.5 | 0 | 133 | 603 | 64 | 2617 | 0 | 8.5 | 598 | 0 | 0 | 0 | 0 | Total Energy Requirement | 252.3816 |  | MKWHr
03:00 | 4447 | 1925 | 902 | 0 | 132 | 586 | 64 | 2526 | 0 | 0 | 369 | 0 | 0 | 0 | 0
03:30 | 4495 | 1916.5 | 902 | 0 | 130 | 582.5 | 64 | 2431.5 | 0 | 0 | 236 | 0 | 0 | 4.5 | 0
04:00 | 4543 | 1908 | 902 | 0 | 128 | 579 | 64 | 2337 | 0 | 0 | 103 | 0 | 0 | 9 | 0
04:30 | 4534 | 1895 | 902 | 0 | 126 | 570 | 64.5 | 2242.5 | 0 | 0 | 73.5 | 0 | 0 | 6.5 | 0
05:00 | 4525 | 1882 | 902 | 0 | 124 | 561 | 65 | 2148 | 0 | 0 | 44 | 0 | 0 | 4 | 0
05:30 | 4499 | 1806.5 | 902 | 0 | 121 | 556.5 | 65 | 2058.5 | 16.185 | 0 | 44 | 0 | 0 | 2 | 0
06:00 | 4473 | 1731 | 902 | 0 | 118 | 552 | 65 | 1969 | 32.37 | 0 | 44 | 0 | 0 | 0 | 0
06:30 | 4481 | 1739 | 902 | 0 | 118 | 555 | 65 | 1952.5 | 93.17 | 0 | 44 | 0 | 0 | 0 | 0
07:00 | 4489 | 1747 | 902 | 0 | 118 | 558 | 65 | 1936 | 153.97 | 0 | 44 | 0 | 0 | 0 | 0
07:30 | 4485.5 | 1758 | 902 | 0 | 117 | 557.5 | 65 | 1932.5 | 222.245 | 6.5 | 44 | 0 | 0 | 0 | 0
08:00 | 4482 | 1769 | 902 | 0 | 116 | 557 | 65 | 1929 | 290.52 | 13 | 44 | 0 | 0 | 0 | 0
08:30 | 4464.5 | 1770.75 | 901.5 | 0 | 115 | 558 | 65.5 | 1928.5 | 383.75 | 15 | 57.5 | 0 | 0 | 0 | 0
09:00 | 4447 | 1772.5 | 901 | 0 | 114 | 559 | 66 | 1928 | 476.98 | 17 | 71 | 0 | 0 | 0 | 0
09:30 | 4360 | 1755.5 | 901.5 | 0 | 116 | 562.645 | 68.5 | 1917 | 556.13 | 17 | 62.5 | 0 | 0 | 0 | 0
10:00 | 4273 | 1738.5 | 902 | 0 | 118 | 566.29 | 71 | 1906 | 635.28 | 17 | 54 | 0 | 0 | 0 | 0
10:30 | 4281 | 1781 | 902 | 0 | 121 | 548.415 | 71 | 1968.5 | 662.615 | 17 | 54 | 0 | 0 | 0 | 0
11:00 | 4289 | 1823.5 | 902 | 0 | 124 | 530.54 | 71 | 2031 | 689.95 | 17 | 54 | 0 | 0 | 0 | 0
11:30 | 4364 | 1911 | 902 | 0 | 125 | 539.425 | 70.5 | 2125 | 695.57 | 18 | 69 | 0 | 0 | 0 | 0
12:00 | 4439 | 1998.5 | 902 | 0 | 126 | 548.31 | 70 | 2219 | 701.19 | 19 | 84 | 0 | 0 | 0 | 0
12:30 | 4490 | 2045 | 902 | 0 | 128 | 586.455 | 70 | 2585.5 | 685.81 | 30 | 86.5 | 0 | 0 | 3.5 | 0
13:00 | 4541 | 2091.5 | 902 | 0 | 130 | 624.6 | 70 | 2952 | 670.43 | 41 | 89 | 0 | 0 | 7 | 0
13:30 | 4483 | 2055.75 | 902 | 0 | 134 | 599.41 | 69 | 2974 | 612.755 | 54.5 | 119 | 0 | 0 | 8.5 | 2.5
14:00 | 4425 | 2020 | 902 | 0 | 138 | 574.22 | 68 | 2996 | 555.08 | 68 | 149 | 0 | 0 | 10 | 5
14:30 | 4458.5 | 1818 | 901.5 | 0 | 137 | 539.83 | 67.5 | 2919.5 | 486.29 | 68 | 130 | 0 | 0 | 9.5 | 2.5
15:00 | 4492 | 1616 | 901 | 0 | 136 | 505.44 | 67 | 2843 | 417.5 | 68 | 111 | 0 | 0 | 9 | 0
15:30 | 4099 | 1526.5 | 901 | 0 | 115 | 465.855 | 68 | 2714 | 302.195 | 59.5 | 92.5 | 0 | 0 | 10.5 | 0
16:00 | 3706 | 1437 | 901 | 0 | 94 | 426.27 | 69 | 2585 | 186.89 | 51 | 74 | 0 | 0 | 12 | 0
16:30 | 3289.5 | 1350 | 768 | 0 | 103 | 428.4 | 69.5 | 2493.5 | 123.46 | 52.5 | 64 | 0 | 0 | 6 | 0
17:00 | 2873 | 1263 | 635 | 0 | 112 | 430.53 | 70 | 2402 | 60.03 | 54 | 54 | 0 | 0 | 0 | 0
17:30 | 2769 | 1337 | 443 | 0 | 112 | 428.675 | 52.5 | 2376.5 | 39.3 | 52.5 | 35.5 | 0 | 0 | 1.5 | 0
18:00 | 2665 | 1411 | 251 | 0 | 112 | 426.82 | 35 | 2351 | 18.57 | 51 | 17 | 0 | 0 | 3 | 0
18:30 | 3036.5 | 1524.75 | 477 | 0 | 93 | 434.295 | 35 | 2418 | 9.285 | 68 | 20 | 0 | 0 | 1.5 | 0
19:00 | 3408 | 1638.5 | 703 | 0 | 74 | 441.77 | 35 | 2485 | 0 | 85 | 23 | 0 | 0 | 0 | 0
19:30 | 3647 | 1935 | 685 | 0 | 110 | 476.93 | 35 | 2565 | 0 | 85 | 36 | 0 | 0 | 4 | 0
20:00 | 3861 | 2151 | 378 | 0 | 120 | 515 | 35 | 2732 | 0 | 85 | 78 | 0 | 0 | 0 | 0
20:30 | 3916.5 | 2205 | 497.5 | 0 | 127 | 534.055 | 35 | 2832.5 | 0 | 91 | 127 | 0 | 0 | 0 | 2.5
21:00 | 3972 | 2259 | 617 | 0 | 134 | 553.11 | 35 | 2933 | 0 | 97 | 176 | 0 | 0 | 0 | 5
21:30 | 3930 | 2252.5 | 759 | 0 | 133 | 559.87 | 35 | 2997.5 | 0 | 99.5 | 167 | 0 | 0 | 1 | 2.5
22:00 | 3888 | 2246 | 901 | 0 | 132 | 566.63 | 35 | 3062 | 0 | 102 | 158 | 0 | 0 | 2 | 0
22:30 | 3855 | 2243.5 | 901.5 | 0 | 136 | 573.325 | 52 | 3031.5 | 0 | 102 | 150 | 0 | 0 | 10 | 0
23:00 | 3822 | 2241 | 902 | 0 | 140 | 580.02 | 69 | 3001 | 0 | 102 | 142 | 0 | 0 | 18 | 0
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 29-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 4 | -48 | 130 | 48 | 386 | -140 | Ishurdi-Ghorashal Ckt-1 | Export | 1783127.27
1:00 | 11 | -47 | 152 | 54 | 312 | -136
2:00 | 21 | -41 | 162 | 58 | 394 | -106 |  | Import | 0
3:00 | 25 | -40 | 230 | 88 | 298 | -110
4:00 | 38 | -39 | 264 | 80 | 342 | -92 | Ishurdi-Ghorashal Ckt-2 | Export | 1672.73
5:00 | 43 | -39 | 280 | 78 | 264 | -80
6:00 | 47 | -39 | 268 | 62 | 246 | -74 |  | Import | 0
7:00 | 48 | -38 | 296 | 72 | 248 | -70
8:00 | 60 | -37 | 308 | 80 | 316 | -66 | Sirajganj-Sreepur Ckt-1 | Export | 1998000
9:00 | 80 | -36 | 350 | 100 | 454 | -44
10:00 | 90 | -36 | 380 | 98 | 552 | -14 |  | Import | 0
11:00 | 101 | -36 | 416 | 104 | 672 | -24
12:00 | 88 | -37 | 368 | 124 | 648 | -12 | Sirajganj-Sreepur Ckt-2 | Export | 2002000
13:00 | 73 | -39 | 368 | 124 | 830 | -14
14:00 | 66 | -36 | 328 | 100 | 664 | 2 |  | Import | 0
15:00 | 106 | -25 | 392 | 106 | 770 | 28
16:00 | 177 | -17 | 524 | 126 | 1144 | 98 | Gopalganj-Aminbazar Ckt-1 | Export | 8390000
17:00 | 182 | -4 | 596 | 170 | 1430 | 144
18:00 | 91 | -15 | 420 | 108 | 1240 | 98 |  | Import | 0
18:30 | 94 | -24 | 372 | 80 | 1142 | 66
19:00 | 86 | -25 | 286 | 88 | 1046 | 68 | Gopalganj-Aminbazar Ckt-2 | Export | 8410000
19:30 | 55 | -21 | 242 | 84 | 872 | 54
20:00 | 26 | -19 | 216 | 94 | 912 | 62 |  | Import | 0
21:00 | 58 | -34 | 272 | 92 | 1030 | 54
22:00 | 92 | -39 | 334 | 104 | 1078 | 26 |  | Total Export | 22584800
23:00 | 95 | -40 | 370 | 116 | 1108 | 12 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 29-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 409 | 16:00 | 396 | 12:00 | Madunaghat | 407 | 00:00 | 394 | 14:00
Amtali | 421 | 18:00 | 411 | 13:00 | Meghnaghat | 411 | 18:00 | 399 | 13:00
Ashuganj | 415 | 6:00 | 401 | 0:00 | Payra | 422 | 18:00 | 412 | 01:00
Bhulta | 410 | 18:00 | 397 | 13:00 | Rahanpur | 418 | 17:00 | 392 | 13:00
Bibiana | 411 | 06:00 | 401 | 23:00 | Rampal | 412 | 18:00 | 393 | 13:00
BIPTC | 408 | 20:00 | 392 | 00:00
Bogura | 410 | 17:00 | 382 | 13:00
Gopalganj | 415 | 18:00 | 397 | 13:00
Kaliakoir | 409 | 18:00 | 394 | 13:00
Korerhat | 413 | 19:30 | 397 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 238 | 18:00 | 229 | 13:00 | Jhenaidah | 244 | 17:00 | 219 | 13:00
AKSML | 236.3 | 18:00 | 221.9 | 13:00 | Kachua | 237 | 18:30 | 220 | 13:00
Aminbazar | 238 | 16:00 | 229 | 12:00 | Kaliakoir | 236 | 18:00 | 227 | 13:00
Ashuganj | 236 | 00:00 | 227 | 23:00 | Keranigonj | 237 | 18:00 | 228 | 13:00
Ashuganj-400 | 236 | 00:00 | 227 | 23:00 | Khulna(S) | 243 | 17:00 | 222 | 13:00
Baghabari | 243 | 18:00 | 229 | 23:00 | Korerhat | 236 | 19:30 | 222 | 13:00
Barapukuria | 232 | 17:00 | 208 | 19:30 | Madunaghat | 235 | 18:00 | 225 | 12:00
Barapukuria-230 | 232 | 17:00 | 208 | 19:30 | Madunaghat-400 | 235 | 20:00 | 225 | 13:00
Barishal | 242 | 18:00 | 227 | 00:00 | Maniknagar | 238 | 18:00 | 230 | 13:00
Bheramara | 240 | 18:00 | 223 | 23:00 | Meghnaghat | 245 | 18:00 | 238 | 15:00
Bhulta | 238 | 18:00 | 230 | 13:00 | Meghnaghat-400 | 239 | 18:00 | 231 | 13:00
Bibiana | 238 | 03:00 | 232 | 13:00 | Mirsorai | 236 | 18:30 | 227 | 13:00
BIPTC | 244 | 13:00 | 224 | 23:00 | Naogaon | 229 | 16:00 | 206 | 23:00
Bogura | 249 | 17:00 | 231 | 13:00 | Purbasadipur | 232 | 17:00 | 204 | 13:00
Bogura-400 | 249 | 17:00 | 230 | 13:00 | Rajshahi | 241 | 17:00 | 220 | 23:00
Borhanuddin | 242 | 18:00 | 230 | 00:00 | Rampal | 240 | 18:00 | 223 | 00:00
BSRM | 235 | 18:30 | 223 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 237 | 19:00 | 225 | 10:00 | Rampura | 238 | 18:30 | 229 | 13:00
Cumilla(N) | 235 | 18:00 | 227 | 14:00 | Shikalbaha | 232 | 17:00 | 221 | 13:00
Faridpur | 243 | 18:00 | 226 | 00:00 | Shyampur | 238 | 18:00 | 229 | 13:00
Fenchuganj | 239 | 09:00 | 234 | 04:00 | Siddhirganj | 240 | 18:00 | 233 | 23:00
Feni | 235 | 19:00 | 222 | 13:00 | Sirajgonj | 245 | 17:00 | 235 | 23:00
Ghorashal | 240 | 08:00 | 235 | 11:00 | Sreepur | 234 | 18:00 | 223 | 13:00
Ghorashal-230 | 234 | 01:00 | 227 | 13:00 | Tongi | 236 | 04:00 | 227 | 22:00
Gopalganj | 241 | 18:00 | 228 | 00:00
GPH | 235 | 18:30 | 228 | 05:00
Haripur | 239 | 18:00 | 231 | 13:00
Hasnabad | 237 | 18:00 | 230 | 13:00
Hathazari | 233 | 19:00 | 223 | 12:00
Ishurdi | 245 | 17:00 | 227 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 17:00 | 129 | 13:00 | Madunaghat | 136 | 18:00 | 128 | 13:00
Agargaon | 134 | 18:00 | 128 | 13:00 | Magura | 138 | 16:00 | 120 | 00:00
Agrabad | 134 | 00:00 | 128 | 12:00 | Mahasthangarh | 142 | 17:00 | 126 | 23:00
AKS | 132 | 18:30 | 127 | 12:00 | Maijdee | 134 | 18:30 | 122 | 13:00
Aminbazar | 137 | 16:00 | 133 | 22:00 | Manikganj | 134 | 17:00 | 127 | 22:00
Amnura | 141 | 17:00 | 127 | 00:00 | Maniknagar | 134 | 03:00 | 130 | 13:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 117 | 16:00 | 105 | 13:00
Ashuganj-230 | 140 | 06:00 | 135 | 13:00 | Matuail | 137 | 18:00 | 132 | 13:00
Bagerhat | 140 | 17:00 | 117 | 13:00 | Metrorail_Motijheel | 134 | 03:00 | 130 | 13:00
Bajitpur | 132 | 18:00 | 122 | 23:00 | Metrorail_Uttara | 133 | 10:00 | 128 | 23:00
Bakerganj | 140 | 18:00 | 129 | 00:00 | Millgate | 133 | 00:00 | 128 | 13:00
Bakulia | 134 | 18:00 | 125 | 13:00 | Mirpur | 136 | 06:00 | 131 | 13:00
Banani | 134 | 05:00 | 129 | 13:00 | Mirzapur | 137 | 18:00 | 125 | 23:00
Bangabhaban | 133 | 18:00 | 129 | 13:00 | Mithapukur | 140 | 18:00 | 123 | 23:00
Barapukuria | 140 | 17:00 | 124 | 19:30 | MI_Cement | 138 | 18:00 | 131 | 13:00
Barguna | 142 | 18:00 | 127 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 142 | 18:00 | 129 | 00:00 | Mogbazar | 135 | 00:00 | 131 | 14:00
Barishal-230 | 141 | 18:00 | 129 | 00:00 | Mongla | 140 | 17:00 | 119 | 13:00
Baroaulia | 135 | 23:00 | 128 | 13:00 | Motijheel | 133 | 18:00 | 129 | 13:00
Baroirhat | 137 | 19:30 | 130 | 13:00 | Muktagacha | 138 | 18:30 | 120 | 23:00
Bashundhara | 134 | 06:00 | 128 | 13:00 | Munshiganj | 136 | 18:00 | 130 | 13:00
BashundharaCement | 137 | 18:00 | 130 | 16:00 | Muradnagar | 137 | 18:30 | 125 | 13:00
Beanibazar | 127 | 06:00 | 121 | 13:00 | Mymensingh | 140 | 18:30 | 111 | 23:00
Benapole | 137 | 16:00 | 116 | 13:00 | Nabinagar | 128 | 06:00 | 121 | 13:00
Bhaluka | 130 | 18:30 | 120 | 23:00 | Naogaon | 144 | 17:00 | 125 | 13:00
Bhandaria | 142 | 17:00 | 118 | 01:00 | Narail | 138 | 16:00 | 121 | 00:00
Bhangura | 142 | 17:00 | 131 | 02:00 | Narinda | 134 | 03:00 | 130 | 13:00
Bheramara | 140 | 17:00 | 132 | 00:00 | Narshingdi | 134 | 05:00 | 127 | 14:00
Bheramara(GK) | 140 | 17:00 | 132 | 00:00 | Natore | 141 | 17:00 | 128 | 00:00
Bhulta | 133 | 18:00 | 128 | 13:00 | Nawabganj | 133 | 17:00 | 126 | 13:00
Bog-Sherpur | 144 | 17:00 | 131 | 13:00 | Netrakona | 123 | 18:30 | 107 | 23:00
Bogura | 144 | 17:00 | 130 | 13:00 | New | 134 | 18:00 | 130 | 13:00
Bogura-230 | 144 | 17:00 | 131 | 23:00 | Niamatpur | 137 | 17:00 | 127 | 13:00
Brahmanbaria | 134 | 18:00 | 127 | 13:00 | Noapara | 138 | 17:00 | 121 | 13:00
Cantonment | 133 | 06:00 | 128 | 13:00 | Pabna | 141 | 17:00 | 129 | 00:00
Chandina | 138 | 18:30 | 129 | 13:00 | Palashbari | 137 | 17:00 | 120 | 23:00
Chandpur | 136 | 07:00 | 120 | 14:00 | Panchagarh | 139 | 16:00 | 122 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 135 | 18:00 | 131 | 10:00 | Patiya | 132 | 18:00 | 123 | 13:00
Chapai | 135 | 16:00 | 129 | 00:00 | Patuakhali | 139 | 18:00 | 128 | 00:00
Charsaidpur | 137 | 18:30 | 130 | 13:00 | Payra | 139 | 18:00 | 132 | 00:00
Chauddagram | 135 | 18:30 | 127 | 13:00 | PHP | 136 | 18:30 | 128 | 13:00
Chhatak | 125 | 05:00 | 118 | 13:00 | Postogola | 139 | 09:00 | 135 | 12:00
Chowmuhani | 134 | 18:30 | 125 | 09:00 | Pubail | 141 | 18:00 | 135 | 23:00
Chuadanga | 139 | 16:00 | 115 | 00:00 | Purbachal | 134 | 03:00 | 128 | 13:00
Coxsbazar | 120 | 15:00 | 111 | 13:00 | Purbasadipur | 138 | 17:00 | 120 | 13:00
Cumilla(N) | 137 | 18:30 | 129 | 14:00 | Rahanpur | 138 | 17:00 | 130 | 00:00
Cumilla(S) | 137 | 18:30 | 122 | 00:00 | Rahanpur-400 | 138 | 17:00 | 129 | 13:00
Daganbhuiyan | 135 | 18:30 | 126 | 13:00 | Rahim | 137 | 18:00 | 132 | 13:00
Daudkandi | 136 | 18:30 | 124 | 13:00 | Rajbari | 139 | 18:00 | 127 | 00:00
DhakaUniversity | 134 | 06:00 | 130 | 23:00 | Rajendrapur | 133 | 18:30 | 122 | 13:00
Dhamrai | 129 | 18:00 | 124 | 23:00 | Rajshahi | 139 | 17:00 | 125 | 00:00
Dhanmondi | 138 | 18:00 | 133 | 13:00 | Rajshahi-230 | 139 | 17:00 | 127 | 00:00
Dohazari | 129 | 17:00 | 120 | 19:00 | Ramganj | 133 | 18:30 | 118 | 14:00
Faridpur | 139 | 18:00 | 127 | 00:00 | Rampur | 133 | 00:00 | 128 | 11:00
Fatullah | 138 | 18:00 | 130 | 13:00 | Rampura | 134 | 06:00 | 129 | 13:00
Fenchuganj | 134 | 06:00 | 129 | 14:00 | Rangamati | 135 | 23:00 | 127 | 13:00
Feni | 135 | 19:30 | 127 | 13:00 | Rangpur | 137 | 17:00 | 126 | 13:00
Feni-230 | 136 | 19:00 | 127 | 13:00 | Ruppur | 142 | 17:00 | 133 | 00:00
Ghatail | 137 | 18:30 | 118 | 23:00 | Saidpur | 137 | 17:00 | 120 | 13:00
Ghorashal | 142 | 18:00 | 136 | 23:00 | Santhia | 142 | 17:00 | 130 | 00:00
Goalpara | 140 | 17:00 | 125 | 12:00 | Satkhira | 139 | 17:00 | 116 | 13:00
Gollamari | 140 | 17:00 | 125 | 01:00 | Satmasjid | 133 | 18:00 | 129 | 14:00
Gopalganj | 140 | 17:00 | 126 | 13:00 | Savar | 135 | 03:00 | 131 | 13:00
Gopalganj-400 | 141 | 18:00 | 132 | 00:00 | SevenRings | 142 | 18:00 | 137 | 13:00
Gulshan | 133 | 04:00 | 129 | 13:00 | ShahCement | 137 | 18:30 | 130 | 13:00
Halishahar | 134 | 00:00 | 126 | 13:00 | Shahjadpur | 145 | 17:00 | 134 | 00:00
Haripur | 137 | 18:00 | 132 | 13:00 | Shahjibazar | 133 | 05:00 | 127 | 23:00
HaripurSBU | 137 | 18:00 | 132 | 16:00 | Shahmirpur | 134 | 00:00 | 126 | 13:00
Hasnabad | 138 | 18:00 | 134 | 13:00 | Shariatpur | 142 | 18:00 | 127 | 00:00
Hathazari | 136 | 18:00 | 131 | 09:00 | Sherpur | 136 | 18:30 | 110 | 23:00
Hatirjheel | 134 | 05:00 | 130 | 23:00 | Shikalbaha | 124 | 02:00 | 118 | 12:00
Ishurdi | 144 | 17:00 | 133 | 00:00 | Shikalbaha-230 | 135 | 17:00 | 128 | 13:00
Jaldhaka | 135 | 17:00 | 119 | 13:00 | Shitalakhya | 138 | 18:00 | 131 | 13:00
Jamalpur | 138 | 18:30 | 116 | 23:00 | Sholosohor | 135 | 23:00 | 128 | 13:00
Jashore | 138 | 17:00 | 119 | 13:00 | Shomvuganj | 128 | 05:00 | 118 | 22:00
Jhenaidah | 140 | 17:00 | 122 | 00:00 | Shyampur | 136 | 18:00 | 131 | 22:00
Jhenaidah-230 | 140 | 17:00 | 123 | 00:00 | Shyampur-230 | 137 | 18:00 | 132 | 13:00
Joydebpur | 140 | 06:00 | 134 | 13:00 | Siddhirganj | 137 | 18:00 | 133 | 13:00
Joypurhat | 143 | 17:00 | 126 | 13:00 | Sirajganj | 142 | 17:00 | 128 | 00:00
Juldah | 134 | 00:00 | 126 | 13:00 | Sonargaon | 137 | 18:30 | 130 | 13:00
Kabirpur | 136 | 18:00 | 129 | 12:00 | Sreemongol | 131 | 06:00 | 126 | 23:00
Kachua | 136 | 19:00 | 124 | 13:00 | Sreepur | 133 | 18:00 | 125 | 13:00
Kaliakoir | 138 | 18:00 | 126 | 13:00 | Srinagar | 134 | 18:00 | 126 | 13:00
Kaliganj | 140 | 17:00 | 128 | 13:00 | SSM | 140 | 00:00 | 134 | 10:00
Kallyanpur | 136 | 06:00 | 132 | 13:00 | Sunamganj | 124 | 06:00 | 116 | 13:00
Kalurghat | 136 | 18:30 | 129 | 13:00 | Sylhet | 128 | 06:00 | 123 | 13:00
Kamrangirchar | 135 | 07:00 | 127 | 13:00 | Sylhet-132 | 127 | 05:00 | 124 | 13:00
Kaptai | N/A | N/A | N/A | N/A | Tangail | 136 | 18:00 | 120 | 23:00
Kasba | 137 | 18:30 | 125 | 13:00 | Taraganj | 137 | 17:00 | 119 | 19:30
Kazla | 133 | 04:00 | 129 | 14:00 | Tasnim | 137 | 18:00 | 129 | 15:00
Keranigonj | 134 | 18:00 | 128 | 13:00 | Thakurgaon | 136 | 16:00 | 119 | 13:00
Khagrachori | 134 | 23:00 | 126 | 13:00 | TK | 139 | 22:00 | 129 | 13:00
Khulna | 138 | 17:00 | 124 | 13:00 | Tongi | 136 | 04:00 | 131 | 13:00
Khulna(S) | 140 | 17:00 | 124 | 13:00 | Ullahpara | 141 | 17:00 | 129 | 13:00
Khulshi | 133 | 19:30 | 127 | 13:00 | Ullon | 134 | 18:00 | 129 | 13:00
Kishoreganj | 129 | 06:00 | 118 | 23:00 | Uttara | 133 | 01:00 | 128 | 13:00
Kodda | 133 | 18:00 | 126 | 22:00 | UttaraNew | 133 | 18:00 | 128 | 13:00
Korerhat | 138 | 19:30 | 131 | 13:00 | Zigatola | 134 | 18:00 | 128 | 14:00
KSRM | 135 | 23:00 | 127 | 13:00
Kulaura | 132 | 18:00 | 127 | 13:00
Kurigram | 131 | 18:00 | 116 | 19:00
Kushtia | 141 | 16:00 | 128 | 00:00
Laksam | 136 | 18:30 | 123 | 13:00
Lakshmipur | 134 | 18:30 | 122 | 13:00
Lalbag | 134 | 18:00 | 128 | 13:00
Lalmonirhat | 127 | 16:00 | 118 | 19:00
Madanganj | 137 | 18:30 | 132 | 12:00
Madaripur | 140 | 18:00 | 130 | 13:00
Madartek | 133 | 04:00 | 129 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division