## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 01-06-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 31-05-2026 | during | 01-06-2026 | during | 01-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 235 | 0 | 230 | 230 | 0 | 0 | Under Maintenance
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 351 | 360 | 412 | 412 | 412 | 412 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 | 225 | Machine Problem
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 303 | 303 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 36 | 0 | 210 | 210 | 40 | 40 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 309 | 0 | 335 | 335 | 0 | 0 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17.5 | 53.97 | 53.97 | 36 | 36 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 1 | 1 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 13 | 14 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 5 | 52.19 | 52.19 | 16 | 50 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 145 | 300 | 300 | 32 | 32 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 96 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 70 | 105 | 105 | 100 | 100 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 108 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 535 | 500 | 584 | 584 | 570 | 570 | AGC+FGMO
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 559 | 259 | 718 | 718 | 350 | 350 | AGC
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 68 | 142 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2694 | 2382.5 | 5820.22 | 5792.22 | 2749.36 | 2845.36
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 8 | 8 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 6 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 0 | 0 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 97 | 217 | 215 | 220 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 99 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 24 | 100 | 100 | 24 | 24 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 31 | 39 | 38 | 38 | 38 | 38 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 24 | 60 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.73 | 0 | 2.04 | 0 | 2.04 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 96 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 46 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 35 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 730 | 1228 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 6 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 379 | 555 | 575 | 575 | 575 | 575 | AGC
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1317.73 | 2562 | 3352.9 | 3403.86 | 2558.4 | 2752.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 201 | 201 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 350 | 360 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 120 | 80 | 250 | 250 | 340 | 340
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 316 | 285 | 393 | 393 | 363 | 363 | FGMO
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 28 | 19 | 41.65 | 41.65 | 29 | 29 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 43 | 45 | 52.82 | 52.82 | 46 | 46 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 20 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 80 | 150 | 150 | 33 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 40 | 40 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 88 | 92 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 138 | 170 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 43 | 43 | Engine Problem
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 16 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 69 | 115 | 115 | 95 | 95 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 62 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1384 | 1468 | 2581.43 | 2526.43 | 2121.76 | 2192.76
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 31-05-2026 | during | 01-06-2026 | during | 01-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 145 | 149 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 75 | 135 | 140 | 140 | 90 | 140 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 20 | 10 | 10 | 110 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 22 | 0 | 46.2 | 0 | 46.2 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | From 17:00 to 20:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 253.2 | 322 | 442.4 | 384 | 334.9 | 436.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | GT#4 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 137 | 138 | 163 | 163 | 147 | 147 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 101 | 100 | 110 | 110 | 100 | 100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 51 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 105 | 105 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 24 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 320 | 294 | 260 | 260 | 320 | 320 | machine problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1113 | 1116 | 1163 | 1163 | 1160 | 1160
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 931 | 931 | 0 | 0 | 950 | 950 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 32 | 32 | 37 | 37 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 362 | 383 | 410 | 410 | 369 | 369 | FGMO
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 34 | 85 | 105 | 105 | 35 | 35 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 53 | 0 | 100 | 0 | 100 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 760 | 1164 | 1234.2 | 1234.2 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2140 | 2563 | 2596.2 | 2496.2 | 2812 | 2712
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 304 | 700 | 1244 | 1244 | 1244 | 1244 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 49 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 124 | 124 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 298 | 540 | 1244 | 1244 | 622 | 622 | AGC+FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 16 | 150 | 150 | 0 | 35 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 180 | 172 | 307 | 307 | 287 | 287 | AGC+FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.64 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1126.64 | 1821 | 3406 | 3405 | 2614 | 2648
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 55.93 | 0 | 63 | 0 | 63 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 170 | 192 | 214 | 214 | 190 | 190 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 161 | 161 | 220 | 220 | 198 | 198 | AGC+FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 171 | 190 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 390 | 360 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 50 | 97 | 97 | 50 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 78 | 113 | 113 | 113 | 113 | -
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 60 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.01 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 422 | 746 | 1435.88 | 1435.88 | 1400 | 1400
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 57.72 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 105 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 1537.66 | 1857 | 3244.57 | 3014.87 | 3020.31 | 2790.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.8 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 16 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 129 | 0 | 176.49 | 0 | 176.49 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 149.8 | 115 | 474.49 | 262 | 440.49 | 228
System Total |  |  |  |  | 28823.2 | 29270.237 | 11716.03 | 14206.5 | 23081.21 | 22447.58 | 17811.22 | 17765.59
Forecast Scenario (01-06-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14400 |  | 0 |  | 14400
|  |  |  | 1:00 | 14240 |  | 0 |  | 14240
|  |  |  | 2:00 | 14140 |  | 0 |  | 14140
|  |  |  | 3:00 | 13930 |  | 0 |  | 13930
|  |  |  | 4:00 | 13580 |  | 0 |  | 13580
|  |  |  | 5:00 | 13210 |  | 0 |  | 13210
|  |  |  | 6:00 | 12238 |  | 0 |  | 12238
|  |  |  | 7:00 | 11760 |  | 0 |  | 11760
|  |  |  | 8:00 | 11580 |  | 0 |  | 11580
|  |  |  | 9:00 | 11460 |  | 0 |  | 11460
|  |  |  | 10:00 | 11570 |  | 0 |  | 11570
|  |  |  | 11:00 | 11640 |  | 0 |  | 11640
|  |  |  | 12:00 | 12180 |  | 0 |  | 12180
|  |  |  | 13:00 | 12820 |  | 0 |  | 12820
|  |  |  | 14:00 | 13200 |  | 0 |  | 13200
|  |  |  | 15:00 | 13180 |  | 0 |  | 13180
|  |  |  | 16:00 | 13080 |  | 0 |  | 13080
|  |  |  | 17:00 | 12660 |  | 0 |  | 12660
|  |  |  | 18:00 | 11900 |  | 0 |  | 11900
|  |  |  | 18:30 | 12350 |  | 0 |  | 12350
|  |  |  | 19:00 | 13250 |  | 0 |  | 13250
|  |  |  | 19:30 | 13710 |  | 0 |  | 13710
|  |  |  | 20:00 | 14000 |  | 0 |  | 14000
|  |  |  | 21:00 | 14550 |  | 0 |  | 14550
|  |  |  | 22:00 | 14780 |  | 0 |  | 14780
|  |  |  | 23:00 | 14850 |  | 0 |  | 14850
Probable Maximum Temperature: |  |  | 35.00°C
Probable Maximum Demand at Day Peak: |  |  | 12180.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14550.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14550.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 314.198 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:50 hrs on 01-06-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 31-05-2026 | [28 empty] | Date: | 31-05-2026 | [28 empty] | Date: | 31-05-2026 | [28 empty] | Date: | 31-05-2026 | [28 empty] | Date: | 31-05-2026 | [17 empty] | Date: | 31-05-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [17 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 230 | 0 | 0 | 371 | 0 | 623 | 17 | 0 | 52 | 0 | 15 | 0 | 0 | 17 | 0 | 0 | 304 | 0 | 0 | 17 | 325 | 99 | 0 | 0 | 142 | 14 | 14 | 0 | 500 | 0 | 0 | 30 | 0 | 0 | 49 | 0 | 0 | 24 | 24 | 0 | 70 | 0 | 38 | 545 | 0 | 0 | 50 | 8 | 17 | 147 | 0 | 0 | 0 | 1160 | 0 | 12 | 0 | 340 | 358 | 120 | 51 | 0 | 201 | 20 | 16 | 93 | 0 | 0 | 19 | 0 | 166 | 0 | 0 | 0 | 155 | 0 | 320 | 30 | 30 | 141 | 0 | 16 | 0 | 86 | 30 | 101 | 0 | 0 | 17 | 9 | 78 | 152 | 0 | 0 | 0 | 7488 | 900 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1208 | 30 | 0 | 0 | 701 | 0 | 0 | 0 | 50 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 160 | 0 | 171 | 0 | 386 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 126 | 220 | 0 | 622 | 570 | 0 | 6135 | 13623 | 76.09
01:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 378 | 0 | 634 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 325 | 99 | 0 | 0 | 142 | 14 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 24 | 24 | 0 | 70 | 0 | 38 | 545 | 0 | 0 | 26 | 8 | 0 | 147 | 0 | 0 | 0 | 1161 | 0 | 0 | 0 | 318 | 358 | 120 | 51 | 0 | 203 | 20 | 0 | 94 | 0 | 0 | 19 | 0 | 162 | 0 | 0 | 0 | 235 | 0 | 320 | 30 | 30 | 143 | 0 | 16 | 0 | 86 | 30 | 100 | 0 | 0 | 17 | 9 | 78 | 152 | 0 | 0 | 0 | 7368 | 900 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1207 | 30 | 0 | 0 | 659 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 161 | 0 | 170 | 0 | 373 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 126 | 220 | 0 | 550 | 545 | 0 | 5932 | 13300 | 76.1
02:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 379 | 0 | 639 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 325 | 99 | 0 | 0 | 142 | 14 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 70 | 0 | 38 | 490 | 0 | 0 | 25 | 8 | 0 | 147 | 0 | 0 | 0 | 1166 | 0 | 0 | 0 | 315 | 360 | 120 | 51 | 0 | 203 | 20 | 0 | 93 | 0 | 0 | 19 | 0 | 158 | 0 | 0 | 0 | 320 | 0 | 320 | 0 | 30 | 141 | 0 | 16 | 0 | 86 | 30 | 98 | 0 | 0 | 17 | 9 | 78 | 152 | 0 | 0 | 0 | 7275 | 930 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1209 | 16 | 0 | 0 | 625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 160 | 0 | 170 | 0 | 386 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 126 | 220 | 0 | 461 | 500 | 0 | 5724 | 12999 | 76.11
03:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 382 | 0 | 602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 303 | 0 | 0 | 0 | 325 | 99 | 0 | 0 | 105 | 14 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 38 | 420 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 1164 | 0 | 0 | 0 | 336 | 359 | 120 | 51 | 0 | 203 | 20 | 0 | 94 | 0 | 0 | 19 | 0 | 152 | 0 | 0 | 0 | 315 | 0 | 320 | 0 | 30 | 147 | 0 | 16 | 0 | 86 | 30 | 102 | 0 | 0 | 17 | 9 | 78 | 154 | 0 | 0 | 0 | 7086 | 931 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1212 | 0 | 0 | 0 | 597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 163 | 0 | 170 | 0 | 373 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 126 | 220 | 0 | 370 | 470 | 0 | 5555 | 12641 | 76.12
04:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 381 | 0 | 620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 305 | 0 | 0 | 0 | 326 | 99 | 0 | 0 | 105 | 14 | 14 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 38 | 366 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 330 | 358 | 120 | 51 | 0 | 198 | 20 | 0 | 93 | 0 | 0 | 19 | 0 | 150 | 0 | 0 | 0 | 305 | 0 | 320 | 0 | 30 | 146 | 0 | 16 | 0 | 86 | 30 | 100 | 0 | 0 | 17 | 9 | 78 | 154 | 0 | 0 | 0 | 7094 | 931 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1208 | 0 | 0 | 0 | 565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 161 | 0 | 170 | 0 | 362 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 126 | 220 | 0 | 309 | 435 | 0 | 5314 | 12408 | 76.13
05:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 380 | 0 | 620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 303 | 0 | 0 | 0 | 280 | 99 | 0 | 0 | 105 | 14 | 14 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 38 | 366 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 1048 | 0 | 0 | 0 | 332 | 359 | 120 | 51 | 4 | 199 | 20 | 0 | 93 | 0 | 0 | 19 | 0 | 144 | 0 | 0 | 0 | 295 | 0 | 320 | 0 | 30 | 147 | 0 | 16 | 0 | 86 | 30 | 100 | 0 | 0 | 17 | 9 | 78 | 154 | 0 | 0 | 0 | 7041 | 931 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 0 | 0 | 539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 163 | 0 | 170 | 0 | 373 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 100 | 180 | 0 | 321 | 405 | 0 | 5087 | 12128 | 76.14
06:00 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 369 | 0 | 572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 303 | 0 | 0 | 0 | 280 | 36 | 0 | 2 | 86 | 14 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21 | 70 | 0 | 38 | 366 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 1003 | 0 | 0 | 0 | 314 | 320 | 120 | 20 | 15 | 199 | 29 | 0 | 93 | 0 | 0 | 19 | 0 | 136 | 0 | 5 | 0 | 295 | 0 | 320 | 0 | 30 | 136 | 1 | 16 | 0 | 86 | 30 | 100 | 0 | 0 | 17 | 9 | 78 | 154 | 0.1 | 3.74 | 0 | 6574.05 | 931 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.48 | 1000 | 0 | 0 | 0 | 488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.84 | 4 | 0 | 0 | 3.23 | 180 | 0 | 158 | 0 | 170 | 0 | 351 | 0 | 0.34 | 0 | 0 | 70 | 2 | 0 | 0 | 0 | 0 | 0.8 | 13 | 0.04 | 0 | 172 | 100 | 180 | 0 | 304 | 372 | 0 | 4852.73 | 11426.78 | 76.15
07:00 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 372 | 0 | 549 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 180 | 298 | 0 | 0 | 0 | 280 | 36 | 0 | 8 | 68 | 14 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0.17 | 70 | 0 | 38 | 366 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 1008 | 0 | 0 | 0 | 316 | 320 | 120 | 20 | 40 | 200 | 29 | 0 | 93 | 0 | 0 | 19 | 0 | 132 | 0 | 17 | 0 | 290 | 0 | 320 | 0 | 30 | 136 | 3 | 16 | 0 | 86 | 30 | 100 | 0 | 0 | 17 | 9 | 78 | 152 | 0.5 | 14.5 | 0 | 6598.17 | 931 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 953 | 0 | 0 | 0 | 434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.72 | 19 | 0 | 0 | 10.78 | 168 | 0 | 157 | 0 | 170 | 0 | 376 | 0 | 0.89 | 0 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 1.5 | 48 | 0.17 | 0 | 178 | 100 | 180 | 0 | 315 | 325 | 0 | 4793.06 | 11391.23 | 76.16
08:00 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 367 | 0 | 485 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 180 | 304 | 0 | 0 | 0 | 280 | 36 | 0 | 16 | 73 | 14 | 14 | 0 | 490 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0.15 | 70 | 0 | 38 | 375 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 950 | 2 | 0 | 0 | 316 | 320 | 120 | 20 | 46 | 200 | 29 | 0 | 91 | 0 | 0 | 16 | 0 | 126 | 0 | 33 | 0 | 290 | 0 | 320 | 0 | 30 | 135 | 6 | 16 | 0 | 52 | 30 | 100 | 0 | 0 | 17 | 9 | 78 | 152 | 1 | 24.61 | 0 | 6473.76 | 932 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 917 | 1 | 0 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.6 | 48 | 0 | 0 | 26.37 | 169 | 0 | 157 | 0 | 171 | 0 | 357 | 0 | 2.26 | 0 | 0 | 35 | 14 | 0 | 0 | 0 | 0 | 3.9 | 122 | 0.31 | 0 | 174 | 100 | 180 | 0 | 303 | 300 | 0 | 4851.44 | 11325.2 | 76.17
09:00 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 337 | 0 | 463 | 0 | 0 | 14 | 0 | 0 | 15 | 0 | 0 | 0 | 180 | 298 | 0 | 0 | 0 | 280 | 36 | 0 | 23 | 86 | 14 | 14 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 70 | 0 | 38 | 375 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 884 | 3 | 0 | 0 | 316 | 320 | 120 | 20 | 42 | 201 | 28 | 0 | 91 | 0 | 0 | 16 | 0 | 128 | 0 | 41 | 0 | 305 | 0 | 320 | 0 | 30 | 133 | 9 | 16 | 0 | 52 | 30 | 100 | 0 | 0 | 0 | 9 | 95 | 148 | 1.5 | 38.86 | 0 | 6333.86 | 931 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 860 | 21 | 0 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.14 | 74 | 0 | 0 | 37.32 | 168 | 0 | 156 | 0 | 170 | 0 | 360 | 0 | 3.53 | 0 | 0 | 0 | 21 | 34 | 0 | 0 | 0 | 5.6 | 117 | 0.4 | 0 | 175 | 100 | 220 | 0 | 298 | 299 | 0 | 4921.99 | 11255.85 | 76.18
10:00 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 336 | 0 | 442 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 180 | 299 | 0 | 0 | 0 | 280 | 36 | 0 | 29 | 86 | 12 | 14 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.04 | 70 | 0 | 38 | 372 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 767 | 3 | 0 | 0 | 305 | 350 | 120 | 20 | 43 | 196 | 28 | 0 | 90 | 0 | 0 | 18 | 0 | 130 | 0 | 31 | 0 | 310 | 0 | 320 | 0 | 30 | 132 | 11 | 16 | 0 | 51 | 30 | 100 | 0 | 0 | 0 | 9 | 95 | 148 | 2 | 43.31 | 0 | 6209.35 | 932 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 788 | 41 | 0 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.06 | 90 | 0 | 0 | 25.59 | 168 | 0 | 156 | 0 | 170 | 0 | 343 | 0 | 4.13 | 0 | 0 | 0 | 26 | 34 | 0 | 0 | 0 | 6.7 | 140 | 0.3 | 0 | 173 | 100 | 220 | 0 | 300 | 297 | 0 | 4895.78 | 11105.13 | 76.18
11:00 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 333 | 0 | 474 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 180 | 303 | 0 | 0 | 0 | 280 | 36 | 0 | 31 | 68 | 12 | 14 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.83 | 70 | 0 | 32 | 374 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 730 | 8 | 0 | 0 | 305 | 350 | 120 | 20 | 43 | 197 | 28 | 0 | 90 | 0 | 0 | 18 | 0 | 136 | 0 | 32 | 0 | 320 | 0 | 320 | 0 | 30 | 131 | 12 | 16 | 0 | 51 | 30 | 100 | 0 | 50 | 0 | 9 | 75 | 146 | 2.1 | 47.17 | 0 | 6303.1 | 931 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 760 | 34 | 0 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.45 | 105 | 0 | 0 | 58.14 | 167 | 0 | 153 | 0 | 171 | 0 | 351 | 0 | 4.85 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 7.6 | 127 | 0.61 | 0 | 177 | 124 | 220 | 0 | 299 | 300 | 0 | 4922.65 | 11225.75 | 76.18
12:00 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 351 | 0 | 559 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 225 | 303 | 0 | 0 | 0 | 309 | 36 | 0 | 31 | 68 | 13 | 14 | 0 | 535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.73 | 70 | 0 | 31 | 379 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 730 | 6 | 0 | 0 | 316 | 350 | 120 | 20 | 43 | 201 | 28 | 0 | 88 | 0 | 0 | 18 | 0 | 138 | 0 | 62 | 0 | 315 | 0 | 320 | 0 | 30 | 137 | 13 | 16 | 0 | 51 | 30 | 101 | 0 | 100 | 0 | 9 | 75 | 145 | 2.2 | 22 | 0 | 6761.93 | 931 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 760 | 34 | 0 | 0 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.93 | 105 | 0 | 0 | 57.72 | 170 | 0 | 161 | 0 | 171 | 0 | 390 | 0 | 5.01 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 4.8 | 129 | 0.64 | 0 | 180 | 124 | 220 | 0 | 304 | 298 | 0 | 4954.1 | 11716.03 | 76.18
13:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 384 | 0 | 646 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 225 | 301 | 0 | 0 | 0 | 307 | 94 | 0 | 24 | 68 | 13 | 14 | 0 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 70 | 0 | 31 | 405 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 730 | 6 | 0 | 0 | 345 | 347 | 155 | 20 | 43 | 207 | 28 | 0 | 88 | 0 | 0 | 18 | 0 | 154 | 0 | 58 | 0 | 315 | 0 | 295 | 0 | 30 | 149 | 10 | 16 | 0 | 72 | 30 | 101 | 0 | 100 | 0 | 9 | 75 | 142 | 2.1 | 42.98 | 0 | 7169.98 | 931 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 761 | 0 | 0 | 0 | 461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.51 | 107 | 0 | 0 | 57.52 | 172 | 0 | 177 | 0 | 175 | 0 | 402 | 0 | 3.25 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 7.5 | 108 | 0.34 | 0 | 207 | 122 | 220 | 0 | 373 | 310 | 0 | 5110.12 | 12280.1 | 76.18
14:00 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 390 | 0 | 598 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 225 | 303 | 0 | 0 | 0 | 307 | 94 | 0 | 15 | 65 | 13 | 14 | 0 | 525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.67 | 70 | 0 | 31 | 400 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 820 | 8 | 0 | 0 | 333 | 352 | 225 | 40 | 43 | 199 | 25 | 0 | 88 | 0 | 0 | 18 | 0 | 152 | 0 | 38 | 0 | 320 | 0 | 295 | 0 | 30 | 146 | 5 | 0 | 0 | 83 | 30 | 100 | 0 | 100 | 0 | 9 | 75 | 142 | 2 | 44.31 | 0 | 7234.98 | 931 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 761 | 0 | 0 | 0 | 478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.96 | 97 | 0 | 0 | 46.45 | 192 | 0 | 180 | 0 | 195 | 0 | 353 | 0 | 4.53 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 6.2 | 149 | 0.51 | 0 | 238 | 122 | 220 | 0 | 452 | 350 | 0 | 5298.65 | 12533.63 | 76.18
15:00 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 385 | 0 | 642 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 180 | 311 | 0 | 0 | 0 | 250 | 0 | 0 | 18 | 68 | 14 | 14 | 0 | 530 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3.39 | 63 | 0 | 36 | 380 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 951 | 8 | 0 | 8 | 335 | 352 | 225 | 51 | 42 | 214 | 28 | 0 | 89 | 0 | 0 | 18 | 0 | 150 | 0 | 20 | 0 | 315 | 0 | 296 | 0 | 30 | 146 | 8 | 0 | 0 | 83 | 30 | 102 | 0 | 100 | 0 | 9 | 85 | 143 | 1.7 | 26.57 | 0 | 7222.66 | 931 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 777 | 0 | 0 | 0 | 481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.89 | 81 | 0 | 0 | 26.43 | 193 | 0 | 169 | 0 | 192 | 0 | 374 | 0 | 2.44 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 5.2 | 134 | 0.49 | 0 | 237 | 120 | 220 | 0 | 456 | 360 | 0 | 5250.45 | 12473.11 | 76.18
16:00 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 381 | 0 | 502 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 170 | 289 | 0 | 0 | 0 | 240 | 0 | 0 | 14 | 68 | 14 | 14 | 0 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68 | 68 | 0 | 36 | 374 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1050 | 8 | 0 | 0 | 280 | 347 | 100 | 51 | 42 | 205 | 19 | 0 | 89 | 0 | 0 | 16 | 0 | 150 | 0 | 32 | 0 | 320 | 0 | 296 | 0 | 30 | 145 | 5 | 16 | 0 | 83 | 30 | 101 | 0 | 100 | 0 | 9 | 95 | 142 | 0.8 | 27.05 | 0 | 6927.53 | 931 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 829 | 0 | 0 | 0 | 476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 36 | 0 | 0 | 25.19 | 193 | 0 | 172 | 0 | 192 | 0 | 363 | 0 | 2.22 | 0 | 0 | 0 | 15 | 25 | 0 | 0 | 0 | 4 | 94 | 0.36 | 0 | 249 | 120 | 220 | 0 | 492 | 390 | 0 | 5279.77 | 12207.3 | 76.17
17:00 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 367 | 0 | 233 | 17.5 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 170 | 287 | 0 | 0 | 0 | 240 | 0 | 0 | 6 | 68 | 14 | 14 | 0 | 525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 69 | 0 | 29 | 377 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1050 | 3 | 0 | 0 | 300 | 353 | 100 | 51 | 42 | 202 | 21 | 0 | 89 | 0 | 0 | 16 | 0 | 142 | 0 | 12 | 0 | 315 | 0 | 296 | 0 | 30 | 143 | 2 | 16 | 0 | 84 | 30 | 100 | 0 | 100 | 0 | 9 | 95 | 142 | 0.6 | 6.66 | 0 | 6631.88 | 931 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 855 | 0 | 0 | 0 | 438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.33 | 26 | 0 | 0 | 8.52 | 192 | 0 | 165 | 0 | 191 | 0 | 355 | 0 | 0.91 | 0 | 0 | 0 | 7 | 31 | 0 | 0 | 0 | 2 | 48 | 0.12 | 0 | 229 | 120 | 220 | 0 | 403 | 510 | 0 | 5144.88 | 11776.76 | 76.17
18:00 | 0 | 0 | 0 | 0 | 0 | 237 | 0 | 0 | 344 | 0 | 250 | 17.5 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 170 | 250 | 0 | 0 | 0 | 240 | 0 | 0 | 2 | 68 | 14 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 29 | 373 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1050 | 1 | 0 | 0 | 295 | 345 | 100 | 51 | 43 | 202 | 20 | 0 | 90 | 0 | 0 | 16 | 0 | 140 | 0 | 2 | 0 | 310 | 0 | 296 | 0 | 30 | 132 | 0 | 23 | 0 | 84 | 30 | 100 | 0 | 100 | 0 | 9 | 95 | 144 | 0.1 | 1.81 | 0 | 6524.41 | 931 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 857 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.02 | 6 | 0 | 0 | 2.11 | 192 | 0 | 156 | 0 | 190 | 0 | 360 | 0 | 0.19 | 0 | 0 | 0 | 2 | 37 | 0 | 0 | 0 | 0 | 16 | 0.06 | 0 | 174 | 120 | 220 | 0 | 286 | 585 | 0 | 4926.38 | 11450.79 | 76.16
19:00 | 0 | 34 | 0 | 0 | 0 | 238 | 0 | 0 | 382 | 0 | 309 | 17.5 | 6 | 3 | 0 | 45 | 25 | 17 | 30 | 0 | 200 | 303 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 100 | 14 | 14 | 0 | 570 | 2 | 10 | 0 | 0 | 9 | 50 | 29 | 1 | 24 | 34 | 0 | 70 | 9 | 39 | 515 | 0 | 0 | 2 | 0 | 12 | 215 | 0 | 0 | 0 | 1213 | 0 | 13 | 0 | 285 | 345 | 100 | 51 | 43 | 200 | 20 | 1 | 91 | 7 | 0 | 16 | 0 | 168 | 5 | 0 | 0 | 315 | 0 | 307 | 0 | 30 | 139 | 0 | 23 | 0 | 85 | 30 | 100 | 0 | 100 | 3 | 9 | 135 | 145 | 0 | 0 | 2 | 7626.5 | 931 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 883 | 35 | 0 | 0 | 570 | 0 | 0 | 0 | 20 | 3 | 0 | 49 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 194 | 0 | 163 | 0 | 192 | 0 | 402 | 0 | 0 | 0 | 0 | 35 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 120 | 220 | 0 | 475 | 550 | 5 | 5486 | 13112.5 | 76.16
19:30 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 272 | 17.5 | 17 | 50 | 0 | 63 | 55 | 35 | 70 | 0 | 225 | 287 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 142 | 14 | 14 | 0 | 475 | 32 | 15 | 0 | 0 | 5 | 50 | 32 | 17 | 24 | 50 | 0 | 70 | 35 | 39 | 535 | 0 | 0 | 40 | 0 | 64 | 216 | 0 | 0 | 0 | 1224 | 0 | 80 | 0 | 285 | 354 | 100 | 51 | 43 | 202 | 18 | 40 | 91 | 17 | 18 | 16 | 0 | 164 | 16 | 0 | 0 | 315 | 0 | 308 | 0 | 30 | 136 | 0 | 23 | 0 | 85 | 30 | 102 | 0 | 100 | 17 | 9 | 135 | 145 | 0 | 0 | 12 | 7537.5 | 931 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 983 | 70 | 0 | 0 | 694 | 0 | 0 | 0 | 50 | 50 | 0 | 50 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 193 | 0 | 170 | 0 | 192 | 0 | 348 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 178 | 127 | 220 | 0 | 536 | 555 | 16 | 5890 | 13427.5
20:00 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 272 | 17.5 | 17 | 51 | 10 | 95 | 55 | 35 | 108 | 0 | 225 | 296 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 142 | 14 | 14 | 0 | 500 | 27 | 15 | 0 | 0 | 5 | 50 | 32 | 17 | 24 | 50 | 0 | 70 | 58 | 39 | 545 | 0 | 0 | 40 | 0 | 81 | 216 | 0 | 0 | 0 | 1232 | 0 | 80 | 0 | 285 | 354 | 100 | 51 | 45 | 197 | 17 | 38 | 91 | 16 | 12 | 16 | 0 | 164 | 16 | 0 | 0 | 315 | 0 | 308 | 0 | 30 | 137 | 0 | 24 | 0 | 85 | 30 | 102 | 0 | 100 | 17 | 9 | 135 | 147 | 0 | 0 | 12 | 7713.5 | 931 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1063 | 75 | 0 | 0 | 754 | 0 | 0 | 0 | 50 | 45 | 0 | 50 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 193 | 0 | 164 | 0 | 191 | 0 | 355 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 172 | 124 | 220 | 0 | 635 | 550 | 16 | 6117 | 13830.5 | 76.15
21:00 | 0 | 70 | 5 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 259 | 17.5 | 17 | 96 | 0 | 145 | 55 | 35 | 108 | 0 | 225 | 303 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 142 | 14 | 14 | 0 | 500 | 46 | 15 | 0 | 0 | 6 | 50 | 0 | 17 | 24 | 50 | 0 | 70 | 96 | 39 | 555 | 0 | 0 | 50 | 0 | 99 | 217 | 0 | 0 | 0 | 1228 | 0 | 80 | 0 | 285 | 360 | 80 | 51 | 45 | 201 | 19 | 69 | 92 | 0 | 0 | 16 | 0 | 170 | 0 | 0 | 0 | 315 | 0 | 294 | 0 | 30 | 138 | 0 | 24 | 0 | 85 | 30 | 100 | 0 | 100 | 17 | 9 | 135 | 149 | 0 | 0 | 12 | 7850.5 | 931 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1164 | 85 | 0 | 0 | 746 | 0 | 0 | 0 | 60 | 78 | 0 | 50 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 192 | 0 | 161 | 0 | 190 | 0 | 360 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 172 | 124 | 220 | 0 | 700 | 540 | 16 | 6356 | 14206.5 | 76.15
22:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 287 | 17.5 | 17 | 114 | 0 | 145 | 55 | 35 | 108 | 0 | 225 | 303 | 0 | 0 | 17 | 0 | 95 | 0 | 0 | 142 | 14 | 14 | 0 | 560 | 0 | 0 | 0 | 0 | 1 | 50 | 0 | 0 | 24 | 50 | 0 | 70 | 98 | 39 | 555 | 0 | 0 | 50 | 0 | 98 | 220 | 0 | 0 | 0 | 1225 | 0 | 80 | 0 | 285 | 358 | 80 | 51 | 46 | 204 | 23 | 84 | 92 | 0 | 0 | 16 | 0 | 172 | 0 | 0 | 0 | 310 | 0 | 296 | 0 | 30 | 138 | 0 | 24 | 0 | 85 | 30 | 100 | 0 | 101 | 17 | 9 | 78 | 147 | 0 | 0 | 0 | 7908.5 | 931 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1141 | 85 | 0 | 0 | 753 | 0 | 0 | 0 | 100 | 113 | 0 | 50 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 193 | 0 | 162 | 0 | 192 | 0 | 395 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 200 | 124 | 220 | 0 | 733 | 540 | 16 | 6542 | 14450.5 | 76.14
23:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 255 | 17.5 | 17 | 115 | 0 | 195 | 55 | 35 | 72 | 0 | 225 | 301 | 0 | 0 | 35 | 0 | 94 | 0 | 0 | 142 | 14 | 14 | 0 | 530 | 32 | 16 | 0 | 0 | 6 | 50 | 0 | 23 | 24 | 50 | 0 | 70 | 98 | 42 | 555 | 0 | 0 | 50 | 0 | 97 | 220 | 0 | 0 | 0 | 1204 | 0 | 110 | 0 | 290 | 356 | 80 | 51 | 44 | 203 | 20 | 91 | 92 | 17 | 13 | 16 | 0 | 174 | 19 | 0 | 0 | 310 | 0 | 296 | 0 | 30 | 138 | 0 | 24 | 0 | 85 | 30 | 100 | 0 | 101 | 17 | 9 | 78 | 150 | 0 | 0 | 0 | 8022.5 | 931 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 954 | 85 | 0 | 0 | 746 | 0 | 0 | 0 | 113 | 113 | 0 | 50 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 191 | 0 | 162 | 0 | 190 | 0 | 400 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 307 | 124 | 220 | 0 | 696 | 545 | 50 | 6491 | 14513.5 | 76.14
Total KWH | 0 | 329280 | 13440 | 0 | 0 | 4143469 | 0 | 0 | 8895600 | 0 | 11338450 | 132588 | 97200 | 615600 | 8640 | 696775 | 463584 | 176969 | 414720 | 0 | 3948500 | 7105745 | 0 | 0 | 142585 | 5633539 | 1327000 | 0 | 223477 | 2463600 | 338400 | 344880 | 0 | 11763181.82 | 181909 | 72764 | 12480 | 0 | 66720 | 335430 | 64512 | 105846 | 176640 | 294720 | 18598 | 1674320 | 461673 | 909600 | 10400000 | 0 | 0 | 324960 | 21506.4 | 502654 | 3558610 | 0 | 0 | 0 | 24572725 | 52920 | 528581 | 16727 | 7523000 | 8716500 | 3010000 | 1047488 | 797280 | 4983000 | 558576 | 384000 | 2169321 | 86880 | 61320 | 413940 | 0 | 3554880 | 98021 | 412955 | 0 | 7437000 | 0 | 7566000 | 56000 | 716400 | 3366572.72 | 79999 | 419520 | 0 | 1840320 | 718080 | 2380000 | 0 | 1273920 | 253080 | 214800 | 2124000 | 3663680 | 15850 | 343530 | 29760 | 171286790.94 | 22477091 | 8946144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 722880 | 23032730 | 660480 | 0 | 0 | 13132819 | 0 | 0 | 0 | 486624 | 545568 | 0 | 254240 | 0 | 0 | 380048 | 827850 | 106602 | 0 | 387536 | 4485000 | 0 | 4133736 | 0 | 4556700 | 0 | 8908946 | 0 | 33600 | 0 | 0 | 1264960 | 222798 | 200678 | 0 | 0 | 0 | 54951.36 | 1229760 | 4650 | 337056 | 5192000 | 3039000 | 5267270 | 0 | 10589090 | 10720000 | 139200 | 132340007.36 | 303626798.3

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 31-05-2026
Power Supply Scenario
| Day Peak Generation |  |  | 11716.03 | MW | 12:00 Hr. | Energy Generated |  |  | 303.6268 |  | MKWHr.
| Day Peak Demand |  |  | 11716.03 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.641 |  | MKWHr.
| Evening Peak Generation |  |  | 14206.5 | MW | 21:00 Hr. | Energy Demand |  |  | 304.2678 |  | MKWHr.
| Evening Peak Demand |  |  | 14255.5 | MW | 21:00 Hr. | Maximum Temperature |  |  | 36.4 |  | °C
| Minimum Generation of the Day |  |  | 11105.13 | MW | 10:00 Hr. | Total Gas Supplied |  |  | 1142.66 |  | MMCFD
| Maximum Generation of the Day |  |  | 14513.5 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 5.5235 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 54.8388 | 0 | 5.555 | 0 | 0 | 0.22348 | 0 | 0 | 60.6172 | Gas | 157.3171 | Gas | 568408756.8118
| Chattogram Zone |  |  | 4.4682 | 34.9727 | 2.5551 | 0 | 1.6743 | 0.071518 | 0 | 0.06672 | 43.8086 | Coal | 84.5065 | Coal | 555629070.4
| Cumilla Zone |  |  | 29.2358 | 0 | 1.1588 | 0 | 0 | 0.41296 | 3.5549 | 0 | 34.3625 | HFO | 15.8859 | HFO | 265508449.358
| Mymensingh Zone |  |  | 3.6637 | 0 | 2.6216 | 0 | 0 | 0.35938 | 0 | 0 | 6.6447 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.7738 | 0 | 0 | 0 | 0 | 0.079999 | 0 | 0 | 25.8538 | Hydro | 1.6743 | Hydro | 167432
| Khulna Zone |  |  | 8.9461 | 23.0327 | 0.66048 | 0 | 0 | 0.72288 | 22.4771 | 0 | 55.8393 | Solar | 5.0114 | Solar | 80991763.0272
| Barishal Zone |  |  | 8.3063 | 26.5011 | 0.47626 | 0 | 0 | 0.00465 | 0 | 0 | 35.2883 | Import | 39.1648 | Import | 205391268.04
| Rajshahi Zone |  |  | 22.0844 | 0 | 1.393 | 0 | 0 | 1.629 | 13.1328 | 0 | 38.2393 | Wind | 0.06672 | Wind | 981451.2
| Rangpur Zone |  |  | 0 | 0 | 1.4656 | 0 | 0 | 1.5075 | 0 | 0 | 2.9731
| Total |  |  | 157.3171 | 84.5065 | 15.8859 | 0 | 1.6743 | 5.0114 | 39.1648 | 0.06672 | 303.6268
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 568408756.8118 |  | Hydro | 167432
|  |  |  | Coal | 555629070.4 |  | Solar | 80991763.0272
|  |  |  | HFO | 265508449.358 |  | Import | 205391268.04
|  |  |  | HSD | 0 |  | Wind | 981451.2
[5 empty] | Total: | 167,70,78,190 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.4771 | Peak Hr Flow | 931.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 17099854.55 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 13.1328 | Peak Hr Flow | 746.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1051 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.5549 | Peak Hr Flow | 170.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1051 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 39.1648 | Peak Hr Flow | 1847.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3795
|  |  |  | Chattogram |  | 0 |  | 1342
|  |  |  | Cumilla |  | 3 |  | 1569
|  |  |  | Mymensingh |  | 33 |  | 1289
|  |  |  | Sylhet |  | 11 |  | 680
|  |  |  | Khulna |  | 0 |  | 1948
|  |  |  | Barishal |  | 0 |  | 529
|  |  |  | Rajshahi |  | 0 |  | 1609
|  |  |  | Rangpur |  | 0 |  | 1031
|  |  |  | Total |  | 47 |  | 13792
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:39 | 12:18 | Khulna(C )-Khulna (S) 132kV Ckt-2 Scheduled S/D from Khulna (C) end Due to Due to
replacement of DS arms for reduce temperature. and from Khulna(S) 230/132kVend.
|  | 09:46 | Barishal 230/132kV S/S T-4 HT is restored.
|  | 09:51 | Barishal 230/132kV S/S T-4 LT is restored.
| 10:10 | 12:20 | Kodda 132/33kV S/S Summit 149 MW PS Scheduled S/D Due to work by Summit
| 10:30 | 16:25 | Kaliakoir 400/230/132kV S/S Bibiyana1 Scheduled S/D Due to Disc cleaning
| 11:11 | 12:55 | Mithapukur 132/33kV S/S TR-1(404T) LT Forced S/D Due to Red hot maintenance. | [7 empty] | 22.0MW load
interrup.
| 11:11 | 12:55 | Mithapukur 132/33kV S/S TR-1(404T) HT Forced S/D Due to Red hot maintenance. | [7 empty] | 22.0MW load
interrup.
| 11:11 | 17:02 | Shyampur-Shyampur(New) 132kV Ckt-2 Scheduled S/D from Shyampur 230/132kV end Due to
Maintenance work at Shyampur old Substation end
| 12:00 |  | Day Peak Generation is 11712 MW.
| 12:25 | 12:56 | Lalmonirhat-Rangpur 132 kV Ckt-2 Tripped from Lalmonirhat 132/33kV end showing
Directional E/F Relay relays. and from Rangpur 132/33kV end showing Distance Relay relays
Due to Unknown
| 12:25 | 12:41 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) LT Tripped showing Over current at 33 kV | [7 empty] | 29.0MW load
|  |  | side relays Due to None | [7 empty] | interrup.
| 12:25 | 12:41 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) HT Tripped showing Over current at 33 kv | [7 empty] | 29.0MW load
|  |  | side relays Due to None | [7 empty] | interrup.
| 12:25 | 12:41 | Kurigram 132/33kV S/S Transformer T-2 (Tr-413T) HT Tripped showing Over current at 33 kV | [7 empty] | 29.0MW load
|  |  | side relays Due to None | [7 empty] | interrup.
| 12:25 | 12:41 | Kurigram 132/33kV S/S Transformer T-2 (Tr-413T) LT Tripped showing Over current at 33 kV | [7 empty] | 29.0MW load
|  |  | side relays Due to None | [7 empty] | interrup.
| 13:41 | 14:14 | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-1 Tripped from Mithapukur 132/33kV end | [7 empty] | 15.0MW load
|  |  | showing R,Y phase operated, DIST/DEF carrier receive, ZCOM trip, 86A relay optd, 86B | [7 empty] | interrup.
|  |  | relay optd, 86LO relay optd. relays. | [7 empty] | Mithapukur 132/33kV
end
| 15:42 | 16:20 | Kabirpur -Tongi 132kV Ckt-2 Tripped from Tongi 230/132/33kV end showing Siprotec
relays.
|  | 19:25 | Bhulta-Ghorasal 230 kV Ckt-2 is restored.
| 19:26 | 01:00 | Aftabnagar-Rampura 132kV Ckt-1 Tripped from Ghorashal 230kV end showing Siprotech
Distance Relay relays Due to Ghorasal PDB AIS Grid End fault and from Ghorashal 230kV end
showing Lockout Relay relays Due to Ghorasal PDB AIS Grid End fault
| 19:26 | 01:00 | Aftabnagar-Rampura 132kV Ckt-1 Tripped from Ghorashal 230kV end showing Lockout Relay
relays Due to Ghorasal PDB AIS Grid End fault and from Ghorashal 230kV end showing
Siprotech Distance Relay relays Due to Ghorasal PDB AIS Grid End fault
| 19:27 |  | All 230kV and 132kV Ckts and 230/132kV AT-1 and AT-2 transformers of Ghorashal AIS (BPDB)
230/132kV grid S/S tripped at 19:27 hrs. Full load interruption occurred under Joydebpur
and Pubail 132/33kV grid S/S from 19:27 hrs to 19:36 hrs due to this tripping. Ghorashal
GIS-Ishwardi 230kV Ckt-1 also tripped at the same time. Full load interruption is
occurring under Ghorashal GIS grid S/S from 19:27 hrs due to this tripping.
| 19:27 |  | Ghorasal Repowered CCPP Unit-4 Tripped
| 19:27 | 20:32 | Ghorasal- Ishwardi 230 kV Ckt-1 Tripped from Ishurdi 230/132kV end showing siemens
siprotec 7sa87 relays Due to A-G fault 1201Km from Isd Side. Z-2 opdt
| 19:58 | 20:33 | Ghorasal- Ishwardi 230 kV Ckt-1 Forced S/D from Ghorashal 230kV end Due to Ghorasal PDB
AIS Grid End fault
| 20:22 | 20:38 | Ghorashal 230kV S/S TARFO-2 HT Forced S/D Due to Ghorasal PDB AIS Grid End fault | [7 empty] | 60.0MW load
interrup.
| 20:27 | 21:18 | Aftabnagar-Rampura 132kV Ckt-1 Forced S/D from Ghorashal 230kV end Due to Ghorasal PDB
AIS Grid End fault and from Ghorashal 230kV end Due to Ghorasal PDB AIS Grid End fault
and from Ghorashal 230kV end Due to Ghorasal PDB AIS Grid End fault
| 20:28 | 21:46 | Ghorasal- Ishwardi 230 kV Ckt-2 Forced S/D from Ghorashal 230kV end Due to Ghorasal PDB
AIS Grid End fault
| 20:33 |  | Ghorashal GIS-Ishwardi 230kV Ckt-1 was switched on.
| 21:55 | 22:24 | Ghorasal- Ishwardi 230 kV Ckt-1 Tripped from Ishurdi 230/132kV end showing siemens
siprotech 7SA87 relays Due to UNKNOWN
| 22:20 |  | Aftabnagar-Rampura 132kV Ckt-1 Forced S/D from Ghorashal 230kV end Due to Fault at
Ghorashal AIS Grid End
| 22:20 |  | Ghorashal 230kV S/S Ghorashal GIS- AIS Ckt-3 Scheduled S/D Due to As NLDC SDE instruction
|  | 01:00 | Aftabnagar-Rampura 132kV Ckt-1 is restored.
|  | 01:00 | Aftabnagar-Rampura 132kV Ckt-1 is restored.
|  | 01:00 | Aftabnagar-Rampura 132kV Ckt-1 is restored.
|  | 01:00 | Aftabnagar-Rampura 132kV Ckt-1 is restored.
| 07:00 |  | Minimum Generation is 12247 MW.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 31-05-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 4143469 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 360 | 8895600 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 3948500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 303 | 7105745 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 463584 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 1327000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 5633539 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17.5 | 132588 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 8640 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 176969 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 142585 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 14 | 338400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 344880 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 5 | 13440 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 696775 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 96 | 615600 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 329280 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 414720 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 223477 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 97200 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 500 | 11763181.82 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 259 | 11338450 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 2463600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2382.5 | 60617222.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 21506.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 52920 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 324960 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1674320 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 3558610 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 99 | 502654 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 64512 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 335430 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 176640 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 39 | 909600 | plant availability zero
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 12480 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 18598 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 72764 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 17 | 105846 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 96 | 461673 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 294720 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 46 | 181909 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1228 | 24572725 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 6 | 66720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 555 | 10400000 | Coal shortage
Chattogram Area Total |  |  |  |  | 4898.863 | 2562 | 43808587.4
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 201 | 4983000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 360 | 8716500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 80 | 3010000 | FGMO not available
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 285 | 7523000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 19 | 558576 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 45 | 797280 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 16727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1047488 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 80 | 528581 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 92 | 2169321 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 86880 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 170 | 3554880 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 98021 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 16 | 413940 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 61320 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 69 | 384000 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 412955 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1468 | 34362469
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 149 | 3663680 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15850 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 135 | 2124000 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 214800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 343530 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 29760 | From 17:00 to 20:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 253080 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 322 | 6644700
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 79999 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 56000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 716400 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 138 | 3366572.72 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 100 | 2380000 | plant availability zero
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 718080 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1840320 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 1273920 | Gas shortage
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 419520 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7437000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 294 | 7566000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1116 | 25853811.72
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 931 | 22477091 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 383 | 8946144 | FGMO
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 85 | 660480 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | FGMO
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 722880 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1164 | 23032730 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2563 | 55839325
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 700 | 10589090 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 49 | 337056 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 124 | 3039000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 540 | 10720000 | plant availability zero
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5267270 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 16 | 139200 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 172 | 5192000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4650 | -
Barishal Area Total |  |  |  |  | 3481.04 | 1821 | 35288266
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 380048 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 192 | 4485000 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 161 | 4133736 | AGC
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 190 | 4556700 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 360 | 8908946 | AGC
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 106602 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 254240 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 78 | 545568 | -
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 60 | 486624 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 33600 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 746 | 13132819 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 387536 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 827850 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1857 | 38239269
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Plant availability zero, U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 200678 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 54951.36 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1264960 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 222798 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1229760 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 115 | 2973147.36
Eastern Grid Total |  |  |  |  | 17418.042 | 7850.5 | 171286790.94
Western Grid Total |  |  |  |  | 11852.195 | 6356 | 132340007.36
National Grid Total |  |  |  |  | 29270.237 | 14206.5 | 303626798.3
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 31-05-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8628.81 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5116.6 | MW
i) Dhaka area |  |  | 3795.41 |  | MW | i) Khulna area |  |  |  | 1947.5 | MW
ii) Chattogram area |  |  | 1342.4 |  | MW | ii) Barishal area |  |  |  | 528.7 | MW
iii) Cumilla area |  |  | 1566 |  | MW | iii) Rajshahi area |  |  |  | 1609.4 | MW
iv) Mymensingh area |  |  | 1256 |  | MW | iv) Rangpur area |  |  |  | 1031 | MW
v) Sylhet area |  |  | 669 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13745.41 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 72 | 23:00 | 133 | Natore | 167 | 22:00
2 | AKSML | 123 | 12:00 | 68 | Hathazari | 98 | 00:00 | 134 | Nawabganj | 67.6 | 23:00
3 | Aftabnagar | 38 | 23:00 | 69 | Hatirjheel | 27 | 17:00 | 135 | Netrakona | 160 | 19:00
4 | Agargaon | 88 | 23:00 | 70 | Ishurdi | 77 | 22:00 | 136 | New | 42 | 19:00
5 | Agrabad | 54 | 18:30 | 71 | Jaldhaka | 89 | 00:00 | 137 | Niamatpur | 88 | 22:00
6 | Amnura | 32 | 00:00 | 72 | Jamalpur | 132 | 21:00 | 138 | Noapara | 35 | 23:00
7 | Ashuganj | 75 | 14:00 | 73 | Jashore | 165 | 21:00 | 139 | PHP | 8 | 11:00
8 | BSRM | 204 | 05:00 | 74 | Jhenaidah | 116 | 21:00 | 140 | Pabna | 101 | 21:00
9 | Bagerhat | 98 | 21:00 | 75 | Joydebpur | 92 | 23:00 | 141 | Palashbari | 132 | 00:00
10 | Bajitpur | 103 | 19:30 | 76 | Joypurhat | 74 | 22:00 | 142 | Panchagarh | 62 | 20:00
11 | Bakerganj | 18 | 23:00 | 77 | Juldah | 12 | 13:00 | 143 | Patiya | 13 | 00:00
12 | Bakulia | 79 | 00:00 | 78 | KSRM | 10 | 09:00 | 144 | Patuakhali | 83.8 | 23:00
13 | Banani | 32 | 19:00 | 79 | Kabirpur | 96 | 19:30 | 145 | Payra | 42 | 23:00
14 | Bangabhaban | 4 | 10:00 | 80 | Kachua | 114 | 22:00 | 146 | Postogola | 49 | 23:00
15 | Barapukuria | 68 | 22:00 | 81 | Kaliganj | 27 | 21:00 | 147 | Pubail | 22 | 21:00
16 | Barguna | 28 | 23:00 | 82 | Kallyanpur | 105 | 23:00 | 148 | Purbachal | 28 | 22:00
17 | Barishal | 106 | 23:00 | 83 | Kalurghat | 27 | 00:00 | 149 | Purbasadipur | 134 | 23:00
18 | Barishal-230 | 112 | 23:00 | 84 | Kamrangirchar | 39 | 00:00 | 150 | Rahanpur | 45 | 21:00
19 | Baroaulia | 57 | 21:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 1 | 00:00
20 | Baroirhat | 67 | 19:30 | 86 | Kasba | 44 | 21:00 | 152 | Rajbari | 92 | 22:00
21 | Bashundhara | 148 | 23:00 | 87 | Kazla | 72 | 23:00 | 153 | Rajendrapur | 109 | 21:00
22 | BashundharaCement | 1 | 08:00 | 88 | Keranigonj | 71 | 23:00 | 154 | Rajshahi | 132 | 23:00
23 | Beanibazar | 86 | 20:00 | 89 | Khagrachori | 30 | 00:00 | 155 | Rajshahi-230 | 82 | 21:00
24 | Benapole | 73 | 23:00 | 90 | Khulna | 63 | 00:00 | 156 | Ramganj | 124 | 19:00
25 | Bhaluka | 144 | 19:30 | 91 | Khulshi | 164 | 19:00 | 157 | Rampur | 42 | 00:00
26 | Bhandaria | 71 | 23:00 | 92 | Kishoreganj | 150 | 19:00 | 158 | Rangamati | 15 | 12:00
27 | Bhangura | 45 | 19:30 | 93 | Kodda | 149 | 19:00 | 159 | Rangpur | 140 | 20:00
28 | Bheramara(GK) | 72 | 23:00 | 94 | Kulaura | 58 | 19:00 | 160 | Ruppur | 4.2 | 10:00
29 | Bhulta | 133 | 19:30 | 95 | Kurigram | 66 | 19:30 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 70 | 19:30 | 96 | Kushtia | 139 | 21:00 | 162 | Saidpur | 96 | 21:00
31 | Bogura | 180 | 23:00 | 97 | Laksam | 25 | 20:00 | 163 | Santhia | 40 | 19:30
32 | Borhanuddin | 100 | 00:00 | 98 | Lakshmipur | 46 | 23:00 | 164 | Satkhira | 154 | 21:00
33 | Brahmanbaria | 152 | 21:00 | 99 | Lalbag | 29 | 09:00 | 165 | Satmasjid | 80 | 23:00
34 | Cantonment | 100 | 23:00 | 100 | Lalmonirhat | 76 | 19:30 | 166 | Savar | 112 | 22:00
35 | Chandina | 22 | 22:00 | 101 | MI_Cement | 1.1 | 14:00 | 167 | SevenRings | 0.64 | 17:00
36 | Chandpur | 96 | 22:00 | 102 | Madanganj | 26 | 22:00 | 168 | ShahCement | 12 | 00:00
37 | Chandraghona | 36 | 00:00 | 103 | Madaripur | 133 | 22:00 | 169 | Shahjadpur | 97 | 23:00
38 | Chapai | 73 | 21:00 | 104 | Madartek | 73 | 23:00 | 170 | Shahjibazar | 128 | 23:00
39 | Charsaidpur | 11 | 16:00 | 105 | Madunaghat | 53 | 00:00 | 171 | Shahmirpur | 49 | 20:00
40 | Chauddagram | 88 | 23:00 | 106 | Magura | 74 | 22:00 | 172 | Shariatpur | 112 | 23:00
41 | Chhatak | 43 | 19:00 | 107 | Mahasthangarh | 88 | 00:00 | 173 | Sherpur | 170 | 19:30
42 | Chowmuhani | 168 | 19:30 | 108 | Maijdee | 47 | 00:00 | 174 | Shikalbaha | 31 | 00:00
43 | Chuadanga | 131 | 23:00 | 109 | Manikganj | 121 | 21:00 | 175 | Shitalakhya | 56.6 | 15:00
44 | Coxsbazar | 143 | 21:00 | 110 | Maniknagar | 52 | 23:00 | 176 | Sholosohor | 35 | 00:00
45 | Cumilla(N) | 126 | 22:00 | 111 | Matarbari | 58 | 22:00 | 177 | Shomvuganj | 24 | 20:00
46 | Cumilla(S) | 174 | 23:00 | 112 | Matuail | 42 | 22:00 | 178 | Shyampur | 55 | 00:00
47 | Daganbhuiyan | 41 | 22:00 | 113 | Metrorail_Motijheel | 16 | 14:00 | 179 | Siddhirganj | 79 | 23:00
48 | Daudkandi | 134 | 22:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 118 | 23:00
49 | DhakaUniversity | 30 | 13:00 | 115 | Millgate | 44 | 23:00 | 181 | Sonargaon | 71 | 23:00
50 | Dhamrai | 78 | 21:00 | 116 | Mirpur | 116 | 19:00 | 182 | Sreemongol | 88 | 22:00
51 | Dhanmondi | 54 | 19:00 | 117 | Mirsorai | 10 | 23:00 | 183 | Sreepur | 63 | 21:00
52 | Dohazari | 114 | 01:00 | 118 | Mirzapur | 46 | 21:00 | 184 | Srinagar | 55.6 | 22:00
53 | Faridpur | 174 | 22:00 | 119 | Mithapukur | 70 | 19:30 | 185 | Sunamganj | 65 | 21:00
54 | Fatullah | 47 | 23:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 75 | 19:00
55 | Fenchuganj | 48 | 00:00 | 121 | Mogbazar | 59.1 | 21:00 | 187 | Sylhet-132 | 104 | 19:30
56 | Feni | 124 | 23:00 | 122 | Mongla | 26 | 19:00 | 188 | TK | 25 | 00:00
57 | GPH | 1 | 00:00 | 123 | Motijheel | 32 | 23:00 | 189 | Tangail | 178 | 21:00
58 | Ghatail | 103 | 19:30 | 124 | Muktagacha | 42 | 19:00 | 190 | Taraganj | 24 | 21:00
59 | Ghorashal | 1 | 00:00 | 125 | Munshiganj | 122 | 23:00 | 191 | Tasnim | 12 | 19:30
60 | Ghorashal-230 | 69 | 00:00 | 126 | Muradnagar | 56 | 20:00 | 192 | Thakurgaon | 118 | 20:00
61 | Goalpara | 42 | 00:00 | 127 | Mymensingh | 176 | 19:30 | 193 | Tongi | 80 | 23:00
62 | Gollamari | 102 | 23:00 | 128 | Nabinagar | 60 | 00:00 | 194 | Ullahpara | 43 | 22:00
63 | Gopalganj | 129 | 22:00 | 129 | Naogaon | 150 | 23:00 | 195 | Ullon | 54 | 19:00
64 | Gulshan | 78 | 15:00 | 130 | Narail | 66 | 23:00 | 196 | Uttara | 73 | 21:00
65 | Halishahar | 59.5 | 21:00 | 131 | Narinda | 39 | 20:00 | 197 | UttaraNew | 46 | 23:00
66 | HaripurSBU | 48 | 21:00 | 132 | Narshingdi | 158 | 22:00 | 198 | Zigatola | 72 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 31-05-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13623 | 67 |  | 13693.02
1:00 | 13300 | 35 |  | 13337
2:00 | 12999 | 35 |  | 13036
3:00 | 12641 | 25 |  | 12667
4:00 | 12408 | 15 |  | 12424
5:00 | 12128 | 5 |  | 12133
6:00 | 11426.78 | 0 |  | 11426.78
7:00 | 11391.23 | 0 |  | 11391.23
8:00 | 11325.2 | 0 |  | 11325.2
9:00 | 11255.85 | 0 |  | 11255.85
10:00 | 11105.13 | 0 |  | 11105.13
11:00 | 11225.75 | 0 |  | 11225.75
12:00 | 11716.03 | 0 |  | 11716.03
13:00 | 12280.1 | 0 |  | 12280.1
14:00 | 12533.63 | 0 |  | 12533.63
15:00 | 12473.11 | 0 |  | 12473.11
16:00 | 12207.3 | 0 |  | 12207.3
17:00 | 11776.76 | 0 |  | 11776.76
18:00 | 11450.79 | 0 |  | 11450.79
19:00 | 13112.5 | 0 |  | 13112.5
19:30 | 13427.5 | 191 |  | 13627.5
20:00 | 13830.5 | 92 |  | 13926.5
21:00 | 14206.5 | 47 |  | 14255.5
22:00 | 14450.5 | 163 |  | 14620.5
23:00 | 14513.5 | 157 |  | 14677.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 31-05-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7488 | 6135 | 13623 | DAILY GENERATION CURVE
00:30 | 7428 | 6033.5 | 13461.5
01:00 | 7368 | 5932 | 13300 | 31-05-2026
01:30 | 7321.5 | 5828 | 13149.5
02:00 | 7275 | 5724 | 12999
02:30 | 7180.5 | 5639.5 | 12820
03:00 | 7086 | 5555 | 12641
03:30 | 7090 | 5434.5 | 12524.5
04:00 | 7094 | 5314 | 12408
04:30 | 7067.5 | 5200.5 | 12268
05:00 | 7041 | 5087 | 12128
05:30 | 6807.525 | 4969.865 | 11777.39
06:00 | 6574.05 | 4852.73 | 11426.78
06:30 | 6586.11 | 4822.895 | 11409.005
07:00 | 6598.17 | 4793.06 | 11391.23
07:30 | 6535.965 | 4822.25 | 11358.215
08:00 | 6473.76 | 4851.44 | 11325.2
08:30 | 6403.81 | 4886.715 | 11290.525
09:00 | 6333.86 | 4921.99 | 11255.85
09:30 | 6271.605 | 4908.885 | 11180.49
10:00 | 6209.35 | 4895.78 | 11105.13
10:30 | 6256.225 | 4909.215 | 11165.44
11:00 | 6303.1 | 4922.65 | 11225.75
11:30 | 6532.515 | 4938.375 | 11470.89
12:00 | 6761.93 | 4954.1 | 11716.03
12:30 | 6965.955 | 5032.11 | 11998.065
13:00 | 7169.98 | 5110.12 | 12280.1
13:30 | 7202.48 | 5204.385 | 12406.865
14:00 | 7234.98 | 5298.65 | 12533.63
14:30 | 7228.82 | 5274.55 | 12503.37
15:00 | 7222.66 | 5250.45 | 12473.11
15:30 | 7075.095 | 5265.11 | 12340.205
16:00 | 6927.53 | 5279.77 | 12207.3
16:30 | 6779.705 | 5212.325 | 11992.03
17:00 | 6631.88 | 5144.88 | 11776.76
17:30 | 6578.145 | 5035.63 | 11613.775
18:00 | 6524.41 | 4926.38 | 11450.79
18:30 | 7075.455 | 5206.19 | 12281.645
19:00 | 7626.5 | 5486 | 13112.5
19:30 | 7537.5 | 5890 | 13427.5
20:00 | 7713.5 | 6117 | 13830.5
20:30 | 7782 | 6236.5 | 14018.5 |  | Executive Engineer
21:00 | 7850.5 | 6356 | 14206.5 |  | Network Operation Division
21:30 | 7879.5 | 6449 | 14328.5
22:00 | 7908.5 | 6542 | 14450.5
22:30 | 7965.5 | 6516.5 | 14482
23:00 | 8022.5 | 6491 | 14513.5

## En-Curve
QF-LDC-12
Date | 31-05-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 4342 | 2181 | 900 | 0 | 166 | 701 | 70 | 4381 | 0 | 216 | 666 | 0 | 0 | 0 | 67 | DAILY ENERGY CURVE
00:30 | 4329 | 2226.5 | 900 | 0 | 164 | 680 | 70 | 4332.5 | 0 | 203.5 | 556 | 0 | 0 | 0 | 51 | 31-05-2026
01:00 | 4316 | 2272 | 900 | 0 | 162 | 659 | 70 | 4284 | 0 | 191 | 446 | 0 | 0 | 0 | 35
01:30 | 4305.5 | 2316 | 915 | 0 | 160 | 642 | 70 | 4193 | 0 | 166.5 | 381.5 | 0 | 0 | 0 | 35 | Energy Generated | 303.6268 |  | MKWHr
02:00 | 4295 | 2360 | 930 | 0 | 158 | 625 | 70 | 4102 | 0 | 142 | 317 | 0 | 0 | 0 | 35 | Energy not Served | 0.641 |  | MKWHr
02:30 | 4304.5 | 2350 | 930.5 | 0 | 155 | 611 | 70 | 4008.5 | 0 | 123.5 | 267 | 0 | 0 | 0 | 30 | Total Energy Requirement | 304.2678 |  | MKWHr
03:00 | 4314 | 2340 | 931 | 0 | 152 | 597 | 70 | 3915 | 0 | 105 | 217 | 0 | 0 | 0 | 25
03:30 | 4300 | 2382 | 931 | 0 | 151 | 581 | 70 | 3809 | 0 | 105 | 195.5 | 0 | 0 | 0 | 20
04:00 | 4286 | 2424 | 931 | 0 | 150 | 565 | 70 | 3703 | 0 | 105 | 174 | 0 | 0 | 0 | 15
04:30 | 4257 | 2458 | 931 | 0 | 147 | 552 | 70 | 3574 | 0 | 105 | 174 | 0 | 0 | 0 | 10
05:00 | 4228 | 2492 | 931 | 0 | 144 | 539 | 70 | 3445 | 0 | 105 | 174 | 0 | 0 | 0 | 5
05:30 | 4059 | 2440 | 931 | 0 | 140 | 513.5 | 70 | 3331 | 23.39 | 95.5 | 174 | 0 | 0 | 0 | 2.5
06:00 | 3890 | 2388 | 931 | 0 | 136 | 488 | 70 | 3217 | 46.78 | 86 | 174 | 0 | 0 | 0 | 0
06:30 | 3898 | 2384 | 931 | 0 | 134 | 461 | 70 | 3181 | 109.505 | 77 | 158.5 | 0 | 0 | 5 | 0
07:00 | 3906 | 2380 | 931 | 0 | 132 | 434 | 70 | 3145 | 172.23 | 68 | 143 | 0 | 0 | 10 | 0
07:30 | 3894 | 2330 | 931.5 | 0 | 129 | 425.5 | 70 | 3082 | 275.215 | 70.5 | 143.5 | 0 | 0 | 7 | 0
08:00 | 3882 | 2280 | 932 | 0 | 126 | 417 | 70 | 3019 | 378.2 | 73 | 144 | 0 | 0 | 4 | 0
08:30 | 3869 | 2240.5 | 931.5 | 0 | 127 | 416.5 | 70 | 2955 | 433.525 | 79.5 | 166 | 0 | 0 | 2 | 0
09:00 | 3856 | 2201 | 931 | 0 | 128 | 416 | 70 | 2891 | 488.85 | 86 | 188 | 0 | 0 | 0 | 0
09:30 | 3855 | 2195.5 | 931.5 | 0 | 129 | 416 | 70 | 2794 | 512.49 | 86 | 191 | 0 | 0 | 0 | 0
10:00 | 3854 | 2190 | 932 | 0 | 130 | 416 | 70 | 2697 | 536.13 | 86 | 194 | 0 | 0 | 0 | 0
10:30 | 3905 | 2227 | 931.5 | 0 | 133 | 416.5 | 70 | 2668.5 | 573.44 | 77 | 163.5 | 0 | 0 | 0 | 0
11:00 | 3956 | 2264 | 931 | 0 | 136 | 417 | 70 | 2640 | 610.75 | 68 | 133 | 0 | 0 | 0 | 0
11:30 | 4095.5 | 2382 | 931 | 0 | 137 | 419.5 | 70 | 2645.5 | 589.39 | 68 | 133 | 0 | 0 | 0 | 0
12:00 | 4235 | 2500 | 931 | 0 | 138 | 422 | 70 | 2651 | 568.03 | 68 | 133 | 0 | 0 | 0 | 0
12:30 | 4363 | 2571.5 | 931 | 0 | 146 | 441.5 | 70 | 2718.5 | 572.565 | 68 | 116 | 0 | 0 | 0 | 0
13:00 | 4491 | 2643 | 931 | 0 | 154 | 461 | 70 | 2786 | 577.1 | 68 | 99 | 0 | 0 | 0 | 0
13:30 | 4534.5 | 2611 | 931 | 0 | 153 | 469.5 | 70 | 2903.5 | 568.865 | 66.5 | 99 | 0 | 0 | 0 | 0
14:00 | 4578 | 2579 | 931 | 0 | 152 | 478 | 70 | 3021 | 560.63 | 65 | 99 | 0 | 0 | 0 | 0
14:30 | 4516.5 | 2594.5 | 931 | 0 | 151 | 479.5 | 66.5 | 3091 | 502.37 | 66.5 | 104 | 0 | 0 | 0.5 | 0
15:00 | 4455 | 2610 | 931 | 0 | 150 | 481 | 63 | 3161 | 444.11 | 68 | 109 | 0 | 0 | 1 | 0
15:30 | 4341.5 | 2509 | 931 | 0 | 150 | 478.5 | 65.5 | 3272.5 | 389.705 | 68 | 134 | 0 | 0 | 0.5 | 0
16:00 | 4228 | 2408 | 931 | 0 | 150 | 476 | 68 | 3384 | 335.3 | 68 | 159 | 0 | 0 | 0 | 0
16:30 | 4226.5 | 2283.5 | 931 | 0 | 146 | 457 | 68.5 | 3404 | 244.28 | 68 | 163.25 | 0 | 0 | 0 | 0
17:00 | 4225 | 2159 | 931 | 0 | 142 | 438 | 69 | 3424 | 153.26 | 68 | 167.5 | 0 | 0 | 0 | 0
17:30 | 4207 | 2132.5 | 931 | 0 | 141 | 421 | 69.5 | 3374.5 | 95.775 | 68 | 170.5 | 0 | 0 | 3 | 0
18:00 | 4189 | 2106 | 931 | 0 | 140 | 404 | 70 | 3325 | 38.29 | 68 | 173.5 | 0 | 0 | 6 | 0
18:30 | 4266 | 2223.5 | 931 | 0 | 154 | 487 | 70 | 3578.5 | 19.145 | 176 | 369 | 0 | 0 | 7.5 | 0
19:00 | 4343 | 2341 | 931 | 0 | 168 | 570 | 70 | 3832 | 0 | 284 | 564.5 | 0 | 0 | 9 | 0
19:30 | 3736 | 2215 | 931 | 0 | 164 | 694 | 70 | 4011 | 0 | 327 | 1274.5 | 0 | 0 | 5 | 191
20:00 | 3743 | 2253 | 931 | 0 | 164 | 754 | 70 | 4197 | 0 | 339 | 1374.5 | 0 | 0 | 5 | 92
20:30 | 3735 | 2250.5 | 931 | 0 | 167 | 750 | 70 | 4278 | 0 | 338 | 1493.5 | 0 | 0 | 5.5 | 69.5
21:00 | 3727 | 2248 | 931 | 0 | 170 | 746 | 70 | 4359 | 0 | 337 | 1612.5 | 0 | 0 | 6 | 47
21:30 | 3796.5 | 2290 | 931 | 0 | 171 | 749.5 | 70 | 4376.5 | 0 | 334.5 | 1606 | 0 | 0 | 3.5 | 105
22:00 | 3866 | 2332 | 931 | 0 | 172 | 753 | 70 | 4394 | 0 | 332 | 1599.5 | 0 | 0 | 1 | 163
22:30 | 3867 | 2300.5 | 931 | 0 | 173 | 749.5 | 70 | 4327.5 | 0 | 332 | 1728 | 0 | 0 | 3.5 | 160
23:00 | 3868 | 2269 | 931 | 0 | 174 | 746 | 70 | 4261 | 0 | 332 | 1856.5 | 0 | 0 | 6 | 157
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 31-05-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 11 | -44 | 232 | 110 | 766 | -108 | Ishurdi-Ghorashal Ckt-1 | Export | 879854.55
1:00 | 7 | -40 | 214 | 116 | 680 | -86
2:00 | 9 | -42 | 204 | 96 | 610 | -86 |  | Import | 0
3:00 | 10 | -41 | 210 | 106 | 562 | -66
4:00 | 10 | -37 | 202 | 106 | 472 | -54 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 12 | -35 | 188 | 92 | 356 | -32
6:00 | 28 | -33 | 224 | 90 | 362 | -16 |  | Import | 0
7:00 | 22 | -34 | 196 | 84 | 302 | -22
8:00 | 44 | -33 | 260 | 112 | 388 | -14 | Sirajganj-Sreepur Ckt-1 | Export | 1414000
9:00 | 44 | -33 | 284 | 102 | 474 | -18
10:00 | 67 | -33 | 292 | 94 | 538 | -8 |  | Import | 0
11:00 | 69 | -34 | 296 | 94 | 520 | 8
12:00 | 61 | -32 | 294 | 102 | 426 | 18 | Sirajganj-Sreepur Ckt-2 | Export | 1416000
13:00 | 55 | -37 | 298 | 112 | 418 | -2
14:00 | 45 | -38 | 246 | 94 | 440 | -24 |  | Import | 0
15:00 | 42 | -36 | 260 | 112 | 460 | -26
16:00 | 51 | -35 | 292 | 118 | 636 | -22 | Gopalganj-Aminbazar Ckt-1 | Export | 6700000
17:00 | 52 | -33 | 288 | 108 | 688 | -8
18:00 | 46 | -32 | 270 | 104 | 586 | -2 |  | Import | 0
18:30 | 50 | -31 | 300 | 108 | 648 | 24
19:00 | 29 | -36 | 280 | 128 | 496 | 0 | Gopalganj-Aminbazar Ckt-2 | Export | 6690000
19:30 | 0 | -10 | 216 | 102 | 562 | -68
20:00 | 0 | -10 | 218 | 102 | 702 | -74 |  | Import | 0
21:00 | 1 | -53 | 254 | 140 | 796 | -70
22:00 | 0 | -10 | 258 | 122 | 650 | -62 |  | Total Export | 17099854.55
23:00 | 57 | -9 | 208 | 100 | 718 | -96 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 31-05-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 408 | 10:00 | 396 | 00:00 | Madunaghat | 402 | 09:00 | 395 | 03:00
Amtali | 419 | 18:30 | 407 | 01:00 | Meghnaghat | 410 | 10:00 | 400 | 01:00
Ashuganj | 421 | 7:00 | 409 | 21:00 | Payra | 419 | 10:00 | 410 | 01:00
Bhulta | 413 | 07:00 | 402 | 21:00 | Rahanpur | 403 | 10:00 | 386 | 20:00
Bibiana | 412 | 10:00 | 402 | 00:00 | Rampal | 410 | 10:00 | 395 | 00:00
BIPTC | 398 | 08:00 | 387 | 23:00
Bogura | 391 | 10:00 | 372 | 00:00
Gopalganj | 409 | 10:00 | 396 | 00:00
Kaliakoir | 408 | 10:00 | 396 | 00:00
Korerhat | 407 | 10:00 | 398 | 01:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 237 | 10:00 | 230 | 00:00 | Jhenaidah | 230 | 10:00 | 214 | 23:00
AKSML | 234.8 | 10:00 | 227.9 | 02:00 | Kachua | 228 | 07:00 | 222 | 00:00
Aminbazar | 237 | 10:00 | 230 | 00:00 | Kaliakoir | 234 | 06:00 | 229 | 00:00
Ashuganj | 235 | 07:00 | 227 | 21:00 | Keranigonj | 236 | 10:00 | 229 | 00:00
Ashuganj-400 | 235 | 07:00 | 227 | 21:00 | Khulna(S) | 235 | 10:00 | 222 | 00:00
Baghabari | 236 | 09:00 | 226 | 00:00 | Korerhat | 231 | 08:00 | 224 | 01:00
Barapukuria | 221 | 06:00 | 198 | 20:00 | Madunaghat | 234 | 08:00 | 229 | 04:00
Barapukuria-230 | 221 | 06:00 | 198 | 20:00 | Madunaghat-400 | 235 | 09:00 | 230 | 03:00
Barishal | 235 | 10:00 | 226 | 00:00 | Maniknagar | 238 | 06:00 | 232 | 00:00
Bheramara | 233 | 09:00 | 221 | 00:00 | Meghnaghat | 242 | 04:00 | 237 | 22:00
Bhulta | 239 | 10:00 | 232 | 00:00 | Meghnaghat-400 | 239 | 07:00 | 232 | 00:00
Bibiana | 237 | 10:00 | 230 | 00:00 | Mirsorai | 234 | 10:00 | 227 | 02:00
BIPTC | 237 | 09:00 | 222 | 00:00 | Naogaon | 217 | 18:00 | 201 | 20:00
Bogura | 241 | 10:00 | 228 | 20:00 | Purbasadipur | 218 | 06:00 | 195 | 20:00
Bogura-400 | 240 | 10:00 | 227 | 20:00 | Rajshahi | 232 | 06:00 | 217 | 00:00
Borhanuddin | 236 | 11:00 | 230 | 00:00 | Rampal | 234 | 09:00 | 221 | 00:00
BSRM | 230 | 06:00 | 224 | 01:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 229 | 10:00 | 222 | 00:00 | Rampura | 238 | 07:00 | 231 | 00:00
Cumilla(N) | 233 | 06:00 | 227 | 00:00 | Shikalbaha | 235 | 19:30 | 228 | 01:00
Faridpur | 235 | 10:00 | 224 | 00:00 | Shyampur | 237 | 06:00 | 231 | 00:00
Fenchuganj | 238 | 07:00 | 230 | 00:00 | Siddhirganj | 240 | 07:00 | 234 | 00:00
Feni | 229 | 06:00 | 223 | 01:00 | Sirajgonj | 241 | 06:00 | 235 | 02:00
Ghorashal | 240 | 01:00 | 235 | 00:00 | Sreepur | 231 | 12:00 | 224 | 00:00
Ghorashal-230 | 237 | 21:00 | 218 | 23:00 | Tongi | 235 | 07:00 | 227 | 18:30
Gopalganj | 236 | 10:00 | 227 | 00:00
GPH | 233 | 10:00 | 228 | 01:00
Haripur | 239 | 10:00 | 233 | 00:00
Hasnabad | 237 | 08:00 | 231 | 00:00
Hathazari | 232 | 06:00 | 228 | 00:00
Ishurdi | 237 | 10:00 | 225 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 06:00 | 123 | 10:00 | Madunaghat | 136 | 10:00 | 132 | 02:00
Agargaon | 133 | 06:00 | 130 | 00:00 | Magura | 133 | 06:00 | 120 | 23:00
Agrabad | 136 | 19:30 | 130 | 03:00 | Mahasthangarh | 135 | 10:00 | 123 | 00:00
AKS | 134 | 19:30 | 130 | 00:00 | Maijdee | 127 | 08:00 | 123 | 00:00
Aminbazar | 137 | 06:00 | 133 | 00:00 | Manikganj | 132 | 10:00 | 126 | 01:00
Amnura | 134 | 09:00 | 124 | 20:00 | Maniknagar | 134 | 08:00 | 130 | 00:00
Ashuganj | 140 | 06:00 | 135 | 00:00 | Matarbari | 125 | 19:30 | 111 | 22:00
Ashuganj-230 | 140 | 06:00 | 135 | 00:00 | Matuail | 137 | 10:00 | 133 | 00:00
Bagerhat | 131 | 10:00 | 117 | 00:00 | Metrorail_Motijheel | 134 | 08:00 | 130 | 00:00
Bajitpur | 128 | 06:00 | 121 | 21:00 | Metrorail_Uttara | 133 | 05:00 | 128 | 00:00
Bakerganj | 133 | 10:00 | 125 | 00:00 | Millgate | 133 | 06:00 | 128 | 19:30
Bakulia | 136 | 06:00 | 131 | 00:00 | Mirpur | 136 | 06:00 | 133 | 00:00
Banani | 134 | 08:00 | 130 | 21:00 | Mirzapur | 132 | 10:00 | 125 | 00:00
Bangabhaban | 134 | 06:00 | 130 | 00:00 | Mithapukur | 131 | 10:00 | 117 | 20:00
Barapukuria | 134 | 18:30 | 116 | 20:00 | MI_Cement | 137 | 10:00 | 132 | 00:00
Barguna | 133 | 09:00 | 127 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 135 | 09:00 | 129 | 00:00 | Mogbazar | 135 | 08:00 | 132 | 20:00
Barishal-230 | 135 | 10:00 | 128 | 00:00 | Mongla | 131 | 10:00 | 119 | 00:00
Baroaulia | 136 | 19:30 | 131 | 13:00 | Motijheel | 134 | 06:00 | 130 | 00:00
Baroirhat | 134 | 09:00 | 130 | 00:00 | Muktagacha | 129 | 10:00 | 119 | 00:00
Bashundhara | 134 | 05:00 | 128 | 19:30 | Munshiganj | 135 | 10:00 | 131 | 00:00
BashundharaCement | 138 | 15:00 | 132 | 00:00 | Muradnagar | 131 | 07:00 | 126 | 00:00
Beanibazar | 126 | 11:00 | 115 | 00:00 | Mymensingh | 129 | 10:00 | 110 | 00:00
Benapole | 129 | 10:00 | 115 | 23:00 | Nabinagar | 128 | 10:00 | 122 | 00:00
Bhaluka | 126 | 04:00 | 119 | 21:00 | Naogaon | 136 | 10:00 | 121 | 00:00
Bhandaria | 129 | 10:00 | 120 | 00:00 | Narail | 134 | 09:00 | 119 | 23:00
Bhangura | 135 | 09:00 | 127 | 20:00 | Narinda | 134 | 08:00 | 130 | 00:00
Bheramara | 137 | 10:00 | 131 | 00:00 | Narshingdi | 134 | 06:00 | 128 | 00:00
Bheramara(GK) | 137 | 08:00 | 131 | 00:00 | Natore | 134 | 09:00 | 125 | 00:00
Bhulta | 133 | 10:00 | 128 | 00:00 | Nawabganj | 132 | 06:00 | 127 | 00:00
Bog-Sherpur | 136 | 10:00 | 128 | 20:00 | Netrakona | 115 | 11:00 | 104 | 00:00
Bogura | 137 | 10:00 | 129 | 19:30 | New | 134 | 06:00 | 129 | 19:30
Bogura-230 | 138 | 10:00 | 130 | 00:00 | Niamatpur | 132 | 10:00 | 123 | 00:00
Brahmanbaria | 134 | 07:00 | 127 | 00:00 | Noapara | 132 | 10:00 | 120 | 23:00
Cantonment | 133 | 06:00 | 129 | 00:00 | Pabna | 134 | 06:00 | 126 | 01:00
Chandina | 134 | 10:00 | 129 | 00:00 | Palashbari | 129 | 10:00 | 113 | 20:00
Chandpur | 127 | 19:30 | 122 | 01:00 | Panchagarh | 139 | 06:00 | 124 | 20:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 137 | 19:30 | 133 | 01:00 | Patiya | 136 | 19:30 | 127 | 04:00
Chapai | 131 | 09:00 | 125 | 23:00 | Patuakhali | 134 | 09:00 | 130 | 00:00
Charsaidpur | 136 | 08:00 | 132 | 00:00 | Payra | 137 | 09:00 | 133 | 00:00
Chauddagram | 131 | 06:00 | 127 | 00:00 | PHP | 133 | 09:00 | 129 | 00:00
Chhatak | 125 | 11:00 | 110 | 00:00 | Postogola | 138 | 06:00 | 134 | 00:00
Chowmuhani | 128 | 09:00 | 124 | 00:00 | Pubail | 140 | 06:00 | 130 | 20:00
Chuadanga | 133 | 10:00 | 115 | 23:00 | Purbachal | 134 | 06:00 | 128 | 19:30
Coxsbazar | 125 | 19:30 | 113 | 22:00 | Purbasadipur | 132 | 06:00 | 118 | 20:00
Cumilla(N) | 134 | 10:00 | 129 | 00:00 | Rahanpur | 133 | 10:00 | 127 | 00:00
Cumilla(S) | 133 | 07:00 | 119 | 19:00 | Rahanpur-400 | 133 | 09:00 | 127 | 00:00
Daganbhuiyan | 130 | 10:00 | 126 | 00:00 | Rahim | 136 | 06:00 | 133 | 00:00
Daudkandi | 130 | 03:00 | 125 | 21:00 | Rajbari | 133 | 10:00 | 125 | 00:00
DhakaUniversity | 134 | 05:00 | 131 | 00:00 | Rajendrapur | 128 | 06:00 | 121 | 22:00
Dhamrai | 128 | 08:00 | 123 | 00:00 | Rajshahi | 132 | 06:00 | 123 | 00:00
Dhanmondi | 137.5 | 10:00 | 134 | 00:00 | Rajshahi-230 | 134 | 10:00 | 125 | 00:00
Dohazari | 129 | 09:00 | 125 | 14:00 | Ramganj | 124 | 19:30 | 119 | 01:00
Faridpur | 135 | 08:00 | 128 | 00:00 | Rampur | 136 | 19:30 | 130 | 13:00
Fatullah | 137 | 06:00 | 132 | 00:00 | Rampura | 134 | 06:00 | 130 | 00:00
Fenchuganj | 134 | 07:00 | 127 | 00:00 | Rangamati | 136 | 19:30 | 131 | 02:00
Feni | 130 | 07:00 | 127 | 00:00 | Rangpur | 132 | 18:00 | 116 | 20:00
Feni-230 | 131 | 06:00 | 128 | 00:00 | Ruppur | 138 | 10:00 | 131 | 00:00
Ghatail | 127 | 18:30 | 118 | 00:00 | Saidpur | 134 | 18:00 | 119 | 00:00
Ghorashal | 141 | 06:00 | 136 | 19:00 | Santhia | 136 | 09:00 | 129 | 00:00
Goalpara | 134 | 10:00 | 124 | 13:00 | Satkhira | 128 | 10:00 | 114 | 23:00
Gollamari | 134 | 10:00 | 124 | 01:00 | Satmasjid | 133 | 07:00 | 129 | 00:00
Gopalganj | 133 | 09:00 | 125 | 22:00 | Savar | 136 | 19:00 | 132 | 00:00
Gopalganj-400 | 137 | 10:00 | 131 | 00:00 | SevenRings | 141 | 06:00 | 137 | 13:00
Gulshan | 134 | 07:00 | 130 | 00:00 | ShahCement | 136 | 08:00 | 132 | 00:00
Halishahar | 137 | 19:30 | 131 | 03:00 | Shahjadpur | 136 | 02:00 | 131 | 21:00
Haripur | 137 | 10:00 | 133 | 00:00 | Shahjibazar | 134 | 10:00 | 126 | 00:00
HaripurSBU | 136 | 07:00 | 133 | 00:00 | Shahmirpur | 137 | 19:30 | 131 | 13:00
Hasnabad | 138 | 10:00 | 134 | 21:00 | Shariatpur | 133 | 10:00 | 125 | 00:00
Hathazari | 136 | 20:00 | 133 | 00:00 | Sherpur | 122 | 11:00 | 109 | 00:00
Hatirjheel | 134 | 06:00 | 131 | 00:00 | Shikalbaha | 124 | 00:00 | 122 | 06:00
Ishurdi | 139 | 10:00 | 132 | 00:00 | Shikalbaha-230 | 137 | 19:30 | 130 | 04:00
Jaldhaka | 128 | 10:00 | 111 | 20:00 | Shitalakhya | 137 | 10:00 | 132 | 00:00
Jamalpur | 127 | 18:30 | 114 | 00:00 | Sholosohor | 136 | 19:30 | 132 | 01:00
Jashore | 131 | 10:00 | 117 | 23:00 | Shomvuganj | 120 | 07:00 | 113 | 19:00
Jhenaidah | 135 | 09:00 | 123 | 23:00 | Shyampur | 135 | 01:00 | 132 | 00:00
Jhenaidah-230 | 135 | 06:00 | 124 | 23:00 | Shyampur-230 | 137 | 10:00 | 133 | 00:00
Joydebpur | 137 | 04:00 | 130 | 21:00 | Siddhirganj | 137 | 06:00 | 134 | 00:00
Joypurhat | 132 | 10:00 | 122 | 00:00 | Sirajganj | 133 | 18:00 | 125 | 00:00
Juldah | 135 | 19:30 | 132 | 01:00 | Sonargaon | 135 | 07:00 | 132 | 00:00
Kabirpur | 134 | 09:00 | 127 | 16:00 | Sreemongol | 133 | 11:00 | 125 | 00:00
Kachua | 129 | 07:00 | 125 | 00:00 | Sreepur | 130 | 06:00 | 124 | 19:00
Kaliakoir | 137 | 10:00 | 126 | 00:00 | Srinagar | 132 | 06:00 | 128 | 00:00
Kaliganj | 134 | 09:00 | 122 | 23:00 | SSM | 136 | 00:00 | 136 | 00:00
Kallyanpur | 136 | 03:00 | 134 | 13:00 | Sunamganj | 122 | 11:00 | 108 | 00:00
Kalurghat | 136 | 10:00 | 132 | 02:00 | Sylhet | 128 | 12:00 | 118 | 00:00
Kamrangirchar | 136 | 06:00 | 129 | 00:00 | Sylhet-132 | 128 | 11:00 | 118 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Tangail | 128 | 10:00 | 121 | 00:00
Kasba | 131 | 10:00 | 125 | 00:00 | Taraganj | 132 | 18:00 | 116 | 20:00
Kazla | 134 | 10:00 | 130 | 22:00 | Tasnim | 135 | 07:00 | 130 | 01:00
Keranigonj | 133 | 06:00 | 129 | 00:00 | Thakurgaon | 137 | 06:00 | 121 | 20:00
Khagrachori | 135 | 19:30 | 129 | 04:00 | TK | 135 | 05:00 | 133 | 00:00
Khulna | 133 | 10:00 | 123 | 00:00 | Tongi | 135 | 04:00 | 131 | 18:30
Khulna(S) | 134 | 10:00 | 124 | 00:00 | Ullahpara | 134 | 06:00 | 127 | 00:00
Khulshi | 135 | 19:30 | 130 | 13:00 | Ullon | 134 | 06:00 | 130 | 00:00
Kishoreganj | 125 | 06:00 | 118 | 00:00 | Uttara | 132 | 06:00 | 127 | 21:00
Kodda | 131 | 08:00 | 127 | 01:00 | UttaraNew | 133 | 05:00 | 128 | 00:00
Korerhat | 135 | 07:00 | 132 | 01:00 | Zigatola | 133 | 07:00 | 129 | 00:00
KSRM | 136 | 07:00 | 132 | 02:00
Kulaura | 133 | 07:00 | 125 | 00:00
Kurigram | 127 | 18:30 | 107 | 20:00
Kushtia | 136 | 10:00 | 127 | 23:00
Laksam | 128 | 07:00 | 124 | 00:00
Lakshmipur | 126 | 08:00 | 122 | 00:00
Lalbag | 134 | 10:00 | 129 | 00:00
Lalmonirhat | 127 | 18:00 | 108 | 20:00
Madanganj | 136 | 07:00 | 132 | 00:00
Madaripur | 134 | 08:00 | 128 | 00:00
Madartek | 134 | 06:00 | 130 | 16:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division