## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 04-06-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-06-2026 | during | 04-06-2026 | during | 04-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Under Maintenance
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 402 | 382 | 412 | 412 | 412 | 412 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 160 | 160 | 225 | 225 | 225 | 225 | GT-1 is under maintenance
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 143 | 146 | 335 | 335 | 165 | 165 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35.5 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 90 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 24 | 23 | 33 | 33 | 14 | 14 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 20 | 22 | 22 | 14 | 14 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 33 | 52.19 | 52.19 | 16 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 32 | 97 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 133 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 460 | 440 | 584 | 584 | 570 | 570 | AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 291 | 248 | 718 | 718 | 340 | 340 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 94 | 142 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1861 | 2264.5 | 5824.22 | 5792.22 | 2792.36 | 2920.36
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 1 | 25.5 | 25.5 | 25.5 | 8 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 100 | 100 | 100 | 100 | 100 | 100 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 210 | 215 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 2 | 47 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 25 | 5 | 25 | 38 | 38 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 71 | 108 | 108 | 24 | 60 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.61 | 0 | 1.43 | 0 | 1.43 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 13 | 38 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 16 | 110 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 24 | 24 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 95 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 35 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1160 | 1224 | 1224 | 1204 | 1204 | AGC
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 0 | 1 | 1 | 1 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 565 | 555 | 575 | 1150 | 575 | 1150 | AGC
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2343.61 | 2711.5 | 3419.29 | 4066.86 | 2723.79 | 3499.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 203 | 201 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 290 | 290 | 350.01 | 350.01 | 300 | 300 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 230 | 240 | 342.01 | 342.01 | 240 | 240 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 220 | 230 | 393 | 393 | 230 | 230 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 10 | 10 | 41.65 | 41.65 | 10 | 10 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 10 | 5 | 52.82 | 52.82 | 10 | 10 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 142 | 150 | 150 | 33 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 36 | 40 | 40 | 40 | 40 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 88 | 91 | 163 | 163 | 94 | 94 | ST Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 13 | 122 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 158 | 154 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 12 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 15 | 15 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 20 | 32 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 4 | 27 | 113 | 113 | 27 | 27 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 89 | 115 | 115 | 34 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 38 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1386 | 1791.2 | 2772.44 | 2696.44 | 1854.45 | 1935.45
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-06-2026 | during | 04-06-2026 | during | 04-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 16.82 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 10 | 157.5 | 157.5 | 157.5 | 157.5 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.8 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 114 | 133 | 140 | 140 | 140 | 140 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 28 | 9 | 10 | 10 | 10 | 10 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 37.67 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 208.29 | 169 | 456.2 | 384 | 396.7 | 324.5
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 41 | 30 | 30 | 0 | 0 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 150 | 148 | 163 | 163 | 147 | 147 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 149 | 152 | 150 | 150 | 100 | 100 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 101 | 100 | 100 | 100 | 100 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 24 | 24 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 302 | 282 | 300 | 300 | 260 | 260 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1209 | 1187 | 1273 | 1273 | 1084 | 1084
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 903 | 903 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 31 | 36 | 36 | 36 | 36 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 46 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 192 | 173 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 77 | 105 | 105 | 90 | 90
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 99 | 0 | 100 | 0 | 100 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1215 | 1170 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2409 | 2400 | 3606.2 | 3506.2 | 2787.2 | 2687.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 1107 | 1200 | 1244 | 1244 | 1244 | 1244 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 2 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 123 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 585 | 775 | 1244 | 1244 | 1244 | 1244 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 36 | 150 | 150 | 0 | 35 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 283 | 275 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.73 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2320.73 | 2642 | 3406 | 3405 | 3236 | 3270
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 51.72 | 0 | 60 | 0 | 60 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 32 | 32 | 32 | 32 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 188 | 174 | 220 | 220 | 170 | 170 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 188 | 181 | 220 | 220 | 170 | 170 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 395 | 384 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 101 | 98 | 98 | 0 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 35 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 35 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.8 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1438.03 | 1444.47 | 1435.88 | 1435.88 | 1356 | 1356 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 53 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 101 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2419.55 | 2471.47 | 3020.57 | 2793.87 | 2513.31 | 2336.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 40 | 40 | 45 | 45 | 45 | 45 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 100 | 100 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.9 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 50 | 94 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 20 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 179 | 0 | 180.67 | 0 | 180.67 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 395.9 | 234 | 523.67 | 307 | 489.67 | 273
System Total |  |  |  |  | 28843.2 | 29290.237 | 14553.08 | 15870.67 | 24301.59 | 24224.59 | 17877.48 | 18330.48
Forecast Scenario (04-06-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 16220 |  | 0 |  | 16220
|  |  |  | 1:00 | 15780 |  | 0 |  | 15780
|  |  |  | 2:00 | 15420 |  | 0 |  | 15420
|  |  |  | 3:00 | 15060 |  | 0 |  | 15060
|  |  |  | 4:00 | 14700 |  | 0 |  | 14700
|  |  |  | 5:00 | 14530 |  | 0 |  | 14530
|  |  |  | 6:00 | 13840 |  | 0 |  | 13840
|  |  |  | 7:00 | 13680 |  | 0 |  | 13680
|  |  |  | 8:00 | 13430 |  | 0 |  | 13430
|  |  |  | 9:00 | 13650 |  | 0 |  | 13650
|  |  |  | 10:00 | 14020 |  | 0 |  | 14020
|  |  |  | 11:00 | 14260 |  | 0 |  | 14260
|  |  |  | 12:00 | 14870 |  | 0 |  | 14870
|  |  |  | 13:00 | 15240 |  | 0 |  | 15240
|  |  |  | 14:00 | 15380 |  | 0 |  | 15380
|  |  |  | 15:00 | 15380 |  | 0 |  | 15380
|  |  |  | 16:00 | 15070 |  | 0 |  | 15070
|  |  |  | 17:00 | 14700 |  | 0 |  | 14700
|  |  |  | 18:00 | 14000 |  | 0 |  | 14000
|  |  |  | 18:30 | 14800 |  | 0 |  | 14800
|  |  |  | 19:00 | 15600 |  | 0 |  | 15600
|  |  |  | 19:30 | 16400 |  | 0 |  | 16400
|  |  |  | 20:00 | 16500 |  | 0 |  | 16500
|  |  |  | 21:00 | 16800 |  | 0 |  | 16800
|  |  |  | 22:00 | 16600 |  | 0 |  | 16600
|  |  |  | 23:00 | 16700 |  | 0 |  | 16700
Probable Maximum Temperature: |  |  | 35.00°C
Probable Maximum Demand at Day Peak: |  |  | 14870.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16800.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16800.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 361.43 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:24 hrs on 04-06-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 03-06-2026 | [28 empty] | Date: | 03-06-2026 | [28 empty] | Date: | 03-06-2026 | [28 empty] | Date: | 03-06-2026 | [28 empty] | Date: | 03-06-2026 | [18 empty] | Date: | 03-06-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [18 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 286 | 0 | 0 | 17 | 90 | 147 | 15 | 17 | 54 | 0 | 160 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 20 | 14 | 0 | 470 | 97 | 16 | 65 | 0 | 0 | 50 | 24 | 54.36 | 24 | 24 | 0 | 100 | 109 | 42 | 560 | 0 | 0 | 50 | 0 | 103 | 217 | 0 | 0 | 0 | 1224 | 0 | 13 | 0 | 230 | 290 | 250 | 51 | 10 | 191 | 10 | 64 | 92 | 175 | 0 | 19 | 17 | 170 | 52.2 | 0 | 38 | 315 | 0 | 296 | 29 | 30 | 153 | 0 | 24 | 0 | 85 | 30 | 122 | 0 | 100 | 17 | 9 | 0 | 77 | 27 | 0 | 0 | 0 | 7870.56 | 903 | 206 | 0 | 23 | 37 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1198 | 67 | 0 | 0 | 1452 | 0 | 32 | 0 | 35 | 35 | 0 | 90 | 24 | 52.2 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 183 | 0 | 181 | 0 | 406 | 0 | 0 | 0 | 0 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 307 | 125 | 220 | 0 | 1244 | 622 | 35 | 7940.2 | 15810.76 | 76.05
01:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 259 | 0 | 0 | 17 | 109 | 32 | 15 | 35 | 17 | 0 | 160 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 20 | 14 | 0 | 420 | 94 | 16 | 39 | 0 | 0 | 50 | 24 | 54.36 | 24 | 24 | 0 | 100 | 108 | 42 | 560 | 0 | 0 | 50 | 8 | 98 | 216 | 0 | 0 | 0 | 1224 | 0 | 35 | 0 | 215 | 290 | 250 | 51 | 10 | 194 | 10 | 48 | 92 | 174 | 0 | 19 | 106 | 152 | 52.2 | 0 | 38 | 310 | 0 | 296 | 29 | 30 | 150 | 0 | 16 | 0 | 85 | 30 | 149 | 0 | 100 | 17 | 9 | 0 | 77 | 27 | 0 | 0 | 0 | 7725.56 | 904 | 204 | 0 | 23 | 37 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1197 | 67 | 0 | 0 | 1442 | 0 | 32 | 0 | 35 | 35 | 0 | 0 | 24 | 52.2 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 183 | 0 | 181 | 0 | 381 | 0 | 0 | 0 | 0 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 307 | 123 | 220 | 0 | 1244 | 610 | 35 | 7795.2 | 15520.76 | 76.04
02:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 201 | 0 | 0 | 17 | 109 | 32 | 15 | 35 | 0 | 0 | 160 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 20 | 14 | 0 | 335 | 90 | 16 | 25 | 0 | 1 | 50 | 24 | 54.36 | 24 | 24 | 0 | 100 | 108 | 42 | 560 | 0 | 0 | 50 | 8 | 96 | 217 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 215 | 290 | 230 | 51 | 10 | 188 | 10 | 0 | 93 | 175 | 0 | 19 | 109 | 148 | 52.2 | 0 | 38 | 310 | 0 | 296 | 29 | 30 | 136 | 0 | 0 | 0 | 85 | 30 | 148 | 0 | 100 | 17 | 9 | 0 | 77 | 27 | 0 | 0 | 0 | 7458.56 | 903 | 204 | 0 | 23 | 37 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1196 | 67 | 0 | 0 | 1446 | 0 | 32 | 0 | 35 | 35 | 0 | 0 | 24 | 52.2 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 183 | 0 | 181 | 0 | 328 | 0 | 0 | 0 | 0 | 95 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 307 | 123 | 220 | 0 | 1244 | 610 | 17 | 7704.2 | 15162.76 | 76.04
03:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 205 | 0 | 0 | 17 | 60 | 32 | 15 | 35 | 0 | 0 | 160 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 20 | 14 | 0 | 340 | 85 | 16 | 24 | 0 | 0 | 0 | 24 | 54.36 | 24 | 24 | 0 | 98 | 106 | 42 | 560 | 0 | 0 | 50 | 0 | 94 | 217 | 0 | 0 | 0 | 1224 | 0 | 55 | 0 | 215 | 290 | 230 | 51 | 10 | 193 | 10 | 0 | 93 | 155 | 0 | 19 | 46 | 148 | 52.2 | 0 | 38 | 305 | 0 | 296 | 29 | 30 | 124 | 0 | 8 | 0 | 85 | 30 | 149 | 0 | 101 | 17 | 9 | 0 | 77 | 28 | 0 | 0 | 0 | 7254.56 | 904 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1202 | 67 | 0 | 0 | 1449 | 0 | 32 | 0 | 35 | 35 | 0 | 0 | 0 | 25 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 183 | 0 | 183 | 0 | 333 | 0 | 0 | 0 | 0 | 95 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 307 | 123 | 220 | 0 | 1244 | 610 | 17 | 7553 | 14807.56 | 76.04
04:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 234 | 0 | 0 | 17 | 30 | 32 | 15 | 0 | 0 | 0 | 160 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 20 | 14 | 0 | 385 | 60 | 15 | 19 | 0 | 0 | 0 | 0 | 35 | 12 | 24 | 0 | 98 | 107 | 42 | 565 | 0 | 0 | 50 | 0 | 98 | 219 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 215 | 290 | 230 | 51 | 10 | 200 | 10 | 0 | 93 | 34 | 0 | 19 | 0 | 144 | 16 | 0 | 15 | 310 | 0 | 320 | 29 | 30 | 134 | 0 | 16 | 0 | 86 | 30 | 149 | 0 | 101 | 0 | 9 | 0 | 77 | 28 | 0 | 0 | 0 | 6960 | 903 | 207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1201 | 67 | 0 | 0 | 1444 | 0 | 32 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 183 | 0 | 184 | 0 | 355 | 0 | 0 | 0 | 0 | 95 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 307 | 123 | 220 | 0 | 1244 | 610 | 17 | 7518 | 14478 | 76.04
05:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 201 | 0 | 0 | 17 | 30 | 32 | 15 | 0 | 0 | 0 | 160 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 20 | 14 | 0 | 345 | 62 | 15 | 9 | 0 | 0 | 0 | 0 | 35 | 12 | 24 | 0 | 97 | 106 | 42 | 565 | 0 | 0 | 50 | 0 | 92 | 221 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 215 | 290 | 230 | 51 | 10 | 203 | 10 | 0 | 93 | 34 | 0 | 19 | 0 | 138 | 0 | 0 | 15 | 310 | 0 | 320 | 29 | 30 | 136 | 0 | 16 | 0 | 86 | 30 | 148 | 0 | 101 | 0 | 9 | 0 | 78 | 29 | 0 | 0 | 0 | 6845 | 903 | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1204 | 51 | 0 | 0 | 1431 | 0 | 32 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 183 | 0 | 184 | 0 | 335 | 0 | 0 | 0 | 0 | 95 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 307 | 123 | 220 | 0 | 1244 | 610 | 17 | 7474 | 14319 | 76.04
06:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 204 | 0 | 0 | 17 | 30 | 32 | 15 | 0 | 0 | 0 | 160 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 142 | 20 | 14 | 0 | 335 | 15 | 15 | 6 | 0 | 0 | 0 | 0 | 17 | 12 | 24 | 0.46 | 100 | 51 | 42 | 565 | 0 | 0 | 50 | 0 | 34 | 221 | 0 | 0 | 0 | 1160 | 0 | 10 | 0 | 215 | 290 | 230 | 51 | 10 | 203 | 10 | 0 | 93 | 0 | 0 | 19 | 0 | 132 | 0 | 5 | 0 | 305 | 0 | 310 | 29 | 30 | 124 | 0 | 16 | 0 | 86 | 30 | 146 | 0 | 101 | 0 | 9 | 1.6 | 77 | 29 | 0.1 | 3.25 | 0 | 6439.41 | 903 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.25 | 1204 | 34 | 0 | 0 | 1438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.88 | 5 | 0 | 0 | 3.59 | 0 | 0 | 186 | 0 | 184 | 0 | 334 | 0 | 0.27 | 0 | 0 | 50 | 2 | 107 | 0 | 0 | 0 | 0.4 | 9 | 0.04 | 21 | 273 | 123 | 220 | 0 | 1244 | 610 | 0 | 7173.43 | 13612.84 | 76.04
07:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 280 | 0 | 0 | 17 | 15 | 0 | 15 | 0 | 0 | 0 | 160 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 125 | 0 | 0 | 0 | 460 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1.03 | 100 | 30 | 42 | 565 | 0 | 0 | 19 | 0 | 17 | 217 | 0 | 0 | 0 | 1140 | 0 | 0 | 0 | 215 | 290 | 230 | 51 | 10 | 204 | 10 | 0 | 92 | 0 | 0 | 19 | 0 | 120 | 0 | 18 | 0 | 305 | 0 | 310 | 29 | 30 | 142 | 2 | 16 | 0 | 86 | 30 | 148 | 0 | 101 | 0 | 9 | 4.77 | 77 | 29 | 0.5 | 11.65 | 0 | 6395.95 | 904 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.97 | 1140 | 17 | 0 | 0 | 1433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.85 | 23 | 0 | 0 | 11.2 | 0 | 0 | 189 | 0 | 187 | 0 | 404 | 0 | 0.97 | 0 | 0 | 50 | 6 | 107 | 0 | 0 | 0 | 1.7 | 30 | 0.14 | 0 | 278 | 123 | 220 | 0 | 1100 | 560 | 0 | 7038.83 | 13434.78 | 76.04
08:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 219 | 0 | 0 | 17 | 15 | 0 | 15 | 0 | 0 | 0 | 160 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 125 | 21 | 0 | 0 | 350 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 2.3 | 100 | 31 | 12 | 565 | 0 | 0 | 19 | 0 | 15 | 216 | 0 | 0 | 0 | 1102 | 9 | 0 | 0 | 215 | 290 | 230 | 51 | 10 | 202 | 10 | 0 | 92 | 0 | 0 | 19 | 0 | 100 | 0 | 30 | 0 | 310 | 0 | 309 | 29 | 30 | 135 | 6 | 16 | 0 | 86 | 30 | 149 | 0 | 101 | 0 | 9 | 10.07 | 77 | 28 | 1 | 21.48 | 0 | 6218.85 | 903 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.23 | 1097 | 17 | 0 | 0 | 1441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.63 | 44 | 0 | 0 | 22.72 | 0 | 0 | 189 | 0 | 187 | 0 | 342 | 0 | 2.02 | 0 | 35 | 50 | 12 | 107 | 0 | 0 | 0 | 3.1 | 74 | 0.28 | 0 | 277 | 123 | 220 | 0 | 1100 | 550 | 0 | 7076.98 | 13295.83 | 76.04
09:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 202 | 0 | 0 | 17 | 15 | 0 | 15 | 0 | 0 | 0 | 160 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 125 | 20 | 14 | 0 | 345 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 3.5 | 100 | 29 | 9 | 565 | 0 | 0 | 19 | 0 | 16 | 216 | 0 | 0 | 0 | 1105 | 16 | 0 | 0 | 215 | 290 | 230 | 51 | 10 | 189 | 10 | 0 | 91 | 0 | 0 | 19 | 0 | 142 | 0 | 47 | 0 | 315 | 0 | 301 | 29 | 30 | 133 | 2 | 17 | 0 | 85 | 30 | 148 | 0 | 101 | 0 | 9 | 14.58 | 104 | 28 | 1.4 | 32.12 | 0 | 6311.6 | 904 | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 1096 | 17 | 0 | 0 | 1441.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.04 | 68 | 0 | 0 | 36.72 | 0 | 0 | 189 | 0 | 185 | 0 | 333 | 0 | 3.19 | 0 | 42 | 50 | 19 | 105 | 0 | 0 | 0 | 4.9 | 122 | 0.57 | 0 | 276 | 123 | 220 | 0 | 1100 | 550 | 0 | 7193.05 | 13504.65 | 76.04
10:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 295 | 0 | 0 | 17 | 0 | 0 | 15 | 0 | 17 | 0 | 160 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 123 | 20 | 14 | 0 | 482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 3.94 | 100 | 17 | 11 | 520 | 0 | 0 | 0 | 0 | 15 | 213 | 0 | 0 | 0 | 1160 | 4 | 0 | 0 | 220 | 290 | 230 | 51 | 10 | 193 | 10 | 0 | 90 | 0 | 0 | 19 | 0 | 142 | 0 | 64 | 0 | 315 | 0 | 302 | 30 | 30 | 145 | 8 | 16 | 0 | 83 | 30 | 148 | 0 | 102 | 0 | 37 | 17.49 | 104 | 27 | 1.7 | 42.74 | 0 | 6594.87 | 904 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 1101 | 0 | 0 | 0 | 1446.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.69 | 86 | 0 | 0 | 45 | 0 | 0 | 195 | 0 | 195 | 0 | 402 | 0 | 4.09 | 0 | 42 | 35 | 24 | 91 | 0 | 0 | 0 | 6.2 | 153 | 0.67 | 0 | 277 | 123 | 220 | 0 | 1100 | 555 | 0 | 7346.26 | 13941.13 | 76.04
11:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 264 | 5 | 0 | 23 | 0 | 32 | 15 | 0 | 17 | 0 | 160 | 145 | 0 | 0 | 17 | 0 | 0 | 0 | 29 | 123 | 22 | 14 | 0 | 445 | 1 | 16 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 24 | 1.52 | 100 | 16 | 2 | 565 | 0 | 0 | 0 | 0 | 28 | 214 | 0 | 0 | 0 | 1160 | 16 | 8 | 0 | 220 | 290 | 230 | 51 | 10 | 199 | 10 | 0 | 90 | 0 | 0 | 19 | 0 | 150 | 0 | 49 | 0 | 310 | 0 | 302 | 30 | 30 | 150 | 11 | 0 | 0 | 83 | 30 | 149 | 0 | 101 | 0 | 37 | 16.22 | 106 | 10 | 1.9 | 40.41 | 0 | 6651.05 | 903 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 1164 | 0 | 0 | 0 | 1435.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.86 | 98 | 0 | 0 | 47 | 0 | 0 | 190 | 0 | 188 | 0 | 384 | 0 | 4.45 | 0 | 44 | 35 | 28 | 68 | 0 | 0 | 0 | 6.9 | 171 | 0.68 | 0 | 270 | 123 | 220 | 0 | 1105 | 580 | 0 | 7412.4 | 14063.45 | 76.04
12:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 291 | 17 | 0 | 35 | 15 | 32 | 15 | 17 | 17 | 0 | 160 | 143 | 0 | 0 | 17 | 0 | 0 | 0 | 30 | 94 | 24 | 14 | 0 | 460 | 17 | 16 | 0 | 0 | 1 | 0 | 2 | 13 | 25 | 24 | 4.61 | 100 | 16 | 2 | 565 | 0 | 0 | 18 | 1 | 88 | 210 | 0 | 0 | 0 | 1224 | 17 | 20 | 0 | 220 | 290 | 230 | 51 | 10 | 203 | 10 | 0 | 88 | 13 | 4 | 19 | 20 | 158 | 12 | 38 | 0 | 315 | 0 | 302 | 30 | 30 | 150 | 11 | 8 | 0 | 83 | 30 | 149 | 0 | 101 | 0 | 28 | 16.82 | 114 | 10 | 1.8 | 37.67 | 0 | 7007.9 | 903 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 1215 | 0 | 0 | 0 | 1438.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.72 | 101 | 0 | 0 | 53 | 0 | 0 | 188 | 0 | 188 | 0 | 395 | 0 | 4.8 | 0 | 40 | 50 | 20 | 100 | 0 | 0 | 0 | 6.9 | 179 | 0.73 | 2 | 283 | 123 | 220 | 0 | 1107 | 585 | 0 | 7545.18 | 14553.08 | 76.04
13:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 258 | 17.5 | 0 | 34 | 90 | 32 | 15 | 17 | 17 | 0 | 160 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 86 | 24 | 12 | 0 | 437 | 45 | 16 | 8 | 0 | 0 | 0 | 16 | 18 | 25 | 24 | 4.45 | 100 | 32 | 14 | 565 | 0 | 0 | 39 | 1 | 90 | 208 | 0 | 0 | 0 | 1224 | 16 | 20 | 0 | 220 | 290 | 230 | 51 | 10 | 205 | 10 | 25 | 87 | 116 | 17 | 19 | 85 | 156 | 43 | 70 | 0 | 310 | 0 | 231 | 29 | 30 | 147 | 8 | 22 | 0 | 82 | 30 | 149 | 0 | 101 | 0 | 18 | 19.54 | 124 | 10 | 2.1 | 47.56 | 0 | 7338.15 | 903 | 198 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 40 | 97 | 1215 | 15 | 0 | 0 | 1441.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 50.75 | 100 | 0 | 0 | 51 | 0 | 0 | 188 | 0 | 185 | 0 | 393 | 0 | 4.78 | 0 | 40 | 80 | 10 | 101 | 0 | 0 | 0 | 6.9 | 173 | 0.27 | 14 | 290 | 120 | 220 | 0 | 1090 | 585 | 36 | 7701.34 | 15039.49 | 76.04
14:00 | 0 | 88 | 48 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 261 | 17.5 | 6 | 34 | 99 | 32 | 15 | 30 | 17 | 0 | 160 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 86 | 26 | 14 | 0 | 445 | 76 | 16 | 33 | 0 | 4 | 0 | 14 | 35 | 25 | 24 | 3.92 | 100 | 37 | 14 | 360 | 0 | 0 | 39 | 20 | 91 | 210 | 0 | 0 | 0 | 1224 | 16 | 20 | 0 | 220 | 290 | 230 | 51 | 10 | 206 | 10 | 34 | 88 | 169 | 14 | 19 | 110 | 160 | 43 | 60 | 34 | 315 | 0 | 219 | 29 | 28 | 147 | 7 | 24 | 0 | 81 | 30 | 149 | 0 | 101 | 0 | 18 | 17.18 | 124 | 10 | 1.7 | 25.26 | 0 | 7382.56 | 903 | 192 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 67 | 87 | 1221 | 23 | 0 | 0 | 1442.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 36.02 | 56 | 0 | 0 | 45 | 0 | 0 | 188 | 0 | 182 | 0 | 392 | 0 | 4.18 | 0 | 40 | 87 | 25 | 96 | 0 | 0 | 0 | 6.9 | 153 | 0.6 | 14 | 291 | 118 | 220 | 0 | 1244 | 585 | 35 | 7810.63 | 15193.19 | 76.04
15:00 | 0 | 88 | 48 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 260 | 0 | 17 | 34 | 122 | 32 | 15 | 35 | 17 | 0 | 160 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 86 | 22 | 14 | 0 | 475 | 109 | 16 | 44 | 0 | 4 | 0 | 14 | 35 | 25 | 24 | 3.34 | 98 | 101 | 3 | 362 | 0 | 0 | 39 | 25.5 | 90 | 209 | 0 | 0 | 0 | 1224 | 13 | 16 | 0 | 220 | 290 | 230 | 51 | 10 | 207 | 10 | 34 | 88 | 176 | 13 | 19 | 114 | 168 | 52.2 | 26 | 33 | 315 | 0 | 219 | 29 | 28 | 146 | 5 | 24 | 0 | 80 | 30 | 150 | 0 | 102 | 0 | 18 | 11.18 | 123 | 10 | 1.4 | 33.12 | 0 | 7509.74 | 903 | 184 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 32 | 68 | 1210 | 26 | 0 | 0 | 1446.86 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 10 | 52.2 | 33.98 | 58 | 0 | 0 | 34 | 0 | 0 | 185 | 0 | 178 | 0 | 389 | 0 | 3.36 | 0 | 40 | 87 | 20 | 90 | 0 | 0 | 0 | 4.9 | 80 | 0.37 | 15 | 307 | 123 | 220 | 0 | 1244 | 582 | 35 | 7679.67 | 15189.41 | 76.04
16:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 231 | 0 | 17 | 34 | 122 | 32 | 15 | 26 | 17 | 0 | 160 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 86 | 22 | 14 | 0 | 395 | 110 | 16 | 44 | 0 | 7 | 0 | 30 | 35 | 25 | 24 | 2.21 | 95 | 110 | 5 | 500 | 0 | 0 | 39 | 25.5 | 89 | 211 | 0 | 0 | 0 | 1224 | 8 | 20 | 0 | 220 | 290 | 230 | 51 | 10 | 207 | 10 | 34 | 88 | 183 | 19 | 19 | 114 | 166 | 52.2 | 33 | 33 | 315 | 0 | 220 | 12 | 28 | 148 | 5 | 16 | 0 | 80 | 30 | 149 | 0 | 101 | 0 | 18 | 9.5 | 124 | 10 | 0.9 | 16.6 | 0 | 7540.91 | 903 | 184 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 1212 | 58 | 0 | 0 | 1444.63 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 27 | 52.2 | 21.7 | 36 | 0 | 0 | 22 | 0 | 0 | 179 | 0 | 175 | 0 | 374 | 0 | 2.13 | 0 | 40 | 87 | 16 | 92 | 0 | 0 | 0 | 3.2 | 82 | 0.33 | 15 | 307 | 122 | 220 | 0 | 1244 | 585 | 17 | 7612.19 | 15153.1 | 76.04
17:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 231 | 0 | 17 | 50 | 90 | 32 | 15 | 50 | 35 | 0 | 160 | 142 | 0 | 0 | 17 | 0 | 0 | 0 | 6 | 112 | 22 | 14 | 0 | 357 | 68 | 16 | 45 | 0 | 6 | 0 | 40 | 35 | 25 | 24 | 1.02 | 94 | 68 | 11 | 530 | 0 | 0 | 50 | 25.5 | 68 | 211 | 0 | 0 | 0 | 1126 | 3 | 20 | 3 | 220 | 290 | 230 | 51 | 10 | 208 | 10 | 33 | 88 | 100 | 27 | 19 | 34 | 152 | 52.2 | 14 | 33 | 310 | 0 | 220 | 12 | 28 | 132 | 1 | 24 | 0 | 80 | 30 | 148 | 0 | 101 | 0 | 9 | 3.05 | 133 | 10 | 0.2 | 10.39 | 0 | 7196.36 | 903 | 179 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1197 | 58 | 0 | 0 | 1442.58 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 27 | 25 | 8.68 | 8 | 0 | 0 | 3 | 0 | 0 | 174 | 0 | 175 | 0 | 344 | 0 | 0.34 | 0 | 40 | 70 | 7 | 68 | 0 | 0 | 0 | 1.9 | 10 | 0.17 | 14 | 301 | 120 | 220 | 0 | 1143 | 559 | 17 | 7178.67 | 14375.03 | 76.04
18:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 211 | 5 | 17 | 58 | 90 | 60 | 15 | 55 | 50 | 0 | 160 | 141 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 142 | 22 | 14 | 0 | 345 | 30 | 16 | 61 | 0 | 1 | 0 | 40 | 17 | 25 | 24 | 0.15 | 97 | 51 | 14 | 535 | 0 | 0 | 33 | 25.5 | 51 | 182 | 0 | 0 | 0 | 1050 | 1 | 20 | 8 | 240 | 290 | 240 | 51 | 7 | 199 | 10 | 34 | 88 | 97 | 27 | 19 | 26 | 144 | 34 | 3 | 34 | 305 | 0 | 219 | 12 | 28 | 129 | 1 | 0 | 0 | 53 | 30 | 95 | 0 | 101 | 1 | 9 | 0.56 | 132 | 10 | 0 | 0.67 | 0 | 6865.88 | 903 | 178 | 0 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.08 | 1078 | 30 | 0 | 0 | 1435.76 | 0 | 0 | 0 | 30 | 35 | 0 | 0 | 27 | 25 | 0.94 | 2 | 0 | 0 | 2.09 | 0 | 0 | 140 | 0 | 140 | 0 | 339 | 0 | 0.19 | 0 | 40 | 35 | 3 | 34 | 0 | 0 | 0 | 0.5 | 11 | 0.04 | 14 | 230 | 100 | 180 | 0 | 913 | 604 | 17 | 6581.6 | 13447.48 | 76.04
19:00 | 0 | 105 | 28 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 270 | 33 | 17 | 95 | 90 | 97 | 15 | 55 | 108 | 0 | 160 | 144 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 142 | 23 | 14 | 0 | 440 | 48 | 16 | 73 | 0 | 0 | 50 | 40 | 21 | 25 | 24 | 0 | 98 | 70 | 19 | 555 | 0 | 0 | 40 | 25.5 | 68 | 214 | 0 | 0 | 0 | 1160 | 0 | 38 | 0 | 230 | 290 | 240 | 51 | 5 | 203 | 10 | 53 | 89 | 104 | 27 | 19 | 34 | 158 | 38 | 0 | 35 | 315 | 0 | 220 | 28 | 28 | 135 | 0 | 16 | 0 | 84 | 30 | 93 | 0 | 103 | 17 | 9 | 0 | 133 | 10 | 0 | 0 | 0 | 7645.5 | 903 | 178 | 0 | 31 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1081 | 32 | 0 | 0 | 1448.17 | 0 | 14 | 0 | 35 | 35 | 0 | 60 | 27 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 165 | 0 | 400 | 0 | 0 | 0 | 39 | 85 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 218 | 120 | 220 | 0 | 1175 | 650 | 36 | 7277.17 | 14922.67 | 76.04
19:30 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 238 | 35.5 | 17 | 115 | 90 | 97 | 15 | 35 | 108 | 0 | 160 | 143 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 142 | 23 | 14 | 0 | 405 | 90 | 16 | 70 | 0 | 0 | 50 | 47 | 37 | 25 | 24 | 0 | 99 | 95 | 24 | 555 | 0 | 0 | 50 | 25.5 | 102 | 215 | 0 | 0 | 0 | 1160 | 0 | 145 | 0 | 230 | 290 | 240 | 51 | 5 | 202 | 10 | 90 | 90 | 148 | 27 | 19 | 52 | 160 | 52.2 | 0 | 35 | 315 | 0 | 242 | 28 | 28 | 132 | 0 | 16 | 0 | 84 | 30 | 150 | 0 | 101 | 17 | 9 | 0 | 133 | 10 | 0 | 0 | 0 | 8034.2 | 904 | 178 | 0 | 34 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166 | 68 | 0 | 0 | 1445.9 | 0 | 40 | 0 | 35 | 35 | 0 | 101 | 20 | 52.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 182 | 0 | 361 | 0 | 0 | 0 | 39 | 93 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 279 | 120 | 220 | 0 | 1200 | 700 | 36 | 7626.1 | 15660.3
20:00 | 0 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 231 | 35.5 | 17 | 118 | 75 | 97 | 15 | 35 | 108 | 0 | 160 | 146 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 142 | 23 | 20 | 0 | 375 | 92 | 16 | 71 | 0 | 0 | 50 | 47 | 38 | 25 | 24 | 0 | 100 | 110 | 24 | 555 | 0 | 0 | 50 | 25.5 | 105 | 215 | 0 | 0 | 0 | 1163 | 0 | 132 | 0 | 230 | 290 | 240 | 51 | 5 | 201 | 10 | 90 | 91 | 120 | 27 | 19 | 34 | 148 | 52.2 | 0 | 36 | 310 | 0 | 254 | 28 | 28 | 134 | 0 | 24 | 0 | 84 | 30 | 151 | 0 | 101 | 17 | 9 | 0 | 133 | 10 | 0 | 0 | 0 | 7951.2 | 903 | 179 | 0 | 25 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1176 | 77 | 0 | 0 | 1441.26 | 0 | 40 | 0 | 35 | 35 | 0 | 101 | 20 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 184 | 0 | 354 | 0 | 0 | 0 | 39 | 94 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 252 | 120 | 220 | 0 | 1161 | 708 | 35 | 7555.26 | 15506.46 | 76.04
21:00 | 0 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 248 | 35.5 | 17 | 133 | 90 | 97 | 15 | 35 | 108 | 0 | 160 | 146 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 142 | 23 | 20 | 0 | 440 | 95 | 16 | 71 | 0 | 0 | 50 | 47 | 38 | 25 | 24 | 0 | 100 | 110 | 25 | 555 | 0 | 0 | 50 | 25.5 | 105 | 215 | 0 | 0 | 0 | 1160 | 0 | 142 | 0 | 230 | 290 | 240 | 51 | 5 | 201 | 10 | 89 | 91 | 122 | 27 | 19 | 32 | 154 | 52.2 | 0 | 36 | 310 | 0 | 282 | 41 | 30 | 148 | 0 | 8 | 0 | 85 | 30 | 152 | 0 | 101 | 17 | 9 | 0 | 133 | 10 | 0 | 0 | 0 | 8123.2 | 903 | 173 | 0 | 31 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1170 | 77 | 0 | 0 | 1444.47 | 0 | 40 | 0 | 35 | 35 | 0 | 101 | 20 | 25 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 174 | 0 | 181 | 0 | 384 | 0 | 0 | 0 | 40 | 94 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 275 | 120 | 220 | 0 | 1200 | 775 | 36 | 7747.47 | 15870.67 | 76.04
22:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 252 | 35.5 | 17 | 108 | 90 | 97 | 15 | 35 | 108 | 0 | 160 | 148 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 142 | 23 | 21 | 0 | 450 | 92 | 16 | 75 | 0 | 0 | 50 | 47 | 38 | 25 | 24 | 0 | 100 | 110 | 25 | 555 | 0 | 0 | 50 | 25.5 | 105 | 216 | 0 | 0 | 0 | 1161 | 0 | 150 | 0 | 230 | 290 | 240 | 51 | 5 | 202 | 10 | 75 | 91 | 146 | 27 | 19 | 31 | 160 | 52.2 | 0 | 36 | 305 | 0 | 286 | 41 | 30 | 140 | 0 | 24 | 0 | 84 | 30 | 150 | 0 | 101 | 17 | 9 | 0 | 2 | 10 | 0 | 0 | 0 | 8029.2 | 903 | 170 | 0 | 29 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1195 | 77 | 0 | 0 | 1446.2 | 0 | 40 | 0 | 35 | 35 | 0 | 101 | 20 | 25 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 175 | 0 | 181 | 0 | 368 | 0 | 0 | 0 | 40 | 94 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 277 | 120 | 220 | 0 | 1200 | 820 | 17 | 7777.2 | 15806.4 | 76.04
23:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 269 | 35.5 | 0 | 95 | 90 | 97 | 15 | 35 | 108 | 0 | 160 | 150 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 142 | 23 | 21 | 0 | 470 | 95 | 16 | 75 | 0 | 0 | 50 | 47 | 38 | 25 | 24 | 0 | 100 | 110 | 26 | 555 | 0 | 0 | 50 | 25.5 | 105 | 216 | 0 | 0 | 0 | 1172 | 0 | 38 | 0 | 230 | 290 | 240 | 42 | 5 | 205 | 10 | 69 | 91 | 146 | 0 | 19 | 32 | 160 | 52.2 | 0 | 36 | 315 | 0 | 288 | 41 | 30 | 152 | 0 | 24 | 0 | 84 | 28 | 152 | 0 | 101 | 17 | 9 | 0 | 74 | 10 | 0 | 0 | 0 | 7999.2 | 903 | 170 | 0 | 30 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1198 | 83 | 0 | 0 | 1452.63 | 0 | 40 | 0 | 35 | 35 | 0 | 100 | 20 | 25 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 178 | 0 | 180 | 0 | 409 | 0 | 0 | 0 | 40 | 92 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 276 | 120 | 220 | 0 | 1244 | 930 | 17 | 7980.63 | 15979.83 | 76.04
Total KWH | 0 | 2045760 | 763680 | 0 | 0 | 0 | 0 | 0 | 9500400 | 0 | 5902210 | 260280 | 156240 | 1083168 | 1581600 | 1071633 | 383108 | 534614 | 796320 | 0 | 4028500 | 3470575 | 0 | 0 | 272672 | 0 | 0 | 0 | 220130 | 3045600 | 499800 | 321840 | 0 | 9948636.36 | 1486636 | 318655 | 823680 | 0 | 25920 | 378953 | 500544 | 707145 | 423360 | 537600 | 32762 | 2493144 | 1870100 | 603840 | 12618181.82 | 0 | 0 | 931680 | 284493.6 | 1875127 | 5138582 | 0 | 0 | 0 | 28232724 | 114345 | 963490 | 10289 | 5417000 | 7387100 | 5792000 | 1208266 | 222720 | 4951000 | 255672 | 708480 | 2117122 | 2357760 | 235200 | 463320 | 1032840 | 3501120 | 787234 | 469827 | 530080 | 7538000 | 0 | 6772000 | 689000 | 695520 | 3374100 | 70280 | 359928 | 0 | 1955520 | 736800 | 3338500 | 0 | 2428900 | 177480 | 336000 | 137000 | 2323200 | 369600 | 13800 | 336500 | 0 | 175346886.78 | 21850182 | 4777632 | 0 | 235200 | 321664 | 0 | 0 | 0 | 0 | 0 | 498960 | 727200 | 28232720 | 1066080 | 0 | 0 | 34560000 | 0 | 364907 | 0 | 410976 | 539136 | 0 | 550528 | 229079 | 537437 | 368816 | 719284 | 275170 | 0 | 378496 | 0 | 0 | 4552900 | 0 | 4576931 | 0 | 8974181 | 0 | 34800 | 0 | 722618 | 1826049 | 192482 | 2290291 | 0 | 0 | 0 | 52165.44 | 1284480 | 4902 | 722112 | 6873000 | 2878000 | 5304680 | 0 | 28210909 | 15930181.82 | 428400 | 181502549.26 | 356849436.04

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 03-06-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14553.08 | MW | 12:00 Hr. | Energy Generated |  |  | 356.8494 |  | MKWHr.
| Day Peak Demand |  |  | 14871.08 | MW | 12:00 Hr. | Energy Unserverd |  |  | 5.885 |  | MKWHr.
| Evening Peak Generation |  |  | 15870.67 | MW | 21:00 Hr. | Energy Demand |  |  | 362.7344 |  | MKWHr.
| Evening Peak Demand |  |  | 16289.67 | MW | 21:00 Hr. | Maximum Temperature |  |  | 36.8 |  | °C
| Minimum Generation of the Day |  |  | 13295.83 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 932.1 |  | MMCFD
| Maximum Generation of the Day |  |  | 15979.83 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 6.7099 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.672 | 0 | 11.9947 | 0 | 0 | 0.22013 | 0 | 0 | 45.8868 | Gas | 126.5611 | Gas | 448149130.3012
| Chattogram Zone |  |  | 5.7424 | 40.8509 | 10.138 | 0 | 2.4931 | 0.14711 | 0 | 0.02592 | 59.3975 | Coal | 120.8203 | Coal | 796147820.5916
| Cumilla Zone |  |  | 27.8245 | 0 | 6.6151 | 0 | 0 | 0.46983 | 3.5011 | 0 | 38.4105 | HFO | 41.8804 | HFO | 719233566.412
| Mymensingh Zone |  |  | 0.3696 | 0 | 2.8367 | 0 | 0 | 0.4873 | 0 | 0 | 3.6936 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.8883 | 0 | 0 | 0 | 0 | 0.07028 | 0 | 0 | 27.9585 | Hydro | 2.4931 | Hydro | 249314.4
| Khulna Zone |  |  | 4.7776 | 28.2327 | 2.1219 | 0 | 0 | 0.7272 | 21.8502 | 0 | 57.7096 | Solar | 5.1573 | Solar | 81103635.4588
| Barishal Zone |  |  | 8.1827 | 51.0141 | 1.1505 | 0 | 0 | 0.004902 | 0 | 0 | 60.3522 | Import | 59.9113 | Import | 349149418.56
| Rajshahi Zone |  |  | 18.104 | 0 | 2.9072 | 0 | 0 | 1.5014 | 34.56 | 0 | 57.0726 | Wind | 0.02592 | Wind | 381283.2
| Rangpur Zone |  |  | 0 | 0.72262 | 4.1163 | 0 | 0 | 1.5291 | 0 | 0 | 6.3681
| Total |  |  | 126.5611 | 120.8203 | 41.8804 | 0 | 2.4931 | 5.1573 | 59.9113 | 0.02592 | 356.8494
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 448149130.3012 |  | Hydro | 249314.4
|  |  |  | Coal | 796147820.5916 |  | Solar | 81103635.4588
|  |  |  | HFO | 719233566.412 |  | Import | 349149418.56
|  |  |  | HSD | 0 |  | Wind | 381283.2
[5 empty] | Total: | 239,44,14,168 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.8502 | Peak Hr Flow | 903.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 50794072.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 34.56 | Peak Hr Flow | 1444.47 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2211 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.5011 | Peak Hr Flow | 154.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2751 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 59.9113 | Peak Hr Flow | 2501.47 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 13 |  | 5082
|  |  |  | Chattogram |  | 5 |  | 1530
|  |  |  | Cumilla |  | 15 |  | 1679
|  |  |  | Mymensingh |  | 355 |  | 1434
|  |  |  | Sylhet |  | 10 |  | 699
|  |  |  | Khulna |  | 0 |  | 2156
|  |  |  | Barishal |  | 3 |  | 557
|  |  |  | Rajshahi |  | 0 |  | 1540
|  |  |  | Rangpur |  | 0 |  | 1068
|  |  |  | Total |  | 401 |  | 15745
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:05 | Bhulta-Haripur 132 kV Ckt-1 is restored.
| 08:24 | 09:35 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Shutdown Taken by PBS for Redhot
Maintenance.
| 08:25 | 09:34 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Shutdown Taken by PBS for Redhot
Maintenance.
|  | 08:32 | Cumilla(S) 132/33kV S/S TR-2 HT is restored.
|  | 08:33 | Cumilla(S) 132/33kV S/S TR-2 LT is restored.
|  | 09:02 | Kulaura 132/33kV S/S TR-1 AB HT is restored.
|  | 09:04 | Kulaura 132/33kV S/S TR-1 AB LT is restored.
| 11:16 |  | BIPTC S/S 20DF13 Forced S/D Due to For corrective maintenance.
| 12:20 | 13:07 | Khulshi-Madunaghat 132kV Ckt-1 Tripped from Khulshi 132/33kV end showing Siemens ,
Zone-1 fault, R-phase Trip, Distance: 4.6km relays Due to Trip from Sholoshahar Grid
Sub-station.
| 12:59 | 13:15 | Satkhira 132/33kV S/S Transformer-2 (T-2) HT Tripped showing WTI relays Due to Winding | [7 empty] | 60.0MW load
|  |  | temperature trip | [7 empty] | interrup.
| 12:59 | 13:15 | Satkhira 132/33kV S/S Transformer-2 (T-2) LT Tripped showing WTI relays Due to Winding | [7 empty] | 60.0MW load
|  |  | temperature trip | [7 empty] | interrup.
| 14:24 | 14:30 | Bhaluka 132/33kV S/S 01. Transformer- 01 LT Tripped showing Micom relays. | [7 empty] | 118.0MW load
interrup.
| 14:24 | 14:30 | Bhaluka 132/33kV S/S 02. Transformer- 02 LT Tripped showing Micom relays. | [7 empty] | 118.0MW load
interrup.
| 15:24 | 17:16 | Satkhira 132/33kV S/S Transformer-2 (T-2) HT Tripped showing WTI relays Due to Winding | [7 empty] | 62.0MW load
|  |  | temperature trip | [7 empty] | interrup.
| 15:24 | 17:19 | Satkhira 132/33kV S/S Transformer-2 (T-2) LT Tripped showing WTI relays Due to Winding | [7 empty] | 62.0MW load
|  |  | temperature trip | [7 empty] | interrup.
| 16:24 | 17:27 | Feni 132/33kV S/S T-1(405T) LT Tripped showing O/C,E/F relays Due to REB-1 33KV feeder CT | [7 empty] | 58.0MW load
|  |  | blust | [7 empty] | interrup.
| 16:43 | 18:03 | Joypurhat 132/33kV S/S Patnitola Ckt.-2 Tripped showing Main protection relay relays Due
to Due to Storm and thundering
| 16:58 |  | Payra 1320 MW unit-2 was sync.
|  | 17:27 | Feni 132/33kV S/S T-1(405T) LT is restored.
| 17:34 | 18:58 | Bogura(New)-Naogaon 132 kV Ckt-2 Tripped from Naogaon 132/33kV end showing Distance
protection main 01. Lockout relay K861 & K862 relays Due to Thundering. and from Bogura
230/132kV end showing A/R in PROGRESS, CARRIER SEND, FAULT TYPE A to G, RECLOSER LO, A
Phase relays.
| 18:23 | 18:55 | Shahjadpur 132/33kV S/S T-4(435T) LT Forced S/D Due to SD Taken by New Bera 33kv Feeder | [7 empty] | 10.0MW load
|  |  | for red hot maintenance at BUS DS. | [7 empty] | interrup.
| 21:00 |  | Evening Peak Generation is 15869 MW.
| 01:22 |  | Bogura(New)-Naogaon 132 kV Ckt-1 Tripped from Naogaon 132/33kV end showing Distance
relay. relays Due to Heavy storm,raining,thundering.
| 02:50 | 03:30 | Maijdee 132/33kV S/S Tr-02 LT Forced S/D Due to Transformer-2 , 33kv Secendary shutdown
is required from due to Read Hot Maintenence 33 kV bus source side of
BREB. Noakhali Palli Bidyut Samity will carry out the work.
| 06:16 |  | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to Hot point maintenance.
| 06:17 |  | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to Hot point maintenance.
| 07:24 |  | Noapara 132/33kV S/S T-1 HT Scheduled S/D Due to DUE TO RED HOT MAINTENANCE OF REB-3 | [7 empty] | 20.0MW load
|  |  | FEEDER BY PBS. | [7 empty] | interrup.
| 07:24 |  | Noapara 132/33kV S/S T-1 LT Scheduled S/D Due to DUE TO RED HOT MAINTENANCE OF REB-3 | [7 empty] | 20.0MW load
|  |  | FEEDER BY PBS. | [7 empty] | interrup.
| 07:28 |  | Noapara 132/33kV S/S Bus Section-1 Scheduled S/D Due to DUE TO RED HOT MAINTENANCE OF | [7 empty] | 20.0MW load
|  |  | REB-3 FEEDER BY PBS. | [7 empty] | interrup.
| 07:41 |  | Kishoreganj 132/33kV S/S Tr-3 (424T) HT Scheduled S/D Due to LA Installation work of
33/0.4 KV Auxiliary T-03.
| 07:42 |  | Madaripur 132/33kV S/S T2-415T LT Scheduled S/D Due to Agoiljhora 33kv feeder source ds | [7 empty] | 25.0MW load
|  |  | problem | [7 empty] | interrup.
| 07:42 |  | Madaripur 132/33kV S/S T2-415T HT Scheduled S/D Due to Agoiljhora 33kv feeder Ds problem
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 03-06-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Under Maintenance
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 382 | 9500400 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 160 | 4028500 | GT is under maintenance
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 146 | 3470575 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 383108 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35.5 | 260280 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 90 | 1581600 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 534614 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 272672 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 499800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 321840 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 763680 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 97 | 1071633 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 1083168 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2045760 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 796320 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 220130 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 156240 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 440 | 9948636.36 | AGC
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 248 | 5902210 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3045600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2264.5 | 45886766.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 284493.6 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 114345 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 931680 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 100 | 2493144 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 215 | 5138582 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1875127 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 47 | 500544 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 378953 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 423360 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 25 | 603840 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 71 | 823680 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 32762 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 318655 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 38 | 707145 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 1870100 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 537600 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 95 | 1486636 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 28232724 | AGC
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 25920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 555 | 12618181.82 | AGC
Chattogram Area Total |  |  |  |  | 4898.863 | 2711.5 | 59397472.42
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 201 | 4951000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 290 | 7387100 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 240 | 5792000 | Can't Start FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 230 | 5417000 | FGMO
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 10 | 255672 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 5 | 222720 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 10289 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1208266 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 142 | 963490 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 530080 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 91 | 2117122 | ST Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 122 | 2357760 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 154 | 3501120 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 787234 | Engine Problem
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 463320 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 32 | 1032840 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 235200 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 708480 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 469827 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1791.2 | 38410520
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 137000 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 10 | 369600 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 133 | 2323200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 336000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 336500 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 177480 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 169 | 3693580
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 70280 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 689000 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 695520 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 148 | 3374100 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 152 | 3338500 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 736800 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1955520 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2428900 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 359928 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7538000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 282 | 6772000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1187 | 27958548
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 903 | 21850182 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 31 | 235200 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 46 | 321664 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 173 | 4777632 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 77 | 1066080 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 498960 | FGMO
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 727200 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1170 | 28232720 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2400 | 57709638
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 1200 | 28210909 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 722112 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2878000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 775 | 15930181.82 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5304680 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 36 | 428400 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 275 | 6873000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4902 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2642 | 60352184.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 368816 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 364907 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 229079 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 174 | 4552900 | AGC
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 181 | 4576931 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 384 | 8974181 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 275170 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 25 | 537437 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 101 | 550528 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 539136 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 410976 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 34800 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1444.47 | 34560000 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 378496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 719284 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2471.47 | 57072641
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 40 | 722618 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 100 | 2290291 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 52165.44 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 94 | 1826049 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 192482 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1284480 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 234 | 6368085.44
Eastern Grid Total |  |  |  |  | 17438.042 | 8123.2 | 175346886.78
Western Grid Total |  |  |  |  | 11852.195 | 7747.47 | 181502549.26
National Grid Total |  |  |  |  | 29290.237 | 15870.67 | 356849436.04
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 03-06-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10026.15 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5317.7 | MW
i) Dhaka area |  |  | 5069.25 |  | MW | i) Khulna area |  |  |  | 2155.5 | MW
ii) Chattogram area |  |  | 1524.9 |  | MW | ii) Barishal area |  |  |  | 554.4 | MW
iii) Cumilla area |  |  | 1664 |  | MW | iii) Rajshahi area |  |  |  | 1539.8 | MW
iv) Mymensingh area |  |  | 1079 |  | MW | iv) Rangpur area |  |  |  | 1068 | MW
v) Sylhet area |  |  | 689 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15343.85 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 74 | 00:00 | 133 | Natore | 181 | 00:00
2 | AKSML | 129 | 17:00 | 68 | Hathazari | 101 | 19:00 | 134 | Nawabganj | 73 | 22:00
3 | Aftabnagar | 46 | 23:00 | 69 | Hatirjheel | 54 | 15:00 | 135 | Netrakona | 126 | 08:00
4 | Agargaon | 127 | 15:00 | 70 | Ishurdi | 87 | 21:00 | 136 | New | 61 | 15:00
5 | Agrabad | 76 | 13:00 | 71 | Jaldhaka | 94 | 22:00 | 137 | Niamatpur | 86 | 22:00
6 | Amnura | 36 | 00:00 | 72 | Jamalpur | 120 | 10:00 | 138 | Noapara | 58 | 19:30
7 | Ashuganj | 96 | 23:00 | 73 | Jashore | 165 | 21:00 | 139 | PHP | 13 | 11:00
8 | BSRM | 182 | 22:00 | 74 | Jhenaidah | 132 | 19:30 | 140 | Pabna | 115 | 21:00
9 | Bagerhat | 106 | 23:00 | 75 | Joydebpur | 122 | 19:30 | 141 | Palashbari | 132 | 01:00
10 | Bajitpur | 107 | 23:00 | 76 | Joypurhat | 80 | 00:00 | 142 | Panchagarh | 66 | 19:30
11 | Bakerganj | 17.6 | 00:00 | 77 | Juldah | 15 | 09:00 | 143 | Patiya | 12.9 | 22:00
12 | Bakulia | 94 | 15:00 | 78 | KSRM | 11 | 12:00 | 144 | Patuakhali | 86.2 | 00:00
13 | Banani | 63.4 | 13:00 | 79 | Kabirpur | 149 | 19:30 | 145 | Payra | 42 | 01:00
14 | Bangabhaban | 23 | 10:00 | 80 | Kachua | 114 | 00:00 | 146 | Postogola | 56 | 21:00
15 | Barapukuria | 74 | 00:00 | 81 | Kaliganj | 21 | 00:00 | 147 | Pubail | 26 | 15:00
16 | Barguna | 26 | 00:00 | 82 | Kallyanpur | 126 | 23:00 | 148 | Purbachal | 35 | 14:00
17 | Barishal | 116 | 13:00 | 83 | Kalurghat | 38 | 12:00 | 149 | Purbasadipur | 151 | 00:00
18 | Barishal-230 | 130 | 23:00 | 84 | Kamrangirchar | 55 | 13:00 | 150 | Rahanpur | 48 | 00:00
19 | Baroaulia | 70 | 23:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 40 | 05:00
20 | Baroirhat | 76 | 18:30 | 86 | Kasba | 43 | 22:00 | 152 | Rajbari | 98 | 19:30
21 | Bashundhara | 195 | 14:00 | 87 | Kazla | 89 | 19:30 | 153 | Rajendrapur | 118 | 15:00
22 | BashundharaCement | 8 | 19:00 | 88 | Keranigonj | 84 | 23:00 | 154 | Rajshahi | 138 | 00:00
23 | Beanibazar | 84 | 00:00 | 89 | Khagrachori | 38 | 19:00 | 155 | Rajshahi-230 | 94 | 00:00
24 | Benapole | 79 | 19:30 | 90 | Khulna | 71 | 13:00 | 156 | Ramganj | 124 | 19:30
25 | Bhaluka | 154 | 20:00 | 91 | Khulshi | 184 | 15:00 | 157 | Rampur | 48 | 23:00
26 | Bhandaria | 68 | 01:00 | 92 | Kishoreganj | 152 | 00:00 | 158 | Rangamati | 20 | 19:30
27 | Bhangura | 49 | 06:00 | 93 | Kodda | 234 | 20:00 | 159 | Rangpur | 152 | 19:30
28 | Bheramara(GK) | 77 | 00:00 | 94 | Kulaura | 63 | 22:00 | 160 | Ruppur | 5 | 10:00
29 | Bhulta | 192 | 23:00 | 95 | Kurigram | 70 | 22:00 | 161 | SSM | 12 | 04:00
30 | Bog-Sherpur | 86 | 00:00 | 96 | Kushtia | 176 | 00:00 | 162 | Saidpur | 110 | 00:00
31 | Bogura | 184 | 00:00 | 97 | Laksam | 38 | 00:00 | 163 | Santhia | 42 | 19:30
32 | Borhanuddin | 107 | 04:00 | 98 | Lakshmipur | 48 | 23:00 | 164 | Satkhira | 164 | 22:00
33 | Brahmanbaria | 155 | 19:30 | 99 | Lalbag | 42 | 14:00 | 165 | Satmasjid | 106 | 16:00
34 | Cantonment | 134 | 13:00 | 100 | Lalmonirhat | 71 | 19:30 | 166 | Savar | 152 | 23:00
35 | Chandina | 41 | 22:00 | 101 | MI_Cement | 8.3 | 00:00 | 167 | SevenRings | 13.82 | 20:00
36 | Chandpur | 104 | 22:00 | 102 | Madanganj | 41 | 11:00 | 168 | ShahCement | 19 | 18:00
37 | Chandraghona | 37 | 22:00 | 103 | Madaripur | 137 | 23:00 | 169 | Shahjadpur | 90 | 19:00
38 | Chapai | 81 | 00:00 | 104 | Madartek | 88 | 23:00 | 170 | Shahjibazar | 128 | 19:00
39 | Charsaidpur | 27 | 00:00 | 105 | Madunaghat | 60 | 18:30 | 171 | Shahmirpur | 59 | 16:00
40 | Chauddagram | 90 | 23:00 | 106 | Magura | 79 | 22:00 | 172 | Shariatpur | 114 | 22:00
41 | Chhatak | 43 | 21:00 | 107 | Mahasthangarh | 105 | 00:00 | 173 | Sherpur | 140 | 20:00
42 | Chowmuhani | 184 | 23:00 | 108 | Maijdee | 48 | 00:00 | 174 | Shikalbaha | 34 | 19:00
43 | Chuadanga | 128 | 00:00 | 109 | Manikganj | 152 | 21:00 | 175 | Shitalakhya | 77.5 | 14:00
44 | Coxsbazar | 151 | 14:00 | 110 | Maniknagar | 66 | 13:00 | 176 | Sholosohor | 45 | 22:00
45 | Cumilla(N) | 135 | 19:00 | 111 | Matarbari | 61 | 20:00 | 177 | Shomvuganj | 22 | 00:00
46 | Cumilla(S) | 170 | 00:00 | 112 | Matuail | 48 | 22:00 | 178 | Shyampur | 92 | 16:00
47 | Daganbhuiyan | 42 | 23:00 | 113 | Metrorail_Motijheel | 28 | 09:00 | 179 | Siddhirganj | 105 | 22:00
48 | Daudkandi | 162 | 19:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 126 | 00:00
49 | DhakaUniversity | 80 | 13:00 | 115 | Millgate | 66 | 15:00 | 181 | Sonargaon | 109 | 21:00
50 | Dhamrai | 108 | 21:00 | 116 | Mirpur | 147 | 19:00 | 182 | Sreemongol | 87 | 00:00
51 | Dhanmondi | 115.5 | 13:00 | 117 | Mirsorai | 42 | 07:00 | 183 | Sreepur | 104 | 19:00
52 | Dohazari | 120 | 20:00 | 118 | Mirzapur | 41 | 10:00 | 184 | Srinagar | 58.8 | 22:00
53 | Faridpur | 202 | 23:00 | 119 | Mithapukur | 80 | 06:00 | 185 | Sunamganj | 65 | 19:00
54 | Fatullah | 57 | 23:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 82 | 00:00
55 | Fenchuganj | 48 | 21:00 | 121 | Mogbazar | 97.6 | 15:00 | 187 | Sylhet-132 | 115 | 13:00
56 | Feni | 124 | 00:00 | 122 | Mongla | 47 | 00:00 | 188 | TK | 26 | 00:00
57 | GPH | 6 | 22:00 | 123 | Motijheel | 50 | 13:00 | 189 | Tangail | 158 | 06:00
58 | Ghatail | 90 | 10:00 | 124 | Muktagacha | 33 | 17:00 | 190 | Taraganj | 26 | 00:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 123 | 23:00 | 191 | Tasnim | 18 | 12:00
60 | Ghorashal-230 | 111 | 21:00 | 126 | Muradnagar | 57 | 22:00 | 192 | Thakurgaon | 128 | 20:00
61 | Goalpara | 48 | 19:30 | 127 | Mymensingh | 185 | 18:00 | 193 | Tongi | 127 | 00:00
62 | Gollamari | 126 | 00:00 | 128 | Nabinagar | 74 | 16:00 | 194 | Ullahpara | 41 | 00:00
63 | Gopalganj | 133 | 00:00 | 129 | Naogaon | 157 | 01:00 | 195 | Ullon | 72 | 23:00
64 | Gulshan | 150 | 14:00 | 130 | Narail | 70.5 | 19:30 | 196 | Uttara | 99 | 16:00
65 | Halishahar | 76 | 15:00 | 131 | Narinda | 56 | 16:00 | 197 | UttaraNew | 60 | 23:00
66 | HaripurSBU | 95 | 12:00 | 132 | Narshingdi | 167 | 23:00 | 198 | Zigatola | 94 | 23:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 03-06-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15810.76 | 391 |  | 16219.36
1:00 | 15520.76 | 252 |  | 15783.76
2:00 | 15162.76 | 255 |  | 15428.76
3:00 | 14807.56 | 245 |  | 15063.56
4:00 | 14478 | 220 |  | 14708
5:00 | 14319 | 210 |  | 14538
6:00 | 13612.84 | 224 |  | 13846.84
7:00 | 13434.78 | 236 |  | 13681.78
8:00 | 13295.83 | 135 |  | 13436.83
9:00 | 13504.65 | 145 |  | 13656.65
10:00 | 13941.13 | 80 |  | 14025.13
11:00 | 14063.45 | 191 |  | 14263.45
12:00 | 14553.08 | 304 |  | 14871.08
13:00 | 15039.49 | 196 |  | 15244.49
14:00 | 15193.19 | 186 |  | 15387.56
15:00 | 15189.41 | 374 |  | 15580.41
16:00 | 15153.1 | 208 |  | 15370.1
17:00 | 14375.03 | 208 |  | 14592.03
18:00 | 13447.48 | 188 |  | 13643.48
19:00 | 14922.67 | 233 |  | 15165.67
19:30 | 15660.3 | 251 |  | 15922.3
20:00 | 15506.46 | 207 |  | 15722.46
21:00 | 15870.67 | 401 |  | 16289.67
22:00 | 15806.4 | 434 |  | 16260.4
23:00 | 15979.83 | 362 |  | 16357.83
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 03-06-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7870.56 | 7940.2 | 15810.76 | DAILY GENERATION CURVE
00:30 | 7798.06 | 7867.7 | 15665.76
01:00 | 7725.56 | 7795.2 | 15520.76 | 03-06-2026
01:30 | 7592.06 | 7749.7 | 15341.76
02:00 | 7458.56 | 7704.2 | 15162.76
02:30 | 7356.56 | 7628.6 | 14985.16
03:00 | 7254.56 | 7553 | 14807.56
03:30 | 7107.28 | 7535.5 | 14642.78
04:00 | 6960 | 7518 | 14478
04:30 | 6902.5 | 7496 | 14398.5
05:00 | 6845 | 7474 | 14319
05:30 | 6642.205 | 7323.715 | 13965.92
06:00 | 6439.41 | 7173.43 | 13612.84
06:30 | 6417.68 | 7106.13 | 13523.81
07:00 | 6395.95 | 7038.83 | 13434.78
07:30 | 6307.4 | 7057.905 | 13365.305
08:00 | 6218.85 | 7076.98 | 13295.83
08:30 | 6265.225 | 7135.015 | 13400.24
09:00 | 6311.6 | 7193.05 | 13504.65
09:30 | 6453.235 | 7269.655 | 13722.89
10:00 | 6594.87 | 7346.26 | 13941.13
10:30 | 6622.96 | 7379.33 | 14002.29
11:00 | 6651.05 | 7412.4 | 14063.45
11:30 | 6829.475 | 7478.79 | 14308.265
12:00 | 7007.9 | 7545.18 | 14553.08
12:30 | 7173.025 | 7623.26 | 14796.285
13:00 | 7338.15 | 7701.34 | 15039.49
13:30 | 7360.355 | 7755.985 | 15116.34
14:00 | 7382.56 | 7810.63 | 15193.19
14:30 | 7446.15 | 7745.15 | 15191.3
15:00 | 7509.74 | 7679.67 | 15189.41
15:30 | 7525.325 | 7645.93 | 15171.255
16:00 | 7540.91 | 7612.19 | 15153.1
16:30 | 7368.635 | 7395.43 | 14764.065
17:00 | 7196.36 | 7178.67 | 14375.03
17:30 | 7031.12 | 6880.135 | 13911.255
18:00 | 6865.88 | 6581.6 | 13447.48
18:30 | 7255.69 | 6929.385 | 14185.075
19:00 | 7645.5 | 7277.17 | 14922.67
19:30 | 8034.2 | 7626.1 | 15660.3
20:00 | 7951.2 | 7555.26 | 15506.46
20:30 | 8037.2 | 7651.365 | 15688.565 |  | Executive Engineer
21:00 | 8123.2 | 7747.47 | 15870.67 |  | Network Operation Division
21:30 | 8076.2 | 7762.335 | 15838.535
22:00 | 8029.2 | 7777.2 | 15806.4
22:30 | 8014.2 | 7878.915 | 15893.115
23:00 | 7999.2 | 7980.63 | 15979.83

## En-Curve
QF-LDC-12
Date | 03-06-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3421 | 2018 | 903 | 0 | 170 | 1452 | 100 | 5155 | 0 | 825 | 1766.76 | 0 | 0 | 0 | 391 | DAILY ENERGY CURVE
00:30 | 3414.5 | 1970.5 | 903.5 | 0 | 161 | 1447 | 100 | 5148.5 | 0 | 789.5 | 1731.26 | 0 | 0 | 0 | 321.5 | 03-06-2026
01:00 | 3408 | 1923 | 904 | 0 | 152 | 1442 | 100 | 5142 | 0 | 754 | 1695.76 | 0 | 0 | 0 | 252
01:30 | 3369.5 | 1834.5 | 903.5 | 0 | 150 | 1444 | 100 | 5141.5 | 0 | 754 | 1644.26 | 0 | 0 | 0.5 | 253.5 | Energy Generated | 356.8494 |  | MKWHr
02:00 | 3331 | 1746 | 903 | 0 | 148 | 1446 | 100 | 5141 | 0 | 754 | 1592.76 | 0 | 0 | 1 | 255 | Energy not Served | 5.885 |  | MKWHr
02:30 | 3340 | 1748 | 903.5 | 0 | 148 | 1447.5 | 99 | 5144 | 0 | 626.5 | 1528.16 | 0 | 0 | 0.5 | 250 | Total Energy Requirement | 362.7344 |  | MKWHr
03:00 | 3349 | 1750 | 904 | 0 | 148 | 1449 | 98 | 5147 | 0 | 499 | 1463.56 | 0 | 0 | 0 | 245
03:30 | 3378 | 1799 | 903.5 | 0 | 146 | 1446.5 | 98 | 5149 | 0 | 425.5 | 1297.28 | 0 | 0 | 0 | 232.5
04:00 | 3407 | 1848 | 903 | 0 | 144 | 1444 | 98 | 5151 | 0 | 352 | 1131 | 0 | 0 | 0 | 220
04:30 | 3397 | 1811 | 903 | 0 | 141 | 1437.5 | 97.5 | 5152.5 | 0 | 352 | 1107 | 0 | 0 | 0 | 215
05:00 | 3387 | 1774 | 903 | 0 | 138 | 1431 | 97 | 5154 | 0 | 352 | 1083 | 0 | 0 | 0 | 210
05:30 | 3359.5 | 1764.5 | 903 | 0 | 135 | 1434.5 | 98.5 | 5105 | 21.42 | 305 | 839.5 | 0 | 0 | 0 | 217
06:00 | 3332 | 1755 | 903 | 0 | 132 | 1438 | 100 | 5056 | 42.84 | 258 | 596 | 0 | 0 | 0 | 224
06:30 | 3364.5 | 1847 | 903.5 | 0 | 126 | 1435.5 | 100 | 4919.5 | 99.81 | 242 | 486 | 0 | 0 | 0 | 230
07:00 | 3397 | 1939 | 904 | 0 | 120 | 1433 | 100 | 4783 | 156.78 | 226 | 376 | 0 | 0 | 0 | 236
07:30 | 3374 | 1845.5 | 903.5 | 0 | 110 | 1437 | 100 | 4754.5 | 239.805 | 226 | 375 | 0 | 0 | 0 | 185.5
08:00 | 3351 | 1752 | 903 | 0 | 100 | 1441 | 100 | 4726 | 322.83 | 226 | 374 | 0 | 0 | 0 | 135
08:30 | 3353 | 1748.5 | 903.5 | 0 | 121 | 1441.315 | 100 | 4730 | 405.425 | 212 | 385.5 | 0 | 0 | 0 | 140
09:00 | 3355 | 1745 | 904 | 0 | 142 | 1441.63 | 100 | 4734 | 488.02 | 198 | 397 | 0 | 0 | 0 | 145
09:30 | 3398.5 | 1867.5 | 904 | 0 | 142 | 1444.12 | 100 | 4744.5 | 554.27 | 189.5 | 378.5 | 0 | 0 | 0 | 112.5
10:00 | 3442 | 1990 | 904 | 0 | 142 | 1446.61 | 100 | 4755 | 620.52 | 181 | 360 | 0 | 0 | 0 | 80
10:30 | 3417 | 1942.5 | 903.5 | 0 | 146 | 1441.06 | 100 | 4821.5 | 644.73 | 181 | 404 | 0 | 0 | 1 | 135.5
11:00 | 3392 | 1895 | 903 | 0 | 150 | 1435.51 | 100 | 4888 | 668.94 | 181 | 448 | 0 | 0 | 2 | 191
11:30 | 3391.5 | 1922.5 | 903 | 0 | 154 | 1436.77 | 100 | 4953.5 | 670.995 | 185 | 589.5 | 0 | 0 | 1.5 | 247.5
12:00 | 3391 | 1950 | 903 | 0 | 158 | 1438.03 | 100 | 5019 | 673.05 | 189 | 731 | 0 | 0 | 1 | 304
12:30 | 3353 | 1927 | 903 | 0 | 157 | 1439.735 | 100 | 5014 | 681.2 | 267 | 953.85 | 0 | 0 | 0.5 | 250
13:00 | 3315 | 1904 | 903 | 0 | 156 | 1441.44 | 100 | 5009 | 689.35 | 345 | 1176.7 | 0 | 0 | 0 | 196
13:30 | 3303.5 | 1918.5 | 903 | 0 | 158 | 1442.085 | 100 | 4987 | 628.055 | 392.5 | 1281.7 | 0 | 0 | 2 | 191
14:00 | 3292 | 1933 | 903 | 0 | 160 | 1442.73 | 100 | 4965 | 566.76 | 440 | 1386.7 | 0 | 0 | 4 | 186
14:30 | 3286.5 | 1938 | 903 | 0 | 164 | 1444.795 | 99 | 4967 | 491.205 | 439.5 | 1454.3 | 0 | 0 | 4 | 280
15:00 | 3281 | 1943 | 903 | 0 | 168 | 1446.86 | 98 | 4969 | 415.65 | 439 | 1521.9 | 0 | 0 | 4 | 374
15:30 | 3260.5 | 1885 | 903 | 0 | 167 | 1445.745 | 96.5 | 5040.5 | 368.11 | 449 | 1550.4 | 0 | 0 | 5.5 | 291
16:00 | 3240 | 1827 | 903 | 0 | 166 | 1444.63 | 95 | 5112 | 320.57 | 459 | 1578.9 | 0 | 0 | 7 | 208
16:30 | 3219.5 | 1806.5 | 903 | 0 | 159 | 1443.605 | 94.5 | 5004 | 206.66 | 463.5 | 1457.3 | 0 | 0 | 6.5 | 208
17:00 | 3199 | 1786 | 903 | 0 | 152 | 1442.58 | 94 | 4896 | 92.75 | 468 | 1335.7 | 0 | 0 | 6 | 208
17:30 | 3111.5 | 1722.5 | 903 | 0 | 148 | 1439.17 | 95.5 | 4673 | 62.485 | 470.5 | 1282.1 | 0 | 0 | 3.5 | 198
18:00 | 3024 | 1659 | 903 | 0 | 144 | 1435.76 | 97 | 4450 | 32.22 | 473 | 1228.5 | 0 | 0 | 1 | 188
18:30 | 3111.5 | 1787 | 903 | 0 | 151 | 1441.965 | 97.5 | 4664 | 16.11 | 560 | 1452.5 | 0 | 0 | 0.5 | 210.5
19:00 | 3199 | 1915 | 903 | 0 | 158 | 1448.17 | 98 | 4878 | 0 | 647 | 1676.5 | 0 | 0 | 0 | 233
19:30 | 3261 | 1849 | 904 | 0 | 160 | 1445.9 | 99 | 5099 | 0 | 747 | 2095.4 | 0 | 0 | 0 | 251
20:00 | 3271 | 1826 | 903 | 0 | 148 | 1441.26 | 100 | 5054 | 0 | 716 | 2047.2 | 0 | 0 | 0 | 207
20:30 | 3304 | 1867 | 903 | 0 | 151 | 1442.865 | 100 | 5114.5 | 0 | 744.5 | 2061.7 | 0 | 0 | 0 | 304
21:00 | 3337 | 1908 | 903 | 0 | 154 | 1444.47 | 100 | 5175 | 0 | 773 | 2076.2 | 0 | 0 | 0 | 401
21:30 | 3329.5 | 1917.5 | 903 | 0 | 157 | 1445.335 | 100 | 5211.5 | 0 | 777.5 | 1997.2 | 0 | 0 | 0 | 417.5
22:00 | 3322 | 1927 | 903 | 0 | 160 | 1446.2 | 100 | 5248 | 0 | 782 | 1918.2 | 0 | 0 | 0 | 434
22:30 | 3346 | 1953.5 | 903 | 0 | 160 | 1449.415 | 100 | 5331.5 | 0 | 778.5 | 1871.2 | 0 | 0 | 0 | 398
23:00 | 3370 | 1980 | 903 | 0 | 160 | 1452.63 | 100 | 5415 | 0 | 775 | 1824.2 | 0 | 0 | 0 | 362
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 03-06-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 133 | 34 | 382 | 128 | 1572 | 108 | Ishurdi-Ghorashal Ckt-1 | Export | 3608072.73
1:00 | 130 | 36 | 380 | 132 | 1552 | 106
2:00 | 131 | 37 | 352 | 144 | 1536 | 88 |  | Import | 0
3:00 | 125 | 32 | 348 | 122 | 1528 | 66
4:00 | 133 | 37 | 382 | 130 | 1574 | 102 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 126 | 30 | 392 | 140 | 1596 | 114
6:00 | 128 | 31 | 400 | 120 | 1668 | 120 |  | Import | 0
7:00 | 135 | 39 | 420 | 132 | 1514 | 134
8:00 | 142 | 41 | 460 | 150 | 1694 | 208 | Sirajganj-Sreepur Ckt-1 | Export | 2843000
9:00 | 156 | 49 | 522 | 164 | 1790 | 260
10:00 | 166 | 54 | 598 | 188 | 1960 | 360 |  | Import | 0
11:00 | 159 | 50 | 578 | 196 | 1956 | 312
12:00 | 159 | 56 | 540 | 196 | 1846 | 324 | Sirajganj-Sreepur Ckt-2 | Export | 2853000
13:00 | 166 | 59 | 530 | 180 | 1826 | 312
14:00 | 163 | 55 | 520 | 174 | 1882 | 258 |  | Import | 0
15:00 | 165 | 57 | 510 | 172 | 1866 | 274
16:00 | 175 | 64 | 570 | 210 | 2006 | 222 | Gopalganj-Aminbazar Ckt-1 | Export | 20720000
17:00 | 189 | 43 | 570 | 192 | 1902 | 348
18:00 | 181 | 30 | 570 | 176 | 1634 | 296 |  | Import | 0
18:30 | 185 | 31 | 580 | 192 | 1648 | 282
19:00 | 174 | 30 | 590 | 206 | 1694 | 212 | Gopalganj-Aminbazar Ckt-2 | Export | 20770000
19:30 | 159 | 20 | 490 | 158 | 1672 | 188
20:00 | 154 | 20 | 470 | 162 | 1616 | 178 |  | Import | 0
21:00 | 139 | 11 | 430 | 136 | 1642 | 154
22:00 | 130 | 10 | 440 | 150 | 1632 | 134 |  | Total Export | 50794072.73
23:00 | 137 | 15 | 460 | 162 | 1720 | 122 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 03-06-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 390 | 07:00 | 377 | 12:00 | Madunaghat | 400 | 00:00 | 393 | 11:00
Amtali | 413 | 18:00 | 404 | 23:00 | Meghnaghat | 396 | 07:00 | 383 | 23:00
Ashuganj | 406 | 6:00 | 391 | 16:00 | Payra | 415 | 18:30 | 407 | 13:00
Bhulta | 400 | 06:00 | 380 | 13:00 | Rahanpur | 403 | 18:00 | 386 | 00:00
Bibiana | 407 | 07:00 | 394 | 23:00 | Rampal | 399 | 18:30 | 383 | 23:00
BIPTC | 400 | 06:00 | 385 | 00:00
Bogura | 388 | 18:00 | 367 | 00:00
Gopalganj | 395 | 18:00 | 380 | 23:00
Kaliakoir | 387 | 02:00 | 373 | 23:00
Korerhat | 401 | 02:00 | 391 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 231 | 03:00 | 220 | 12:00 | Jhenaidah | 224 | 06:00 | 208 | 23:00
AKSML | 234 | 02:00 | 224 | 10:00 | Kachua | 227 | 18:00 | 218 | 11:00
Aminbazar | 232 | 05:00 | 221 | 12:00 | Kaliakoir | 229 | 06:00 | 218 | 12:00
Ashuganj | 228 | 05:00 | 221 | 12:00 | Keranigonj | 229 | 06:00 | 218 | 12:00
Ashuganj-400 | 228 | 05:00 | 221 | 12:00 | Khulna(S) | 224 | 08:00 | 208 | 23:00
Baghabari | 234 | 17:00 | 224 | 22:00 | Korerhat | 227 | 01:00 | 221 | 10:00
Barapukuria | 221 | 16:00 | 201 | 00:00 | Madunaghat | 234 | 01:00 | 227 | 10:00
Barapukuria-230 | 221 | 16:00 | 201 | 00:00 | Madunaghat-400 | 235 | 00:00 | 228 | 11:00
Barishal | 230 | 18:00 | 221 | 22:00 | Maniknagar | 229 | 07:00 | 216 | 12:00
Bheramara | 234 | 08:00 | 221 | 23:00 | Meghnaghat | 236 | 06:00 | 225 | 14:00
Bhulta | 231 | 06:00 | 217 | 13:00 | Meghnaghat-400 | 231 | 07:00 | 219 | 13:00
Bibiana | 235 | 05:00 | 228 | 13:00 | Mirsorai | 229 | 01:00 | 224 | 10:00
BIPTC | 237 | 08:00 | 220 | 23:00 | Naogaon | 217 | 17:00 | 197 | 00:00
Bogura | 241 | 18:00 | 226 | 00:00 | Purbasadipur | 219 | 18:00 | 199 | 00:00
Bogura-400 | 241 | 18:00 | 226 | 00:00 | Rajshahi | 234 | 18:30 | 218 | 23:00
Borhanuddin | 233 | 18:00 | 226 | 23:00 | Rampal | 225 | 08:00 | 212 | 23:00
BSRM | 228 | 02:00 | 221 | 10:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 227 | 18:00 | 219 | 10:00 | Rampura | 230 | 07:00 | 216 | 12:00
Cumilla(N) | 227 | 06:00 | 219 | 13:00 | Shikalbaha | 235 | 22:00 | 226 | 10:00
Faridpur | 227 | 08:00 | 216 | 23:00 | Shyampur | 229 | 07:00 | 219 | 12:00
Fenchuganj | 235 | 07:00 | 230 | 21:00 | Siddhirganj | 229 | 03:00 | 221 | 17:00
Feni | 226 | 01:00 | 219 | 12:00 | Sirajgonj | 240 | 18:00 | 233 | 00:00
Ghorashal | 230 | 04:00 | 220 | 14:00 | Sreepur | 225 | 06:00 | 218 | 16:00
Ghorashal-230 | 216 | 18:00 | 199 | 14:00 | Tongi | 224 | 04:00 | 210 | 13:00
Gopalganj | 229 | 18:00 | 219 | 23:00
GPH | 232 | 18:30 | 225 | 10:00
Haripur | 230 | 07:00 | 218 | 12:00
Hasnabad | 228 | 04:00 | 219 | 12:00
Hathazari | 232 | 18:00 | 225 | 10:00
Ishurdi | 236 | 18:30 | 223 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 06:00 | 123 | 13:00 | Madunaghat | 136 | 17:00 | 132 | 11:00
Agargaon | 133 | 06:00 | 124 | 13:00 | Magura | 129 | 09:00 | 116 | 23:00
Agrabad | 135 | 23:00 | 127 | 10:00 | Mahasthangarh | 139 | 18:00 | 123 | 00:00
AKS | 132 | 00:00 | 127 | 10:00 | Maijdee | 127 | 18:00 | 122 | 10:00
Aminbazar | 133 | 03:00 | 126 | 12:00 | Manikganj | 133 | 18:30 | 124 | 10:00
Amnura | 135 | 18:00 | 124 | 00:00 | Maniknagar | 128 | 05:00 | 119 | 13:00
Ashuganj | 135 | 04:00 | 131 | 23:00 | Matarbari | 116 | 17:00 | 110 | 00:00
Ashuganj-230 | 135 | 04:00 | 131 | 23:00 | Matuail | 131 | 07:00 | 124 | 12:00
Bagerhat | 126 | 08:00 | 112 | 23:00 | Metrorail_Motijheel | 129 | 05:00 | 119 | 13:00
Bajitpur | 125 | 18:00 | 121 | 14:00 | Metrorail_Uttara | 135 | 02:00 | 124 | 10:00
Bakerganj | 132 | 18:30 | 124 | 23:00 | Millgate | 136 | 02:00 | 125 | 12:00
Bakulia | 135 | 00:00 | 129 | 10:00 | Mirpur | 133 | 05:00 | 125 | 12:00
Banani | 134 | 06:00 | 123 | 12:00 | Mirzapur | 131 | 18:30 | 122 | 10:00
Bangabhaban | 128 | 05:00 | 119 | 12:00 | Mithapukur | 134 | 18:00 | 119 | 00:00
Barapukuria | 138 | 09:00 | 120 | 00:00 | MI_Cement | 131.5 | 06:00 | 123 | 13:00
Barguna | 131 | 18:00 | 123 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 18:00 | 124 | 23:00 | Mogbazar | 133 | 03:00 | 124 | 14:00
Barishal-230 | 132 | 18:00 | 125 | 22:00 | Mongla | 126 | 08:00 | 113 | 23:00
Baroaulia | 134 | 01:00 | 129 | 11:00 | Motijheel | 128 | 05:00 | 119 | 12:00
Baroirhat | 132 | 01:00 | 128 | 10:00 | Muktagacha | 127 | 09:00 | 116 | 00:00
Bashundhara | 136 | 03:00 | 123 | 13:00 | Munshiganj | 129 | 05:00 | 122 | 12:00
BashundharaCement | 130 | 08:00 | 123 | 12:00 | Muradnagar | 126 | 18:00 | 121 | 12:00
Beanibazar | 129 | 03:00 | 120 | 21:00 | Mymensingh | 126 | 18:30 | 113 | 12:00
Benapole | 125 | 07:00 | 111 | 23:00 | Nabinagar | 131 | 05:00 | 122 | 23:00
Bhaluka | 127 | 06:00 | 122 | 01:00 | Naogaon | 137 | 17:00 | 119 | 00:00
Bhandaria | 126 | 00:00 | 115 | 22:00 | Narail | 129 | 05:00 | 114 | 23:00
Bhangura | 134 | 18:00 | 126 | 00:00 | Narinda | 128 | 05:00 | 119 | 13:00
Bheramara | 136 | 08:00 | 129 | 23:00 | Narshingdi | 131 | 08:00 | 119 | 23:00
Bheramara(GK) | 137 | 18:30 | 130 | 00:00 | Natore | 137 | 01:00 | 126 | 00:00
Bhulta | 126 | 04:00 | 121 | 12:00 | Nawabganj | 133 | 06:00 | 125 | 13:00
Bog-Sherpur | 138 | 18:00 | 126 | 00:00 | Netrakona | 115 | 00:00 | 111 | 01:00
Bogura | 141 | 18:00 | 128 | 00:00 | New | 136 | 01:00 | 127 | 12:00
Bogura-230 | 140 | 18:00 | 129 | 00:00 | Niamatpur | 131 | 17:00 | 123 | 23:00
Brahmanbaria | 131 | 09:00 | 125 | 13:00 | Noapara | 128 | 08:00 | 116 | 23:00
Cantonment | 133 | 06:00 | 124 | 12:00 | Pabna | 134 | 18:00 | 127 | 00:00
Chandina | 130 | 03:00 | 125 | 12:00 | Palashbari | 133 | 18:00 | 116 | 00:00
Chandpur | 130 | 00:00 | 121 | 11:00 | Panchagarh | 137 | 05:00 | 127 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 136 | 01:00 | 131 | 10:00 | Patiya | 133 | 18:00 | 126 | 10:00
Chapai | 133 | 18:00 | 125 | 00:00 | Patuakhali | 131 | 18:00 | 125 | 23:00
Charsaidpur | 129 | 06:00 | 119 | 13:00 | Payra | 135 | 18:00 | 131 | 23:00
Chauddagram | 129 | 01:00 | 125 | 10:00 | PHP | 131 | 01:00 | 127 | 11:00
Chhatak | 126 | 01:00 | 117 | 19:00 | Postogola | 133 | 04:00 | 125 | 12:00
Chowmuhani | 127 | 18:00 | 121 | 11:00 | Pubail | 128 | 05:00 | 120 | 12:00
Chuadanga | 127 | 09:00 | 113 | 21:00 | Purbachal | 135 | 05:00 | 123 | 12:00
Coxsbazar | 119 | 07:00 | 112 | 06:00 | Purbasadipur | 132 | 16:00 | 120 | 00:00
Cumilla(N) | 130 | 02:00 | 125 | 13:00 | Rahanpur | 134 | 18:00 | 127 | 00:00
Cumilla(S) | 131 | 03:00 | 124 | 09:00 | Rahanpur-400 | 135 | 18:00 | 128 | 00:00
Daganbhuiyan | 129 | 01:00 | 124 | 11:00 | Rahim | 130 | 07:00 | 123 | 12:00
Daudkandi | 124 | 05:00 | 117 | 12:00 | Rajbari | 128 | 08:00 | 120 | 23:00
DhakaUniversity | 134 | 06:00 | 123 | 13:00 | Rajendrapur | 126 | 06:00 | 123 | 12:00
Dhamrai | 133 | 04:00 | 122 | 23:00 | Rajshahi | 133 | 18:00 | 124 | 00:00
Dhanmondi | 134 | 05:00 | 123 | 13:00 | Rajshahi-230 | 135 | 18:30 | 125 | 23:00
Dohazari | 130 | 23:00 | 122 | 10:00 | Ramganj | 125 | 00:00 | 118 | 11:00
Faridpur | 130 | 08:00 | 125 | 23:00 | Rampur | 134 | 03:00 | 128 | 11:00
Fatullah | 132 | 03:00 | 122 | 13:00 | Rampura | 134 | 06:00 | 123 | 13:00
Fenchuganj | 134 | 09:00 | 129 | 21:00 | Rangamati | 134 | 00:00 | 130 | 10:00
Feni | 129 | 01:00 | 125 | 10:00 | Rangpur | 132 | 17:00 | 116 | 00:00
Feni-230 | 130 | 01:00 | 126 | 10:00 | Ruppur | 137 | 18:00 | 129 | 23:00
Ghatail | 125 | 18:30 | 117 | 00:00 | Saidpur | 132 | 19:00 | 122 | 00:00
Ghorashal | 130 | 06:00 | 120 | 14:00 | Santhia | 135 | 18:00 | 128 | 00:00
Goalpara | 132 | 17:00 | 120 | 23:00 | Satkhira | 128 | 16:00 | 108 | 23:00
Gollamari | 131 | 08:00 | 120 | 23:00 | Satmasjid | 132 | 06:00 | 124 | 12:00
Gopalganj | 130 | 18:00 | 121 | 23:00 | Savar | 134 | 13:00 | 125 | 12:00
Gopalganj-400 | 133 | 07:00 | 126 | 23:00 | SevenRings | 130 | 05:00 | 121 | 12:00
Gulshan | 134 | 07:00 | 123 | 12:00 | ShahCement | 129 | 06:00 | 123 | 12:00
Halishahar | 135 | 00:00 | 125 | 13:00 | Shahjadpur | 136 | 17:00 | 132 | 00:00
Haripur | 131 | 07:00 | 124 | 12:00 | Shahjibazar | 133 | 09:00 | 125 | 22:00
HaripurSBU | 131 | 02:00 | 124 | 12:00 | Shahmirpur | 135 | 00:00 | 130 | 10:00
Hasnabad | 134 | 06:00 | 126 | 13:00 | Shariatpur | 130 | 18:00 | 120 | 23:00
Hathazari | 136 | 23:00 | 132 | 10:00 | Sherpur | 126 | 18:30 | 107 | 00:00
Hatirjheel | 134 | 07:00 | 124 | 12:00 | Shikalbaha | 126 | 23:00 | 118 | 10:00
Ishurdi | 138 | 18:00 | 130 | 23:00 | Shikalbaha-230 | 137 | 22:00 | 125 | 13:00
Jaldhaka | 130 | 17:00 | 117 | 00:00 | Shitalakhya | 131 | 03:00 | 123 | 13:00
Jamalpur | 128 | 18:30 | 113 | 00:00 | Sholosohor | 135 | 02:00 | 130 | 10:00
Jashore | 126 | 08:00 | 113 | 23:00 | Shomvuganj | 120 | 18:00 | 114 | 00:00
Jhenaidah | 132 | 08:00 | 119 | 23:00 | Shyampur | 130 | 07:00 | 122 | 14:00
Jhenaidah-230 | 132 | 09:00 | 120 | 23:00 | Shyampur-230 | 131 | 03:00 | 124 | 12:00
Joydebpur | 127 | 18:00 | 117 | 12:00 | Siddhirganj | 131 | 04:00 | 124 | 12:00
Joypurhat | 137 | 17:00 | 120 | 00:00 | Sirajganj | 134 | 18:00 | 124 | 00:00
Juldah | 136 | 00:00 | 130 | 10:00 | Sonargaon | 129 | 03:00 | 122 | 12:00
Kabirpur | 136 | 18:30 | 123 | 12:00 | Sreemongol | 130 | 06:00 | 124 | 21:00
Kachua | 129 | 18:00 | 124 | 10:00 | Sreepur | 130 | 05:00 | 126 | 13:00
Kaliakoir | 136 | 18:30 | 128 | 11:00 | Srinagar | 133 | 03:00 | 126 | 12:00
Kaliganj | 131 | 18:00 | 119 | 23:00 | SSM | 140 | 18:00 | 134 | 11:00
Kallyanpur | 133 | 00:00 | 126 | 12:00 | Sunamganj | 123 | 08:00 | 116 | 19:00
Kalurghat | 136 | 02:00 | 131 | 10:00 | Sylhet | 130 | 09:00 | 122 | 21:00
Kamrangirchar | 134 | 06:00 | 123 | 13:00 | Sylhet-132 | 129 | 07:00 | 124 | 19:00
Kaptai | N/A | N/A | N/A | N/A | Tangail | 126 | 18:30 | 118 | 10:00
Kasba | 125 | 03:00 | 120 | 12:00 | Taraganj | 131 | 17:00 | 118 | 00:00
Kazla | 128 | 07:00 | 119 | 13:00 | Tasnim | 128 | 05:00 | 122 | 12:00
Keranigonj | 134 | 03:00 | 127 | 12:00 | Thakurgaon | 134 | 05:00 | 124 | 23:00
Khagrachori | 133 | 01:00 | 130 | 11:00 | TK | 135 | 14:00 | 131 | 10:00
Khulna | 131 | 17:00 | 119 | 23:00 | Tongi | 137 | 04:00 | 128 | 15:00
Khulna(S) | 132 | 17:00 | 120 | 23:00 | Ullahpara | 135 | 18:30 | 126 | 00:00
Khulshi | 133 | 18:00 | 127 | 10:00 | Ullon | 133 | 05:00 | 123 | 12:00
Kishoreganj | 123 | 18:00 | 118 | 12:00 | Uttara | 136 | 02:00 | 124 | 13:00
Kodda | 135 | 19:30 | 124 | 10:00 | UttaraNew | 135 | 02:00 | 124 | 12:00
Korerhat | 134 | 01:00 | 130 | 10:00 | Zigatola | 135 | 06:00 | 127 | 12:00
KSRM | 135 | 00:00 | 130 | 10:00
Kulaura | 133 | 07:00 | 127 | 21:00
Kurigram | 129 | 18:00 | 112 | 00:00
Kushtia | 133 | 08:00 | 125 | 21:00
Laksam | 128 | 00:00 | 122 | 12:00
Lakshmipur | 126 | 18:00 | 121 | 11:00
Lalbag | 133 | 00:00 | 127 | 13:00
Lalmonirhat | 126 | 12:00 | 113 | 00:00
Madanganj | 130 | 07:00 | 123 | 12:00
Madaripur | 131 | 18:00 | 125 | 22:00
Madartek | 134 | 07:00 | 123 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division