## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 05-06-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-06-2026 | during | 05-06-2026 | during | 05-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Under Maintenance
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 402 | 409 | 412 | 412 | 412 | 412 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 160 | 160 | 225 | 225 | 161 | 161 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 140 | 139 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35.5 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 22 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 25 | 33 | 33 | 26 | 26 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 42 | 16 | 52.19 | 52.19 | 16 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 32 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 125 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 35 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 445 | 343 | 584 | 584 | 480 | 480 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 265 | 223 | 718 | 718 | 280 | 280 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 142 | 142 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1929 | 1822.5 | 5824.22 | 5792.22 | 2433.36 | 2561.36
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 8 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 100 | 100 | 100 | 100 | 100 | 100 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 211 | 215 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 92 | 97 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 21 | 67 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 22 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 2 | 74 | 108 | 108 | 24 | 60 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.37 | 0 | 4.61 | 0 | 4.61 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 32 | 51 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 24 | 24 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 10 | 15 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 35 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1225 | 1160 | 1224 | 1224 | 1204 | 1204 | AGC
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 0 | 0 | 2 | 0 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 521 | 1060 | 1150 | 1150 | 1150 | 1150 | AGC
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2329.37 | 2993 | 3996.47 | 4066.86 | 3267.97 | 3486.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 208 | 216 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 290 | 290 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 240 | 240 | 342.01 | 342.01 | 342.01 | 342.01 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 230 | 230 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 10 | 20 | 41.35 | 41.35 | 11 | 11 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 11 | 11 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 10 | 150 | 150 | 33 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 38 | 40 | 40 | 40 | 40 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 88 | 90 | 163 | 163 | 94 | 94 | ST Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 13 | 16 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 164 | 164 | 84 | 76 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 15 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 20 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 13 | 32 | 113 | 113 | 27 | 27 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 1 | 89 | 115 | 115 | 34 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1450 | 1505 | 2757.14 | 2694.14 | 2160.47 | 2278.47
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-06-2026 | during | 05-06-2026 | during | 05-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 9.61 | 0 | 10 | 0 | 10 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 9 | 10 | 157.5 | 157.5 | 25 | 25 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.1 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 134 | 127 | 140 | 140 | 140 | 140 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 18 | 10 | 10 | 10 | 10 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 7 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 0 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 182.71 | 172 | 443.9 | 384 | 251.9 | 204
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 41 | 41 | 41 | 41 | ps availability is less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 0 | 0 | 30 | 30 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 145 | 147 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 148 | 151 | 150 | 150 | 150 | 150 | ps availability is less
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 101 | 100 | 100 | 100 | 100 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 22 | 24 | 25 | 25 | 24 | 24 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 344 | 344 | 300 | 300 | 300 | 300 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1265 | 1263 | 1254 | 1254 | 1215 | 1215
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 904 | 903 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 33 | 36 | 36 | 36 | 36 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 187 | 188 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 33 | 105 | 105 | 90 | 90 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 95 | 0 | 60 | 0 | 60 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1107 | 1191 | 1234.2 | 1234.2 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2293 | 2348 | 3566.2 | 3506.2 | 2707 | 2647
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 957 | 1248 | 622 | 622 | 1244 | 1244 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 124 | 124 | STG Under Maintenance
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1130 | 972 | 1244 | 1244 | 1184 | 1184 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 0 | 150 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 232 | 274 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.49 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2659.49 | 2850 | 2784 | 2783 | 3170 | 3319
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 48.68 | 0 | 60 | 0 | 60 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 32 | 32 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 3 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 182 | 160 | 220 | 220 | 220 | 220 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 140 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 394 | 375 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 100 | 100 | 0 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 105 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 99 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.95 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1452.55 | 1182.53 | 1435.88 | 1435.88 | 1356 | 1356 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 45 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 76 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2346.18 | 1857.53 | 3028.57 | 2801.87 | 2613.31 | 2570.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 40 | 40 | 40 | 40 | 40 | 40 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 66 | 49 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.2 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 19 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 157 | 0 | 187.05 | 0 | 187.05 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 289.2 | 89 | 525.05 | 302 | 491.05 | 268
System Total |  |  |  |  | 28843.2 | 29290.237 | 14743.95 | 14900.03 | 24179.55 | 23584.29 | 18310.06 | 18549.8
Forecast Scenario (05-06-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 16090 |  | 0 |  | 16090
|  |  |  | 1:00 | 15425.0471 |  | 0 |  | 15425.0471
|  |  |  | 2:00 | 15366.5759 |  | 0 |  | 15366.5759
|  |  |  | 3:00 | 14860.6335 |  | 0 |  | 14860.6335
|  |  |  | 4:00 | 14408.3979 |  | 0 |  | 14408.3979
|  |  |  | 5:00 | 14054.1623 |  | 0 |  | 14054.1623
|  |  |  | 6:00 | 13459.6963 |  | 0 |  | 13459.6963
|  |  |  | 7:00 | 12931.7173 |  | 0 |  | 12931.7173
|  |  |  | 8:00 | 12950 |  | 0 |  | 12950
|  |  |  | 9:00 | 12800 |  | 0 |  | 12800
|  |  |  | 10:00 | 12980 |  | 0 |  | 12980
|  |  |  | 11:00 | 13070 |  | 0 |  | 13070
|  |  |  | 12:00 | 13200 |  | 0 |  | 13200
|  |  |  | 13:00 | 13562 |  | 0 |  | 13562
|  |  |  | 14:00 | 13554 |  | 0 |  | 13554
|  |  |  | 15:00 | 13566 |  | 0 |  | 13566
|  |  |  | 16:00 | 13480 |  | 0 |  | 13480
|  |  |  | 17:00 | 13214 |  | 0 |  | 13214
|  |  |  | 18:00 | 12544 |  | 0 |  | 12544
|  |  |  | 18:30 | 13859 |  | 0 |  | 13859
|  |  |  | 19:00 | 14291 |  | 0 |  | 14291
|  |  |  | 19:30 | 14351 |  | 0 |  | 14351
|  |  |  | 20:00 | 14527 |  | 0 |  | 14527
|  |  |  | 21:00 | 14600 |  | 0 |  | 14600
|  |  |  | 22:00 | 14578 |  | 0 |  | 14578
|  |  |  | 23:00 | 14300 |  | 0 |  | 14300
Probable Maximum Temperature: |  |  | 36.00°C
Probable Maximum Demand at Day Peak: |  |  | 13200.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14600.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14600.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 355.06 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:36 hrs on 05-06-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 04-06-2026 | [28 empty] | Date: | 04-06-2026 | [28 empty] | Date: | 04-06-2026 | [28 empty] | Date: | 04-06-2026 | [28 empty] | Date: | 04-06-2026 | [18 empty] | Date: | 04-06-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [18 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 236 | 0 | 0 | 42 | 142 | 97 | 15 | 35 | 35 | 0 | 160 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 23 | 21 | 0 | 400 | 95 | 16 | 76 | 0 | 0 | 50 | 47 | 38 | 25 | 24 | 0 | 100 | 110 | 36 | 555 | 0 | 0 | 50 | 25.5 | 105 | 217 | 0 | 0 | 0 | 1224 | 0 | 20 | 0 | 230 | 290 | 280 | 43 | 5 | 200 | 10 | 69 | 90 | 158 | 0 | 19 | 80 | 156 | 52.2 | 0 | 36 | 310 | 0 | 294 | 41 | 30 | 145 | 0 | 24 | 0 | 84 | 30 | 152 | 0 | 101 | 17 | 9 | 0 | 76 | 10 | 0 | 0 | 0 | 7898.7 | 904 | 164 | 0 | 30 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1207 | 77 | 0 | 0 | 1445.01 | 0 | 40 | 0 | 35 | 35 | 0 | 100 | 20 | 52.2 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 179 | 0 | 175 | 0 | 380 | 0 | 0 | 0 | 40 | 95 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 1244 | 1050 | 17 | 8117.21 | 16015.91 | 76.04
01:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 216 | 0 | 0 | 17 | 142 | 32 | 15 | 35 | 17 | 0 | 160 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 23 | 21 | 0 | 350 | 91 | 16 | 38 | 0 | 0 | 50 | 47 | 38 | 25 | 24 | 0 | 100 | 110 | 37 | 555 | 0 | 0 | 50 | 0 | 105 | 217 | 0 | 0 | 0 | 1225 | 0 | 20 | 0 | 230 | 290 | 280 | 43 | 5 | 200 | 10 | 52 | 90 | 171 | 0 | 19 | 102 | 148 | 52.2 | 0 | 36 | 310 | 0 | 294 | 41 | 30 | 136 | 9 | 24 | 0 | 85 | 30 | 151 | 0 | 103 | 17 | 9 | 0 | 67 | 10 | 0 | 0 | 0 | 7664.2 | 904 | 162 | 0 | 29 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1225 | 77 | 0 | 0 | 1451.62 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 20 | 52.2 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 179 | 0 | 175 | 0 | 345 | 0 | 0 | 0 | 40 | 93 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 1250 | 1130 | 17 | 8087.82 | 15752.02 | 76.03
02:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 256 | 0 | 0 | 17 | 110 | 32 | 15 | 35 | 0 | 0 | 160 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 23 | 21 | 0 | 450 | 92 | 16 | 24 | 0 | 0 | 0 | 0 | 17 | 25 | 24 | 0 | 100 | 110 | 37 | 555 | 0 | 0 | 50 | 0 | 105 | 217 | 0 | 0 | 0 | 1160 | 0 | 16 | 0 | 230 | 290 | 280 | 43 | 5 | 200 | 10 | 0 | 90 | 171 | 0 | 19 | 37 | 148 | 43 | 0 | 36 | 305 | 0 | 294 | 41 | 30 | 141 | 0 | 24 | 0 | 85 | 30 | 150 | 0 | 102 | 17 | 9 | 0 | 77 | 10 | 0 | 0 | 0 | 7390 | 904 | 165 | 0 | 29 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1174 | 77 | 0 | 0 | 1362.67 | 0 | 39 | 0 | 35 | 35 | 0 | 0 | 20 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 175 | 0 | 393 | 0 | 0 | 0 | 40 | 94 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 275 | 120 | 180 | 0 | 1246 | 1120 | 17 | 7853.67 | 15243.67 | 76.03
03:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 268 | 0 | 0 | 17 | 46 | 32 | 15 | 0 | 0 | 0 | 160 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 23 | 21 | 0 | 480 | 95 | 16 | 24 | 0 | 0 | 0 | 0 | 17 | 25 | 24 | 0 | 100 | 110 | 38 | 555 | 0 | 0 | 50 | 0 | 105 | 217 | 0 | 0 | 0 | 1160 | 0 | 20 | 0 | 230 | 290 | 280 | 43 | 5 | 195 | 10 | 0 | 92 | 120 | 0 | 19 | 0 | 146 | 52.2 | 0 | 37 | 315 | 0 | 294 | 41 | 30 | 152 | 0 | 24 | 0 | 85 | 30 | 151 | 0 | 102 | 0 | 9 | 0 | 77 | 22 | 0 | 0 | 0 | 7263.2 | 903 | 166 | 0 | 29 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1059 | 79 | 0 | 0 | 1362.68 | 0 | 38 | 0 | 35 | 35 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 175 | 0 | 407 | 0 | 0 | 0 | 40 | 95 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 240 | 120 | 180 | 0 | 1200 | 1120 | 17 | 7649.68 | 14912.88 | 76.03
04:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 253 | 0 | 0 | 17 | 15 | 32 | 15 | 0 | 0 | 0 | 160 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 23 | 21 | 0 | 450 | 94 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 25 | 24 | 0 | 100 | 110 | 38 | 555 | 0 | 0 | 50 | 0 | 105 | 219 | 0 | 0 | 0 | 1160 | 0 | 20 | 0 | 230 | 290 | 280 | 43 | 5 | 200 | 10 | 0 | 92 | 85 | 0 | 19 | 0 | 144 | 52.2 | 0 | 15 | 310 | 0 | 294 | 41 | 30 | 149 | 0 | 24 | 0 | 85 | 30 | 152 | 0 | 102 | 0 | 9 | 0 | 78 | 33 | 0 | 0 | 0 | 7063.2 | 904 | 170 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1046 | 78 | 0 | 0 | 1367.36 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 175 | 0 | 409 | 0 | 0 | 0 | 41 | 70 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 238 | 100 | 180 | 0 | 1200 | 1110 | 17 | 7484.36 | 14547.56 | 76.03
05:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 229 | 0 | 0 | 17 | 0 | 32 | 15 | 0 | 0 | 0 | 160 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 23 | 21 | 0 | 395 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 25 | 24 | 0 | 97 | 110 | 22 | 555 | 0 | 0 | 0 | 0 | 105 | 219 | 0 | 0 | 0 | 1160 | 0 | 20 | 0 | 230 | 290 | 280 | 51 | 5 | 193 | 10 | 0 | 93 | 17 | 0 | 19 | 0 | 138 | 8 | 0 | 0 | 310 | 0 | 294 | 41 | 30 | 148 | 0 | 24 | 0 | 85 | 30 | 151 | 0 | 101 | 0 | 9 | 0 | 78 | 33 | 0 | 0 | 0 | 6682 | 903 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1076 | 63 | 0 | 0 | 1368.44 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 176 | 0 | 359 | 0 | 0 | 0 | 41 | 67 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 235 | 120 | 220 | 0 | 1200 | 1110 | 17 | 7501.44 | 14183.44 | 76.03
06:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 208 | 0 | 0 | 17 | 0 | 32 | 15 | 0 | 0 | 0 | 160 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 142 | 23 | 21 | 0 | 330 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 25 | 24 | 0.36 | 97 | 85 | 29 | 555 | 0 | 0 | 0 | 0 | 51 | 219 | 0 | 0 | 0 | 1160 | 0 | 20 | 0 | 230 | 290 | 240 | 51 | 5 | 203 | 10 | 0 | 93 | 14 | 0 | 19 | 0 | 134 | 8 | 5 | 0 | 305 | 0 | 325 | 41 | 30 | 125 | 0 | 24 | 0 | 85 | 30 | 151 | 0 | 101 | 0 | 9 | 1.35 | 78 | 33 | 0.2 | 0 | 0 | 6494.91 | 904 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.11 | 1142 | 50 | 0 | 0 | 1272.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.61 | 3 | 0 | 0 | 2.59 | 0 | 0 | 187 | 0 | 181 | 0 | 339 | 0 | 0.29 | 0 | 41 | 35 | 2 | 70 | 0 | 0 | 0 | 0.4 | 10 | 0.04 | 0 | 238 | 120 | 220 | 0 | 1100 | 1110 | 0 | 7216.71 | 13711.62 | 76.03
07:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 206 | 0 | 0 | 17 | 0 | 32 | 15 | 0 | 0 | 0 | 160 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 123 | 23 | 21 | 0 | 330 | 13 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 0.87 | 95 | 17 | 32 | 555 | 0 | 0 | 0 | 0 | 17 | 216 | 0 | 0 | 0 | 1160 | 5 | 20 | 0 | 230 | 290 | 240 | 51 | 5 | 215 | 10 | 0 | 92 | 15 | 0 | 19 | 0 | 132 | 8 | 17 | 0 | 310 | 0 | 337 | 41 | 30 | 124 | 1 | 20 | 0 | 85 | 30 | 150 | 0 | 101 | 0 | 9 | 5.15 | 77 | 34 | 0.6 | 5.32 | 0 | 6402.94 | 904 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.37 | 1147 | 32 | 0 | 0 | 1276.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.26 | 20 | 0 | 0 | 10.95 | 0 | 0 | 187 | 0 | 185 | 0 | 335 | 0 | 0.97 | 0 | 40 | 33 | 5 | 70 | 0 | 0 | 0 | 1.5 | 41 | 0.02 | 0 | 238 | 120 | 220 | 0 | 1000 | 1110 | 0 | 7193.33 | 13596.27 | 76.03
08:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 205 | 0 | 0 | 17 | 0 | 32 | 15 | 0 | 0 | 0 | 160 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 123 | 23 | 21 | 0 | 345 | 13 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 1.6 | 98 | 17 | 8 | 555 | 0 | 0 | 0 | 0 | 17 | 215 | 0 | 0 | 0 | 1160 | 10 | 20 | 0 | 230 | 290 | 240 | 51 | 5 | 199 | 10 | 0 | 90 | 15 | 0 | 19 | 0 | 136 | 8 | 35 | 0 | 300 | 0 | 344 | 40 | 30 | 122 | 0 | 20 | 0 | 85 | 30 | 151 | 0 | 101 | 0 | 9 | 9.79 | 77 | 31 | 0.6 | 21.18 | 0 | 6417.17 | 904 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.39 | 1132 | 32 | 0 | 0 | 1212.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.69 | 35 | 0 | 0 | 21.66 | 0 | 0 | 186 | 0 | 184 | 0 | 334 | 0 | 1.86 | 0 | 40 | 0 | 12 | 70 | 0 | 0 | 0 | 3.3 | 82 | 0.33 | 0 | 218 | 120 | 180 | 0 | 917 | 1105 | 0 | 7035.78 | 13452.95 | 76.03
09:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 230 | 0 | 0 | 17 | 0 | 32 | 15 | 0 | 0 | 0 | 160 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 130 | 23 | 21 | 0 | 430 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 3.23 | 99 | 17 | 2 | 555 | 0 | 0 | 0 | 0 | 17 | 214 | 0 | 0 | 0 | 1160 | 13 | 20 | 0 | 230 | 290 | 240 | 51 | 5 | 212 | 10 | 0 | 89 | 15 | 0 | 19 | 0 | 144 | 8 | 48 | 0 | 310 | 0 | 355 | 40 | 30 | 136 | 3 | 20 | 0 | 86 | 30 | 152 | 0 | 101 | 0 | 9 | 13.18 | 117 | 30 | 0.6 | 33.13 | 0 | 6699.14 | 903 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 1086 | 0 | 0 | 0 | 1206.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.89 | 58 | 0 | 0 | 24.22 | 0 | 0 | 185 | 0 | 140 | 0 | 348 | 0 | 2.63 | 0 | 40 | 0 | 16 | 70 | 0 | 0 | 0 | 5 | 121 | 0.5 | 0 | 221 | 120 | 180 | 0 | 855 | 1115 | 0 | 6981.56 | 13680.7 | 76.03
10:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 253 | 0 | 0 | 17 | 0 | 32 | 15 | 0 | 17 | 0 | 160 | 140 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 142 | 23 | 21 | 0 | 440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 4.02 | 99 | 17 | 7 | 545 | 0 | 0 | 2 | 0 | 17 | 214 | 0 | 0 | 0 | 1160 | 16 | 20 | 0 | 230 | 290 | 240 | 51 | 0 | 211 | 10 | 0 | 89 | 0 | 0 | 19 | 0 | 148 | 0 | 60 | 0 | 310 | 0 | 356 | 40 | 30 | 146 | 6 | 20 | 0 | 85 | 30 | 151 | 0 | 101 | 0 | 9 | 16.67 | 133 | 10 | 1.7 | 13.76 | 0 | 6741.15 | 903 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 1086 | 0 | 0 | 0 | 1247.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.33 | 80 | 0 | 0 | 40.07 | 0 | 0 | 184 | 0 | 140 | 0 | 387 | 0 | 3.98 | 0 | 40 | 0 | 25 | 70 | 0 | 0 | 0 | 6.2 | 148 | 0.63 | 0 | 217 | 120 | 220 | 0 | 880 | 1105 | 0 | 7203.64 | 13944.79 | 76.03
11:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 258 | 4 | 0 | 29 | 0 | 32 | 15 | 10 | 17 | 0 | 160 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 142 | 23 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 4.53 | 100 | 17 | 3 | 522 | 0 | 0 | 24 | 0 | 18 | 212 | 0 | 0 | 0 | 1160 | 16 | 20 | 0 | 230 | 290 | 240 | 51 | 0 | 210 | 10 | 0 | 89 | 0 | 0 | 19 | 0 | 156 | 0 | 65 | 0 | 315 | 0 | 356 | 41 | 30 | 151 | 10 | 20 | 0 | 84 | 30 | 148 | 0 | 101 | 0 | 9 | 14.13 | 134 | 10 | 1.8 | 1.28 | 10 | 6805.74 | 903 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 1112 | 0 | 0 | 0 | 1309.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.84 | 91 | 0 | 0 | 49.85 | 0 | 0 | 182 | 0 | 140 | 0 | 378 | 0 | 4.66 | 0 | 40 | 0 | 28 | 69 | 0 | 0 | 0 | 6.7 | 174 | 0.64 | 0 | 241 | 120 | 220 | 0 | 973 | 1125 | 0 | 7499.7 | 14305.44 | 76.03
12:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 265 | 17 | 0 | 34 | 22 | 32 | 15 | 35 | 17 | 0 | 160 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 142 | 23 | 21 | 0 | 445 | 10 | 16 | 2 | 0 | 1 | 0 | 21 | 0 | 25 | 24 | 4.37 | 100 | 32 | 3 | 521 | 0 | 0 | 25 | 0 | 92 | 211 | 0 | 0 | 0 | 1225 | 17 | 20 | 0 | 230 | 290 | 240 | 51 | 0 | 208 | 10 | 1 | 88 | 13 | 13 | 19 | 20 | 164 | 15 | 68 | 0 | 310 | 0 | 344 | 41 | 30 | 145 | 10 | 22 | 0 | 84 | 30 | 148 | 0 | 101 | 0 | 9 | 9.61 | 134 | 9 | 2.1 | 7 | 12 | 7156.08 | 904 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 1107 | 0 | 0 | 0 | 1452.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 48.68 | 76 | 0 | 0 | 45 | 0 | 0 | 182 | 0 | 140 | 0 | 394 | 0 | 4.95 | 0 | 40 | 0 | 19 | 66 | 0 | 0 | 0 | 7.2 | 157 | 0.49 | 0 | 232 | 120 | 220 | 0 | 957 | 1130 | 0 | 7587.87 | 14743.95 | 76.03
13:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 267 | 17.5 | 0 | 34 | 47 | 32 | 15 | 35 | 17 | 0 | 160 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 142 | 23 | 21 | 0 | 440 | 17 | 16 | 22 | 0 | 1 | 0 | 22 | 0 | 25 | 24 | 4.18 | 100 | 74 | 3 | 523 | 0 | 0 | 25 | 6 | 105 | 209 | 0 | 0 | 0 | 1224 | 17 | 20 | 0 | 230 | 290 | 240 | 51 | 0 | 202 | 20 | 27 | 87 | 88 | 17 | 18 | 52 | 164 | 43 | 66 | 28 | 310 | 0 | 344 | 41 | 30 | 156 | 9 | 22 | 0 | 83 | 30 | 145 | 0 | 101 | 0 | 9 | 8.15 | 133 | 8 | 2 | 2.84 | 12 | 7448.67 | 903 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 1118 | 10 | 0 | 0 | 1458.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 44.59 | 92 | 0 | 0 | 46.58 | 0 | 0 | 160 | 0 | 140 | 0 | 382 | 0 | 4.68 | 0 | 40 | 0 | 18 | 69 | 0 | 0 | 0 | 6.6 | 132 | 0.22 | 0 | 243 | 120 | 220 | 0 | 958 | 1100 | 0 | 7548.55 | 14997.22 | 76.03
14:00 | 0 | 105 | 40 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 243 | 17.5 | 3 | 34 | 75 | 32 | 15 | 35 | 17 | 0 | 160 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 142 | 0 | 21 | 0 | 380 | 37 | 16 | 47 | 0 | 8 | 0 | 22 | 0 | 25 | 24 | 3.66 | 100 | 107 | 2 | 525 | 0 | 0 | 25 | 15 | 105 | 209 | 0 | 0 | 0 | 1160 | 16 | 20 | 0 | 230 | 290 | 240 | 51 | 0 | 201 | 20 | 34 | 86 | 138 | 11 | 18 | 72 | 162 | 43 | 61 | 27 | 310 | 0 | 320 | 42 | 30 | 143 | 3 | 22 | 0 | 83 | 30 | 143 | 0 | 101 | 0 | 9 | 5.5 | 137 | 7 | 0.6 | 38.81 | 12 | 7472.07 | 904 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 1207 | 35 | 0 | 0 | 1376.75 | 0 | 0 | 0 | 5 | 8 | 0 | 0 | 5 | 0 | 27.3 | 82 | 0 | 0 | 38.58 | 0 | 0 | 160 | 0 | 140 | 0 | 378 | 0 | 3.64 | 0 | 38 | 70 | 20 | 69 | 0 | 0 | 0 | 3.4 | 113 | 0.23 | 0 | 211 | 120 | 220 | 0 | 928 | 1100 | 0 | 7529.9 | 15001.97 | 76.03
15:00 | 0 | 105 | 31 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 271 | 0 | 17 | 34 | 75 | 32 | 0 | 35 | 17 | 0 | 160 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 142 | 24 | 21 | 0 | 440 | 48 | 16 | 48 | 0 | 6 | 0 | 36 | 0 | 25 | 24 | 1.85 | 99 | 106 | 2 | 525 | 0 | 0 | 0 | 15 | 100 | 209 | 0 | 0 | 0 | 1160 | 12 | 20 | 0 | 230 | 290 | 240 | 51 | 0 | 199 | 20 | 32 | 86 | 141 | 8 | 18 | 84 | 172 | 41 | 30 | 27 | 310 | 0 | 320 | 42 | 30 | 153 | 3 | 22 | 0 | 85 | 30 | 145 | 0 | 101 | 0 | 9 | 11.97 | 136 | 7 | 1.5 | 33.58 | 12 | 7537.9 | 903 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 1216 | 48 | 0 | 0 | 1400.65 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 7 | 0 | 25.66 | 63 | 0 | 0 | 15.46 | 0 | 0 | 160 | 0 | 140 | 0 | 403 | 0 | 1.85 | 0 | 37 | 93 | 18 | 68 | 0 | 0 | 0 | 4.9 | 90 | 0.47 | 0 | 227 | 120 | 220 | 0 | 992 | 1065 | 0 | 7609.99 | 15147.89 | 76.03
16:00 | 0 | 105 | 32 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 229 | 0 | 0 | 34 | 75 | 32 | 0 | 35 | 17 | 0 | 160 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 142 | 24 | 21 | 0 | 400 | 50 | 16 | 54 | 0 | 6 | 0 | 58 | 0 | 25 | 24 | 1.76 | 95 | 107 | 2 | 530 | 0 | 0 | 0 | 15 | 96 | 210 | 0 | 0 | 0 | 1160 | 8 | 20 | 0 | 230 | 290 | 240 | 51 | 0 | 210 | 20 | 31 | 86 | 140 | 8 | 18 | 83 | 162 | 43 | 29 | 27 | 315 | 0 | 326 | 42 | 30 | 144 | 1 | 22 | 0 | 85 | 30 | 144 | 0 | 101 | 0 | 9 | 8.78 | 0 | 7 | 1.1 | 20.69 | 0 | 7290.33 | 903 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 1218 | 46 | 0 | 0 | 1355.28 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 8 | 0 | 21.62 | 43 | 0 | 0 | 22.17 | 0 | 0 | 160 | 0 | 140 | 0 | 350 | 0 | 2.11 | 0 | 37 | 93 | 13 | 68 | 0 | 0 | 0 | 1.8 | 86 | 0.3 | 0 | 200 | 120 | 220 | 0 | 886 | 1095 | 0 | 7362.28 | 14652.61 | 76.03
17:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 209 | 0 | 12 | 53 | 46 | 32 | 0 | 35 | 17 | 0 | 160 | 139 | 0 | 0 | 17 | 0 | 0 | 0 | 3 | 142 | 20 | 21 | 0 | 350 | 52 | 16 | 56 | 0 | 4 | 0 | 68 | 0 | 25 | 24 | 0.85 | 95 | 51 | 2 | 620 | 0 | 0 | 0 | 19 | 95 | 211 | 0 | 0 | 0 | 1160 | 3 | 18 | 0 | 230 | 290 | 240 | 51 | 0 | 215 | 20 | 35 | 87 | 100 | 25 | 18 | 34 | 166 | 25 | 14 | 29 | 310 | 0 | 354 | 42 | 30 | 130 | 1 | 22 | 0 | 85 | 30 | 151 | 0 | 101 | 0 | 9 | 5.21 | 0 | 7 | 0.5 | 11.59 | 1 | 7191.15 | 904 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1212 | 46 | 0 | 0 | 1219.76 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 2.08 | 18 | 0 | 0 | 9.24 | 0 | 0 | 160 | 0 | 140 | 0 | 342 | 0 | 0.83 | 0 | 38 | 50 | 5 | 77 | 0 | 0 | 0 | 0.5 | 32 | 0.15 | 0 | 176 | 120 | 220 | 0 | 748 | 990 | 0 | 6779.56 | 13970.71 | 76.02
18:00 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 209 | 17 | 17 | 52 | 15 | 30 | 0 | 35 | 16 | 0 | 160 | 137 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 142 | 24 | 21 | 0 | 340 | 17 | 16 | 66 | 0 | 6 | 0 | 67 | 0 | 25 | 24 | 0.14 | 96 | 33 | 12 | 650 | 0 | 0 | 0 | 25.5 | 17 | 212 | 0 | 0 | 0 | 1000 | 1 | 13 | 0 | 230 | 290 | 240 | 51 | 0 | 216 | 20 | 34 | 88 | 17 | 27 | 18 | 30 | 144 | 8 | 3 | 29 | 300 | 0 | 307 | 42 | 30 | 121 | 0 | 0 | 0 | 43 | 30 | 148 | 0 | 101 | 16 | 18 | 0.38 | 64 | 7 | 0 | 1.9 | 0 | 6657.92 | 903 | 183 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 1161 | 47 | 0 | 0 | 1079.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72 | 0 | 0 | 0 | 0.36 | 0 | 0 | 160 | 0 | 140 | 0 | 345 | 0 | 0.03 | 0 | 39 | 35 | 1 | 77 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 171 | 100 | 180 | 0 | 749 | 925 | 0 | 6317.28 | 12975.2 | 76.02
19:00 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 277 | 35 | 17 | 71 | 42 | 32 | 0 | 35 | 65 | 0 | 160 | 144 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 142 | 24 | 21 | 0 | 440 | 30 | 16 | 75 | 0 | 1 | 15 | 67 | 1 | 25 | 24 | 0 | 100 | 35 | 13 | 662 | 0 | 0 | 0 | 25.5 | 33 | 212 | 0 | 0 | 0 | 1224 | 0 | 25 | 0 | 230 | 290 | 240 | 51 | 0 | 215 | 20 | 36 | 90 | 16 | 27 | 19 | 50 | 174 | 11 | 0 | 31 | 310 | 0 | 341 | 41 | 30 | 140 | 0 | 16 | 0 | 86 | 30 | 147 | 0 | 101 | 17 | 18 | 0 | 121 | 10 | 0 | 0 | 0 | 7534.5 | 903 | 188 | 0 | 30 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1052 | 55 | 0 | 0 | 1094.54 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 404 | 0 | 0 | 0 | 39 | 35 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222 | 120 | 220 | 0 | 932 | 940 | 7 | 6710.54 | 14245.04 | 76.02
19:30 | 0 | 90 | 50 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 202 | 35 | 17 | 133 | 60 | 75 | 0 | 35 | 66 | 0 | 160 | 136 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 142 | 24 | 21 | 0 | 330 | 45 | 16 | 75 | 0 | 0 | 44 | 67 | 17 | 25 | 24 | 0 | 100 | 65 | 16 | 680 | 16 | 0 | 0 | 25.5 | 105 | 215 | 0 | 0 | 0 | 1120 | 0 | 148 | 0 | 230 | 290 | 240 | 51 | 0 | 216 | 20 | 90 | 90 | 46 | 27 | 19 | 80 | 162 | 43 | 0 | 38 | 310 | 0 | 349 | 41 | 30 | 130 | 0 | 16 | 0 | 85 | 30 | 147 | 0 | 101 | 17 | 18 | 0 | 121 | 10 | 0 | 0 | 0 | 7816.5 | 893 | 188 | 0 | 38 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1138 | 67 | 0 | 0 | 1023.49 | 0 | 32 | 0 | 0 | 0 | 0 | 95 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 332 | 0 | 0 | 0 | 40 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 258 | 100 | 180 | 0 | 1102 | 976 | 35 | 6943.49 | 14759.99 | 0
20:00 | 0 | 86 | 24 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 229 | 35.5 | 17 | 120 | 15 | 97 | 0 | 35 | 66 | 0 | 160 | 138 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 142 | 24 | 21 | 0 | 330 | 17 | 16 | 75 | 0 | 0 | 50 | 67 | 17 | 25 | 24 | 0 | 100 | 85 | 20 | 783 | 11 | 0 | 0 | 8 | 105 | 214 | 0 | 0 | 0 | 1120 | 0 | 80 | 0 | 230 | 290 | 240 | 51 | 0 | 216 | 20 | 84 | 90 | 17 | 27 | 19 | 17 | 160 | 8 | 0 | 38 | 305 | 0 | 350 | 41 | 29 | 133 | 0 | 16 | 0 | 85 | 30 | 152 | 0 | 101 | 17 | 18 | 0 | 126 | 10 | 0 | 0 | 0 | 7684.5 | 903 | 190 | 0 | 27 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1180 | 67 | 0 | 0 | 1020.67 | 0 | 40 | 0 | 0 | 0 | 0 | 100 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 379 | 0 | 0 | 0 | 39 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 257 | 120 | 220 | 0 | 1250 | 960 | 17 | 7196.67 | 14881.17 | 76.02
21:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 223 | 35.5 | 17 | 125 | 0 | 45 | 0 | 0 | 35 | 0 | 160 | 139 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 142 | 25 | 21 | 0 | 343 | 15 | 16 | 74 | 0 | 0 | 50 | 67 | 17 | 25 | 24 | 0 | 100 | 51 | 22 | 1060 | 0 | 0 | 0 | 0 | 97 | 215 | 0 | 0 | 0 | 1160 | 0 | 10 | 0 | 230 | 290 | 240 | 51 | 0 | 216 | 20 | 89 | 90 | 16 | 32 | 19 | 0 | 164 | 0 | 0 | 38 | 310 | 0 | 344 | 41 | 30 | 147 | 0 | 24 | 0 | 85 | 30 | 151 | 0 | 101 | 17 | 18 | 0 | 127 | 10 | 0 | 0 | 0 | 7755.5 | 903 | 188 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1191 | 33 | 0 | 0 | 1182.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 375 | 0 | 0 | 0 | 40 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 274 | 120 | 220 | 0 | 1248 | 972 | 0 | 7144.53 | 14900.03 | 76.02
22:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 209 | 35.5 | 17 | 96 | 0 | 15 | 0 | 0 | 16 | 0 | 160 | 141 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 142 | 25 | 21 | 0 | 340 | 13 | 16 | 61 | 0 | 0 | 50 | 67 | 17 | 25 | 24 | 0 | 100 | 51 | 23 | 1065 | 0 | 0 | 14 | 0 | 91 | 216 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 230 | 290 | 240 | 51 | 0 | 217 | 20 | 50 | 91 | 14 | 27 | 19 | 0 | 162 | 0 | 0 | 37 | 305 | 0 | 320 | 41 | 30 | 124 | 0 | 24 | 0 | 85 | 28 | 154 | 0 | 101 | 0 | 9 | 0 | 77 | 10 | 0 | 0 | 0 | 7459.5 | 904 | 189 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1187 | 0 | 0 | 0 | 1455.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 355 | 0 | 0 | 0 | 40 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 275 | 120 | 180 | 0 | 1144 | 1150 | 0 | 7398.75 | 14858.25 | 76.02
23:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 280 | 35.5 | 17 | 96 | 0 | 15 | 0 | 0 | 31 | 0 | 160 | 143 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 142 | 15 | 21 | 0 | 460 | 16 | 16 | 56 | 0 | 0 | 50 | 67 | 17 | 25 | 24 | 0 | 100 | 51 | 25 | 1070 | 0 | 0 | 50 | 0 | 100 | 216 | 0 | 0 | 0 | 1165 | 0 | 0 | 0 | 230 | 290 | 240 | 51 | 0 | 215 | 20 | 50 | 91 | 17 | 0 | 19 | 0 | 166 | 0 | 0 | 37 | 315 | 0 | 320 | 41 | 30 | 148 | 0 | 24 | 0 | 85 | 28 | 149 | 0 | 100 | 0 | 9 | 0 | 77 | 10 | 0 | 0 | 0 | 7678.5 | 903 | 190 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1195 | 0 | 0 | 0 | 1461.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 408 | 0 | 0 | 0 | 40 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 275 | 120 | 180 | 0 | 969 | 1230 | 0 | 7370.06 | 15048.56 | 76.02
Total KWH | 0 | 2060160 | 849600 | 0 | 0 | 0 | 0 | 0 | 9122400 | 0 | 5822292 | 259920 | 152640 | 1070064 | 789600 | 862876 | 217664 | 415487 | 427680 | 0 | 4027000 | 3357498 | 0 | 0 | 220507 | 0 | 0 | 0 | 194000 | 3445200 | 516000 | 513360 | 0 | 9724545.45 | 904527 | 356291 | 795840 | 0 | 34080 | 306103 | 728064 | 253464 | 575040 | 584640 | 29684 | 2283956 | 1714545 | 435360 | 15214545.46 | 6691 | 0 | 464160 | 161969.4 | 1937018 | 5244076 | 0 | 0 | 0 | 27850906 | 131355 | 538618 | 0 | 5677500 | 7393200 | 6076000 | 1235064 | 54720 | 5100000 | 374904 | 639360 | 2141559 | 1535040 | 232680 | 460840 | 703380 | 3672960 | 541781 | 511855 | 509664 | 7500000 | 0 | 7995000 | 964000 | 712320 | 3383509.09 | 47790 | 523896 | 0 | 1987200 | 711168 | 3470600 | 0 | 2430300 | 118440 | 253200 | 96681 | 2176800 | 315840 | 11550 | 184130 | 70080 | 174412437.4 | 21821091 | 4531680 | 0 | 279360 | 178304 | 0 | 0 | 0 | 0 | 0 | 0 | 648000 | 27534550 | 924480 | 0 | 0 | 31326671 | 0 | 158158 | 0 | 297216 | 356640 | 0 | 204176 | 104292 | 97320 | 327824 | 668799 | 51154 | 0 | 318896 | 0 | 0 | 4369082 | 0 | 3982515 | 0 | 8997600 | 0 | 30960 | 0 | 923345 | 969600 | 171541 | 1802707 | 0 | 0 | 0 | 48523.44 | 1195920 | 4144 | 162912 | 5738000 | 2792000 | 5146970 | 0 | 24807273 | 26503272.73 | 148800 | 177623776.17 | 352036213.57

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 04-06-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14743.95 | MW | 12:00 Hr. | Energy Generated |  |  | 352.0362 |  | MKWHr.
| Day Peak Demand |  |  | 14971.95 | MW | 12:00 Hr. | Energy Unserverd |  |  | 5.529 |  | MKWHr.
| Evening Peak Generation |  |  | 14900.03 | MW | 21:00 Hr. | Energy Demand |  |  | 357.5652 |  | MKWHr.
| Evening Peak Demand |  |  | 15275.03 | MW | 21:00 Hr. | Maximum Temperature |  |  | 36.8 |  | °C
| Minimum Generation of the Day |  |  | 13452.95 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 934.11 |  | MMCFD
| Maximum Generation of the Day |  |  | 16015.91 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.4003 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.0831 | 0 | 10.7714 | 0 | 0 | 0.194 | 0 | 0 | 44.0485 | Gas | 127.09 | Gas | 447545545.6093
| Chattogram Zone |  |  | 5.6794 | 43.0655 | 8.7884 | 0 | 2.284 | 0.16104 | 0 | 0.03408 | 60.0123 | Coal | 128.5719 | Coal | 844547831.1293
| Cumilla Zone |  |  | 28.5138 | 0 | 4.7005 | 0 | 0 | 0.51185 | 3.673 | 0 | 37.3991 | HFO | 32.6139 | HFO | 559574372.738
| Mymensingh Zone |  |  | 0.31584 | 0 | 2.6185 | 0 | 0 | 0.29236 | 0 | 0 | 3.2267 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 29.678 | 0 | 0 | 0 | 0 | 0.04779 | 0 | 0 | 29.7258 | Hydro | 2.284 | Hydro | 228395.6
| Khulna Zone |  |  | 4.5317 | 27.5345 | 1.3821 | 0 | 0 | 0.648 | 21.8211 | 0 | 55.9175 | Solar | 4.6217 | Solar | 72242314.8588
| Barishal Zone |  |  | 7.939 | 57.0485 | 0.31171 | 0 | 0 | 0.004144 | 0 | 0 | 65.3034 | Import | 56.8207 | Import | 328514194.92
| Rajshahi Zone |  |  | 17.3492 | 0 | 1.269 | 0 | 0 | 1.3465 | 31.3267 | 0 | 51.2913 | Wind | 0.03408 | Wind | 501316.8
| Rangpur Zone |  |  | 0 | 0.92334 | 2.7723 | 0 | 0 | 1.416 | 0 | 0 | 5.1116
| Total |  |  | 127.09 | 128.5719 | 32.6139 | 0 | 2.284 | 4.6217 | 56.8207 | 0.03408 | 352.0362
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 447545545.6093 |  | Hydro | 228395.6
|  |  |  | Coal | 844547831.1293 |  | Solar | 72242314.8588
|  |  |  | HFO | 559574372.738 |  | Import | 328514194.92
|  |  |  | HSD | 0 |  | Wind | 501316.8
[5 empty] | Total: | 225,31,53,971 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.8211 | Peak Hr Flow | 903.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 53532090.91 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.3267 | Peak Hr Flow | 1182.53 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2683 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.673 | Peak Hr Flow | 164.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2790 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 56.8207 | Peak Hr Flow | 2249.53 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 12 |  | 5087
|  |  |  | Chattogram |  | 9 |  | 1591
|  |  |  | Cumilla |  | 16 |  | 1640
|  |  |  | Mymensingh |  | 308 |  | 1378
|  |  |  | Sylhet |  | 10 |  | 637
|  |  |  | Khulna |  | 0 |  | 1645
|  |  |  | Barishal |  | 4 |  | 568
|  |  |  | Rajshahi |  | 0 |  | 1385
|  |  |  | Rangpur |  | 0 |  | 803
|  |  |  | Total |  | 359 |  | 14734
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:26 | Baroaulia 132/33kV S/S T2(415T) HT is restored.
| 08:30 | 08:54 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) LT Forced S/D Due to Redhot maintenance
of CT Connector nutbolt.
| 08:31 | 08:53 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) HT Forced S/D Due to Redhot maintenance
of CT Connector nutbolt.
| 08:34 | 09:38 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Scheduled S/D Due to Due to Keranihat 33 | [7 empty] | 63.0MW load
|  |  | kv feeder redhot maintenance. Shutdown taken by Shahidul Islam AGM (Zonal office | [7 empty] | interrup.
Satkania) Ctg pbs -01
| 08:34 | 09:38 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Scheduled S/D Due to Due to Keranihat 33 | [7 empty] | 63.0MW load
|  |  | kv feeder redhot maintenance. Shutdown taken by Shahidul Islam AGM (Zonal office | [7 empty] | interrup.
Satkania) Ctg pbs -01
|  | 08:35 | Barishal 132/33kV S/S T-2 (415T) HT is restored.
|  | 08:36 | Barishal 132/33kV S/S T-2 (415T) LT is restored.
| 08:42 | 10:43 | Kishoreganj-Mymensingh 132kV Ckt-1 Scheduled S/D from Bajitpur 132/33kV end Due to Due
to VT alarm Removal purpose.
| 08:42 | 10:43 | Kishoreganj-Mymensingh 132kV Ckt-1 Scheduled S/D from Bajitpur 132/33kV end Due to Due
to VT alarm Removal purpose.
| 08:47 |  | Bajitpur 132/33kV S/S 132 kV Bus-2 Scheduled S/D Due to Due To Reduce Temparature and
Clamp Maintenance.
| 08:50 | 09:16 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Tripped showing P142 relays Due to Durgapur 33 | [7 empty] | 39.0MW load
|  |  | kv feeder fault. | [7 empty] | interrup.
| 09:28 | 11:23 | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bhandaria 132/33kV end Due to Shutdown
taken by Barishal 132/33 kV Grid SS and from Barishal 132/33kV end Due to High
temperature maintenance at different points
| 10:02 | 17:01 | Gopalganj(N)-Madaripur 132kV Ckt-1 Scheduled S/D from Madaripur 132/33kV end Due to
Schedule shutdown and from Gopalganj 400/132kVend.
| 10:03 | 17:01 | Gopalganj(N)-Madaripur 132kV Ckt-2 Scheduled S/D from Madaripur 132/33kV end Due to
Schedule shutdown and from Gopalganj 400/132kVend.
|  | 10:23 | Madaripur 132/33kV S/S T2-415T LT is restored.
|  | 10:23 | Madaripur 132/33kV S/S T2-415T HT is restored.
| 10:30 | 11:11 | Sylhet 132/33kV S/S Sylhet-90MW P/S Scheduled S/D Due to bird's nest remove.
| 10:45 | 11:40 | Bajitpur 132/33kV S/S Tr-2(414T) HT Tripped showing RET650 REC650 relays Due to OIL | [7 empty] | 24.0MW load
|  |  | SURGED Trip Closed Blocked Signal show | [7 empty] | interrup.
|  | 10:55 | Noapara 132/33kV S/S T-1 HT is restored.
|  | 10:55 | Noapara 132/33kV S/S T-1 LT is restored.
|  | 10:56 | Noapara 132/33kV S/S Bus Section-1 is restored.
| 12:00 |  | Day Peak Generation is 14740 MW.
|  | 12:22 | BIPTC S/S 20DF13 is restored.
| 12:26 | 13:45 | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 Forced S/D Due to Due to broken nest
| 13:09 | 15:15 | GPH 230/33kV S/S BSRM CKT-1 Forced S/D Due to emergency tree trimming needed at mirsorai
side .
| 13:11 | 15:16 | BSRM 230/33kV S/S GPH Ispat Ckt. -01 Forced S/D Due to Emergency work by Mirshary 230kV
ss
| 15:27 |  | Matarbari 2*600 MW (CPGCBL) Synchronized with remarks:- U1
| 17:35 | 19:13 | Bogura(New)-Naogaon 132 kV Ckt-1 Tripped from Naogaon 132/33kV end showing Distains
Protection Relay relays Due to Thunderstorm
| 17:35 | 18:15 | Joypurhat-Naogaon 132kV Ckt-1 Tripped from Naogaon 132/33kV end showing Main-1 relays
Due to Over Voltage (Thunderstorm)
| 17:36 | 18:14 | Bogura(New)-Naogaon 132 kV Ckt-2 Tripped from Bogura 230/132kV end showing Distance
Protection Trip Zone 1 Fault Location: 27.71 k.m. Type: Phase A to G Fault Current:
3562A relays Due to Bad Weather
| 17:52 | 21:01 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Forced S/D
| 17:52 | 21:01 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 Forced S/D
|  | 19:22 | Kishoreganj 132/33kV S/S Tr-3 (424T) HT is restored.
| 20:58 |  | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D
| 21:00 |  | Evening Peak Generation is 14899 MW.
| 00:14 |  | Summit Meghnaghat-2 589 MW CCPP GT was sync.
| 00:14 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- GT
| 01:19 |  | Nutan Biddut CCPP GT-11 was shut down due to offline water wash.
| 02:51 |  | Patuakhali 1320 MW (RNPL) Unit-1 was shut down due to boiler tube leakage.
| 03:00 |  | Summit Meghnaghat-2 589 MW CCPP ST was sync.
| 03:00 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- ST
| 05:41 |  | Savar 132/33kV S/S T-3 HT Scheduled S/D Due to Bushing CT control cable change work.
| 05:41 |  | Savar 132/33kV S/S T-3 LT Scheduled S/D Due to Bushing CT control cable change work.
| 05:50 |  | Meghnaghat Summit 335 MW CCPP was shutdown.
| 05:54 |  | Mymensingh RPCL-Tangail 132kV Ckt-1 Forced S/D from Ghatail 132/33kV end Due to OPGW | [7 empty] | 20.0MW load
|  |  | Restringing in Tangail Grid Sub-Station. | [7 empty] | interrup. Ghatail
132/33kV end
| 05:59 |  | Mymensingh RPCL-Tangail 132kV Ckt-2 Forced S/D from Ghatail 132/33kV end Due to OPGW | [7 empty] | 20.0MW load
|  |  | Restringing in Tangail Grid Sub-Station. | [7 empty] | interrup. Ghatail
132/33kV end
| 06:00 |  | Tangail 132/33kV S/S RPCL-2 Scheduled S/D Due to OPGW Re-conductoring
| 06:00 |  | Tangail 132/33kV S/S RPCL-1 Scheduled S/D Due to OPGW Re-conductoring
| 06:05 |  | Bagerhat-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end Due to
Suspension Disc insulator change of 5 no. Tower.
| 06:18 |  | Bhulta 132/33kV S/S GT1 HT Scheduled S/D Due to Maintenance work at Narsingdi line DS-104 | [7 empty] | 40.0MW load
|  |  | (Substation drawing identification number DS-201S) | [7 empty] | interrup.
| 07:11 |  | JERA Meghnaghat Power Limited 718 MW CCPP was shut down.
| 07:14 |  | Jhenaidah 132/33kV S/S Transformer T-1 LT Forced S/D Due to Maintainance of 'DS' Y-phase, | [7 empty] | 32.0MW load
|  |  | 33kv T-1A Redhot. | [7 empty] | interrup.
| 07:14 |  | Jhenaidah 132/33kV S/S Transformer T-1 HT Forced S/D Due to Maintainance of 'DS' Y-phase, | [7 empty] | 32.0MW load
|  |  | 33kv T-1A Redhot. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 04-06-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Under Maintenance
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 409 | 9122400 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 160 | 4027000 | GT is under maintenance
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 139 | 3357498 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 217664 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35.5 | 259920 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 789600 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 415487 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 220507 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25 | 516000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 513360 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 849600 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 862876 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 125 | 1070064 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 2060160 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 427680 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 194000 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 152640 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 343 | 9724545.45 | AGC
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 223 | 5822292 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3445200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1822.5 | 44048493.45
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 161969.4 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 131355 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 464160 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 100 | 2283956 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 215 | 5244076 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 97 | 1937018 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 67 | 728064 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 306103 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 575040 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 22 | 435360 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 74 | 795840 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 29684 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 356291 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 17 | 253464 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 1714545 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 584640 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 15 | 904527 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 6691 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 27850906 | AGC
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 34080 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1060 | 15214545.46 | AGC
Chattogram Area Total |  |  |  |  | 4898.863 | 2993 | 60012314.86
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 216 | 5100000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 290 | 7393200 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 240 | 6076000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 230 | 5677500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 374904 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 54720 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1235064 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 10 | 538618 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 38 | 509664 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2141559 | ST Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 16 | 1535040 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 164 | 3672960 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 541781 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 460840 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 703380 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 32 | 232680 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 639360 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 511855 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1505 | 37399125
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 96681 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 10 | 315840 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11550 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 127 | 2176800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 18 | 253200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 184130 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 70080 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 118440 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 172 | 3226721
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 47790 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 964000 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 712320 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 147 | 3383509.09 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 151 | 3470600 | ST Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 711168 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1987200 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2430300 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 523896 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7500000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 344 | 7995000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1263 | 29725783.09
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 903 | 21821091 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 33 | 279360 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 178304 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 188 | 4531680 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 33 | 924480 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | FGMO
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 648000 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1191 | 27534550 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2348 | 55917465
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 1248 | 24807273 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 162912 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2792000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 972 | 26503272.73 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5146970 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 148800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 274 | 5738000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4144 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2850 | 65303371.73
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 327824 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 158158 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 104292 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 160 | 4369082 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 140 | 3982515 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 375 | 8997600 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 51154 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 97320 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 204176 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 356640 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 297216 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30960 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1182.53 | 31326671 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 318896 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 668799 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 1857.53 | 51291303
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 40 | 923345 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 1802707 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 48523.44 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 969600 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 171541 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1195920 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 89 | 5111636.44
Eastern Grid Total |  |  |  |  | 17438.042 | 7755.5 | 174412437.4
Western Grid Total |  |  |  |  | 11852.195 | 7144.53 | 177623776.17
National Grid Total |  |  |  |  | 29290.237 | 14900.03 | 352036213.57
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 04-06-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9977.79 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4397.8 | MW
i) Dhaka area |  |  | 5075.09 |  | MW | i) Khulna area |  |  |  | 1645 | MW
ii) Chattogram area |  |  | 1581.7 |  | MW | ii) Barishal area |  |  |  | 564.4 | MW
iii) Cumilla area |  |  | 1624 |  | MW | iii) Rajshahi area |  |  |  | 1385.4 | MW
iv) Mymensingh area |  |  | 1070 |  | MW | iv) Rangpur area |  |  |  | 803 | MW
v) Sylhet area |  |  | 627 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14375.59 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 81 | 23:00 | 133 | Natore | 170 | 00:00
2 | AKSML | 116 | 01:00 | 68 | Hathazari | 102 | 19:30 | 134 | Nawabganj | 72 | 23:00
3 | Aftabnagar | 46 | 00:00 | 69 | Hatirjheel | 51 | 15:00 | 135 | Netrakona | 133 | 08:00
4 | Agargaon | 133 | 13:00 | 70 | Ishurdi | 88 | 15:00 | 136 | New | 64 | 13:00
5 | Agrabad | 78 | 14:00 | 71 | Jaldhaka | 94 | 00:00 | 137 | Niamatpur | 84 | 00:00
6 | Amnura | 35 | 01:00 | 72 | Jamalpur | 124 | 18:30 | 138 | Noapara | 62 | 20:00
7 | Ashuganj | 111 | 02:00 | 73 | Jashore | 163 | 19:30 | 139 | PHP | 13 | 18:30
8 | BSRM | 193 | 22:00 | 74 | Jhenaidah | 131 | 00:00 | 140 | Pabna | 111 | 00:00
9 | Bagerhat | 108 | 19:30 | 75 | Joydebpur | 125 | 13:00 | 141 | Palashbari | 134 | 23:00
10 | Bajitpur | 102 | 00:00 | 76 | Joypurhat | 70 | 01:00 | 142 | Panchagarh | 60 | 00:00
11 | Bakerganj | 17 | 00:00 | 77 | Juldah | 16 | 18:30 | 143 | Patiya | 12.7 | 00:00
12 | Bakulia | 98 | 15:00 | 78 | KSRM | 12 | 15:00 | 144 | Patuakhali | 85.9 | 22:00
13 | Banani | 66 | 13:00 | 79 | Kabirpur | 164 | 19:00 | 145 | Payra | 42 | 23:00
14 | Bangabhaban | 23 | 10:00 | 80 | Kachua | 116 | 00:00 | 146 | Postogola | 60 | 00:00
15 | Barapukuria | 70 | 00:00 | 81 | Kaliganj | 20 | 00:00 | 147 | Pubail | 27 | 19:30
16 | Barguna | 26 | 00:00 | 82 | Kallyanpur | 129 | 00:00 | 148 | Purbachal | 38 | 13:00
17 | Barishal | 119 | 13:00 | 83 | Kalurghat | 37 | 11:00 | 149 | Purbasadipur | 147 | 00:00
18 | Barishal-230 | 128 | 00:00 | 84 | Kamrangirchar | 58 | 13:00 | 150 | Rahanpur | 45 | 00:00
19 | Baroaulia | 72 | 19:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 27 | 17:00
20 | Baroirhat | 80 | 19:30 | 86 | Kasba | 42 | 22:00 | 152 | Rajbari | 98 | 01:00
21 | Bashundhara | 204 | 14:00 | 87 | Kazla | 99 | 16:00 | 153 | Rajendrapur | 114 | 01:00
22 | BashundharaCement | 8 | 00:00 | 88 | Keranigonj | 86 | 23:00 | 154 | Rajshahi | 130 | 00:00
23 | Beanibazar | 78 | 20:00 | 89 | Khagrachori | 36 | 19:00 | 155 | Rajshahi-230 | 96 | 13:00
24 | Benapole | 79 | 00:00 | 90 | Khulna | 71 | 20:00 | 156 | Ramganj | 122 | 03:00
25 | Bhaluka | 150 | 19:30 | 91 | Khulshi | 191 | 12:00 | 157 | Rampur | 48 | 00:00
26 | Bhandaria | 68 | 23:00 | 92 | Kishoreganj | 144 | 22:00 | 158 | Rangamati | 19 | 18:30
27 | Bhangura | 42 | 00:00 | 93 | Kodda | 239 | 18:00 | 159 | Rangpur | 143 | 15:00
28 | Bheramara(GK) | 80 | 20:00 | 94 | Kulaura | 59 | 00:00 | 160 | Ruppur | 5 | 11:00
29 | Bhulta | 187 | 00:00 | 95 | Kurigram | 70 | 00:00 | 161 | SSM | 13 | 06:00
30 | Bog-Sherpur | 74 | 13:00 | 96 | Kushtia | 186 | 00:00 | 162 | Saidpur | 107 | 10:00
31 | Bogura | 178 | 01:00 | 97 | Laksam | 37 | 00:00 | 163 | Santhia | 40 | 00:00
32 | Borhanuddin | 105 | 05:00 | 98 | Lakshmipur | 47 | 01:00 | 164 | Satkhira | 171 | 20:00
33 | Brahmanbaria | 148 | 03:00 | 99 | Lalbag | 48 | 17:00 | 165 | Satmasjid | 108 | 16:00
34 | Cantonment | 141 | 13:00 | 100 | Lalmonirhat | 65 | 01:00 | 166 | Savar | 172 | 15:00
35 | Chandina | 42 | 19:00 | 101 | MI_Cement | 8.6 | 07:00 | 167 | SevenRings | 11.61 | 06:00
36 | Chandpur | 100 | 00:00 | 102 | Madanganj | 43 | 13:00 | 168 | ShahCement | 24 | 17:00
37 | Chandraghona | 38 | 19:30 | 103 | Madaripur | 143 | 22:00 | 169 | Shahjadpur | 84 | 00:00
38 | Chapai | 80 | 13:00 | 104 | Madartek | 90 | 00:00 | 170 | Shahjibazar | 127 | 23:00
39 | Charsaidpur | 28 | 21:00 | 105 | Madunaghat | 60 | 18:30 | 171 | Shahmirpur | 66 | 00:00
40 | Chauddagram | 91 | 19:00 | 106 | Magura | 84 | 19:30 | 172 | Shariatpur | 116 | 23:00
41 | Chhatak | 42 | 00:00 | 107 | Mahasthangarh | 95 | 00:00 | 173 | Sherpur | 124 | 10:00
42 | Chowmuhani | 186 | 03:00 | 108 | Maijdee | 48 | 22:00 | 174 | Shikalbaha | 35 | 00:00
43 | Chuadanga | 129 | 01:00 | 109 | Manikganj | 148 | 19:00 | 175 | Shitalakhya | 82.1 | 13:00
44 | Coxsbazar | 148 | 20:00 | 110 | Maniknagar | 81 | 15:00 | 176 | Sholosohor | 46 | 19:00
45 | Cumilla(N) | 130 | 19:00 | 111 | Matarbari | 62 | 20:00 | 177 | Shomvuganj | 22 | 19:00
46 | Cumilla(S) | 173 | 19:00 | 112 | Matuail | 50 | 00:00 | 178 | Shyampur | 96 | 14:00
47 | Daganbhuiyan | 41 | 00:00 | 113 | Metrorail_Motijheel | 32 | 10:00 | 179 | Siddhirganj | 109 | 14:00
48 | Daudkandi | 154 | 21:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 112 | 21:00
49 | DhakaUniversity | 84 | 13:00 | 115 | Millgate | 101 | 08:00 | 181 | Sonargaon | 110 | 23:00
50 | Dhamrai | 106 | 21:00 | 116 | Mirpur | 149 | 00:00 | 182 | Sreemongol | 83 | 00:00
51 | Dhanmondi | 130 | 13:00 | 117 | Mirsorai | 47 | 12:00 | 183 | Sreepur | 100 | 21:00
52 | Dohazari | 113 | 20:00 | 118 | Mirzapur | 42 | 14:00 | 184 | Srinagar | 58.6 | 23:00
53 | Faridpur | 200 | 00:00 | 119 | Mithapukur | 70 | 03:00 | 185 | Sunamganj | 62 | 21:00
54 | Fatullah | 60 | 23:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 74 | 00:00
55 | Fenchuganj | 48 | 00:00 | 121 | Mogbazar | 102.2 | 13:00 | 187 | Sylhet-132 | 103 | 19:00
56 | Feni | 125 | 14:00 | 122 | Mongla | 49 | 12:00 | 188 | TK | 26 | 00:00
57 | GPH | 75 | 14:00 | 123 | Motijheel | 52 | 13:00 | 189 | Tangail | 190 | 14:00
58 | Ghatail | 92 | 18:00 | 124 | Muktagacha | 35 | 18:00 | 190 | Taraganj | 25 | 09:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 127 | 23:00 | 191 | Tasnim | 15 | 16:00
60 | Ghorashal-230 | 107 | 00:00 | 126 | Muradnagar | 56 | 19:30 | 192 | Thakurgaon | 119 | 00:00
61 | Goalpara | 48 | 00:00 | 127 | Mymensingh | 194 | 23:00 | 193 | Tongi | 136 | 23:00
62 | Gollamari | 128 | 13:00 | 128 | Nabinagar | 84 | 19:00 | 194 | Ullahpara | 44 | 19:00
63 | Gopalganj | 132 | 21:00 | 129 | Naogaon | 155 | 00:00 | 195 | Ullon | 73 | 00:00
64 | Gulshan | 156 | 13:00 | 130 | Narail | 72 | 20:00 | 196 | Uttara | 107 | 14:00
65 | Halishahar | 75 | 14:00 | 131 | Narinda | 56 | 13:00 | 197 | UttaraNew | 60 | 00:00
66 | HaripurSBU | 90 | 00:00 | 132 | Narshingdi | 162 | 01:00 | 198 | Zigatola | 94 | 15:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 04-06-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 16015.91 | 552 |  | 16592.75
1:00 | 15752.02 | 349 |  | 16116.73
2:00 | 15243.67 | 330 |  | 15588.67
3:00 | 14912.88 | 308 |  | 15234.88
4:00 | 14547.56 | 283 |  | 14843.56
5:00 | 14183.44 | 278 |  | 14474.44
6:00 | 13711.62 | 257 |  | 13980.62
7:00 | 13596.27 | 235 |  | 13842.27
8:00 | 13452.95 | 200 |  | 13661.95
9:00 | 13680.7 | 243 |  | 13934.7
10:00 | 13944.79 | 186 |  | 14138.79
11:00 | 14305.44 | 136 |  | 14447.44
12:00 | 14743.95 | 218 |  | 14971.95
13:00 | 14997.22 | 77 |  | 15077.22
14:00 | 15001.97 | 64 |  | 15068.97
15:00 | 15147.89 | 86 |  | 15237.89
16:00 | 14652.61 | 256 |  | 14920.13
17:00 | 13970.71 | 206 |  | 14185.71
18:00 | 12975.2 | 116 |  | 13096.2
19:00 | 14245.04 | 242 |  | 14497.93
19:30 | 14759.99 | 210 |  | 14978.99
20:00 | 14881.17 | 187 |  | 15076.17
21:00 | 14900.03 | 359 |  | 15275.03
22:00 | 14858.25 | 186 |  | 15052.25
23:00 | 15048.56 | 175 |  | 15231.44
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 04-06-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 140 | 21 | 440 | 152 | 1878 | 128 | Ishurdi-Ghorashal Ckt-1 | Export | 3795418.18
1:00 | 133 | 21 | 420 | 150 | 1936 | 124
2:00 | 136 | 23 | 446 | 154 | 1814 | 170 |  | Import | 0
3:00 | 140 | 26 | 466 | 162 | 1746 | 198
4:00 | 138 | 24 | 464 | 164 | 1772 | 196 | Ishurdi-Ghorashal Ckt-2 | Export | 1672.73
5:00 | 149 | 30 | 482 | 174 | 1902 | 212
6:00 | 138 | 25 | 430 | 144 | 1844 | 208 |  | Import | 0
7:00 | 138 | 27 | 420 | 158 | 1776 | 216
8:00 | 148 | 36 | 430 | 164 | 1776 | 306 | Sirajganj-Sreepur Ckt-1 | Export | 2844000
9:00 | 167 | 44 | 460 | 156 | 1812 | 74
10:00 | 176 | 49 | 500 | 190 | 1942 | 368 |  | Import | 0
11:00 | 186 | 50 | 530 | 186 | 2028 | 378
12:00 | 172 | 43 | 490 | 150 | 1870 | 360 | Sirajganj-Sreepur Ckt-2 | Export | 2851000
13:00 | 149 | 31 | 410 | 104 | 1794 | 290
14:00 | 143 | 32 | 390 | 114 | 1736 | 322 |  | Import | 0
15:00 | 152 | 37 | 460 | 168 | 1838 | 328
16:00 | 161 | 40 | 480 | 170 | 1730 | 320 | Gopalganj-Aminbazar Ckt-1 | Export | 22000000
17:00 | 179 | 48 | 520 | 180 | 1676 | 368
18:00 | 209 | 44 | 610 | 166 | 1798 | 374 |  | Import | 0
18:30 | 223 | 43 | 670 | 186 | 1874 | 382
19:00 | 210 | 45 | 660 | 204 | 1920 | 362 | Gopalganj-Aminbazar Ckt-2 | Export | 22040000
19:30 | 183 | 32 | 510 | 150 | 1892 | 276
20:00 | 173 | 28 | 500 | 160 | 1930 | 266 |  | Import | 0
21:00 | 163 | 31 | 490 | 194 | 2030 | 338
22:00 | 165 | 34 | 500 | 182 | 2002 | 316 |  | Total Export | 53532090.91
23:00 | 127 | 21 | 430 | 170 | 1642 | 264 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 04-06-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7898.7 | 8117.21 | 16015.91 | DAILY GENERATION CURVE
00:30 | 7781.45 | 8102.515 | 15883.965
01:00 | 7664.2 | 8087.82 | 15752.02 | 04-06-2026
01:30 | 7527.1 | 7970.745 | 15497.845
02:00 | 7390 | 7853.67 | 15243.67
02:30 | 7326.6 | 7751.675 | 15078.275
03:00 | 7263.2 | 7649.68 | 14912.88
03:30 | 7163.2 | 7567.02 | 14730.22
04:00 | 7063.2 | 7484.36 | 14547.56
04:30 | 6872.6 | 7492.9 | 14365.5
05:00 | 6682 | 7501.44 | 14183.44
05:30 | 6588.455 | 7359.075 | 13947.53
06:00 | 6494.91 | 7216.71 | 13711.62
06:30 | 6448.925 | 7205.02 | 13653.945
07:00 | 6402.94 | 7193.33 | 13596.27
07:30 | 6410.055 | 7114.555 | 13524.61
08:00 | 6417.17 | 7035.78 | 13452.95
08:30 | 6558.155 | 7008.67 | 13566.825
09:00 | 6699.14 | 6981.56 | 13680.7
09:30 | 6720.145 | 7092.6 | 13812.745
10:00 | 6741.15 | 7203.64 | 13944.79
10:30 | 6773.445 | 7351.67 | 14125.115
11:00 | 6805.74 | 7499.7 | 14305.44
11:30 | 6980.91 | 7543.785 | 14524.695
12:00 | 7156.08 | 7587.87 | 14743.95
12:30 | 7302.375 | 7568.21 | 14870.585
13:00 | 7448.67 | 7548.55 | 14997.22
13:30 | 7460.37 | 7539.225 | 14999.595
14:00 | 7472.07 | 7529.9 | 15001.97
14:30 | 7504.985 | 7569.945 | 15074.93
15:00 | 7537.9 | 7609.99 | 15147.89
15:30 | 7414.115 | 7486.135 | 14900.25
16:00 | 7290.33 | 7362.28 | 14652.61
16:30 | 7240.74 | 7070.92 | 14311.66
17:00 | 7191.15 | 6779.56 | 13970.71
17:30 | 6924.535 | 6548.42 | 13472.955
18:00 | 6657.92 | 6317.28 | 12975.2
18:30 | 7096.21 | 6513.91 | 13610.12
19:00 | 7534.5 | 6710.54 | 14245.04
19:30 | 7816.5 | 6943.49 | 14759.99
20:00 | 7684.5 | 7196.67 | 14881.17
20:30 | 7720 | 7170.6 | 14890.6 |  | Executive Engineer
21:00 | 7755.5 | 7144.53 | 14900.03 |  | Network Operation Division
21:30 | 7607.5 | 7271.64 | 14879.14
22:00 | 7459.5 | 7398.75 | 14858.25
22:30 | 7569 | 7384.405 | 14953.405
23:00 | 7678.5 | 7370.06 | 15048.56

## En-Curve
QF-LDC-12
Date | 04-06-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3397 | 1863 | 904 | 0 | 156 | 1445.01 | 100 | 5627 | 0 | 828 | 1695.9 | 0 | 0 | 0 | 552 | DAILY ENERGY CURVE
00:30 | 3381.5 | 1825.5 | 904 | 0 | 152 | 1448.315 | 100 | 5679.5 | 4.5 | 777 | 1611.65 | 0 | 0 | 0 | 450.5 | 04-06-2026
01:00 | 3366 | 1788 | 904 | 0 | 148 | 1451.62 | 100 | 5732 | 9 | 726 | 1527.4 | 0 | 0 | 0 | 349
01:30 | 3370.5 | 1839 | 904 | 0 | 148 | 1407.145 | 100 | 5651 | 4.5 | 645 | 1428.7 | 0 | 0 | 0 | 339.5 | Energy Generated | 352.0362 |  | MKWHr
02:00 | 3375 | 1890 | 904 | 0 | 148 | 1362.67 | 100 | 5570 | 0 | 564 | 1330 | 0 | 0 | 0 | 330 | Energy not Served | 5.529 |  | MKWHr
02:30 | 3381 | 1923 | 903.5 | 0 | 147 | 1362.675 | 100 | 5472 | 0 | 532 | 1257.1 | 0 | 0 | 0 | 319 | Total Energy Requirement | 357.5652 |  | MKWHr
03:00 | 3387 | 1956 | 903 | 0 | 146 | 1362.68 | 100 | 5374 | 0 | 500 | 1184.2 | 0 | 0 | 0 | 308
03:30 | 3388.5 | 1929.5 | 903.5 | 0 | 145 | 1365.02 | 100 | 5362 | 0 | 397 | 1139.7 | 0 | 0 | 0 | 295.5
04:00 | 3390 | 1903 | 904 | 0 | 144 | 1367.36 | 100 | 5350 | 0 | 294 | 1095.2 | 0 | 0 | 0 | 283
04:30 | 3377.5 | 1876.5 | 903.5 | 0 | 141 | 1367.9 | 98.5 | 5363.5 | 0 | 269.5 | 967.6 | 0 | 0 | 0 | 280.5
05:00 | 3365 | 1850 | 903 | 0 | 138 | 1368.44 | 97 | 5377 | 0 | 245 | 840 | 0 | 0 | 0 | 278
05:30 | 3360 | 1796.5 | 903.5 | 0 | 136 | 1320.555 | 97 | 5361.5 | 16.975 | 245 | 710.5 | 0 | 0 | 0 | 267.5
06:00 | 3355 | 1743 | 904 | 0 | 134 | 1272.67 | 97 | 5346 | 33.95 | 245 | 581 | 0 | 0 | 0 | 257
06:30 | 3366 | 1744 | 904 | 0 | 133 | 1274.465 | 96 | 5298 | 92.48 | 235.5 | 510.5 | 0 | 0 | 0 | 246
07:00 | 3377 | 1745 | 904 | 0 | 132 | 1276.26 | 95 | 5250 | 151.01 | 226 | 440 | 0 | 0 | 0 | 235
07:30 | 3369 | 1713 | 904 | 0 | 134 | 1244.405 | 96.5 | 5188.5 | 225.705 | 226 | 423.5 | 0 | 0 | 0 | 217.5
08:00 | 3361 | 1681 | 904 | 0 | 136 | 1212.55 | 98 | 5127 | 300.4 | 226 | 407 | 0 | 0 | 0 | 200
08:30 | 3363 | 1746 | 903.5 | 0 | 140 | 1209.435 | 98.5 | 5079.5 | 376.39 | 238.5 | 412 | 0 | 0 | 0 | 221.5
09:00 | 3365 | 1811 | 903 | 0 | 144 | 1206.32 | 99 | 5032 | 452.38 | 251 | 417 | 0 | 0 | 0 | 243
09:30 | 3377.5 | 1853 | 903 | 0 | 146 | 1226.875 | 99 | 5032.5 | 503.87 | 261.5 | 409.5 | 0 | 0 | 0 | 214.5
10:00 | 3390 | 1895 | 903 | 0 | 148 | 1247.43 | 99 | 5033 | 555.36 | 272 | 402 | 0 | 0 | 0 | 186
10:30 | 3394 | 1904 | 903 | 0 | 152 | 1278.22 | 99.5 | 5103 | 596.395 | 272 | 423 | 0 | 0 | 0 | 161
11:00 | 3398 | 1913 | 903 | 0 | 156 | 1309.01 | 100 | 5173 | 637.43 | 272 | 444 | 0 | 0 | 0 | 136
11:30 | 3401.5 | 1910.5 | 903.5 | 0 | 160 | 1380.78 | 100 | 5192.5 | 618.915 | 295 | 561.5 | 0 | 0 | 0.5 | 177
12:00 | 3405 | 1908 | 904 | 0 | 164 | 1452.55 | 100 | 5212 | 600.4 | 318 | 679 | 0 | 0 | 1 | 218
12:30 | 3386 | 1910.5 | 903.5 | 0 | 164 | 1455.715 | 100 | 5209 | 583.62 | 345.5 | 811.75 | 0 | 0 | 1 | 147.5
13:00 | 3367 | 1913 | 903 | 0 | 164 | 1458.88 | 100 | 5206 | 566.84 | 373 | 944.5 | 0 | 0 | 1 | 77
13:30 | 3349.5 | 1852 | 903.5 | 0 | 163 | 1417.815 | 100 | 5187.5 | 546.28 | 394.5 | 1081 | 0 | 0 | 4.5 | 70.5
14:00 | 3332 | 1791 | 904 | 0 | 162 | 1376.75 | 100 | 5169 | 525.72 | 416 | 1217.5 | 0 | 0 | 8 | 64
14:30 | 3344 | 1854.5 | 903.5 | 0 | 167 | 1388.7 | 99.5 | 5195.5 | 447.48 | 419.5 | 1248.25 | 0 | 0 | 7 | 75
15:00 | 3356 | 1918 | 903 | 0 | 172 | 1400.65 | 99 | 5222 | 369.24 | 423 | 1279 | 0 | 0 | 6 | 86
15:30 | 3337.5 | 1873 | 903 | 0 | 167 | 1377.965 | 97 | 5174 | 332.285 | 435 | 1197.5 | 0 | 0 | 6 | 171
16:00 | 3319 | 1828 | 903 | 0 | 162 | 1355.28 | 95 | 5126 | 295.33 | 447 | 1116 | 0 | 0 | 6 | 256
16:30 | 3339 | 1782.5 | 903.5 | 0 | 164 | 1287.52 | 95 | 5035 | 209.64 | 435.5 | 1055 | 0 | 0 | 5 | 231
17:00 | 3359 | 1737 | 904 | 0 | 166 | 1219.76 | 95 | 4944 | 123.95 | 424 | 994 | 0 | 0 | 4 | 206
17:30 | 3299 | 1676.5 | 903.5 | 0 | 155 | 1149.465 | 95.5 | 4819.5 | 72.24 | 394.5 | 902.75 | 0 | 0 | 5 | 161
18:00 | 3239 | 1616 | 903 | 0 | 144 | 1079.17 | 96 | 4695 | 20.53 | 365 | 811.5 | 0 | 0 | 6 | 116
18:30 | 3324.5 | 1768.5 | 903 | 0 | 159 | 1086.855 | 98 | 4883 | 10.265 | 435.5 | 938 | 0 | 0 | 3.5 | 179
19:00 | 3410 | 1921 | 903 | 0 | 174 | 1094.54 | 100 | 5071 | 0 | 506 | 1064.5 | 0 | 0 | 1 | 242
19:30 | 3284 | 1680 | 893 | 0 | 162 | 1023.49 | 100 | 5314 | 0 | 702 | 1601.5 | 0 | 0 | 0 | 210
20:00 | 3375 | 1751 | 903 | 0 | 160 | 1020.67 | 100 | 5589 | 0 | 651 | 1331.5 | 0 | 0 | 0 | 187
20:30 | 3387.5 | 1770 | 903 | 0 | 162 | 1101.6 | 100 | 5767 | 0 | 533.5 | 1166 | 0 | 0 | 0 | 273
21:00 | 3400 | 1789 | 903 | 0 | 164 | 1182.53 | 100 | 5945 | 0 | 416 | 1000.5 | 0 | 0 | 0 | 359
21:30 | 3371 | 1748 | 903.5 | 0 | 163 | 1319.14 | 100 | 5983 | 0 | 416 | 875.5 | 0 | 0 | 0 | 272.5
22:00 | 3342 | 1707 | 904 | 0 | 162 | 1455.75 | 100 | 6021 | 0 | 416 | 750.5 | 0 | 0 | 0 | 186
22:30 | 3345 | 1816.5 | 903.5 | 0 | 164 | 1458.405 | 100 | 5982.5 | 0 | 416 | 767.5 | 0 | 0 | 0 | 180.5
23:00 | 3348 | 1926 | 903 | 0 | 166 | 1461.06 | 100 | 5944 | 0 | 416 | 784.5 | 0 | 0 | 0 | 175
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 04-06-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 381 | 06:00 | 37 | 12:00 | Madunaghat | 398 | 00:00 | 387 | 01:00
Amtali | 411 | 17:00 | 401 | 22:00 | Meghnaghat | 387 | 06:00 | 373 | 22:00
Ashuganj | 378 | 06:00 | 365 | 12:00 | Payra | 413 | 18:00 | 404 | 22:00
Bhulta | 393 | 06:00 | 378 | 11:00 | Rahanpur | 408 | 17:00 | 384 | 23:00
Bibiana | 399 | 08:00 | 390 | 21:00 | Rampal | 396 | 09:00 | 381 | 00:00
BIPTC | 402 | 07:00 | 389 | 00:00
Bogura | 389 | 18:00 | 365 | 23:00
Gopalganj | 392 | 18:00 | 376 | 22:00
Kaliakoir | 378 | 06:00 | 365 | 12:00
Korerhat | 396 | 18:30 | 383 | 22:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 225 | 06:00 | 215 | 22:00 | Jhenaidah | 225 | 18:00 | 210 | 00:00
AKSML | 231 | 00:00 | 222 | 23:00 | Kachua | 224 | 16:00 | 213 | 22:00
Aminbazar | 226 | 06:00 | 216 | 22:00 | Kaliakoir | 222 | 06:00 | 211 | 22:00
Ashuganj | 226 | 06:00 | 218 | 22:00 | Keranigonj | 224 | 06:00 | 213 | 22:00
Ashuganj-400 | 226 | 06:00 | 218 | 22:00 | Khulna(S) | 224 | 18:00 | 209 | 00:00
Baghabari | 234 | 17:00 | 222 | 23:00 | Korerhat | 224 | 01:00 | 216 | 23:00
Barapukuria | 230 | 18:00 | 202 | 13:00 | Madunaghat | 233 | 01:00 | 225 | 21:00
Barapukuria-230 | 230 | 18:00 | 202 | 13:00 | Madunaghat-400 | 234 | 00:00 | 227 | 11:00
Barishal | 228 | 18:00 | 219 | 00:00 | Maniknagar | 224 | 06:00 | 212 | 15:00
Bheramara | 234 | 08:00 | 221 | 22:00 | Meghnaghat | 230 | 07:00 | 221 | 22:00
Bhulta | 225 | 06:00 | 214 | 13:00 | Meghnaghat-400 | 226 | 06:00 | 217 | 12:00
Bibiana | 231 | 07:00 | 225 | 22:00 | Mirsorai | 229 | 17:00 | 222 | 22:00
BIPTC | 236 | 08:00 | 221 | 22:00 | Naogaon | 225 | 18:00 | 195 | 23:00
Bogura | 243 | 18:30 | 224 | 23:00 | Purbasadipur | 230 | 18:30 | 199 | 00:00
Bogura-400 | 243 | 18:30 | 225 | 23:00 | Rajshahi | 232 | 17:00 | 218 | 13:00
Borhanuddin | 231 | 08:00 | 225 | 22:00 | Rampal | 223 | 08:00 | 211 | 00:00
BSRM | 225 | 00:00 | 216 | 22:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 229 | 00:00 | 214 | 22:00 | Rampura | 224 | 06:00 | 212 | 13:00
Cumilla(N) | 223 | 07:00 | 215 | 23:00 | Shikalbaha | 233 | 00:00 | 225 | 10:00
Faridpur | 225 | 18:00 | 215 | 00:00 | Shyampur | 224 | 06:00 | 214 | 22:00
Fenchuganj | 235 | 08:00 | 227 | 22:00 | Siddhirganj | 224 | 05:00 | 215 | 13:00
Feni | 223 | 01:00 | 214 | 22:00 | Sirajgonj | 240 | 17:00 | 230 | 22:00
Ghorashal | 228 | 04:00 | 220 | 09:00 | Sreepur | 225 | 18:00 | 213 | 22:00
Ghorashal-230 | 213 | 06:00 | 200 | 22:00 | Tongi | 216 | 04:00 | 206 | 13:00
Gopalganj | 227 | 18:30 | 217 | 22:00
GPH | 230 | 00:00 | 22 | 04:00
Haripur | 225 | 06:00 | 214 | 15:00
Hasnabad | 224 | 05:00 | 214 | 21:00
Hathazari | 230 | 00:00 | 223 | 23:00
Ishurdi | 235 | 08:00 | 223 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 130 | 04:00 | 121 | 13:00 | Madunaghat | 134 | 00:00 | 130 | 10:00
Agargaon | 130 | 18:00 | 122 | 11:00 | Magura | 131 | 21:00 | 116 | 00:00
Agrabad | 133 | 00:00 | 127 | 11:00 | Mahasthangarh | 140 | 18:30 | 124 | 13:00
AKS | 130 | 00:00 | 126 | 11:00 | Maijdee | 124 | 00:00 | 118 | 22:00
Aminbazar | 129 | 06:00 | 123 | 15:00 | Manikganj | 129 | 13:00 | 122 | 21:00
Amnura | 136 | 20:00 | 124 | 13:00 | Maniknagar | 129 | 18:00 | 118 | 11:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 114 | 09:00 | 106 | 21:00
Ashuganj-230 | 135 | 07:00 | 130 | 22:00 | Matuail | 130 | 18:00 | 121.6 | 12:00
Bagerhat | 128 | 18:00 | 112 | 00:00 | Metrorail_Motijheel | 129 | 18:00 | 118 | 11:00
Bajitpur | 128 | 13:00 | 117 | 22:00 | Metrorail_Uttara | 129 | 08:00 | 120 | 12:00
Bakerganj | 130 | 18:00 | 122 | 22:00 | Millgate | 131 | 05:00 | 121 | 12:00
Bakulia | 134 | 00:00 | 127 | 11:00 | Mirpur | 129 | 07:00 | 122 | 15:00
Banani | 131 | 06:00 | 120 | 13:00 | Mirzapur | 128 | 14:00 | 121 | 11:00
Bangabhaban | 129 | 18:00 | 117 | 11:00 | Mithapukur | 138 | 18:30 | 120 | 00:00
Barapukuria | 141 | 18:00 | 121 | 00:00 | MI_Cement | 128 | 05:00 | 120 | 13:00
Barguna | 129 | 18:00 | 122 | 00:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 129 | 08:00 | 123 | 00:00 | Mogbazar | 132 | 07:00 | 122 | 12:00
Barishal-230 | 130 | 18:00 | 123 | 22:00 | Mongla | 128 | 18:00 | 112 | 11:00
Baroaulia | 133 | 00:00 | 128 | 10:00 | Motijheel | 129 | 18:00 | 117 | 11:00
Baroirhat | 130 | 00:00 | 124 | 22:00 | Muktagacha | 131 | 14:00 | 115 | 21:00
Bashundhara | 129 | 03:00 | 120 | 12:00 | Munshiganj | 128 | 18:00 | 120 | 12:00
BashundharaCement | 129 | 18:00 | 121 | 12:00 | Muradnagar | 125 | 18:00 | 119 | 12:00
Beanibazar | 130 | 08:00 | 121 | 23:00 | Mymensingh | 132 | 14:00 | 110 | 21:00
Benapole | 132 | 21:00 | 111 | 00:00 | Nabinagar | 130 | 23:00 | 118 | 15:00
Bhaluka | 129 | 18:00 | 121 | 21:00 | Naogaon | 137 | 17:00 | 118 | 23:00
Bhandaria | 122 | 18:00 | 107 | 11:00 | Narail | 131 | 21:00 | 116 | 00:00
Bhangura | 134 | 17:00 | 127 | 00:00 | Narinda | 129 | 18:00 | 118 | 11:00
Bheramara | 137 | 18:00 | 130 | 00:00 | Narshingdi | 130 | 06:00 | 118 | 11:00
Bheramara(GK) | 137 | 18:00 | 130 | 00:00 | Natore | 136 | 18:30 | 124 | 23:00
Bhulta | 126 | 18:00 | 119 | 13:00 | Nawabganj | 130 | 18:30 | 124 | 11:00
Bog-Sherpur | 139 | 18:00 | 126 | 13:00 | Netrakona | 121 | 13:00 | 107 | 21:00
Bogura | 142 | 18:30 | 128 | 23:00 | New | 131 | 04:00 | 121 | 13:00
Bogura-230 | 142 | 18:30 | 128 | 23:00 | Niamatpur | 136 | 17:00 | 121 | 23:00
Brahmanbaria | 130 | 15:00 | 122 | 23:00 | Noapara | 130 | 18:00 | 116 | 00:00
Cantonment | 129 | 06:00 | 122 | 11:00 | Pabna | 136 | 18:00 | 127 | 00:00
Chandina | 128 | 18:00 | 122 | 22:00 | Palashbari | 136 | 18:30 | 118 | 00:00
Chandpur | 129 | 00:00 | 120 | 11:00 | Panchagarh | 140 | 18:00 | 123 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 135 | 01:00 | 131 | 10:00 | Patiya | 132 | 00:00 | 125 | 11:00
Chapai | 135 | 17:00 | 124 | 13:00 | Patuakhali | 129 | 08:00 | 123 | 22:00
Charsaidpur | 130 | 18:00 | 120 | 12:00 | Payra | 134 | 09:00 | 130 | 00:00
Chauddagram | 127 | 01:00 | 121 | 22:00 | PHP | 129 | 00:00 | 124 | 22:00
Chhatak | 128 | 06:00 | 117 | 22:00 | Postogola | 131 | 06:00 | 123 | 13:00
Chowmuhani | 126 | 14:00 | 121 | 21:00 | Pubail | 127 | 18:00 | 121 | 11:00
Chuadanga | 131 | 20:00 | 114 | 01:00 | Purbachal | 131 | 05:00 | 120 | 12:00
Coxsbazar | 116 | 08:00 | 108 | 20:00 | Purbasadipur | 140 | 18:00 | 119 | 23:00
Cumilla(N) | 128 | 02:00 | 123 | 21:00 | Rahanpur | 136 | 17:00 | 127 | 23:00
Cumilla(S) | 131 | 05:00 | 122 | 22:00 | Rahanpur-400 | 137 | 17:00 | 127 | 23:00
Daganbhuiyan | 127 | 17:00 | 121 | 22:00 | Rahim | 130 | 18:00 | 122 | 11:00
Daudkandi | 124 | 17:00 | 116 | 12:00 | Rajbari | 127 | 18:30 | 120 | 00:00
DhakaUniversity | 131 | 05:00 | 121 | 12:00 | Rajendrapur | 128 | 09:00 | 121 | 21:00
Dhamrai | 130 | 23:00 | 120 | 15:00 | Rajshahi | 133 | 17:00 | 122 | 23:00
Dhanmondi | 131 | 05:00 | 120.7 | 13:00 | Rajshahi-230 | 134 | 17:00 | 125 | 13:00
Dohazari | 127 | 15:00 | 120 | 10:00 | Ramganj | 123 | 00:00 | 115 | 23:00
Faridpur | 129 | 18:30 | 123 | 22:00 | Rampur | 132 | 00:00 | 127 | 10:00
Fatullah | 129 | 06:00 | 121 | 11:00 | Rampura | 131 | 06:00 | 121 | 13:00
Fenchuganj | 135 | 08:00 | 129 | 01:00 | Rangamati | 133 | 01:00 | 33 | 00:00
Feni | 127 | 00:00 | 122 | 21:00 | Rangpur | 139 | 18:30 | 116 | 00:00
Feni-230 | 128 | 00:00 | 122 | 22:00 | Ruppur | 137 | 18:00 | 129 | 13:00
Ghatail | 127 | 14:00 | 115 | 12:00 | Saidpur | 140 | 18:30 | 120 | 00:00
Ghorashal | 128 | 03:00 | 122 | 22:00 | Santhia | 135 | 17:00 | 128 | 00:00
Goalpara | 133 | 18:30 | 120 | 13:00 | Satkhira | 125 | 18:30 | 109 | 00:00
Gollamari | 133 | 18:00 | 120 | 00:00 | Satmasjid | 130 | 18:30 | 122 | 11:00
Gopalganj | 130 | 18:00 | 120 | 23:00 | Savar | 128 | 07:00 | 121 | 15:00
Gopalganj-400 | 132 | 18:00 | 125 | 22:00 | SevenRings | 129 | 07:00 | 121 | 13:00
Gulshan | 130 | 06:00 | 121 | 12:00 | ShahCement | 130 | 18:00 | 120 | 12:00
Halishahar | 134 | 00:00 | 128 | 11:00 | Shahjadpur | 138 | 17:00 | 131 | 22:00
Haripur | 130 | 18:00 | 122 | 12:00 | Shahjibazar | 132 | 08:00 | 123 | 23:00
HaripurSBU | 130 | 18:00 | 122 | 12:00 | Shahmirpur | 134 | 00:00 | 128 | 22:00
Hasnabad | 130 | 03:00 | 123 | 13:00 | Shariatpur | 128 | 18:00 | 119 | 23:00
Hathazari | 135 | 17:00 | 130 | 10:00 | Sherpur | 131 | 14:00 | 109 | 23:00
Hatirjheel | 131 | 06:00 | 121 | 12:00 | Shikalbaha | 124 | 00:00 | 117 | 11:00
Ishurdi | 138 | 17:00 | 131 | 00:00 | Shikalbaha-230 | 135 | 00:00 | 129 | 21:00
Jaldhaka | 138 | 18:30 | 116 | 00:00 | Shitalakhya | 128 | 05:00 | 120 | 13:00
Jamalpur | 134 | 14:00 | 112 | 17:00 | Sholosohor | 133 | 00:00 | 128 | 10:00
Jashore | 132 | 21:00 | 113 | 13:00 | Shomvuganj | 124 | 13:00 | 112 | 22:00
Jhenaidah | 133 | 21:00 | 119 | 13:00 | Shyampur | 129 | 18:00 | 120 | 11:00
Jhenaidah-230 | 133 | 13:00 | 120 | 14:00 | Shyampur-230 | 128 | 06:00 | 122 | 12:00
Joydebpur | 125 | 06:00 | 118 | 11:00 | Siddhirganj | 129 | 18:00 | 122 | 11:00
Joypurhat | 141 | 18:30 | 114 | 13:00 | Sirajganj | 134 | 18:30 | 124 | 13:00
Juldah | 135 | 02:00 | 128 | 10:00 | Sonargaon | 128 | 18:00 | 120 | 11:00
Kabirpur | 133 | 16:00 | 119 | 12:00 | Sreemongol | 131 | 08:00 | 124 | 21:00
Kachua | 127 | 00:00 | 120 | 22:00 | Sreepur | 131 | 14:00 | 123 | 22:00
Kaliakoir | 133 | 16:00 | 123 | 22:00 | Srinagar | 130 | 07:00 | 124 | 11:00
Kaliganj | 131 | 18:00 | 119 | 13:00 | SSM | 138 | 00:00 | 132 | 10:00
Kallyanpur | 128 | 04:00 | 123 | 11:00 | Sunamganj | 128 | 05:00 | 116 | 21:00
Kalurghat | 135 | 00:00 | 130 | 11:00 | Sylhet | 130 | 07:00 | 123 | 22:00
Kamrangirchar | 131 | 18:00 | 121 | 22:00 | Sylhet-132 | 129 | 06:00 | 124 | 23:00
Kaptai | N/A | N/A | N/A | N/A | Tangail | 127 | 16:00 | 117 | 12:00
Kasba | 124 | 18:00 | 118 | 12:00 | Taraganj | 139 | 18:30 | 122 | 13:00
Kazla | 128 | 18:00 | 118 | 11:00 | Tasnim | 128 | 18:00 | 120 | 11:00
Keranigonj | 131 | 06:00 | 125 | 11:00 | Thakurgaon | 140 | 18:00 | 120 | 23:00
Khagrachori | 132 | 00:00 | 128 | 10:00 | TK | 134 | 00:00 | 130 | 21:00
Khulna | 132 | 18:00 | 119 | 00:00 | Tongi | 134 | 04:00 | 126 | 11:00
Khulna(S) | 133 | 18:00 | 120 | 00:00 | Ullahpara | 134 | 17:00 | 125 | 23:00
Khulshi | 131 | 00:00 | 126 | 10:00 | Ullon | 133 | 05:00 | 121 | 12:00
Kishoreganj | 127 | 14:00 | 114 | 22:00 | Uttara | 129 | 04:00 | 118 | 13:00
Kodda | 132 | 00:00 | 125 | 21:00 | UttaraNew | 129 | 08:00 | 120 | 12:00
Korerhat | 132 | 00:00 | 127 | 23:00 | Zigatola | 131 | 18:00 | 125 | 11:00
KSRM | 135 | 00:00 | 128 | 23:00
Kulaura | 134 | 09:00 | 127 | 22:00
Kurigram | 133 | 18:30 | 112 | 00:00
Kushtia | 134 | 18:00 | 123 | 13:00
Laksam | 128 | 12:00 | 119 | 22:00
Lakshmipur | 124 | 17:00 | 117 | 23:00
Lalbag | 130 | 07:00 | 125 | 11:00
Lalmonirhat | 133 | 18:30 | 114 | 00:00
Madanganj | 129 | 18:00 | 121 | 12:00
Madaripur | 130 | 08:00 | 123 | 15:00
Madartek | 131 | 06:00 | 121 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division