## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 06-06-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-06-2026 | during | 06-06-2026 | during | 06-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Under Maintenance
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 350 | 330 | 412 | 412 | 412 | 412 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 160 | 160 | 225 | 225 | 161 | 161 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 220 | 220 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 15.5 | 53.97 | 53.97 | 55 | 55 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0.02 | 0.02 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0.02 | 0.02 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 17 | 33 | 33 | 26 | 26 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 16 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 105 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 34 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 15 | 162 | 162 | 0.01 | 0.01 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 22 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 390 | 485 | 584 | 584 | 480 | 480 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 350 | 455 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 105 | 142 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1453 | 1809.5 | 5822.22 | 5792.22 | 2320.41 | 2343.41
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 8 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 14 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 10 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 100 | 95 | 100 | 100 | 100 | 100 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 216 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 34 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 27 | 36 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 26 | 108 | 108 | 100 | 100 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.38 | 0 | 4.36 | 0 | 4.36 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 24 | 12 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 35 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1000 | 1224 | 1224 | 1224 | 1204 | 1204 | AGC
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 2 | 0 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 900 | 1080 | 700 | 700 | 1150 | 1150 | AGC
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2292.38 | 2804 | 3546.22 | 3607.86 | 3343.72 | 3517.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 195 | 208 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 290 | 290 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 240 | 240 | 342.01 | 342.01 | 342.01 | 342.01 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 230 | 270 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 28 | 32 | 41.65 | 41.65 | 11 | 11 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 42 | 30 | 52.82 | 52.82 | 11 | 11 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0.02 | 0.02 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 50 | 150 | 150 | 161 | 161 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 88 | 92 | 163 | 163 | 94 | 94 | ST Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 130 | 134 | 84 | 80 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 0.01 | 0.01 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 16 | 115 | 115 | 34 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 43 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1356 | 1432 | 2757.44 | 2698.44 | 2261.5 | 2262.5
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-06-2026 | during | 06-06-2026 | during | 06-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 9.95 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 10 | 157.5 | 157.5 | 25 | 25 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.5 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 78 | 28 | 10 | 10 | 9 | 9 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 12 | 88 | 90 | 90 | 85 | 85 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 29.53 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 140.98 | 143 | 404.2 | 334 | 206.2 | 148
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 41 | 41 | 41 | 41 | ps availability is less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 143 | 140 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 151 | 151 | 150 | 150 | 150 | 150 | ps availability is less
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 101 | 100 | 100 | 100 | 100 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.02 | 0.02 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 24 | 25 | 25 | 24 | 24 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 364 | 314 | 350 | 350 | 300 | 300 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1271 | 1227 | 1336 | 1336 | 1215.02 | 1215.02
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 906 | 906 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 32 | 32 | 36 | 36 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.02 | 0.02 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 205 | 210 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 52 | 105 | 105 | 90 | 90 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 7.17 | 0 | 55 | 0 | 55 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0.02 | 0.02 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 905 | 1212 | 1234.2 | 1234.2 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2023.17 | 2380 | 3557.2 | 3502.2 | 2702.04 | 2647.04
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 455 | 530 | 500 | 500 | 500 | 500 | U-1 Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 60 | 60 | 60 | 60 | 124 | 124 | STG Under Maintenance
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 896 | 1232 | 1244 | 1244 | 1184 | 1184 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 110 | 110 | 110 | 110 | 110 | 110 | GT is under maintenance
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 0 | 150 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 196 | 307 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.03 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 1717.03 | 2239 | 2482 | 2481 | 2316 | 2465
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 21.58 | 0 | 60 | 0 | 60 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 32 | 32 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 160 | 160 | 220 | 220 | 220 | 220 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 140 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 356 | 404 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 97 | 97 | 0.02 | 0.02 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 100 | 100 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 99 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.17 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1265 | 1457 | 1435.88 | 1435.88 | 1356 | 1356 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 37.4 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 41 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2024.15 | 2161 | 3027.57 | 2800.87 | 2678.33 | 2515.63
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 39 | 40 | 40 | 40 | 40 | 40 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 99 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.4 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 17 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 125 | 0 | 188.97 | 0 | 188.97 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 183.4 | 254 | 512.97 | 288 | 492.97 | 268
System Total |  |  |  |  | 28843.2 | 29290.237 | 12461.11 | 14449.5 | 23445.82 | 22840.59 | 17536.19 | 17381.96
Forecast Scenario (06-06-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13442 |  | 0 |  | 13442
|  |  |  | 1:00 | 14465 |  | 0 |  | 14465
|  |  |  | 2:00 | 13949 |  | 0 |  | 13949
|  |  |  | 3:00 | 13577 |  | 0 |  | 13577
|  |  |  | 4:00 | 13247 |  | 0 |  | 13247
|  |  |  | 5:00 | 13052 |  | 0 |  | 13052
|  |  |  | 6:00 | 12674 |  | 0 |  | 12674
|  |  |  | 7:00 | 12767 |  | 0 |  | 12767
|  |  |  | 8:00 | 12992 |  | 0 |  | 12992
|  |  |  | 9:00 | 13220 |  | 0 |  | 13220
|  |  |  | 10:00 | 13300 |  | 0 |  | 13300
|  |  |  | 11:00 | 13700 |  | 0 |  | 13700
|  |  |  | 12:00 | 13800 |  | 0 |  | 13800
|  |  |  | 13:00 | 13500 |  | 0 |  | 13500
|  |  |  | 14:00 | 13600 |  | 0 |  | 13600
|  |  |  | 15:00 | 13700 |  | 0 |  | 13700
|  |  |  | 16:00 | 13600 |  | 0 |  | 13600
|  |  |  | 17:00 | 13400 |  | 0 |  | 13400
|  |  |  | 18:00 | 13380 |  | 0 |  | 13380
|  |  |  | 18:30 | 14200 |  | 0 |  | 14200
|  |  |  | 19:00 | 14900 |  | 0 |  | 14900
|  |  |  | 19:30 | 15414 |  | 0 |  | 15414
|  |  |  | 20:00 | 15270 |  | 0 |  | 15270
|  |  |  | 21:00 | 15380 |  | 0 |  | 15380
|  |  |  | 22:00 | 15270 |  | 0 |  | 15270
|  |  |  | 23:00 | 15100 |  | 0 |  | 15100
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 13800.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15414.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15414.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 308.306 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:15 hrs on 06-06-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 05-06-2026 | [28 empty] | Date: | 05-06-2026 | [28 empty] | Date: | 05-06-2026 | [28 empty] | Date: | 05-06-2026 | [28 empty] | Date: | 05-06-2026 | [18 empty] | Date: | 05-06-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [18 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 297 | 0 | 0 | 60 | 0 | 80 | 0 | 0 | 65 | 0 | 160 | 146 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 470 | 22 | 16 | 58 | 0 | 2 | 50 | 67 | 17 | 25 | 24 | 0 | 100 | 59 | 27 | 1065 | 0 | 0 | 50 | 0 | 101 | 215 | 0 | 0 | 0 | 1177 | 0 | 13 | 0 | 230 | 290 | 240 | 51 | 0 | 209 | 20 | 49 | 91 | 53 | 0 | 19 | 0 | 166 | 0 | 0 | 37 | 320 | 0 | 320 | 41 | 30 | 154 | 0 | 24 | 0 | 85 | 28 | 149 | 0 | 101 | 0 | 9 | 0 | 78 | 10 | 0 | 0 | 0 | 7813 | 903 | 190 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1191 | 27 | 0 | 0 | 1460.89 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 39 | 50 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 282 | 120 | 220 | 0 | 877 | 1237 | 0 | 7469.89 | 15282.89 | 76.02
01:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 232 | 0 | 0 | 17 | 38 | 80 | 0 | 7 | 69 | 0 | 160 | 136 | 60 | 0 | 17 | 0 | 0 | 0 | 0 | 142 | 21 | 21 | 0 | 430 | 74 | 16 | 27 | 0 | 0 | 50 | 67 | 17 | 25 | 24 | 0 | 100 | 96 | 35 | 1070 | 0 | 0 | 50 | 0 | 100 | 217 | 0 | 0 | 0 | 1162 | 0 | 63 | 0 | 230 | 290 | 240 | 51 | 0 | 197 | 20 | 0 | 91 | 119 | 0 | 19 | 34 | 156 | 4 | 0 | 37 | 310 | 0 | 320 | 41 | 30 | 146 | 0 | 24 | 0 | 83 | 28 | 152 | 0 | 101 | 0 | 9 | 0 | 78 | 10 | 0 | 0 | 0 | 7887 | 830 | 185 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1190 | 34 | 0 | 0 | 1457.44 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 374 | 0 | 0 | 0 | 40 | 50 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 274 | 120 | 220 | 0 | 812 | 1232 | 5 | 7337.44 | 15224.44 | 76.01
02:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 259 | 0 | 0 | 17 | 45 | 80 | 0 | 17 | 68 | 0 | 160 | 140 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 21 | 21 | 0 | 433 | 96 | 16 | 25 | 0 | 2 | 0 | 67 | 17 | 25 | 24 | 0 | 100 | 108 | 35 | 1070 | 0 | 0 | 50 | 0 | 98 | 217 | 0 | 0 | 0 | 1163 | 0 | 80 | 0 | 230 | 290 | 240 | 51 | 0 | 194 | 20 | 0 | 91 | 145 | 0 | 19 | 32 | 146 | 25 | 0 | 38 | 315 | 0 | 320 | 41 | 30 | 149 | 0 | 24 | 0 | 83 | 28 | 152 | 0 | 101 | 0 | 9 | 0 | 78 | 10 | 0 | 0 | 0 | 7961 | 906 | 185 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1191 | 34 | 0 | 0 | 1449.44 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 398 | 0 | 0 | 0 | 40 | 50 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 277 | 120 | 110 | 0 | 673 | 1232 | 35 | 7215.44 | 15176.44 | 76.01
03:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 253 | 0 | 0 | 17 | 30 | 80 | 0 | 17 | 69 | 0 | 160 | 140 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 21 | 21 | 0 | 425 | 60 | 16 | 0 | 0 | 0 | 0 | 30 | 0 | 25 | 24 | 0 | 100 | 109 | 36 | 1070 | 0 | 0 | 50 | 0 | 96 | 216 | 0 | 0 | 0 | 1164 | 0 | 80 | 0 | 230 | 290 | 240 | 51 | 0 | 193 | 20 | 0 | 91 | 34 | 0 | 19 | 0 | 156 | 8 | 0 | 38 | 315 | 0 | 320 | 41 | 30 | 138 | 0 | 24 | 0 | 83 | 28 | 153 | 0 | 101 | 0 | 9 | 0 | 78 | 10 | 0 | 0 | 0 | 7655 | 906 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1187 | 34 | 0 | 0 | 1443.22 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 387 | 0 | 0 | 0 | 40 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 276 | 120 | 110 | 0 | 611 | 1232 | 35 | 7036.22 | 14691.22 | 76.01
04:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 229 | 0 | 0 | 17 | 30 | 80 | 0 | 17 | 0 | 0 | 160 | 140 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 21 | 21 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 0 | 97 | 106 | 36 | 1070 | 0 | 0 | 28 | 0 | 97 | 217 | 0 | 0 | 0 | 1165 | 0 | 80 | 0 | 230 | 290 | 240 | 51 | 0 | 198 | 20 | 0 | 92 | 0 | 0 | 19 | 0 | 156 | 0 | 0 | 38 | 310 | 0 | 318 | 41 | 30 | 138 | 0 | 24 | 0 | 83 | 28 | 151 | 0 | 101 | 0 | 9 | 0 | 78 | 10 | 0 | 0 | 0 | 7338 | 905 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1193 | 17 | 0 | 0 | 1453.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 350 | 0 | 0 | 0 | 40 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 276 | 120 | 110 | 0 | 622 | 1232 | 0 | 6906.09 | 14244.09 | 76.01
05:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 230 | 0 | 0 | 17 | 30 | 45 | 0 | 0 | 0 | 0 | 160 | 82 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 21 | 21 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 94 | 85 | 37 | 1070 | 0 | 0 | 19 | 0 | 51 | 217 | 0 | 0 | 0 | 1162 | 0 | 20 | 0 | 230 | 290 | 240 | 51 | 0 | 192 | 20 | 0 | 91 | 0 | 0 | 19 | 0 | 154 | 0 | 0 | 22 | 310 | 0 | 318 | 41 | 30 | 137 | 0 | 24 | 0 | 83 | 28 | 152 | 0 | 101 | 0 | 9 | 0 | 78 | 10 | 0 | 0 | 0 | 7046 | 906 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1194 | 17 | 0 | 0 | 1446.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 350 | 0 | 0 | 0 | 40 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 275 | 60 | 110 | 0 | 622 | 1232 | 0 | 6849.82 | 13895.82 | 76.01
06:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 203 | 0 | 0 | 17 | 30 | 45 | 0 | 0 | 0 | 0 | 160 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 1 | 142 | 20 | 21 | 0 | 325 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 24 | 0.36 | 93 | 106 | 39 | 1070 | 0 | 0 | 19 | 0 | 17 | 217 | 0 | 0 | 0 | 1050 | 1 | 12 | 0 | 230 | 290 | 240 | 51 | 0 | 189 | 20 | 0 | 90 | 0 | 0 | 19 | 0 | 136 | 0 | 5 | 16 | 300 | 0 | 318 | 41 | 30 | 124 | 0 | 16 | 0 | 83 | 30 | 153 | 0 | 101 | 0 | 9 | 0.72 | 77 | 10 | 0.2 | 0.22 | 0 | 6751.5 | 905 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.02 | 1144 | 17 | 0 | 0 | 1307.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.87 | 9 | 0 | 0 | 4.21 | 0 | 0 | 160 | 0 | 140 | 0 | 329 | 0 | 0.38 | 0 | 40 | 35 | 2 | 34 | 0 | 0 | 0 | 0.4 | 7 | 0.02 | 16 | 276 | 60 | 110 | 0 | 550 | 1120 | 0 | 6473.96 | 13225.46 | 76.01
07:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 100 | 0 | 0 | 17 | 15 | 15 | 0 | 0 | 0 | 0 | 160 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 6 | 105 | 20 | 21 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 1.26 | 96 | 0 | 38 | 1000 | 0 | 0 | 19 | 0 | 15 | 217 | 0 | 0 | 0 | 1002 | 4 | 12 | 0 | 230 | 290 | 240 | 51 | 10 | 200 | 32 | 0 | 91 | 0 | 0 | 19 | 0 | 134 | 0 | 17 | 16 | 305 | 0 | 320 | 41 | 30 | 131 | 0 | 16 | 0 | 83 | 30 | 152 | 0 | 101 | 0 | 9 | 5.23 | 78 | 10 | 0.5 | 9.5 | 0 | 6546.49 | 905 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.55 | 1034 | 17 | 0 | 0 | 1260.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6 | 22 | 0 | 0 | 9.62 | 0 | 0 | 160 | 0 | 140 | 0 | 385 | 0 | 0.8 | 0 | 40 | 0 | 6 | 34 | 0 | 0 | 0 | 1.6 | 36 | 0.01 | 0 | 196 | 60 | 110 | 0 | 545 | 1000 | 0 | 6197.16 | 12743.65 | 76.01
08:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 13 | 105 | 20 | 21 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 1.78 | 100 | 0 | 36 | 915 | 0 | 0 | 19 | 0 | 0 | 214 | 0 | 0 | 0 | 1001 | 10 | 0 | 0 | 230 | 290 | 240 | 51 | 33 | 200 | 29 | 0 | 90 | 0 | 0 | 19 | 0 | 136 | 0 | 30 | 0 | 315 | 0 | 340 | 41 | 30 | 140 | 0 | 16 | 0 | 83 | 30 | 150 | 0 | 101 | 0 | 9 | 10.07 | 78 | 10 | 0.8 | 15.29 | 0 | 6525.94 | 905 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.93 | 954 | 0 | 0 | 0 | 1267.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.81 | 28 | 0 | 0 | 15.9 | 0 | 0 | 160 | 0 | 140 | 0 | 383 | 0 | 1.23 | 0 | 40 | 0 | 12 | 34 | 0 | 0 | 0 | 3.5 | 90 | 0.03 | 0 | 198 | 60 | 110 | 0 | 460 | 900 | 0 | 6005.83 | 12531.77 | 76.01
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 22 | 105 | 21 | 21 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 3.38 | 100 | 0 | 27 | 900 | 0 | 0 | 10 | 0 | 0 | 214 | 0 | 0 | 0 | 1000 | 14 | 0 | 0 | 230 | 290 | 240 | 51 | 42 | 195 | 28 | 0 | 88 | 0 | 0 | 19 | 0 | 130 | 0 | 43 | 0 | 310 | 0 | 364 | 41 | 30 | 143 | 1 | 16 | 0 | 84 | 30 | 151 | 0 | 101 | 0 | 12 | 9.95 | 78 | 10 | 1.5 | 29.53 | 0 | 6513.36 | 906 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.17 | 905 | 0 | 0 | 0 | 1265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.58 | 41 | 0 | 0 | 37.4 | 0 | 0 | 160 | 0 | 140 | 0 | 356 | 0 | 3.17 | 0 | 39 | 0 | 17 | 0 | 0 | 0 | 0 | 2.4 | 125 | 0.03 | 0 | 196 | 60 | 110 | 0 | 455 | 896 | 0 | 5947.75 | 12461.11 | 76.01
10:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 18 | 105 | 21 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 3.87 | 100 | 0 | 25 | 900 | 0 | 0 | 19 | 0 | 0 | 214 | 0 | 0 | 0 | 1001 | 0 | 0 | 0 | 230 | 290 | 240 | 51 | 44 | 199 | 32 | 0 | 88 | 0 | 0 | 19 | 0 | 134 | 0 | 49 | 0 | 310 | 0 | 367 | 41 | 30 | 130 | 2 | 16 | 0 | 86 | 30 | 153 | 0 | 102 | 0 | 85 | 18.95 | 9 | 10 | 1.6 | 21.95 | 0 | 6449.37 | 905 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.07 | 898 | 0 | 0 | 0 | 1289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.89 | 82 | 0 | 0 | 43.5 | 0 | 0 | 160 | 0 | 140 | 0 | 350 | 0 | 3.57 | 0 | 40 | 0 | 24 | 0 | 0 | 0 | 0 | 3.5 | 129 | 0.5 | 0 | 199 | 60 | 110 | 0 | 367 | 840 | 0 | 5912.03 | 12361.4 | 76.01
11:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 5 | 0 | 21 | 0 | 0 | 13 | 0 | 0 | 0 | 160 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 13 | 105 | 21 | 14 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 3.58 | 100 | 0 | 24 | 850 | 0 | 0 | 19 | 0 | 0 | 213 | 0 | 0 | 0 | 950 | 17 | 0 | 0 | 230 | 290 | 240 | 51 | 30 | 201 | 31 | 0 | 88 | 0 | 0 | 19 | 0 | 122 | 0 | 62 | 0 | 315 | 0 | 356 | 41 | 30 | 132 | 10 | 22 | 0 | 86 | 30 | 153 | 0 | 102 | 0 | 84 | 21.15 | 9 | 10 | 1.5 | 44.31 | 0 | 6448.54 | 905 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.24 | 869 | 0 | 0 | 0 | 1269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.59 | 71 | 0 | 0 | 33.67 | 0 | 0 | 160 | 0 | 140 | 0 | 380 | 0 | 4.31 | 0 | 40 | 0 | 19 | 0 | 0 | 0 | 0 | 4.6 | 145 | 0.06 | 0 | 198 | 60 | 110 | 0 | 386 | 720 | 0 | 5790.47 | 12239.01 | 76.01
12:00 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 14.5 | 10 | 34 | 0 | 0 | 15 | 0 | 0 | 0 | 160 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 21 | 139 | 21 | 14 | 0 | 390 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 12 | 2.84 | 100 | 0 | 31 | 850 | 0 | 0 | 19 | 0 | 0 | 211 | 0 | 0 | 0 | 951 | 16 | 0 | 0 | 230 | 290 | 240 | 51 | 15 | 205 | 34 | 0 | 92 | 0 | 0 | 7 | 0 | 114 | 0 | 66 | 0 | 310 | 0 | 357 | 41 | 30 | 140 | 10 | 22 | 0 | 86 | 30 | 153 | 0 | 101 | 0 | 86 | 15.27 | 9 | 10 | 1.6 | 33.98 | 0 | 6540.19 | 906 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.05 | 859 | 0 | 0 | 0 | 1280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.08 | 103 | 0 | 0 | 53.49 | 0 | 0 | 160 | 0 | 140 | 0 | 387 | 0 | 4.65 | 0 | 40 | 0 | 16 | 0 | 0 | 0 | 0 | 4.5 | 133 | 0.1 | 0 | 200 | 60 | 110 | 0 | 398 | 670 | 0 | 5799.87 | 12340.06 | 76
13:00 | 0 | 56 | 8 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 17.5 | 17 | 34 | 0 | 0 | 15 | 0 | 0 | 0 | 160 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 5 | 142 | 21 | 14 | 0 | 460 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 12 | 3.14 | 100 | 0 | 24 | 991 | 0 | 0 | 19 | 0 | 0 | 211 | 0 | 0 | 0 | 1045 | 16 | 0 | 0 | 215 | 290 | 240 | 51 | 0 | 205 | 34 | 0 | 93 | 0 | 0 | 7 | 0 | 110 | 0 | 8 | 0 | 325 | 0 | 356 | 41 | 30 | 149 | 11 | 23 | 0 | 85 | 30 | 153 | 0 | 101 | 0 | 88 | 18.73 | 9 | 10 | 1.8 | 50.32 | 10 | 6829.49 | 905 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 883 | 0 | 0 | 0 | 1274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.78 | 79 | 0 | 0 | 39.05 | 0 | 0 | 160 | 0 | 140 | 0 | 374 | 0 | 2.32 | 0 | 39 | 0 | 17 | 0 | 0 | 0 | 0 | 6.7 | 85 | 0.16 | 0 | 197 | 60 | 110 | 0 | 472 | 735 | 0 | 5842.01 | 12671.5 | 75.99
14:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 17.5 | 0 | 34 | 0 | 0 | 15 | 0 | 0 | 0 | 160 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 5 | 142 | 16 | 14 | 0 | 380 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 12 | 3.76 | 100 | 0 | 31 | 900 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 984 | 15 | 0 | 0 | 215 | 290 | 240 | 51 | 0 | 216 | 34 | 0 | 93 | 0 | 0 | 7 | 0 | 122 | 0 | 3 | 0 | 305 | 0 | 307 | 41 | 30 | 136 | 9 | 23 | 0 | 85 | 30 | 154 | 0 | 101 | 0 | 88 | 11.54 | 9 | 10 | 1.2 | 28.99 | 12 | 6430.99 | 905 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 905 | 0 | 0 | 0 | 1167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.89 | 55 | 0 | 0 | 21.77 | 0 | 0 | 160 | 0 | 140 | 0 | 389 | 0 | 2.27 | 0 | 39 | 0 | 22 | 0 | 0 | 0 | 0 | 6.1 | 122 | 0.12 | 0 | 201 | 60 | 110 | 0 | 392 | 805 | 0 | 5765.15 | 12196.14 | 75.98
15:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 15 | 0 | 0 | 0 | 160 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 7 | 123 | 17 | 14 | 0 | 470 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 12 | 0.75 | 100 | 0 | 28 | 900 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 980 | 12 | 0 | 0 | 215 | 290 | 240 | 51 | 0 | 200 | 10 | 0 | 93 | 0 | 0 | 19 | 0 | 106 | 0 | 4 | 0 | 310 | 0 | 308 | 41 | 30 | 146 | 5 | 23 | 0 | 85 | 30 | 152 | 0 | 101 | 0 | 88 | 5.5 | 9 | 10 | 1.3 | 9.15 | 12 | 6378.7 | 905 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 875 | 0 | 0 | 0 | 1177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.25 | 60 | 0 | 0 | 1 | 0 | 0 | 160 | 0 | 140 | 0 | 405 | 0 | 0 | 0 | 39 | 0 | 20 | 0 | 0 | 0 | 0 | 4.9 | 62 | 0.1 | 0 | 200 | 60 | 110 | 0 | 418 | 780 | 0 | 5677.25 | 12055.95 | 75.97
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 8 | 86 | 17 | 14 | 0 | 490 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 12 | 0.82 | 95 | 0 | 13 | 860 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 980 | 8 | 0 | 0 | 230 | 290 | 240 | 51 | 0 | 199 | 10 | 0 | 93 | 0 | 0 | 19 | 0 | 110 | 0 | 5 | 0 | 315 | 0 | 307 | 41 | 30 | 147 | 3 | 23 | 0 | 83 | 30 | 149 | 0 | 101 | 0 | 88 | 3.48 | 9 | 10 | 0.2 | 5.82 | 12 | 6307.32 | 905 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.71 | 854 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.28 | 40 | 0 | 0 | 16.34 | 0 | 0 | 160 | 0 | 140 | 0 | 387 | 0 | 0 | 0 | 39 | 0 | 15 | 0 | 0 | 0 | 0 | 2.7 | 83 | 0.17 | 0 | 203 | 60 | 110 | 0 | 404 | 800 | 0 | 5622.2 | 11929.52 | 75.96
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 5 | 86 | 17 | 14 | 0 | 490 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.5 | 94 | 0 | 31 | 840 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 900 | 3 | 0 | 0 | 230 | 290 | 240 | 51 | 0 | 201 | 10 | 0 | 92 | 0 | 0 | 19 | 0 | 102 | 0 | 5 | 0 | 315 | 0 | 320 | 41 | 30 | 148 | 2 | 23 | 0 | 83 | 30 | 151 | 0 | 101 | 0 | 88 | 5.86 | 9 | 10 | 0.5 | 7.96 | 12 | 6218.82 | 905 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 784 | 0 | 0 | 0 | 1185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.27 | 26 | 0 | 0 | 7.58 | 0 | 0 | 160 | 0 | 140 | 0 | 406 | 0 | 0.73 | 0 | 40 | 0 | 6 | 0 | 0 | 0 | 0 | 1.6 | 39 | 0.1 | 0 | 213 | 60 | 110 | 0 | 416 | 820 | 0 | 5546.28 | 11765.1 | 75.94
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 25 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 1 | 86 | 17 | 14 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 90 | 0 | 35 | 860 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 900 | 0 | 0 | 0 | 230 | 290 | 240 | 51 | 0 | 197 | 15 | 0 | 91 | 0 | 0 | 19 | 0 | 108 | 0 | 1 | 0 | 310 | 0 | 314 | 41 | 30 | 150 | 0 | 23 | 0 | 83 | 30 | 151 | 0 | 101 | 0 | 88 | 2.04 | 9 | 10 | 0.2 | 3.98 | 0 | 6207.32 | 905 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 780 | 0 | 0 | 0 | 1154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.77 | 10 | 0 | 0 | 3 | 0 | 0 | 160 | 0 | 140 | 0 | 408 | 0 | 0.34 | 0 | 40 | 0 | 1 | 3 | 0 | 0 | 0 | 0.5 | 11 | 0.02 | 0 | 221 | 60 | 110 | 0 | 407 | 880 | 0 | 5503.63 | 11710.95 | 75.92
19:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 35 | 0 | 44 | 0 | 50 | 4 | 4 | 48 | 0 | 160 | 0 | 350 | 0 | 17 | 0 | 0 | 0 | 0 | 105 | 17 | 14 | 0 | 460 | 1 | 0 | 0 | 0 | 4 | 49 | 0 | 0 | 12 | 12 | 0 | 91 | 11 | 36 | 1020 | 0 | 0 | 14 | 0 | 38 | 216 | 0 | 0 | 0 | 1224 | 0 | 21 | 0 | 230 | 290 | 240 | 51 | 16 | 203 | 27 | 2 | 91 | 0 | 0 | 19 | 0 | 132 | 0.5 | 0 | 23 | 305 | 0 | 314 | 41 | 30 | 135 | 0 | 24 | 0 | 86 | 30 | 151 | 0 | 101 | 0 | 88 | 0 | 9 | 10 | 0 | 0 | 0 | 7099.5 | 905 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 813 | 24 | 0 | 0 | 1358 | 0 | 0 | 0 | 0 | 13 | 0 | 73 | 11 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 404 | 0 | 0 | 0 | 40 | 86 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 207 | 60 | 110 | 0 | 500 | 940 | 0 | 6141 | 13240.5 | 75.9
19:30 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 35 | 0 | 87 | 0 | 95 | 15 | 17 | 17 | 0 | 160 | 0 | 390 | 0 | 17 | 0 | 0 | 0 | 0 | 142 | 17 | 14 | 0 | 380 | 0 | 0 | 20 | 0 | 1 | 50 | 0 | 0 | 12 | 12 | 0 | 94 | 22 | 36 | 1030 | 0 | 0 | 50 | 0 | 68 | 216 | 0 | 0 | 0 | 1224 | 0 | 54 | 0 | 270 | 290 | 240 | 51 | 38 | 194 | 27 | 16 | 92 | 0 | 0 | 19 | 0 | 130 | 16 | 0 | 25 | 315 | 0 | 314 | 41 | 30 | 133 | 0 | 24 | 0 | 86 | 30 | 151 | 0 | 101 | 3 | 87 | 0 | 9 | 10 | 0 | 0 | 0 | 7373 | 905 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 936 | 34 | 0 | 0 | 1459 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 345 | 0 | 0 | 0 | 40 | 110 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 262 | 60 | 110 | 0 | 500 | 1090 | 0 | 6565 | 13938 | 0
20:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 27 | 0 | 83 | 0 | 45 | 15 | 0 | 16 | 0 | 160 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 17 | 16 | 0 | 360 | 0 | 0 | 24 | 0 | 0 | 50 | 0 | 0 | 12 | 12 | 0 | 95 | 0 | 36 | 1060 | 0 | 0 | 50 | 0 | 66 | 217 | 0 | 0 | 0 | 1224 | 0 | 50 | 0 | 270 | 290 | 240 | 51 | 39 | 193 | 32 | 17 | 92 | 0 | 0 | 19 | 0 | 134 | 0 | 0 | 0 | 305 | 0 | 314 | 41 | 30 | 136 | 0 | 24 | 0 | 85 | 30 | 151 | 0 | 101 | 10 | 88 | 0 | 9 | 10 | 0 | 0 | 0 | 7254 | 906 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1070 | 36 | 0 | 0 | 1454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 340 | 0 | 0 | 0 | 40 | 115 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 60 | 110 | 0 | 500 | 1120 | 0 | 6660 | 13914 | 75.88
21:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 15.5 | 0 | 105 | 0 | 15 | 15 | 0 | 15 | 0 | 160 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 17 | 21 | 0 | 485 | 0 | 0 | 26 | 0 | 0 | 50 | 0 | 0 | 12 | 12 | 0 | 95 | 0 | 36 | 1080 | 0 | 0 | 19 | 0 | 34 | 216 | 0 | 0 | 0 | 1224 | 0 | 50 | 0 | 270 | 290 | 240 | 51 | 30 | 208 | 32 | 16 | 92 | 0 | 0 | 19 | 0 | 134 | 0 | 0 | 0 | 310 | 0 | 314 | 41 | 30 | 140 | 0 | 24 | 0 | 86 | 30 | 151 | 0 | 101 | 17 | 88 | 0 | 28 | 10 | 0 | 0 | 0 | 7415.5 | 906 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1212 | 52 | 0 | 0 | 1457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 404 | 0 | 0 | 0 | 40 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 60 | 110 | 0 | 530 | 1232 | 0 | 7034 | 14449.5 | 75.86
22:00 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 16.6 | 12 | 110 | 0 | 95 | 25 | 0 | 49 | 0 | 160 | 0 | 525 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 17 | 21 | 0 | 390 | 0 | 0 | 25 | 0 | 0 | 50 | 0 | 0 | 12 | 12 | 0 | 97 | 0 | 42 | 1080 | 0 | 0 | 19 | 0 | 53 | 218 | 0 | 0 | 0 | 1224 | 0 | 62 | 0 | 215 | 290 | 240 | 51 | 10 | 207 | 33 | 33 | 92 | 0 | 0 | 19 | 0 | 142 | 0 | 0 | 0 | 310 | 0 | 314 | 41 | 30 | 148 | 0 | 24 | 0 | 86 | 30 | 151 | 0 | 101 | 17 | 78 | 0 | 28 | 10 | 0 | 0 | 0 | 7492.6 | 905 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1216 | 74 | 0 | 0 | 1444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 390 | 0 | 0 | 0 | 40 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 60 | 110 | 0 | 530 | 1244 | 0 | 7044 | 14536.6 | 75.84
23:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 0 | 0 | 15.6 | 17 | 132 | 0 | 95 | 55 | 0 | 53 | 0 | 160 | 0 | 545 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 400 | 0 | 0 | 42 | 0 | 0 | 50 | 0 | 0 | 12 | 12 | 0 | 100 | 0 | 40 | 1090 | 0 | 0 | 19 | 0 | 66 | 219 | 0 | 0 | 0 | 1224 | 0 | 80 | 0 | 215 | 290 | 240 | 51 | 10 | 215 | 30 | 49 | 93 | 0 | 0 | 19 | 0 | 136 | 0 | 0 | 0 | 305 | 0 | 320 | 41 | 30 | 135 | 0 | 24 | 0 | 86 | 28 | 151 | 0 | 101 | 17 | 77 | 0 | 28 | 10 | 0 | 0 | 0 | 7661.6 | 906 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1212 | 85 | 0 | 0 | 1452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 140 | 0 | 368 | 0 | 0 | 0 | 40 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 60 | 110 | 0 | 500 | 1244 | 0 | 7008 | 14669.6 | 75.82
Total KWH | 0 | 1092480 | 215520 | 0 | 0 | 0 | 0 | 0 | 8244000 | 0 | 1723020 | 187560 | 140400 | 1010160 | 207840 | 849578 | 262633 | 75795 | 434880 | 0 | 4035000 | 720611 | 7456818 | 0 | 44820 | 0 | 0 | 0 | 125309 | 3118800 | 469200 | 429120 | 0 | 9830909.09 | 312382 | 67745 | 243840 | 0 | 48960 | 352111 | 253776 | 54585 | 159360 | 384000 | 25007 | 2312982 | 596327 | 784800 | 23527272.73 | 0 | 0 | 527520 | 0 | 928363 | 4980716 | 0 | 0 | 0 | 25854543 | 123390 | 759418 | 0 | 5664500 | 7378100 | 5880000 | 1246976 | 295200 | 4958000 | 622584 | 215040 | 2098296 | 399840 | 0 | 433580 | 55860 | 3161280 | 65102 | 301927 | 236112 | 7520000 | 0 | 7947000 | 968000 | 708720 | 3374100 | 52300 | 529704 | 0 | 2012160 | 703296 | 3517500 | 0 | 2431880 | 820800 | 1350000 | 115956 | 907200 | 224640 | 12750 | 263810 | 61680 | 169505443.82 | 21840000 | 4996512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258480 | 24480000 | 525120 | 0 | 0 | 31922841 | 0 | 0 | 0 | 86784 | 184896 | 0 | 76352 | 9401 | 0 | 280056 | 656016 | 27713 | 0 | 285304 | 0 | 0 | 4131282 | 0 | 3638491 | 0 | 9066181 | 0 | 24900 | 0 | 933382 | 891671 | 177824 | 1075430 | 0 | 0 | 0 | 44200.32 | 1003680 | 1948 | 118368 | 5869000 | 1636000 | 2788890 | 0 | 12320000 | 24898909.09 | 106800 | 154356431.41 | 323861875.23

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 05-06-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12461.11 | MW | 09:00 Hr. | Energy Generated |  |  | 323.8619 |  | MKWHr.
| Day Peak Demand |  |  | 12671.11 | MW | 09:00 Hr. | Energy Unserverd |  |  | 3.708 |  | MKWHr.
| Evening Peak Generation |  |  | 14449.5 | MW | 21:00 Hr. | Energy Demand |  |  | 327.5699 |  | MKWHr.
| Evening Peak Demand |  |  | 14730.5 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33.5 |  | °C
| Minimum Generation of the Day |  |  | 11765.1 | MW | 17:00 Hr. | Total Gas Supplied |  |  | 897.07 |  | MMCFD
| Maximum Generation of the Day |  |  | 15282.89 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.9426 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.9087 | 0 | 7.6405 | 0 | 0 | 0.12531 | 0 | 0 | 40.6745 | Gas | 123.4458 | Gas | 433733467.0553
| Chattogram Zone |  |  | 5.7655 | 49.3818 | 3.88 | 0 | 2.313 | 0.1484 | 0 | 0.04896 | 61.5377 | Coal | 117.8831 | Coal | 773624002.0684
| Cumilla Zone |  |  | 28.5772 | 0 | 1.7314 | 0 | 0 | 0.30193 | 3.1613 | 0 | 33.7718 | HFO | 19.4941 | HFO | 329437339.42
| Mymensingh Zone |  |  | 0.22464 | 0 | 3.1397 | 0 | 0 | 0.39252 | 0 | 0 | 3.7568 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 29.7124 | 0 | 0 | 0 | 0 | 0.0523 | 0 | 0 | 29.7647 | Hydro | 2.313 | Hydro | 231298.2
| Khulna Zone |  |  | 4.9965 | 24.48 | 0.52512 | 0 | 0 | 0.25848 | 21.84 | 0 | 52.1001 | Solar | 3.7529 | Solar | 58896381.4364
| Barishal Zone |  |  | 4.4249 | 43.0879 | 0.22517 | 0 | 0 | 0.001948 | 0 | 0 | 47.7399 | Import | 56.9241 | Import | 327933659.64
| Rajshahi Zone |  |  | 16.836 | 0 | 0.38515 | 0 | 0 | 1.2463 | 31.9228 | 0 | 50.3902 | Wind | 0.04896 | Wind | 720201.6
| Rangpur Zone |  |  | 0 | 0.93338 | 1.9671 | 0 | 0 | 1.2257 | 0 | 0 | 4.1262
| Total |  |  | 123.4458 | 117.8831 | 19.4941 | 0 | 2.313 | 3.7529 | 56.9241 | 0.04896 | 323.8619
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 433733467.0553 |  | Hydro | 231298.2
|  |  |  | Coal | 773624002.0684 |  | Solar | 58896381.4364
|  |  |  | HFO | 329437339.42 |  | Import | 327933659.64
|  |  |  | HSD | 0 |  | Wind | 720201.6
[5 empty] | Total: | 192,45,76,349 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.84 | Peak Hr Flow | 906.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 8146909.09 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.9228 | Peak Hr Flow | 1457.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1824 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.1613 | Peak Hr Flow | 134.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2126 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 56.9241 | Peak Hr Flow | 2497.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 12 |  | 4435
|  |  |  | Chattogram |  | 10 |  | 1496
|  |  |  | Cumilla |  | 0 |  | 1439
|  |  |  | Mymensingh |  | 247 |  | 1321
|  |  |  | Sylhet |  | 0 |  | 622
|  |  |  | Khulna |  | 0 |  | 1881
|  |  |  | Barishal |  | 0 |  | 486
|  |  |  | Rajshahi |  | 0 |  | 1590
|  |  |  | Rangpur |  | 0 |  | 1038
|  |  |  | Total |  | 269 |  | 14308
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:29 | 13:18 | Madaripur 132/33kV S/S T3-426T HT Forced S/D Due to Differential relay trip due to
restricted earth fault
| 08:29 |  | Meghnaghat CCPP(Summit)-2 GT Synchronized with remarks:- 00:14 hrs. on 05.06.2026 GT Sync
| 09:00 |  | Day Peak Generation is 12457 MW.
| 09:17 | 10:30 | Aminbazar 400/230/132kV S/S Bus-1 (400kV) Project Work S/D Due to 400kV Rupur bay jumper
connection
| 09:24 | 13:11 | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-1 Scheduled S/D from Rangpur 132/33kV end
Due to Temperature Rises
|  | 09:26 | Bhulta 132/33kV S/S GT1 HT is restored.
| 10:03 | 11:22 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) LT Scheduled S/D
| 10:04 | 11:22 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) HT Scheduled S/D
|  | 10:07 | Bhulta-Narsingdi 132 kV Ckt-1 is restored.
|  | 10:16 | Tangail 132/33kV S/S RPCL-1 is restored.
|  | 10:17 | Tangail 132/33kV S/S RPCL-2 is restored.
| 10:27 |  | Korerhat 400/230/132kV S/S 400kV BUS-2 Project Work S/D Due to Due to project work
|  | 10:32 | Mymensingh RPCL-Tangail 132kV Ckt-2 is restored.
|  | 10:32 | Mymensingh RPCL-Tangail 132kV Ckt-1 is restored.
|  | 10:45 | Jhenaidah 132/33kV S/S Transformer T-1 HT is restored.
|  | 10:46 | Jhenaidah 132/33kV S/S Transformer T-1 LT is restored.
| 10:52 | 12:50 | Bhulta-Haripur 132 kV Ckt-1 Scheduled S/D from Bhulta 132/33kV end Due to For changing
DS(203) finger and maintenance riser point(B Phase)
| 11:38 | 12:16 | Maniknagar 132/33kV S/S Kazla Ckt -2 Scheduled S/D Due to Dc supply replacement work with
new charger /distribution panel for main and backup protection relay.. Work by DPDC.
| 12:01 | 14:15 | Aminbazar 400/230/132kV S/S Bus-2 (400kV) Project Work S/D Due to IDRNPP Prihect
| 12:20 | 13:09 | Maniknagar 132/33kV S/S Kazla Ckt -1 Scheduled S/D Due to 132 kV Kazla Ckt -2 Scheduled
S/D due to Dc supply replacement work with new charger /distribution panel for main and
backup protection relay.. Work by DPDC..
|  | 12:30 | Shahjadpur 132/33kV S/S T-2(415T) HT is restored.
|  | 12:30 | Shahjadpur 132/33kV S/S T-2(415T) LT is restored.
| 12:30 |  | Barishal 132/33kV S/S Bus B Scheduled S/D Due to 132kv patuakhali &T3 Bay extention work
|  | 12:35 | Barishal 132/33kV S/S Bus A is restored.
| 12:53 |  | Bhulta-Narsingdi 132 kV Ckt-1 Scheduled S/D from Bhulta 132/33kV end Due to This line
using Only for backup time so it’s must be shutdown always from bhulta 132KV end.
|  | 13:00 | Bagerhat-Bhandaria 132 kV Ckt-1 is restored.
| 13:24 | 14:21 | Feni 132/33kV S/S T-1(405T) LT Tripped showing O/C,E/F relays Due to Heavy rain. | [7 empty] | 34.0MW load
interrup.
| 14:52 | 15:07 | Madaripur 132/33kV S/S T1-405T LT Tripped showing Frequency and earth fault relays Due to | [7 empty] | 32.0MW load
|  |  | Earth fault,under frequency takerhat 1 feeder | [7 empty] | interrup.
| 14:52 | 15:11 | Madaripur 132/33kV S/S T2-415T LT Tripped showing Frequency,earth fault relays Due to | [7 empty] | 32.0MW load
|  |  | Earth fault,under frequency takerhat 1 feeder | [7 empty] | interrup.
|  | 18:05 | Savar 132/33kV S/S T-3 HT is restored.
|  | 18:10 | Savar 132/33kV S/S T-3 LT is restored.
| 18:44 | 20:41 | Bhulta 132/33kV S/S GT1 HT Scheduled S/D Due to For Redhot GT-01 HT side (R phase) | [7 empty] | 54.0MW load
|  |  | bushing and shutdown taken by Deepok Kumar Sutradhar(AE), Bhulta 132 KV Grid substation | [7 empty] | interrup.
| 20:37 | 23:03 | Siddhirganj 132/33kV S/S T-1 HT Forced S/D Due to Red Hot 33 kV ACB Breaker Y-Phase Pole
| 20:37 | 23:06 | Siddhirganj 132/33kV S/S T-1 LT Forced S/D Due to Red Hot 33 kV ACB Breaker Y-Phase Pole
| 21:00 |  | Evening peak generation 14449 MW
| 22:55 | 23:54 | Chowmuhani 230/132/33kV S/S TR1-415T LT Forced S/D Due to 132/33 kV, TR-01 X-former S/D | [7 empty] | 40.0MW load
|  |  | for 33kV BUS Loop Red-hot Maintenance | [7 empty] | interrup.
| 22:55 | 23:54 | Chowmuhani 230/132/33kV S/S TR1-415T HT Forced S/D Due to 33kV BUS Loop Redhot | [7 empty] | 50.0MW load
interrup.
| 06:00 |  | Minimum generation 12674 MW
| 06:58 | 07:14 | Sonargaon 132/33kV S/S Tr-1 LT Tripped showing Trip Relay(MVAJM) relays Due to pbs 33kv | [7 empty] | 30.0MW load
|  |  | side Everest Feeder trip due to isolator jumper blast | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 05-06-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Under Maintenance
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 330 | 8244000 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 160 | 4035000 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 720611 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 262633 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 15.5 | 187560 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 207840 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 75795 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 44820 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 469200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 429120 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 215520 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 15 | 849578 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 105 | 1010160 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 1092480 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 15 | 434880 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 125309 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 140400 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 485 | 9830909.09 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 455 | 7456818 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 1723020 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3118800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 1809.5 | 40674453.09
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 123390 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 527520 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 95 | 2312982 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 216 | 4980716 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 928363 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 253776 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 352111 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 159360 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 36 | 784800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 26 | 243840 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 25007 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 67745 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 54585 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 596327 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 384000 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 312382 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 25854543 | AGC
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 48960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1080 | 23527272.73 | AGC
Chattogram Area Total |  |  |  |  | 4898.863 | 2804 | 61537679.73
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 208 | 4958000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 290 | 7378100 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 240 | 5880000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 270 | 5664500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 32 | 622584 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 30 | 295200 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1246976 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 759418 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 236112 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 92 | 2098296 | ST Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 399840 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 134 | 3161280 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 65102 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 433580 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 55860 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 16 | 215040 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 301927 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1432 | 33771815
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 115956 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 10 | 224640 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12750 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 28 | 907200 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 88 | 1350000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 263810 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 61680 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 820800 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 143 | 3756836
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 52300 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 968000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 708720 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 140 | 3374100 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 151 | 3517500 | ps availability is less
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 703296 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2012160 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2431880 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 529704 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7520000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 314 | 7947000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1227 | 29764660
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 906 | 21840000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 210 | 4996512 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 52 | 525120 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | FGMO
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 258480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1212 | 24480000 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2380 | 52100112
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 530 | 12320000 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 118368 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 60 | 1636000 | STG Under Maintenance
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1232 | 24898909.09 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 110 | 2788890 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 106800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5869000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1948 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2239 | 47739915.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 280056 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 9401 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 160 | 4131282 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 140 | 3638491 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 404 | 9066181 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 27713 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 76352 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 184896 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 86784 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24900 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1457 | 31922841 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 285304 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 656016 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2161 | 50390217
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 40 | 933382 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 1075430 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 44200.32 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 891671 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 177824 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1003680 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 254 | 4126187.32
Eastern Grid Total |  |  |  |  | 17438.042 | 7415.5 | 169505443.82
Western Grid Total |  |  |  |  | 11852.195 | 7034 | 154356431.41
National Grid Total |  |  |  |  | 29290.237 | 14449.5 | 323861875.23
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 05-06-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9043.71 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4995 | MW
i) Dhaka area |  |  | 4422.51 |  | MW | i) Khulna area |  |  |  | 1881 | MW
ii) Chattogram area |  |  | 1486.2 |  | MW | ii) Barishal area |  |  |  | 485.6 | MW
iii) Cumilla area |  |  | 1439 |  | MW | iii) Rajshahi area |  |  |  | 1590.4 | MW
iv) Mymensingh area |  |  | 1074 |  | MW | iv) Rangpur area |  |  |  | 1038 | MW
v) Sylhet area |  |  | 622 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14038.71 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 78 | 00:00 | 133 | Natore | 165 | 22:00
2 | AKSML | 118 | 01:00 | 68 | Hathazari | 96 | 00:00 | 134 | Nawabganj | 67.4 | 00:00
3 | Aftabnagar | 44 | 00:00 | 69 | Hatirjheel | 35 | 12:00 | 135 | Netrakona | 154 | 19:00
4 | Agargaon | 111 | 01:00 | 70 | Ishurdi | 82 | 13:00 | 136 | New | 58.6 | 00:00
5 | Agrabad | 62 | 00:00 | 71 | Jaldhaka | 87 | 19:30 | 137 | Niamatpur | 88 | 22:00
6 | Amnura | 35 | 23:00 | 72 | Jamalpur | 106 | 14:00 | 138 | Noapara | 50 | 02:00
7 | Ashuganj | 86 | 01:00 | 73 | Jashore | 147 | 19:30 | 139 | PHP | 13 | 19:30
8 | BSRM | 197 | 17:00 | 74 | Jhenaidah | 114 | 22:00 | 140 | Pabna | 96 | 22:00
9 | Bagerhat | 106 | 00:00 | 75 | Joydebpur | 110 | 09:00 | 141 | Palashbari | 132 | 00:00
10 | Bajitpur | 96 | 03:00 | 76 | Joypurhat | 68 | 22:00 | 142 | Panchagarh | 59 | 20:00
11 | Bakerganj | 18 | 00:00 | 77 | Juldah | 15 | 00:00 | 143 | Patiya | 12.3 | 22:00
12 | Bakulia | 98 | 00:00 | 78 | KSRM | 11 | 09:00 | 144 | Patuakhali | 83 | 00:00
13 | Banani | 36.4 | 11:00 | 79 | Kabirpur | 151 | 00:00 | 145 | Payra | 44 | 00:00
14 | Bangabhaban | 5 | 11:00 | 80 | Kachua | 112 | 00:00 | 146 | Postogola | 60 | 00:00
15 | Barapukuria | 69 | 23:00 | 81 | Kaliganj | 25 | 22:00 | 147 | Pubail | 27 | 10:00
16 | Barguna | 26 | 00:00 | 82 | Kallyanpur | 111 | 00:00 | 148 | Purbachal | 32 | 00:00
17 | Barishal | 114 | 00:00 | 83 | Kalurghat | 32 | 13:00 | 149 | Purbasadipur | 150 | 23:00
18 | Barishal-230 | 126 | 00:00 | 84 | Kamrangirchar | 56 | 00:00 | 150 | Rahanpur | 47 | 23:00
19 | Baroaulia | 66 | 00:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 18 | 01:00
20 | Baroirhat | 77 | 00:00 | 86 | Kasba | 41 | 00:00 | 152 | Rajbari | 93 | 00:00
21 | Bashundhara | 179 | 00:00 | 87 | Kazla | 99 | 01:00 | 153 | Rajendrapur | 115 | 21:00
22 | BashundharaCement | 8 | 00:00 | 88 | Keranigonj | 81 | 00:00 | 154 | Rajshahi | 126 | 23:00
23 | Beanibazar | 82 | 23:00 | 89 | Khagrachori | 34 | 10:00 | 155 | Rajshahi-230 | 98 | 23:00
24 | Benapole | 81 | 01:00 | 90 | Khulna | 66 | 01:00 | 156 | Ramganj | 126 | 02:00
25 | Bhaluka | 149 | 00:00 | 91 | Khulshi | 184 | 00:00 | 157 | Rampur | 50 | 00:00
26 | Bhandaria | 66 | 00:00 | 92 | Kishoreganj | 148 | 00:00 | 158 | Rangamati | 18 | 12:00
27 | Bhangura | 40 | 13:00 | 93 | Kodda | 219 | 00:00 | 159 | Rangpur | 137 | 00:00
28 | Bheramara(GK) | 73 | 22:00 | 94 | Kulaura | 59 | 19:00 | 160 | Ruppur | 4.4 | 11:00
29 | Bhulta | 173 | 00:00 | 95 | Kurigram | 70 | 19:30 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 78 | 23:00 | 96 | Kushtia | 167 | 00:00 | 162 | Saidpur | 100 | 21:00
31 | Bogura | 170 | 23:00 | 97 | Laksam | 36 | 00:00 | 163 | Santhia | 40 | 00:00
32 | Borhanuddin | 105 | 02:00 | 98 | Lakshmipur | 45 | 02:00 | 164 | Satkhira | 160 | 01:00
33 | Brahmanbaria | 145 | 00:00 | 99 | Lalbag | 43 | 00:00 | 165 | Satmasjid | 102 | 01:00
34 | Cantonment | 122 | 00:00 | 100 | Lalmonirhat | 68 | 21:00 | 166 | Savar | 168 | 02:00
35 | Chandina | 45 | 01:00 | 101 | MI_Cement | 8.6 | 00:00 | 167 | SevenRings | 11.69 | 11:00
36 | Chandpur | 100 | 01:00 | 102 | Madanganj | 39 | 21:00 | 168 | ShahCement | 20 | 03:00
37 | Chandraghona | 36 | 00:00 | 103 | Madaripur | 144 | 00:00 | 169 | Shahjadpur | 80 | 00:00
38 | Chapai | 82 | 21:00 | 104 | Madartek | 88 | 00:00 | 170 | Shahjibazar | 126 | 01:00
39 | Charsaidpur | 37 | 03:00 | 105 | Madunaghat | 58 | 00:00 | 171 | Shahmirpur | 61 | 05:00
40 | Chauddagram | 90 | 00:00 | 106 | Magura | 71 | 00:00 | 172 | Shariatpur | 116 | 00:00
41 | Chhatak | 44 | 22:00 | 107 | Mahasthangarh | 90 | 23:00 | 173 | Sherpur | 130 | 18:00
42 | Chowmuhani | 179 | 00:00 | 108 | Maijdee | 49 | 01:00 | 174 | Shikalbaha | 31 | 01:00
43 | Chuadanga | 127 | 22:00 | 109 | Manikganj | 130 | 22:00 | 175 | Shitalakhya | 69.5 | 00:00
44 | Coxsbazar | 153 | 22:00 | 110 | Maniknagar | 73 | 00:00 | 176 | Sholosohor | 45 | 00:00
45 | Cumilla(N) | 129 | 03:00 | 111 | Matarbari | 59 | 19:30 | 177 | Shomvuganj | 18 | 15:00
46 | Cumilla(S) | 165 | 00:00 | 112 | Matuail | 50 | 00:00 | 178 | Shyampur | 120 | 12:00
47 | Daganbhuiyan | 42 | 01:00 | 113 | Metrorail_Motijheel | 18 | 19:00 | 179 | Siddhirganj | 103 | 00:00
48 | Daudkandi | 150 | 00:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 112 | 00:00
49 | DhakaUniversity | 38 | 00:00 | 115 | Millgate | 66 | 09:00 | 181 | Sonargaon | 117 | 01:00
50 | Dhamrai | 92 | 22:00 | 116 | Mirpur | 141 | 00:00 | 182 | Sreemongol | 78 | 23:00
51 | Dhanmondi | 90.8 | 12:00 | 117 | Mirsorai | 48 | 11:00 | 183 | Sreepur | 97 | 01:00
52 | Dohazari | 117 | 19:00 | 118 | Mirzapur | 45 | 12:00 | 184 | Srinagar | 55.8 | 00:00
53 | Faridpur | 195 | 01:00 | 119 | Mithapukur | 68 | 01:00 | 185 | Sunamganj | 61 | 22:00
54 | Fatullah | 60 | 00:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 72 | 23:00
55 | Fenchuganj | 48 | 00:00 | 121 | Mogbazar | 78.4 | 00:00 | 187 | Sylhet-132 | 97 | 23:00
56 | Feni | 119 | 00:00 | 122 | Mongla | 38 | 03:00 | 188 | TK | 26 | 00:00
57 | GPH | 74 | 00:00 | 123 | Motijheel | 42 | 00:00 | 189 | Tangail | 176 | 07:00
58 | Ghatail | 79 | 14:00 | 124 | Muktagacha | 35 | 19:00 | 190 | Taraganj | 26 | 20:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 110 | 04:00 | 191 | Tasnim | 12 | 03:00
60 | Ghorashal-230 | 109 | 02:00 | 126 | Muradnagar | 56 | 00:00 | 192 | Thakurgaon | 120 | 20:00
61 | Goalpara | 36 | 00:00 | 127 | Mymensingh | 180 | 00:00 | 193 | Tongi | 136 | 00:00
62 | Gollamari | 120 | 00:00 | 128 | Nabinagar | 82 | 12:00 | 194 | Ullahpara | 38 | 01:00
63 | Gopalganj | 123 | 00:00 | 129 | Naogaon | 149 | 23:00 | 195 | Ullon | 60 | 01:00
64 | Gulshan | 94 | 11:00 | 130 | Narail | 61 | 21:00 | 196 | Uttara | 84 | 11:00
65 | Halishahar | 83 | 19:30 | 131 | Narinda | 50 | 00:00 | 197 | UttaraNew | 55 | 01:00
66 | HaripurSBU | 90 | 15:00 | 132 | Narshingdi | 152 | 00:00 | 198 | Zigatola | 90 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 05-06-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15282.89 | 360 |  | 15659.09
1:00 | 15224.44 | 192 |  | 15425.08
2:00 | 15176.44 | 182 |  | 15366.63
3:00 | 14691.22 | 162 |  | 14860.51
4:00 | 14244.09 | 157 |  | 14408.16
5:00 | 13895.82 | 152 |  | 14054.66
6:00 | 13225.46 | 217 |  | 13452.23
7:00 | 12743.65 | 185 |  | 12936.65
8:00 | 12531.77 | 204 |  | 12744.95
9:00 | 12461.11 | 201 |  | 12671.11
10:00 | 12361.4 | 193 |  | 12563.4
11:00 | 12239.01 | 90 |  | 12333.01
12:00 | 12340.06 | 168 |  | 12516.06
13:00 | 12671.5 | 92 |  | 12767.5
14:00 | 12196.14 | 65 |  | 12264.14
15:00 | 12055.95 | 135 |  | 12196.95
16:00 | 11929.52 | 0 |  | 11929.52
17:00 | 11765.1 | 0 |  | 11765.1
18:00 | 11710.95 | 20 |  | 11731.95
19:00 | 13240.5 | 119 |  | 13364.5
19:30 | 13938 | 205 |  | 14152.23
20:00 | 13914 | 203 |  | 14126.14
21:00 | 14449.5 | 269 |  | 14730.5
22:00 | 14536.6 | 180 |  | 14724.6
23:00 | 14669.6 | 162 |  | 14838.6
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 05-06-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 122 | 16 | 390 | 128 | 1614 | 210 | Ishurdi-Ghorashal Ckt-1 | Export | 3286909.09
1:00 | 116 | 22 | 368 | 136 | 1530 | 220
2:00 | 126 | 20 | 410 | 150 | 1446 | 228 |  | Import | 0
3:00 | 131 | 20 | 420 | 144 | 1446 | 216
4:00 | 130 | 19 | 420 | 134 | 1488 | 218 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 141 | 24 | 440 | 130 | 1518 | 256
6:00 | 141 | 20 | 410 | 114 | 1372 | 236 |  | Import | 0
7:00 | 131 | 18 | 390 | 116 | 1200 | 258
8:00 | 155 | 24 | 420 | 116 | 1210 | 192 | Sirajganj-Sreepur Ckt-1 | Export | 2426000
9:00 | 177 | 26 | 460 | 118 | 1302 | 330
10:00 | 191 | 29 | 490 | 124 | 1310 | 366 |  | Import | 0
11:00 | 190 | 28 | 480 | 116 | 1378 | 384
12:00 | 168 | 20 | 430 | 108 | 1268 | 392 | Sirajganj-Sreepur Ckt-2 | Export | 2434000
13:00 | 124 | 6 | 340 | 120 | 1120 | 262
14:00 | 118 | 0 | 364 | 124 | 1000 | 236 |  | Import | 0
15:00 | 143 | 9 | 380 | 96 | 1194 | 294
16:00 | 140 | 8 | 410 | 108 | 1130 | 280 | Gopalganj-Aminbazar Ckt-1 | Export | 0
17:00 | 148 | 11 | 430 | 110 | 1196 | 300
18:00 | 145 | 10 | 420 | 104 | 1166 | 270 |  | Import | 0
18:30 | 134 | 7 | 400 | 108 | 1150 | 246
19:00 | 134 | 8 | 420 | 140 | 1238 | 236 | Gopalganj-Aminbazar Ckt-2 | Export | 0
19:30 | 102 | -10 | 320 | 110 | 1190 | 134
20:00 | 95 | -5 | 320 | 120 | 1326 | 130 |  | Import | 0
21:00 | 108 | 2 | 366 | 150 | 1350 | 184
22:00 | 103 | 4 | 340 | 124 | 1336 | 138 |  | Total Export | 8146909.09
23:00 | 105 | 4 | 360 | 130 | 1334 | 122 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 05-06-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7813 | 7469.89 | 15282.89 | DAILY GENERATION CURVE
00:30 | 7850 | 7403.665 | 15253.665
01:00 | 7887 | 7337.44 | 15224.44 | 05-06-2026
01:30 | 7924 | 7276.44 | 15200.44
02:00 | 7961 | 7215.44 | 15176.44
02:30 | 7808 | 7125.83 | 14933.83
03:00 | 7655 | 7036.22 | 14691.22
03:30 | 7496.5 | 6971.155 | 14467.655
04:00 | 7338 | 6906.09 | 14244.09
04:30 | 7192 | 6877.955 | 14069.955
05:00 | 7046 | 6849.82 | 13895.82
05:30 | 6898.75 | 6661.89 | 13560.64
06:00 | 6751.5 | 6473.96 | 13225.46
06:30 | 6648.995 | 6335.56 | 12984.555
07:00 | 6546.49 | 6197.16 | 12743.65
07:30 | 6536.215 | 6101.495 | 12637.71
08:00 | 6525.94 | 6005.83 | 12531.77
08:30 | 6519.65 | 5976.79 | 12496.44
09:00 | 6513.36 | 5947.75 | 12461.11
09:30 | 6481.365 | 5929.89 | 12411.255
10:00 | 6449.37 | 5912.03 | 12361.4
10:30 | 6448.955 | 5851.25 | 12300.205
11:00 | 6448.54 | 5790.47 | 12239.01
11:30 | 6494.365 | 5795.17 | 12289.535
12:00 | 6540.19 | 5799.87 | 12340.06
12:30 | 6684.84 | 5820.94 | 12505.78
13:00 | 6829.49 | 5842.01 | 12671.5
13:30 | 6630.24 | 5803.58 | 12433.82
14:00 | 6430.99 | 5765.15 | 12196.14
14:30 | 6404.845 | 5721.2 | 12126.045
15:00 | 6378.7 | 5677.25 | 12055.95
15:30 | 6343.01 | 5649.725 | 11992.735
16:00 | 6307.32 | 5622.2 | 11929.52
16:30 | 6263.07 | 5584.24 | 11847.31
17:00 | 6218.82 | 5546.28 | 11765.1
17:30 | 6213.07 | 5524.955 | 11738.025
18:00 | 6207.32 | 5503.63 | 11710.95
18:30 | 6653.41 | 5822.315 | 12475.725
19:00 | 7099.5 | 6141 | 13240.5
19:30 | 7373 | 6565 | 13938
20:00 | 7254 | 6660 | 13914
20:30 | 7334.75 | 6847 | 14181.75 |  | Executive Engineer
21:00 | 7415.5 | 7034 | 14449.5 |  | Network Operation Division
21:30 | 7454.05 | 7039 | 14493.05
22:00 | 7492.6 | 7044 | 14536.6
22:30 | 7577.1 | 7026 | 14603.1
23:00 | 7661.6 | 7008 | 14669.6

## En-Curve
QF-LDC-12
Date | 05-06-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3348 | 2013 | 903 | 0 | 166 | 1460.89 | 100 | 5868 | 0 | 424 | 998 | 0 | 0 | 2 | 360 | DAILY ENERGY CURVE
00:30 | 3322 | 1980.5 | 866.5 | 0 | 161 | 1459.165 | 100 | 5824 | 0 | 440.5 | 1099 | 0 | 0 | 1 | 276 | 05-06-2026
01:00 | 3296 | 1948 | 830 | 0 | 156 | 1457.44 | 100 | 5780 | 0 | 457 | 1200 | 0 | 0 | 0 | 192
01:30 | 3306.5 | 1914 | 868 | 0 | 151 | 1453.44 | 100 | 5713 | 0 | 436.5 | 1257 | 0 | 0 | 1 | 187 | Energy Generated | 323.8619 |  | MKWHr
02:00 | 3317 | 1880 | 906 | 0 | 146 | 1449.44 | 100 | 5646 | 0 | 416 | 1314 | 0 | 0 | 2 | 182 | Energy not Served | 3.708 |  | MKWHr
02:30 | 3310.5 | 1868 | 906 | 0 | 151 | 1446.33 | 100 | 5613 | 0 | 375 | 1163 | 0 | 0 | 1 | 172 | Total Energy Requirement | 327.5699 |  | MKWHr
03:00 | 3304 | 1856 | 906 | 0 | 156 | 1443.22 | 100 | 5580 | 0 | 334 | 1012 | 0 | 0 | 0 | 162
03:30 | 3289 | 1824 | 905.5 | 0 | 156 | 1448.155 | 98.5 | 5589 | 0 | 319 | 838.5 | 0 | 0 | 0 | 159.5
04:00 | 3274 | 1792 | 905 | 0 | 156 | 1453.09 | 97 | 5598 | 0 | 304 | 665 | 0 | 0 | 0 | 157
04:30 | 3245.5 | 1761 | 905.5 | 0 | 155 | 1449.955 | 95.5 | 5596.5 | 0 | 296 | 565 | 0 | 0 | 0 | 154.5
05:00 | 3217 | 1730 | 906 | 0 | 154 | 1446.82 | 94 | 5595 | 0 | 288 | 465 | 0 | 0 | 0 | 152
05:30 | 3206.5 | 1658 | 905.5 | 0 | 145 | 1376.94 | 93.5 | 5422.5 | 20.7 | 285 | 446.5 | 0 | 0 | 0.5 | 184.5
06:00 | 3196 | 1586 | 905 | 0 | 136 | 1307.06 | 93 | 5250 | 41.4 | 282 | 428 | 0 | 0 | 1 | 217
06:30 | 3240 | 1625 | 905 | 0 | 135 | 1284.02 | 94.5 | 5033.5 | 95.035 | 238 | 334 | 0 | 0 | 0.5 | 201
07:00 | 3284 | 1664 | 905 | 0 | 134 | 1260.98 | 96 | 4817 | 148.67 | 194 | 240 | 0 | 0 | 0 | 185
07:30 | 3288.5 | 1714 | 905 | 0 | 135 | 1264.205 | 98 | 4642.5 | 209.505 | 170.5 | 210.5 | 0 | 0 | 0 | 194.5
08:00 | 3293 | 1764 | 905 | 0 | 136 | 1267.43 | 100 | 4468 | 270.34 | 147 | 181 | 0 | 0 | 0 | 204
08:30 | 3288 | 1754 | 905.5 | 0 | 133 | 1266.215 | 100 | 4429.5 | 324.725 | 134.5 | 161 | 0 | 0 | 0 | 202.5
09:00 | 3283 | 1744 | 906 | 0 | 130 | 1265 | 100 | 4391 | 379.11 | 122 | 141 | 0 | 0 | 0 | 201
09:30 | 3287 | 1700.5 | 905.5 | 0 | 132 | 1277 | 100 | 4318 | 421.755 | 122 | 147.5 | 0 | 0 | 0 | 197
10:00 | 3291 | 1657 | 905 | 0 | 134 | 1289 | 100 | 4245 | 464.4 | 122 | 154 | 0 | 0 | 0 | 193
10:30 | 3300.5 | 1685.5 | 905 | 0 | 128 | 1279 | 100 | 4129 | 492.705 | 122 | 158.5 | 0 | 0 | 0 | 141.5
11:00 | 3310 | 1714 | 905 | 0 | 122 | 1269 | 100 | 4013 | 521.01 | 122 | 163 | 0 | 0 | 0 | 90
11:30 | 3319.5 | 1710.5 | 905.5 | 0 | 118 | 1274.5 | 100 | 3990.5 | 534.785 | 153.5 | 181.25 | 0 | 0 | 1.5 | 129
12:00 | 3329 | 1707 | 906 | 0 | 114 | 1280 | 100 | 3968 | 548.56 | 185 | 199.5 | 0 | 0 | 3 | 168
12:30 | 3308.5 | 1750.5 | 905.5 | 0 | 112 | 1277 | 100 | 4165 | 474.78 | 195.5 | 210.5 | 0 | 0 | 6.5 | 130
13:00 | 3288 | 1794 | 905 | 0 | 110 | 1274 | 100 | 4362 | 401 | 206 | 221.5 | 0 | 0 | 10 | 92
13:30 | 3261.5 | 1733.5 | 905 | 0 | 116 | 1220.5 | 100 | 4294 | 383.82 | 199 | 204.5 | 0 | 0 | 16 | 78.5
14:00 | 3235 | 1673 | 905 | 0 | 122 | 1167 | 100 | 4226 | 366.64 | 192 | 187.5 | 0 | 0 | 22 | 65
14:30 | 3231.5 | 1728 | 905 | 0 | 114 | 1172 | 100 | 4209 | 308.295 | 166 | 175.75 | 0 | 0 | 16.5 | 100
15:00 | 3228 | 1783 | 905 | 0 | 106 | 1177 | 100 | 4192 | 249.95 | 140 | 164 | 0 | 0 | 11 | 135
15:30 | 3242.5 | 1787.5 | 905 | 0 | 108 | 1168.5 | 97.5 | 4166 | 240.735 | 113 | 155 | 0 | 0 | 9 | 67.5
16:00 | 3257 | 1792 | 905 | 0 | 110 | 1160 | 95 | 4140 | 231.52 | 86 | 146 | 0 | 0 | 7 | 0
16:30 | 3271 | 1804 | 905 | 0 | 106 | 1172.5 | 94.5 | 4076.5 | 183.31 | 86 | 144.5 | 0 | 0 | 4 | 0
17:00 | 3285 | 1816 | 905 | 0 | 102 | 1185 | 94 | 4013 | 135.1 | 86 | 143 | 0 | 0 | 1 | 0
17:30 | 3281.5 | 1809 | 905 | 0 | 105 | 1169.5 | 92 | 4050.5 | 88.025 | 86 | 151 | 0 | 0 | 0.5 | 10
18:00 | 3278 | 1802 | 905 | 0 | 108 | 1154 | 90 | 4088 | 40.95 | 86 | 159 | 0 | 0 | 0 | 20
18:30 | 3285 | 1792.5 | 905 | 0 | 120 | 1256 | 90.5 | 4416 | 20.475 | 209.5 | 378.75 | 0 | 0 | 2 | 69.5
19:00 | 3292 | 1783 | 905 | 0 | 132 | 1358 | 91 | 4744 | 0 | 333 | 598.5 | 0 | 0 | 4 | 119
19:30 | 3230 | 1773 | 905 | 0 | 130 | 1459 | 94 | 5082 | 0 | 364 | 900 | 0 | 0 | 1 | 205
20:00 | 3249 | 1748 | 906 | 0 | 134 | 1454 | 95 | 5321 | 0 | 234 | 773 | 0 | 0 | 0 | 203
20:30 | 3289 | 1846 | 906 | 0 | 134 | 1455.5 | 95 | 5473 | 0 | 230 | 753.25 | 0 | 0 | 0 | 236
21:00 | 3329 | 1944 | 906 | 0 | 134 | 1457 | 95 | 5625 | 0 | 226 | 733.5 | 0 | 0 | 0 | 269
21:30 | 3279.5 | 1928.5 | 905.5 | 0 | 138 | 1450.5 | 96 | 5633 | 0 | 228 | 834.05 | 0 | 0 | 0 | 224.5
22:00 | 3230 | 1913 | 905 | 0 | 142 | 1444 | 97 | 5641 | 0 | 230 | 934.6 | 0 | 0 | 0 | 180
22:30 | 3217 | 1918.5 | 905.5 | 0 | 139 | 1448 | 98.5 | 5629 | 0 | 246 | 1001.6 | 0 | 0 | 0 | 171
23:00 | 3204 | 1924 | 906 | 0 | 136 | 1452 | 100 | 5617 | 0 | 262 | 1068.6 | 0 | 0 | 0 | 162
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 05-06-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 394 | 18:00 | 374 | 00:00 | Madunaghat | 399 | 15:00 | 389 | 00:00
Amtali | 414 | 11:00 | 403 | 00:00 | Meghnaghat | 399 | 18:30 | 380 | 00:00
Ashuganj | 401 | 18:30 | 380 | 00:00 | Payra | 416 | 14:00 | 406 | 00:00
Bhulta | 403 | 18:30 | 382 | 00:00 | Rahanpur | 404 | 18:30 | 388 | 21:00
Bibiana | 405 | 18:30 | 391 | 00:00 | Rampal | 403 | 18:30 | 383 | 00:00
BIPTC | 405 | 06:00 | 393 | 00:00
Bogura | 389 | 18:30 | 370 | 00:00
Gopalganj | 401 | 18:30 | 380 | 00:00
Kaliakoir | 391 | 14:00 | 371 | 00:00
Korerhat | 402 | 14:00 | 387 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 18:30 | 219 | 00:00 | Jhenaidah | 228 | 08:00 | 209 | 00:00
AKSML | 232 | 14:00 | 224 | 04:00 | Kachua | 229 | 12:00 | 216 | 00:00
Aminbazar | 233 | 18:00 | 220 | 00:00 | Kaliakoir | 229 | 14:00 | 217 | 00:00
Ashuganj | 234 | 18:00 | 218 | 00:00 | Keranigonj | 230 | 18:30 | 218 | 00:00
Ashuganj-400 | 234 | 18:00 | 218 | 00:00 | Khulna(S) | 232 | 11:00 | 210 | 00:00
Baghabari | 234 | 17:00 | 224 | 00:00 | Korerhat | 229 | 14:00 | 218 | 00:00
Barapukuria | 222 | 06:00 | 206 | 13:00 | Madunaghat | 232 | 18:00 | 227 | 04:00
Barapukuria-230 | 222 | 06:00 | 206 | 13:00 | Madunaghat-400 | 232 | 14:00 | 228 | 00:00
Barishal | 234 | 11:00 | 220 | 00:00 | Maniknagar | 228 | 18:00 | 216 | 00:00
Bheramara | 234 | 06:00 | 221 | 21:00 | Meghnaghat | 236 | 17:00 | 224 | 00:00
Bhulta | 231 | 18:00 | 218 | 00:00 | Meghnaghat-400 | 231 | 18:30 | 220 | 00:00
Bibiana | 236 | 07:00 | 227 | 00:00 | Mirsorai | 233 | 14:00 | 224 | 00:00
BIPTC | 237 | 08:00 | 220 | 21:00 | Naogaon | 218 | 18:30 | 203 | 00:00
Bogura | 240 | 18:30 | 228 | 00:00 | Purbasadipur | 224 | 06:00 | 203 | 13:00
Bogura-400 | 239 | 17:00 | 228 | 00:00 | Rajshahi | 233 | 18:30 | 219 | 00:00
Borhanuddin | 237 | 12:00 | 226 | 00:00 | Rampal | 229 | 18:30 | 214 | 00:00
BSRM | 229 | 14:00 | 219 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 229 | 13:00 | 214 | 00:00 | Rampura | 230 | 18:00 | 217 | 00:00
Cumilla(N) | 228 | 14:00 | 217 | 00:00 | Shikalbaha | 229 | 01:00 | 226 | 05:00
Faridpur | 233 | 12:00 | 216 | 00:00 | Shyampur | 229 | 14:00 | 218 | 00:00
Fenchuganj | 238 | 08:00 | 228 | 00:00 | Siddhirganj | 231 | 17:00 | 217 | 00:00
Feni | 228 | 14:00 | 215 | 00:00 | Sirajgonj | 239 | 06:00 | 232 | 00:00
Ghorashal | 230 | 07:00 | 225 | 00:00 | Sreepur | 226 | 08:00 | 218 | 01:00
Ghorashal-230 | 220 | 18:30 | 208 | 00:00 | Tongi | 220 | 15:00 | 210 | 00:00
Gopalganj | 233 | 12:00 | 219 | 00:00
GPH | 231 | 14:00 | 223 | 05:00
Haripur | 230 | 18:30 | 218 | 00:00
Hasnabad | 230 | 17:00 | 216 | 00:00
Hathazari | 230 | 14:00 | 224 | 05:00
Ishurdi | 236 | 06:00 | 223 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 17:00 | 126 | 00:00 | Madunaghat | 134 | 14:00 | 131 | 00:00
Agargaon | 136 | 18:30 | 128 | 00:00 | Magura | 132 | 08:00 | 120 | 00:00
Agrabad | 132 | 18:30 | 128 | 04:00 | Mahasthangarh | 133 | 18:00 | 125 | 00:00
AKS | 130 | 07:00 | 127 | 01:00 | Maijdee | 129 | 13:00 | 119 | 04:00
Aminbazar | 133 | 18:00 | 126 | 00:00 | Manikganj | 133 | 14:00 | 124 | 10:00
Amnura | 135 | 08:00 | 125 | 00:00 | Maniknagar | 135 | 18:30 | 126 | 00:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 118 | 16:00 | 105 | 04:00
Ashuganj-230 | 138 | 08:00 | 130 | 00:00 | Matuail | 134.5 | 18:00 | 127 | 00:00
Bagerhat | 134 | 10:00 | 113 | 00:00 | Metrorail_Motijheel | 135 | 18:30 | 126 | 00:00
Bajitpur | 128 | 15:00 | 120 | 21:00 | Metrorail_Uttara | 134 | 18:30 | 124 | 01:00
Bakerganj | 136 | 11:00 | 124 | 00:00 | Millgate | 134 | 18:00 | 128 | 12:00
Bakulia | 132 | 18:30 | 128 | 05:00 | Mirpur | 132 | 18:30 | 125 | 00:00
Banani | 133 | 16:00 | 126 | 01:00 | Mirzapur | 133 | 14:00 | 123 | 02:00
Bangabhaban | 134 | 17:00 | 126 | 00:00 | Mithapukur | 131 | 06:00 | 122 | 13:00
Barapukuria | 135 | 06:00 | 123 | 13:00 | MI_Cement | 133 | 18:30 | 124 | 00:00
Barguna | 136 | 11:00 | 123 | 00:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 135 | 11:00 | 124 | 00:00 | Mogbazar | 135 | 14:00 | 126 | 00:00
Barishal-230 | 135 | 11:00 | 124 | 00:00 | Mongla | 135 | 09:00 | 113 | 00:00
Baroaulia | 131 | 14:00 | 128 | 01:00 | Motijheel | 134 | 17:00 | 126 | 00:00
Baroirhat | 132 | 14:00 | 125 | 00:00 | Muktagacha | 127 | 16:00 | 114 | 03:00
Bashundhara | 135 | 18:30 | 125 | 00:00 | Munshiganj | 134 | 12:00 | 124 | 05:00
BashundharaCement | 135 | 12:00 | 128 | 00:00 | Muradnagar | 130 | 12:00 | 121 | 00:00
Beanibazar | 132 | 07:00 | 121 | 00:00 | Mymensingh | 128 | 18:30 | 111 | 19:00
Benapole | 131 | 10:00 | 115 | 00:00 | Nabinagar | 133 | 14:00 | 124 | 12:00
Bhaluka | 130 | 05:00 | 122 | 00:00 | Naogaon | 136 | 18:30 | 122 | 00:00
Bhandaria | 133 | 12:00 | 114 | 00:00 | Narail | 134 | 18:30 | 120 | 21:00
Bhangura | 134 | 07:00 | 127 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
Bheramara | 137 | 08:00 | 130 | 21:00 | Narshingdi | 133 | 12:00 | 120 | 00:00
Bheramara(GK) | 137 | 18:00 | 130 | 20:00 | Natore | 134 | 17:00 | 125 | 00:00
Bhulta | 131 | 14:00 | 120 | 00:00 | Nawabganj | 135 | 14:00 | 126 | 00:00
Bog-Sherpur | 136 | 18:30 | 128 | 00:00 | Netrakona | 121 | 00:00 | 109 | 19:00
Bogura | 137 | 18:30 | 129 | 18:00 | New | 136 | 18:30 | 128 | 00:00
Bogura-230 | 138 | 18:30 | 130 | 00:00 | Niamatpur | 132 | 06:00 | 122 | 00:00
Brahmanbaria | 133 | 08:00 | 124 | 00:00 | Noapara | 135 | 09:00 | 120 | 00:00
Cantonment | 135 | 14:00 | 127 | 00:00 | Pabna | 135 | 18:30 | 128 | 00:00
Chandina | 132 | 14:00 | 124 | 00:00 | Palashbari | 129 | 18:30 | 120 | 00:00
Chandpur | 130 | 13:00 | 120 | 04:00 | Panchagarh | 138 | 06:00 | 125 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 134 | 14:00 | 131 | 04:00 | Patiya | 129 | 14:00 | 125 | 05:00
Chapai | 133 | 18:00 | 127 | 22:00 | Patuakhali | 135 | 11:00 | 124 | 00:00
Charsaidpur | 135 | 12:00 | 125 | 00:00 | Payra | 136 | 10:00 | 130 | 00:00
Chauddagram | 131 | 14:00 | 123 | 00:00 | PHP | 132 | 14:00 | 124 | 00:00
Chhatak | 130 | 06:00 | 118 | 00:00 | Postogola | 134 | 18:00 | 126 | 00:00
Chowmuhani | 128 | 12:00 | 120 | 02:00 | Pubail | 130 | 18:00 | 124 | 00:00
Chuadanga | 133 | 10:00 | 116 | 23:00 | Purbachal | 134 | 18:00 | 125 | 00:00
Coxsbazar | 120 | 16:00 | 109 | 00:00 | Purbasadipur | 134 | 06:00 | 120 | 00:00
Cumilla(N) | 135 | 13:00 | 125 | 00:00 | Rahanpur | 135 | 18:00 | 129 | 00:00
Cumilla(S) | 131 | 12:00 | 123 | 14:00 | Rahanpur-400 | 135 | 07:00 | 129 | 00:00
Daganbhuiyan | 131 | 14:00 | 123 | 00:00 | Rahim | 134 | 12:00 | 127 | 00:00
Daudkandi | 131 | 12:00 | 119 | 00:00 | Rajbari | 131 | 12:00 | 119 | 00:00
DhakaUniversity | 133 | 14:00 | 126 | 00:00 | Rajendrapur | 131 | 06:00 | 123 | 21:00
Dhamrai | 136 | 14:00 | 126 | 21:00 | Rajshahi | 132 | 06:00 | 123 | 21:00
Dhanmondi | 135.5 | 18:30 | 127 | 00:00 | Rajshahi-230 | 133 | 06:00 | 125 | 00:00
Dohazari | 125 | 10:00 | 121 | 05:00 | Ramganj | 129 | 13:00 | 117 | 03:00
Faridpur | 134 | 12:00 | 124 | 00:00 | Rampur | 131 | 14:00 | 128 | 21:00
Fatullah | 135 | 12:00 | 124 | 00:00 | Rampura | 134 | 18:00 | 126 | 00:00
Fenchuganj | 137 | 08:00 | 129 | 00:00 | Rangamati | 134 | 14:00 | 130 | 00:00
Feni | 132 | 14:00 | 125 | 00:00 | Rangpur | 129 | 06:00 | 122 | 00:00
Feni-230 | 131 | 14:00 | 123 | 00:00 | Ruppur | 137 | 08:00 | 130 | 21:00
Ghatail | 128 | 16:00 | 115 | 02:00 | Saidpur | 133 | 06:00 | 121 | 13:00
Ghorashal | 130 | 06:00 | 127 | 13:00 | Santhia | 135 | 18:00 | 128 | 00:00
Goalpara | 137 | 18:30 | 121 | 00:00 | Satkhira | 134 | 08:00 | 112 | 00:00
Gollamari | 137 | 10:00 | 122 | 01:00 | Satmasjid | 136 | 18:30 | 128 | 00:00
Gopalganj | 134 | 11:00 | 121 | 00:00 | Savar | 131 | 19:00 | 125 | 00:00
Gopalganj-400 | 135 | 10:00 | 126 | 00:00 | SevenRings | 132 | 18:30 | 125 | 00:00
Gulshan | 134 | 18:30 | 125 | 00:00 | ShahCement | 135 | 12:00 | 125 | 00:00
Halishahar | 132 | 18:30 | 128 | 05:00 | Shahjadpur | 138 | 04:00 | 131 | 00:00
Haripur | 135 | 18:30 | 127 | 00:00 | Shahjibazar | 135 | 08:00 | 125 | 01:00
HaripurSBU | 135 | 19:00 | 127 | 00:00 | Shahmirpur | 132 | 16:00 | 128 | 00:00
Hasnabad | 133 | 14:00 | 126 | 00:00 | Shariatpur | 135 | 12:00 | 121 | 00:00
Hathazari | 134 | 14:00 | 131 | 00:00 | Sherpur | 124 | 18:30 | 110 | 02:00
Hatirjheel | 134 | 18:00 | 126 | 00:00 | Shikalbaha | 120 | 00:00 | 118 | 09:00
Ishurdi | 138 | 07:00 | 130 | 21:00 | Shikalbaha-230 | 132 | 02:00 | 129 | 05:00
Jaldhaka | 132 | 06:00 | 119 | 13:00 | Shitalakhya | 133 | 18:30 | 124 | 00:00
Jamalpur | 129 | 18:30 | 113 | 12:00 | Sholosohor | 133 | 14:00 | 129 | 04:00
Jashore | 133 | 09:00 | 118 | 00:00 | Shomvuganj | 123 | 15:00 | 112 | 18:30
Jhenaidah | 134 | 08:00 | 124 | 00:00 | Shyampur | 133 | 12:00 | 121 | 00:00
Jhenaidah-230 | 135 | 08:00 | 123 | 00:00 | Shyampur-230 | 131 | 18:00 | 123 | 00:00
Joydebpur | 129 | 17:00 | 123 | 00:00 | Siddhirganj | 135 | 18:00 | 127 | 00:00
Joypurhat | 134 | 18:30 | 121 | 00:00 | Sirajganj | 132 | 15:00 | 125 | 00:00
Juldah | 131 | 16:00 | 128 | 21:00 | Sonargaon | 133 | 11:00 | 124 | 00:00
Kabirpur | 135 | 14:00 | 124 | 00:00 | Sreemongol | 135 | 07:00 | 124 | 00:00
Kachua | 131 | 12:00 | 122 | 04:00 | Sreepur | 133 | 06:00 | 127 | 02:00
Kaliakoir | 137 | 14:00 | 129 | 00:00 | Srinagar | 136 | 14:00 | 127 | 00:00
Kaliganj | 134 | 08:00 | 122 | 00:00 | SSM | 136 | 18:30 | 132 | 00:00
Kallyanpur | 132 | 18:00 | 126 | 00:00 | Sunamganj | 129 | 06:00 | 116 | 00:00
Kalurghat | 133 | 13:00 | 130 | 05:00 | Sylhet | 132 | 07:00 | 124 | 00:00
Kamrangirchar | 135 | 14:00 | 125 | 00:00 | Sylhet-132 | 131 | 07:00 | 124 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Tangail | 130 | 15:00 | 118 | 04:00
Kasba | 130 | 12:00 | 120 | 00:00 | Taraganj | 133 | 05:00 | 123 | 21:00
Kazla | 134 | 18:00 | 126 | 00:00 | Tasnim | 134 | 18:00 | 124 | 00:00
Keranigonj | 136 | 14:00 | 128 | 00:00 | Thakurgaon | 136 | 06:00 | 123 | 13:00
Khagrachori | 134 | 14:00 | 129 | 00:00 | TK | 134 | 18:30 | 130 | 21:00
Khulna | 136 | 08:00 | 122 | 00:00 | Tongi | 136 | 17:00 | 129 | 00:00
Khulna(S) | 138 | 09:00 | 123 | 00:00 | Ullahpara | 134 | 15:00 | 126 | 00:00
Khulshi | 130 | 14:00 | 127 | 02:00 | Ullon | 133 | 16:00 | 127 | 01:00
Kishoreganj | 126 | 06:00 | 117 | 21:00 | Uttara | 133 | 18:30 | 125 | 00:00
Kodda | 133 | 14:00 | 127 | 00:00 | UttaraNew | 134 | 18:30 | 124 | 01:00
Korerhat | 134 | 14:00 | 130 | 00:00 | Zigatola | 136 | 18:30 | 128 | 00:00
KSRM | 132 | 00:00 | 129 | 05:00
Kulaura | 135 | 07:00 | 128 | 00:00
Kurigram | 129 | 06:00 | 118 | 13:00
Kushtia | 135 | 08:00 | 127 | 00:00
Laksam | 130 | 13:00 | 120 | 00:00
Lakshmipur | 129 | 13:00 | 119 | 00:00
Lalbag | 136 | 14:00 | 127 | 00:00
Lalmonirhat | 130 | 06:00 | 119 | 19:30
Madanganj | 135 | 12:00 | 126 | 00:00
Madaripur | 135 | 16:00 | 124 | 00:00
Madartek | 133 | 18:00 | 125 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division